## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.311 | 311 (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.311E | 311E (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.321 | 321 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.321E | 321E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.331 | 331 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.331E | 331E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.341 | 341 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.341E | 341E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.211E | 211E (非取樣點) | SC | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.211 | 211 (非取樣點) | SC | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A11_DS | 4A11_DS (非取樣點) | FEEDER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A11_ES | 4A11_ES (非取樣點) | FEEDER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A12_DS | 4A12_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A12_ES | 4A12_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A13_DS | 4A13_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A13_ES | 4A13_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A14_DS | 4A14_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A14_ES | 4A14_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A15_DS | 4A15_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A15_ES | 4A15_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.101E | 101E (非取樣點) | TIE | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.102E | 102E (非取樣點) | TIE | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.101 | 101 (非取樣點) | TIE | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.102 | 102 (非取樣點) | TIE | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.221E | 221E (非取樣點) | SC | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.221 | 221 (非取樣點) | SC | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A16_DS | 4A16_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A16_ES | 4A16_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A17_DS | 4A17_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A17_ES | 4A17_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A18_DS | 4A18_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A18_ES | 4A18_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A19_DS | 4A19_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A19_ES | 4A19_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A20_DS | 4A20_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A20_ES | 4A20_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.231E | 231E (非取樣點) | SC | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | DS1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.231 | 231 (非取樣點) | SC | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A21_DS | 4A21_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A21_ES | 4A21_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A22_DS | 4A22_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A22_ES | 4A22_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A23_DS | 4A23_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A23_ES | 4A23_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A24_DS | 4A24_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A24_ES | 4A24_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A25_DS | 4A25_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A25_ES | 4A25_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.241E | 241E (非取樣點) | SC | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | DS1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.241 | 241 (非取樣點) | SC | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A26_DS | 4A26_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A26_ES | 4A26_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A27_DS | 4A27_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A27_ES | 4A27_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A28_DS | 4A28_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A28_ES | 4A28_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A29_DS | 4A29_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A29_ES | 4A29_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A30_DS | 4A30_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A30_ES | 4A30_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.201E | 201E (非取樣點) | TIE | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.202E | 202E (非取樣點) | TIE | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.201 | 201 (非取樣點) | TIE | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.202 | 202 (非取樣點) | TIE | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D20_A1 | [8 empty] | 和順DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D20_A1 | [8 empty] | 和順DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | 道爺和順新化線 1510 MW |  |  | MW_-560_560(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1510_MW | 道爺和順新化線 MW | LINE161 | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 道爺和順新化線 1510 MVAR |  |  | MVAR_-560_560(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1510_MVAR | 道爺和順新化線 MVAR | LINE161 | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 安南和順線 1520 MW |  |  | MW_-560_560(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1520_MW | 安南和順線 MW | LINE161 | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 安南和順線 1520 MVAR |  |  | MVAR_-560_560(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1520_MVAR | 安南和順線 MVAR | LINE161 | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 和順公學二路 1540 MW |  |  | MW_-560_560(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1540_MW | 和順公學二路 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 和順公學二路 1540 MVAR |  |  | MVAR_-560_560(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1540_MVAR | 和順公學二路 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 變電所 DC V ( P-G) |  |  | kV_-150_150(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 變電所 DC V ( N-G) |  |  | kV_-150_150(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0024 |  |  | 1-98 |  |  | 161KV #1 BUS PT KV1 |  |  | kV_-210_210(-2000_2000) | aaa | B2/D20_A1 | [8 empty] | 和順DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0025 |  |  | 1-99 |  |  | 161KV #2 BUS PT KV1 |  |  | kV_-210_210(-2000_2000) | aab | B2/D20_A1 | [8 empty] | 和順DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 161KV 1500 TIE A1 |  |  | A_-2000_2000(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | DTR #1 油溫 ℃ |  |  | OIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | DTR #1 A 線溫 ℃ |  |  | COIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | DTR #1 B 線溫 ℃ |  |  | COIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | DTR #1 A TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | DTR #1 B TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | DTR #2 油溫 ℃ |  |  | OIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | DTR #2 A 線溫 ℃ |  |  | COIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | DTR #2 B 線溫 ℃ |  |  | COIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | DTR #2 A TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | DTR #2 B TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | DTR #3 油溫 ℃ |  |  | OIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | DTR #3 線溫 ℃ |  |  | COIL_-120_120(-2000_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | DTR #3 TAP |  |  | TAP_-8.5_8.5(0_2000) |  | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | M1A(310) MW |  |  | MW_-54_54(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | M1A(310) MVAR |  |  | MVAR_-36_36(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | M1A(310) A1 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | M1A(310) A2 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | M1A(310) A3 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0051 |  |  | 1-B3 |  |  | 11KV #1ABUS |  |  | kV_-9_9(-2000_2000) | aaa | B3/D20_A1 | [8 empty] | 和順DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 和11線(4A11) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和11線KVAR | 11KV和11線 KVAR | FEEDER | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 和11線(4A11) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和11線A1 | 11KV和11線 R相AMP | FEEDER | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 和11線(4A11) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和11線A2 | 11KV和11線 S相AMP | FEEDER | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 和11線(4A11) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和11線A3 | 11KV和11線 T相AMP | FEEDER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 和11線(4A11) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和11線A0 | 11KV和11線 N相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 和12線(4A12) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和12線KVAR | 11KV和12線 KVAR | FEEDER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 和12線(4A12) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和12線A1 | 11KV和12線 R相AMP | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 和12線(4A12) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和12線A2 | 11KV和12線 S相AMP | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 和12線(4A12) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和12線A3 | 11KV和12線 T相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 和12線(4A12) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和12線A0 | 11KV和12線 N相AMP | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 和13線(4A13) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和13線KVAR | 11KV和13線 KVAR | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 和13線(4A13) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和13線A1 | 11KV和13線 R相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 和13線(4A13) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和13線A2 | 11KV和13線 S相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 和13線(4A13) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和13線A3 | 11KV和13線 T相AMP | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 和13線(4A13) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和13線A0 | 11KV和13線 N相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 和14線(4A14) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和14線KVAR | 11KV和14線 KVAR | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 和14線(4A14) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和14線A1 | 11KV和14線 R相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 和14線(4A14) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和14線A2 | 11KV和14線 S相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 和14線(4A14) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和14線A3 | 11KV和14線 T相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 和14線(4A14) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和14線A0 | 11KV和14線 N相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 和15線(4A15) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和15線KVAR | 11KV和15線 KVAR | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 和15線(4A15) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和15線A1 | 11KV和15線 R相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 和15線(4A15) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和15線A2 | 11KV和15線 S相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 和15線(4A15) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和15線A3 | 11KV和15線 T相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 和15線(4A15) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和15線A0 | 11KV和15線 N相AMP | FEEDER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | TIE1A(100) A1 |  |  | A_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | TIE1A(100) A2 |  |  | A_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | TIE1A(100) A3 |  |  | A_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | M1B(320) MW |  |  | MW_-54_54(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | M1B(320) MVAR |  |  | MVAR_-36_36(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | M1B(320) A1 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | M1B(320) A2 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | M1B(320) A3 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0087 |  |  | 1-D7 |  |  | 11KV #1BBUS |  |  | kV_-9_9(-2000_2000) | baa | B3/D20_A1 | [8 empty] | 和順DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 和16線(4A16) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和16線KVAR | 11KV和16線 KVAR | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 和16線(4A16) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和16線A1 | 11KV和16線 R相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 和16線(4A16) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和16線A2 | 11KV和16線 S相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 和16線(4A16) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和16線A3 | 11KV和16線 T相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 和16線(4A16) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和16線A0 | 11KV和16線 N相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 和17線(4A17) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和17線KVAR | 11KV和17線 KVAR | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 和17線(4A17) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和17線A1 | 11KV和17線 R相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 和17線(4A17) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和17線A2 | 11KV和17線 S相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 和17線(4A17) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和17線A3 | 11KV和17線 T相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 和17線(4A17) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和17線A0 | 11KV和17線 N相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 和18線(4A18) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和18線KVAR | 11KV和18線 KVAR | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 和18線(4A18) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和18線A1 | 11KV和18線 R相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 和18線(4A18) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和18線A2 | 11KV和18線 S相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 和18線(4A18) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和18線A3 | 11KV和18線 T相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 和18線(4A18) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和18線A0 | 11KV和18線 N相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 和19線(4A19) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和19線KVAR | 11KV和19線 KVAR | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 和19線(4A19) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和19線A1 | 11KV和19線 R相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 和19線(4A19) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和19線A2 | 11KV和19線 S相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 和19線(4A19) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和19線A3 | 11KV和19線 T相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 和19線(4A19) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和19線A0 | 11KV和19線 N相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 和20線(4A20) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和20線KVAR | 11KV和20線 KVAR | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 和20線(4A20) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和20線A1 | 11KV和20線 R相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 和20線(4A20) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和20線A2 | 11KV和20線 S相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 和20線(4A20) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和20線A3 | 11KV和20線 T相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 和20線(4A20) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和20線A0 | 11KV和20線 N相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | M2A(330) MW |  |  | MW_-54_54(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | M2A(330) MVAR |  |  | MVAR_-36_36(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | M2A(330) A1 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | M2A(330) A2 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | M2A(330) A3 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0118 |  |  | 1-F6 |  |  | 11KV #2ABUS |  |  | kV_-9_9(-2000_2000) | aba | B3/D20_A1 | [8 empty] | 和順DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 和21線(4A21) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和21線KVAR | 11KV和21線 KVAR | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 和21線(4A21) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和21線A1 | 11KV和21線 R相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 和21線(4A21) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和21線A2 | 11KV和21線 S相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 和21線(4A21) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和21線A3 | 11KV和21線 T相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 和21線(4A21) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和21線A0 | 11KV和21線 N相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 和22線(4A22) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和22線KVAR | 11KV和22線 KVAR | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 和22線(4A22) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和22線A1 | 11KV和22線 R相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 和22線(4A22) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和22線A2 | 11KV和22線 S相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 和22線(4A22) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和22線A3 | 11KV和22線 T相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 和22線(4A22) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和22線A0 | 11KV和22線 N相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 和23線(4A23) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和23線KVAR | 11KV和23線 KVAR | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 和23線(4A23) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和23線A1 | 11KV和23線 R相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 和23線(4A23) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和23線A2 | 11KV和23線 S相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 和23線(4A23) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和23線A3 | 11KV和23線 T相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 和23線(4A23) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和23線A0 | 11KV和23線 N相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 和24線(4A24) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和24線KVAR | 11KV和24線 KVAR | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 和24線(4A24) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和24線A1 | 11KV和24線 R相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 和24線(4A24) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和24線A2 | 11KV和24線 S相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 和24線(4A24) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和24線A3 | 11KV和24線 T相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 和24線(4A24) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和24線A0 | 11KV和24線 N相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 和25線(4A25) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和25線KVAR | 11KV和25線 KVAR | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 和25線(4A25) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和25線A1 | 11KV和25線 R相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 和25線(4A25) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和25線A2 | 11KV和25線 S相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 和25線(4A25) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和25線A3 | 11KV和25線 T相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 和25線(4A25) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和25線A0 | 11KV和25線 N相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | M2B(340) MW |  |  | MW_-54_54(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.054 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | M2B(340) MVAR |  |  | MVAR_-36_36(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.036 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | M2B(340) A1 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | M2B(340) A2 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | M2B(340) A3 |  |  | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0151 |  |  | 2-97 |  |  | 11KV #2BBUS |  |  | kV_-9_9(-2000_2000) | bba | B3/D20_A1 | [8 empty] | 和順DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 和26線(4A26) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和26線KVAR | 11KV和26線 KVAR | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 和26線(4A26) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和26線A1 | 11KV和26線 R相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 和26線(4A26) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和26線A2 | 11KV和26線 S相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 和26線(4A26) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和26線A3 | 11KV和26線 T相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 和26線(4A26) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和26線A0 | 11KV和26線 N相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 和27線(4A27) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和27線KVAR | 11KV和27線 KVAR | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 和27線(4A27) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和27線A1 | 11KV和27線 R相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 和27線(4A27) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和27線A2 | 11KV和27線 S相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 和27線(4A27) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和27線A3 | 11KV和27線 T相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 和27線(4A27) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和27線A0 | 11KV和27線 N相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 和28線(4A28) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和28線KVAR | 11KV和28線 KVAR | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 和28線(4A28) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和28線A1 | 11KV和28線 R相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 和28線(4A28) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和28線A2 | 11KV和28線 S相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 和28線(4A28) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和28線A3 | 11KV和28線 T相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 和28線(4A28) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和28線A0 | 11KV和28線 N相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 和29線(4A29) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和29線KVAR | 11KV和29線 KVAR | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 和29線(4A29) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和29線A1 | 11KV和29線 R相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 和29線(4A29) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和29線A2 | 11KV和29線 S相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 和29線(4A29) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和29線A3 | 11KV和29線 T相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 和29線(4A29) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和29線A0 | 11KV和29線 N相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 和30線(4A30) KVAR |  |  | KVAR_-10800_10800(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和30線KVAR | 11KV和30線 KVAR | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 和30線(4A30) A1 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和30線A1 | 11KV和30線 R相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 和30線(4A30) A2 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和30線A2 | 11KV和30線 S相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 和30線(4A30) A3 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和30線A3 | 11KV和30線 T相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 和30線(4A30) A0 |  |  | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和30線A0 | 11KV和30線 N相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | TIE2B(200) A1 |  |  | A_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | TIE2B(200) A2 |  |  | A_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | TIE2B(200) A3 |  |  | A_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 道爺和順新化線 1510 LPT KV |  |  | kV_-210_210(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1510LPD_KV | 道爺和順新化線(1510) LPD KV | LINE161 | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 安南和順線 1520 LPT KV |  |  | kV_-210_210(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1520LPD_KV | 安南和順線(1520) LPD KV | LINE161 | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 和順公學二路 1540 LPT KV |  |  | kV_-210_210(-2000_2000) |  | B2/D20_A1 | [8 empty] | 和順DS.1540LPD_KV | 和順公學二路(1540) LPD KV | LINE161 | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 3-C0 |  |  | 10% TEST |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 3-C1 |  |  | 90% TEST |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D20TN04/T2 |  | 0000 |  |  | 1-00-00 |  |  | 道爺和順新化線 1510 CB ON/OFF |  | PPU-1 PT-1 |  | aaca | B2/D20_A1 | [8 empty] | 和順DS.1510_CB | 1510(道爺和順新化線) CB | LINE161 | [5 empty] | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 道爺和順新化線 1510 87A |  | PPU-1 PT-2 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_87A | 道爺和順新化線(1510) 87RY | LINE161 | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 道爺和順新化線 1510 (85BA) |  | PPU-1 PT-3 |  |  | B2/D20_A1 | [16 empty] | 251 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 道爺和順新化線 1510 PHA |  | PPU-1 PT-4 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_PHA | 道爺和順新化線(1510) 相間RY | LINE161 | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 道爺和順新化線 1510 GDA |  | PPU-1 PT-5 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_GDA | 道爺和順新化線(1510) 接地RY | LINE161 | [5 empty] | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D20/T2 |  | 0005 |  |  | 1-00-05 |  |  | 安南和順線 1520 CB ON/OFF |  | PPU-1 PT-6 |  | aada | B2/D20_A1 | [8 empty] | 和順DS.1520_CB | 1520(安南和順線) CB | LINE161 | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 安南和順線 1520 87A (85MA) |  | PPU-1 PT-7 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_87A | 安南和順線(1520) 87RY | LINE161 | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 安南和順線 1520 (85BA) |  | PPU-1 PT-8 |  |  | B2/D20_A1 | [16 empty] | 256 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 安南和順線 1520 PHA |  | PPU-1 PT-9 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_PHA | 安南和順線(1520) 相間RY | LINE161 | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 安南和順線 1520 GDA |  | PPU-1 PT-10 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_GDA | 安南和順線(1520) 接地RY | LINE161 | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0015 |  |  | 1-01-07 |  |  | 和順公學二路 1540 CB ON/OFF |  | PPU-1 PT-16 |  | aaha | B2/D20_A1 | [8 empty] | 和順DS.1540_CB | 1540(和順公學二路) CB | LINE161 | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 和順公學二路 1540 87A (85MA) |  | PPU-1 PT-17 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_87A | 和順公學二路(1540) 87RY | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 和順公學二路 1540 (85BA) |  | PPU-1 PT-18 |  |  | B2/D20_A1 | [16 empty] | 261 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 和順公學二路 1540 PHA |  | PPU-1 PT-19 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_PHA | 和順公學二路(1540) 相間RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 和順公學二路 1540 GDA |  | PPU-1 PT-20 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_GDA | 和順公學二路(1540) 接地RY | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | 161KV #1 BUS 87B1A |  | PPU-2 PT-3 |  |  | B2/D20_A1 | [8 empty] | 和順DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 161KV #2 BUS 87B2A |  | PPU-2 PT-4 |  |  | B2/D20_A1 | [8 empty] | 和順DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint | #BUS |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 161KV BUS 81A |  | PPU-2 PT-6 |  |  | B2/D20_A1 | [16 empty] | 266 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0054 |  |  | 1-06-06 |  |  | 161KV 1500TIE CB ON/OFF |  | PPU-2 PT-7 |  | aafz | B2/D20_A1 | [8 empty] | 和順DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 161KV 1500TIE 50A |  | PPU-2 PT-8 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 161KV RCA |  | PPU-2 PT-9 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | OSCA |  | PPU-2 PT-10 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0060 |  |  | 1-07-04 |  |  | DTR1 CB ON/OFF |  | PPU-2 PT-13 |  | aabb | ELEM/D20_A1 | [8 empty] | 和順DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | DTR1 87A |  | PPU-2 PT-14 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | DTR1 96PA |  | PPU-2 PT-15 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR(A) | #1DTR(A) |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | DTR1 A 51ZA |  | PPU-2 PT-16 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR(B) | #1DTR(B) |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | DTR1 B 51ZA |  | PPU-2 PT-17 |  |  | B1/D20_A1 | [16 empty] | 275 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | DTR1 PHA |  | PPU-2 PT-18 |  |  | B2/D20_A1 | [8 empty] | 和順DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | DTR1 GDA |  | PPU-2 PT-19 |  |  | B2/D20_A1 | [8 empty] | 和順DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0067 |  |  | 1-08-03 |  |  | M1A(310) CB ON/OFF |  | PPU-2 PT-20 |  | aaaa | ELEM/D20_A1 | [8 empty] | 和順DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | M1A(310) PHA |  | PPU-2 PT-21 |  |  | B3/D20_A1 | [8 empty] | 和順DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | M1A(310) GDA |  | PPU-2 PT-22 |  |  | B3/D20_A1 | [8 empty] | 和順DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0070 |  |  | 1-08-06 |  |  | M1B(320) CB ON/OFF |  | PPU-2 PT-23 |  | baaa | ELEM/D20_A1 | [8 empty] | 和順DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | M1B(320) PHA |  | PPU-2 PT-24 |  |  | B3/D20_A1 | [8 empty] | 和順DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | M1B(320) GDA |  | PPU-2 PT-25 |  |  | B3/D20_A1 | [8 empty] | 和順DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0074 |  |  | 1-09-02 |  |  | DTR2 CB ON/OFF |  | PPU-2 PT-27 |  | aaeb | ELEM/D20_A1 | [8 empty] | 和順DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | DTR2 87A |  | PPU-2 PT-28 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | DTR2 96A |  | PPU-2 PT-29 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR(A) | #2DTR(A) |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | DTR2 A 51ZA |  | PPU-2 PT-30 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR(B) | #2DTR(B) |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | DTR2 B 51ZA |  | PPU-2 PT-31 |  |  | B1/D20_A1 | [16 empty] | 288 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | DTR2 PHA |  | PPU-2 PT-32 |  |  | B2/D20_A1 | [8 empty] | 和順DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | DTR2 GDA |  | PPU-2 PT-33 |  |  | B2/D20_A1 | [8 empty] | 和順DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0081 |  |  | 1-0A-01 |  |  | M2A(330) CB ON/OFF |  | PPU-2 PT-34 |  | abaa | ELEM/D20_A1 | [8 empty] | 和順DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | M2A(330) PHA |  | PPU-2 PT-35 |  |  | B3/D20_A1 | [8 empty] | 和順DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | M2A(330) GDA |  | PPU-2 PT-36 |  |  | B3/D20_A1 | [8 empty] | 和順DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0084 |  |  | 1-0A-04 |  |  | M2B(340) CB ON/OFF |  | PPU-2 PT-37 |  | bbka | ELEM/D20_A1 | [8 empty] | 和順DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | M2B(340) PHA |  | PPU-2 PT-38 |  |  | B3/D20_A1 | [8 empty] | 和順DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | M2B(340) GDA |  | PPU-2 PT-39 |  |  | B3/D20_A1 | [8 empty] | 和順DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0160 |  |  | 2-00-00 |  |  | #1SC 210 CB ON/OFF |  | PPU-1 PT-1 |  | aacb | B3/D20_A1 | [8 empty] | 和順DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0161 |  |  | 2-00-01 |  |  | #1SC 210 SCA |  | PPU-1 PT-2 |  |  | B3/D20_A1 | [8 empty] | 和順DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0162 |  |  | 2-00-02 |  |  | #1SC 210 UVA |  | PPU-1 PT-3 |  |  | B3/D20_A1 | [8 empty] | 和順DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4A11/T1 |  |  | 0163 |  |  | 2-00-03 |  |  | 和11線(4A11) CB ON/OFF |  | PPU-1 PT-4 |  | aajb | B2/D20_D1 | [8 empty] | 和順DS.4A11_CB | 4A11(11KV和11線) CB | FEEDER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 2-00-04 |  |  | 和11線(4A11) PHA |  | PPU-1 PT-5 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A11_PHA | 11KV和11線(4A11) 相間RY | FEEDER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 2-00-05 |  |  | 和11線(4A11) GDA |  | PPU-1 PT-6 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A11_GDA | 11KV和11線(4A11) 接地RY | FEEDER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4A12/T1 |  |  | 0166 |  |  | 2-00-06 |  |  | 和12線(4A12) CB ON/OFF |  | PPU-1 PT-7 |  | aaib | B2/D20_D1 | [8 empty] | 和順DS.4A12_CB | 4A12(11KV和12線) CB | FEEDER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 2-00-07 |  |  | 和12線(4A12) PHA |  | PPU-1 PT-8 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A12_PHA | 11KV和12線(4A12) 相間RY | FEEDER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 2-01-00 |  |  | 和12線(4A12) GDA |  | PPU-1 PT-9 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A12_GDA | 11KV和12線(4A12) 接地RY | FEEDER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4A13/T1 |  |  | 0169 |  |  | 2-01-01 |  |  | 和13線(4A13) CB ON/OFF |  | PPU-1 PT-10 |  | aahb | B2/D20_D1 | [8 empty] | 和順DS.4A13_CB | 4A13(11KV和13線) CB | FEEDER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 2-01-02 |  |  | 和13線(4A13) PHA |  | PPU-1 PT-11 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A13_PHA | 11KV和13線(4A13) 相間RY | FEEDER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 2-01-03 |  |  | 和13線(4A13) GDA |  | PPU-1 PT-12 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A13_GDA | 11KV和13線(4A13) 接地RY | FEEDER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4A14/T1 |  |  | 0172 |  |  | 2-01-04 |  |  | 和14線(4A14) CB ON/OFF |  | PPU-1 PT-13 |  | aaeb | B2/D20_D1 | [8 empty] | 和順DS.4A14_CB | 4A14(11KV和14線) CB | FEEDER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 2-01-05 |  |  | 和14線(4A14) PHA |  | PPU-1 PT-14 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A14_PHA | 11KV和14線(4A14) 相間RY | FEEDER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 2-01-06 |  |  | 和14線(4A14) GDA |  | PPU-1 PT-15 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A14_GDA | 11KV和14線(4A14) 接地RY | FEEDER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4A15/T1 |  |  | 0175 |  |  | 2-01-07 |  |  | 和15線(4A15) CB ON/OFF |  | PPU-1 PT-16 |  | aadb | B2/D20_D1 | [8 empty] | 和順DS.4A15_CB | 4A15(11KV和15線) CB | FEEDER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 2-02-00 |  |  | 和15線(4A15) PHA |  | PPU-1 PT-17 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A15_PHA | 11KV和15線(4A15) 相間RY | FEEDER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 2-02-01 |  |  | 和15線(4A15) GDA |  | PPU-1 PT-18 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A15_GDA | 11KV和15線(4A15) 接地RY | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0178 |  |  | 2-02-02 |  |  | #1SSTR 390 CB ON/OFF |  | PPU-1 PT-19 |  | aabb | B3/D20_A1 | [8 empty] | 和順DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 2-02-03 |  |  | #1SSTR 390 PHA |  | PPU-1 PT-20 |  |  | B3/D20_A1 | [8 empty] | 和順DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 2-02-04 |  |  | #1SSTR 390 GDA |  | PPU-1 PT-21 |  |  | B3/D20_A1 | [8 empty] | 和順DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0181 |  |  | 2-02-05 |  |  | TIE1A(100) CB ON/OFF |  | PPU-1 PT-22 |  | aakb | B3/D20_A1 | [8 empty] | 和順DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 2-02-06 |  |  | TIE1A(100) PHA |  | PPU-1 PT-23 |  |  | B3/D20_A1 | [8 empty] | 和順DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 2-02-07 |  |  | TIE1A(100) GDA |  | PPU-1 PT-24 |  |  | B3/D20_A1 | [8 empty] | 和順DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0184 |  |  | 2-03-00 |  |  | #2SC 220 CB ON/OFF |  | PPU-1 PT-25 |  | babb | B3/D20_A1 | [8 empty] | 和順DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0185 |  |  | 2-03-01 |  |  | #2SC 220 SCA |  | PPU-1 PT-26 |  |  | B3/D20_A1 | [8 empty] | 和順DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0186 |  |  | 2-03-02 |  |  | #2SC 220 UVA |  | PPU-1 PT-27 |  |  | B3/D20_A1 | [8 empty] | 和順DS.220_OUVA | 11KV #2SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4A16/T1 |  |  | 0187 |  |  | 2-03-03 |  |  | 和16線(4A16) CB ON/OFF |  | PPU-1 PT-28 |  | bacb | B2/D20_D1 | [8 empty] | 和順DS.4A16_CB | 4A16(11KV和16線) CB | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 2-03-04 |  |  | 和16線(4A16) PHA |  | PPU-1 PT-29 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A16_PHA | 11KV和16線(4A16) 相間RY | FEEDER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 2-03-05 |  |  | 和16線(4A16) GDA |  | PPU-1 PT-30 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A16_GDA | 11KV和16線(4A16) 接地RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4A17/T1 |  |  | 0190 |  |  | 2-03-06 |  |  | 和17線(4A17) CB ON/OFF |  | PPU-1 PT-31 |  | badb | B2/D20_D1 | [8 empty] | 和順DS.4A17_CB | 4A17(11KV和17線) CB | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 2-03-07 |  |  | 和17線(4A17) PHA |  | PPU-1 PT-32 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A17_PHA | 11KV和17線(4A17) 相間RY | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 2-04-00 |  |  | 和17線(4A17) GDA |  | PPU-1 PT-33 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A17_GDA | 11KV和17線(4A17) 接地RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4A18/T1 |  |  | 0193 |  |  | 2-04-01 |  |  | 和18線(4A18) CB ON/OFF |  | PPU-1 PT-34 |  | baeb | B2/D20_D1 | [8 empty] | 和順DS.4A18_CB | 4A18(11KV和18線) CB | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 2-04-02 |  |  | 和18線(4A18) PHA |  | PPU-1 PT-35 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A18_PHA | 11KV和18線(4A18) 相間RY | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 2-04-03 |  |  | 和18線(4A18) GDA |  | PPU-1 PT-36 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A18_GDA | 11KV和18線(4A18) 接地RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4A19/T1 |  |  | 0196 |  |  | 2-04-04 |  |  | 和19線(4A19) CB ON/OFF |  | PPU-1 PT-37 |  | bafb | B2/D20_D1 | [8 empty] | 和順DS.4A19_CB | 4A19(11KV和19線) CB | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 2-04-05 |  |  | 和19線(4A19) PHA |  | PPU-1 PT-38 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A19_PHA | 11KV和19線(4A19) 相間RY | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 2-04-06 |  |  | 和19線(4A19) GDA |  | PPU-1 PT-39 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A19_GDA | 11KV和19線(4A19) 接地RY | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4A20/T1 |  |  | 0199 |  |  | 2-04-07 |  |  | 和20線(4A20) CB ON/OFF |  | PPU-1 PT-40 |  | baib | B2/D20_D1 | [8 empty] | 和順DS.4A20_CB | 4A20(11KV和20線) CB | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 2-05-00 |  |  | 和20線(4A20) PHA |  | PPU-1 PT-41 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A20_PHA | 11KV和20線(4A20) 相間RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 2-05-01 |  |  | 和20線(4A20) GDA |  | PPU-1 PT-42 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A20_GDA | 11KV和20線(4A20) 接地RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0204 |  |  | 2-05-04 |  |  | #3SC 230 CB ON/OFF |  | PPU-1 PT-45 |  | abib | B3/D20_A1 | [8 empty] | 和順DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 2-05-05 |  |  | #3SC 230 SCA |  | PPU-1 PT-46 |  |  | B3/D20_A1 | [8 empty] | 和順DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0206 |  |  | 2-05-06 |  |  | #3SC 230 UVA |  | PPU-1 PT-47 |  |  | B3/D20_A1 | [8 empty] | 和順DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4A21/T1 |  |  | 0207 |  |  | 2-05-07 |  |  | 和21線(4A21) CB ON/OFF |  | PPU-1 PT-48 |  | abbb | B2/D20_D1 | [8 empty] | 和順DS.4A21_CB | 4A21(11KV和21線) CB | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 2-06-00 |  |  | 和21線(4A21) PHA |  | PPU-2 PT-1 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A21_PHA | 11KV和21線(4A21) 相間RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 2-06-01 |  |  | 和21線(4A21) GDA |  | PPU-2 PT-2 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A21_GDA | 11KV和21線(4A21) 接地RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4A22/T1 |  |  | 0210 |  |  | 2-06-02 |  |  | 和22線(4A22) CB ON/OFF |  | PPU-2 PT-3 |  | abcb | B2/D20_D1 | [8 empty] | 和順DS.4A22_CB | 4A22(11KV和22線) CB | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 2-06-03 |  |  | 和22線(4A22) PHA |  | PPU-2 PT-4 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A22_PHA | 11KV和22線(4A22) 相間RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 2-06-04 |  |  | 和22線(4A22) GDA |  | PPU-2 PT-5 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A22_GDA | 11KV和22線(4A22) 接地RY | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4A23/T1 |  |  | 0213 |  |  | 2-06-05 |  |  | 和23線(4A23) CB ON/OFF |  | PPU-2 PT-6 |  | abfb | B2/D20_D1 | [8 empty] | 和順DS.4A23_CB | 4A23(11KV和23線) CB | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 2-06-06 |  |  | 和23線(4A23) PHA |  | PPU-2 PT-7 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A23_PHA | 11KV和23線(4A23) 相間RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 2-06-07 |  |  | 和23線(4A23) GDA |  | PPU-2 PT-8 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A23_GDA | 11KV和23線(4A23) 接地RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4A24/T1 |  |  | 0216 |  |  | 2-07-00 |  |  | 和24線(4A24) CB ON/OFF |  | PPU-2 PT-9 |  | abgb | B2/D20_D1 | [8 empty] | 和順DS.4A24_CB | 4A24(11KV和24線) CB | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 2-07-01 |  |  | 和24線(4A24) PHA |  | PPU-2 PT-10 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A24_PHA | 11KV和24線(4A24) 相間RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 2-07-02 |  |  | 和24線(4A24) GDA |  | PPU-2 PT-11 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A24_GDA | 11KV和24線(4A24) 接地RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4A25/T1 |  |  | 0219 |  |  | 2-07-03 |  |  | 和25線(4A25) CB ON/OFF |  | PPU-2 PT-12 |  | abhb | B2/D20_D1 | [8 empty] | 和順DS.4A25_CB | 4A25(11KV和25線) CB | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 2-07-04 |  |  | 和25線(4A25) PHA |  | PPU-2 PT-13 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A25_PHA | 11KV和25線(4A25) 相間RY | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 2-07-05 |  |  | 和25線(4A25) GDA |  | PPU-2 PT-14 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A25_GDA | 11KV和25線(4A25) 接地RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/LBS240^C/4SC(A) |  |  | 0222 |  |  | 2-07-06 |  |  | #4SC 240 CB ON/OFF |  | PPU-2 PT-15 |  | bbcb | B3/D20_A1 | [8 empty] | 和順DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0223 |  |  | 2-07-07 |  |  | #4SC 240 SCA |  | PPU-2 PT-16 |  |  | B3/D20_A1 | [8 empty] | 和順DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0224 |  |  | 2-08-00 |  |  | #4SC 240 UVA |  | PPU-2 PT-17 |  |  | B3/D20_A1 | [8 empty] | 和順DS.240_OUVA | 11KV #4SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4A26/T1 |  |  | 0225 |  |  | 2-08-01 |  |  | 和26線(4A26) CB ON/OFF |  | PPU-2 PT-18 |  | bbdb | B2/D20_D1 | [8 empty] | 和順DS.4A26_CB | 4A26(11KV和26線) CB | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 2-08-02 |  |  | 和26線(4A26) PHA |  | PPU-2 PT-19 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A26_PHA | 11KV和26線(4A26) 相間RY | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 2-08-03 |  |  | 和26線(4A26) GDA |  | PPU-2 PT-20 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A26_GDA | 11KV和26線(4A26) 接地RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4A27/T1 |  |  | 0228 |  |  | 2-08-04 |  |  | 和27線(4A27) CB ON/OFF |  | PPU-2 PT-21 |  | bbeb | B2/D20_D1 | [8 empty] | 和順DS.4A27_CB | 4A27(11KV和27線) CB | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 2-08-05 |  |  | 和27線(4A27) PHA |  | PPU-2 PT-22 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A27_PHA | 11KV和27線(4A27) 相間RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 2-08-06 |  |  | 和27線(4A27) GDA |  | PPU-2 PT-23 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A27_GDA | 11KV和27線(4A27) 接地RY | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4A28/T1 |  |  | 0231 |  |  | 2-08-07 |  |  | 和28線(4A28) CB ON/OFF |  | PPU-2 PT-24 |  | bbgb | B2/D20_D1 | [8 empty] | 和順DS.4A28_CB | 4A28(11KV和28線) CB | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 |  |  | 2-09-00 |  |  | 和28線(4A28) PHA |  | PPU-2 PT-25 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A28_PHA | 11KV和28線(4A28) 相間RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 2-09-01 |  |  | 和28線(4A28) GDA |  | PPU-2 PT-26 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A28_GDA | 11KV和28線(4A28) 接地RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4A29/T1 |  |  | 0234 |  |  | 2-09-02 |  |  | 和29線(4A29) CB ON/OFF |  | PPU-2 PT-27 |  | bbib | B2/D20_D1 | [8 empty] | 和順DS.4A29_CB | 4A29(11KV和29線) CB | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 2-09-03 |  |  | 和29線(4A29) PHA |  | PPU-2 PT-28 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A29_PHA | 11KV和29線(4A29) 相間RY | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 2-09-04 |  |  | 和29線(4A29) GDA |  | PPU-2 PT-29 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A29_GDA | 11KV和29線(4A29) 接地RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4A30/T1 |  |  | 0237 |  |  | 2-09-05 |  |  | 和30線(4A30) CB ON/OFF |  | PPU-2 PT-30 |  | bbjb | B2/D20_D1 | [8 empty] | 和順DS.4A30_CB | 4A30(11KV和30線) CB | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 2-09-06 |  |  | 和30線(4A30) PHA |  | PPU-2 PT-31 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A30_PHA | 11KV和30線(4A30) 相間RY | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 2-09-07 |  |  | 和30線(4A30) GDA |  | PPU-2 PT-32 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A30_GDA | 11KV和30線(4A30) 接地RY | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0240 |  |  | 2-0A-00 |  |  | #2SSTR 490 CB ON/OFF |  | PPU-2 PT-33 |  | bbbb | B3/D20_A1 | [8 empty] | 和順DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 2-0A-01 |  |  | #2SSTR 490 PHA |  | PPU-2 PT-34 |  |  | B3/D20_A1 | [8 empty] | 和順DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 |  |  | 2-0A-02 |  |  | #2SSTR 490 GDA |  | PPU-2 PT-35 |  |  | B3/D20_A1 | [8 empty] | 和順DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0243 |  |  | 2-0A-03 |  |  | TIE2B(200) CB ON/OFF |  | PPU-2 PT-36 |  | bbab | B3/D20_A1 | [8 empty] | 和順DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 2-0A-04 |  |  | TIE2B(200) PHA |  | PPU-2 PT-37 |  |  | B3/D20_A1 | [8 empty] | 和順DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0245 |  |  | 2-0A-05 |  |  | TIE2B(200) GDA |  | PPU-2 PT-38 |  |  | B3/D20_A1 | [8 empty] | 和順DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0320 |  |  | 1-30-00 |  |  | TEST CB ON/OFF |  |  |  |  | ELEM/ALL | [8 empty] | 和順DS.TEST_CB | TEST CB | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0321 |  |  | 1-30-01 |  |  | MCCA 故障 |  | 161KV IED 故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.MCC故障 | 161KV IED故障 | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 1-30-02 |  |  | PMCCA故障 |  | 23KV IED 故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.PMCC故障 | 11/23KV IED故障 | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  |  | 1-30-03 |  |  | 道爺和順新化線 1510 87UL |  | 差動電驛 使用/閉鎖 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_87UL | 道爺和順新化線(1510) 87RY U/L | LINE161 | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0324 |  |  | 1-30-04 |  |  | 道爺和順新化線 1510 (85BS) |  |  |  |  | B2/D20_A1 | [16 empty] | 385 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0325 |  |  | 1-30-05 |  |  | 道爺和順新化線 1510 79UL |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_79UL | 道爺和順新化線(1510) 79RY U/L | LINE161 | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0326 |  |  | 1-30-06 |  |  | 安南和順線 1520 87UL |  | 差動電驛 使用/閉鎖 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_87UL | 安南和順線(1520) 87RY U/L | LINE161 | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  |  | 1-30-07 |  |  | 安南和順線 1520 (85BS) |  |  |  |  | B2/D20_A1 | [16 empty] | 388 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  |  | 1-30-08 |  |  | 安南和順線 1520 79UL |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_79UL | 安南和順線(1520) 79RY U/L | LINE161 | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0332 |  |  | 1-30-12 |  |  | 和順公學二路 1540 87UL |  | 差動電驛 使用/閉鎖 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_87UL | 和順公學二路(1540) 87RY U/L | LINE161 | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0333 |  |  | 1-30-13 |  |  | 和順公學二路 1540 (85BS) |  |  |  |  | B2/D20_A1 | [16 empty] | 391 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0334 |  |  | 1-30-14 |  |  | 和順公學二路 1540 79UL |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_79UL | 和順公學二路(1540) 79RY U/L | LINE161 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0353 |  |  | 1-32-01 |  |  | 161KV #1 BUS╴87UL |  | 差動電驛 ON/OFF |  |  | B2/D20_A1 | [8 empty] | 和順DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0354 |  |  | 1-32-02 |  |  | 161KV #2 BUS╴87UL |  | 差動電驛 ON/OFF |  |  | B2/D20_A1 | [8 empty] | 和順DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 1-32-04 |  |  | DTR1 87UL |  | 差動電驛 使用/閉鎖 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0357 |  |  | 1-32-05 |  |  | M1A(310) 43RS S/L S/L |  | OLTC 遙控/現場 |  | c | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0358 |  |  | 1-32-06 |  |  | M1A(310) 43AS A/M |  | OLTC 自動/手動 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D20 | 和順DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0359 |  |  | 1-32-07 |  |  | M1B(320) 43RS S/L |  | OLTC 遙控/現場 |  | b | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0360 |  |  | 1-32-08 |  |  | M1B(320) 43AS A/M |  | OLTC 自動/手動 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D20 | 和順DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0361 |  |  | 1-32-09 |  |  | DTR1 TRA |  | DTR 重故障 |  | a | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0362 |  |  | 1-32-10 |  |  | DTR1 TRF |  | DTR 輕故障 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0363 |  |  | 1-32-11 |  |  | DTR1 96B1 |  | 撲氣電驛第一段警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0364 |  |  | 1-32-12 |  |  | DTR1 96B2 |  | 撲氣電驛第二段警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0365 |  |  | 1-32-13 |  |  | DTR1 96D |  | 放壓電驛警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0366 |  |  | 1-32-14 |  |  | DTR1 96P |  | 衝擊油壓電驛警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0367 |  |  | 1-32-15 |  |  | DTR1 63Q |  | OLTC 保護電驛警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-33-00 |  |  | DTR2 87S |  | 差動電驛 使用/閉鎖 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0369 |  |  | 1-33-01 |  |  | M2A(330) 43RS S/L |  | OLTC 遙控/現場 |  | c | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0370 |  |  | 1-33-02 |  |  | M2A(330) 43AS A/M |  | OLTC 自動/手動 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D20 | 和順DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0371 |  |  | 1-33-03 |  |  | M2B(340) 43RS S/L |  | OLTC 遙控/現場 |  | b | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0372 |  |  | 1-33-04 |  |  | M2B(340) 43AS A/M |  | OLTC 自動/手動 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D20 | 和順DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0373 |  |  | 1-33-05 |  |  | DTR2 TRA |  | DTR 重故障 |  | a | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0374 |  |  | 1-33-06 |  |  | DTR2 TRF |  | DTR 輕故障 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0375 |  |  | 1-33-07 |  |  | DTR2 96B1 |  | 撲氣電驛第一段警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0376 |  |  | 1-33-08 |  |  | DTR2 96B2 |  | 撲氣電驛第二段警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0377 |  |  | 1-33-09 |  |  | DTR2 96D |  | 放壓電驛警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0378 |  |  | 1-33-10 |  |  | DTR2 96P |  | 衝擊油壓電驛警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0379 |  |  | 1-33-11 |  |  | DTR2 63Q |  | OLTC 保護電驛警報 |  |  | B1/D20_A1 | [8 empty] | 和順DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0400 |  |  | 1-35-00 |  |  | 道爺和順新化線 1510 87CFA (RAOA) |  | 電驛通訊故障 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_87CFA | 道爺和順新化線(1510)RY通訊故障 | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0401 |  |  | 1-35-01 |  |  | 道爺和順新化線 1510 RYFA (85uA) |  | 電驛故障 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1510_RYFA | 道爺和順新化線(1510)數位RY故障 | OTHER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 74MA |  |  | Status | 74RY(M) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0402 |  |  | 1-35-02 |  |  | 道爺和順新化線 1510 (74MA) |  | 主保護監視警報 |  |  | B2/D20_A1 | [16 empty] | 421 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | 74BA |  |  | Status | 74RY(B) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0403 |  |  | 1-35-03 |  |  | 道爺和順新化線 1510 (74BA) |  | 後衛保護監視警報 |  |  | B2/D20_A1 | [16 empty] | 422 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0404 |  |  | 1-35-04 |  |  | 安南和順線 1520 87CFA (RAOA) |  | 電驛通訊故障 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_87CFA | 安南和順線(1520)87RY通訊故障 | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0405 |  |  | 1-35-05 |  |  | 安南和順線 1520 RYFA (85uA) |  | 電驛故障 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1520_RYFA | 安南和順線(1520)數位電驛故障 | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 74MA |  |  | Status | 74RY(M) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0406 |  |  | 1-35-06 |  |  | 安南和順線 1520 (74MA) |  | 主保護監視警報 |  |  | B2/D20_A1 | [16 empty] | 425 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | 74BA |  |  | Status | 74RY(B) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0407 |  |  | 1-35-07 |  |  | 安南和順線 1520 (74BA) |  | 後衛保護監視警報 |  |  | B2/D20_A1 | [16 empty] | 426 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0412 |  |  | 1-35-12 |  |  | 和順公學二路 1540 87CFA (RAOA) |  | 電驛通訊故障 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_87CFA | 和順公學二路(1540)87RY通訊故障 | OTHER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0413 |  |  | 1-35-13 |  |  | 和順公學二路 1540 RYFA (85uA) |  | 電驛故障 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1540_RYFA | 和順公學二路(1540)數位電驛故障 | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 74MA |  |  | Status | 74RY(M) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0414 |  |  | 1-35-14 |  |  | 和順公學二路 1540 (74MA) |  | 主保護監視警報 |  |  | B2/D20_A1 | [16 empty] | 429 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 74BA |  |  | Status | 74RY(B) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0415 |  |  | 1-35-15 |  |  | 和順公學二路 1540 (74BA) |  | 後衛保護監視警報 |  |  | B2/D20_A1 | [16 empty] | 430 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0440 |  |  | 1-37-08 |  |  | 南科和順新化線 1510 DTTA |  |  |  |  | B2/D20_A1 | [16 empty] | 431 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0441 |  |  | 1-37-09 |  |  | 本所各GRZ100 RY U/L |  | LOCK為1 |  |  | B3/D20_A1 | [8 empty] | 和順DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0442 |  |  | 1-37-10 |  |  | 161KV BUS數位電驛故障 |  | 電驛故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0443 |  |  | 1-37-11 |  |  | 161KV BUS 87RY CT 迴路故障 |  | CT 迴路故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0444 |  |  | 1-37-12 |  |  | 15分鐘內連動3次警報 (OLTCA) |  | OLTC 3連動警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0448 | 449 |  | 1-38-00 | 1-38-01 |  | 道爺和順新化線 1511DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1511_DS | 1511(道爺和順新化線) DS | LINE161 | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0450 | 451 |  | 1-38-02 | 1-38-03 |  | 道爺和順新化線 1512DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1512_DS | 1512(道爺和順新化線) DS | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0452 | 453 |  | 1-38-04 | 1-38-05 |  | 道爺和順新化線 1513DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1513_DS | 1513(道爺和順新化線) DS | LINE161 | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0454 | 455 |  | 1-38-06 | 1-38-07 |  | 道爺和順新化線 1513ES AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1513E_ES | 1513E(道爺和順新化線) ES | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0456 | 457 |  | 1-38-08 | 1-38-09 |  | 安南和順線 1521DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1521_DS | 1521(安南和順線) DS | LINE161 | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0458 | 459 |  | 1-38-10 | 1-38-11 |  | 安南和順線 1522DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1522_DS | 1522(安南和順線) DS | LINE161 | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0460 | 461 |  | 1-38-12 | 1-38-13 |  | 安南和順線 1523DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1523_DS | 1523(安南和順線) DS | LINE161 | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0462 | 463 |  | 1-38-14 | 1-38-15 |  | 安南和順線 1523ES AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1523E_ES | 1523E(安南和順線) ES | LINE161 | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0472 | 473 |  | 1-39-08 | 1-39-09 |  | 和順公學二路 1541DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1541_DS | 1541(和順公學二路) DS | LINE161 | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0474 | 475 |  | 1-39-10 | 1-39-11 |  | 和順公學二路 1542DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1542_DS | 1542(和順公學二路) DS | LINE161 | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0476 | 477 |  | 1-39-12 | 1-39-13 |  | 和順公學二路 1543DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1543_DS | 1543(和順公學二路) DS | LINE161 | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0478 | 479 |  | 1-39-14 | 1-39-15 |  | 和順公學二路 1543ES AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1543E_ES | 1543E(和順公學二路) ES | LINE161 | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0528 | 529 |  | 1-3D-00 | 1-3D-01 |  | DTR1 1DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0530 | 531 |  | 1-3D-02 | 1-3D-03 |  | DTR1 2DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0532 | 533 |  | 1-3D-04 | 1-3D-05 |  | DTR2 1DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0534 | 535 |  | 1-3D-06 | 1-3D-07 |  | DTR2 2DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0544 | 545 |  | 1-3E-00 | 1-3E-01 |  | 161KV TIE 1501DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0546 | 547 |  | 1-3E-02 | 1-3E-03 |  | 161KV TIE 1502DS AS |  |  |  |  | B2/D20_A1 | [8 empty] | 和順DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 2-30-00 |  |  | 和11線(4A11) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A11_79UL | 11KV和11線(4A11) 79RY U/L | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0577 |  |  | 2-30-01 |  |  | 和11線(4A11) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A11_LCO_TAP | 11KV和11線(4A11) LCO TAP | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0578 |  |  | 2-30-02 |  |  | 和12線(4A12) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A12_79UL | 11KV和12線(4A12) 79RY U/L | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0579 |  |  | 2-30-03 |  |  | 和12線(4A12) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A12_LCO_TAP | 11KV和12線(4A12) LCO TAP | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 2-30-04 |  |  | 和13線(4A13) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A13_79UL | 11KV和13線(4A13) 79RY U/L | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0581 |  |  | 2-30-05 |  |  | 和13線(4A13) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A13_LCO_TAP | 11KV和13線(4A13) LCO TAP | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 2-30-06 |  |  | 和14線(4A14) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A14_79UL | 11KV和14線(4A14) 79RY U/L | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0583 |  |  | 2-30-07 |  |  | 和14線(4A14) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A14_LCO_TAP | 11KV和14線(4A14) LCO TAP | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 2-30-08 |  |  | 和15線(4A15) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A15_79UL | 11KV和15線(4A15) 79RY U/L | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0585 |  |  | 2-30-09 |  |  | 和15線(4A15) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A15_LCO_TAP | 11KV和15線(4A15) LCO TAP | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0586 |  |  | 2-30-10 |  |  | 和16線(4A16) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A16_79UL | 11KV和16線(4A16) 79RY U/L | FEEDER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0587 |  |  | 2-30-11 |  |  | 和16線(4A16) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A16_LCO_TAP | 11KV和16線(4A16) LCO TAP | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0588 |  |  | 2-30-12 |  |  | 和17線(4A17) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A17_79UL | 11KV和17線(4A17) 79RY U/L | FEEDER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0589 |  |  | 2-30-13 |  |  | 和17線(4A17) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A17_LCO_TAP | 11KV和17線(4A17) LCO TAP | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 2-30-14 |  |  | 和18線(4A18) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A18_79UL | 11KV和18線(4A18) 79RY U/L | FEEDER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0591 |  |  | 2-30-15 |  |  | 和18線(4A18) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A18_LCO_TAP | 11KV和18線(4A18) LCO TAP | FEEDER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 2-31-00 |  |  | 和19線(4A19) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A19_79UL | 11KV和19線(4A19) 79RY U/L | FEEDER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0593 |  |  | 2-31-01 |  |  | 和19線(4A19) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A19_LCO_TAP | 11KV和19線(4A19) LCO TAP | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0594 |  |  | 2-31-02 |  |  | 和20線(4A20) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A20_79UL | 11KV和20線(4A20) 79RY U/L | FEEDER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0595 |  |  | 2-31-03 |  |  | 和20線(4A20) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A20_LCO_TAP | 11KV和20線(4A20) LCO TAP | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 2-31-04 |  |  | 和21線(4A21) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A21_79UL | 11KV和21線(4A21) 79RY U/L | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0597 |  |  | 2-31-05 |  |  | 和21線(4A21) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A21_LCO_TAP | 11KV和21線(4A21) LCO TAP | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0598 |  |  | 2-31-06 |  |  | 和22線(4A22) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A22_79UL | 11KV和22線(4A22) 79RY U/L | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0599 |  |  | 2-31-07 |  |  | 和22線(4A22) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A22_LCO_TAP | 11KV和22線(4A22) LCO TAP | FEEDER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 2-31-08 |  |  | 和23線(4A23) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A23_79UL | 11KV和23線(4A23) 79RY U/L | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0601 |  |  | 2-31-09 |  |  | 和23線(4A23) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A23_LCO_TAP | 11KV和23線(4A23) LCO TAP | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0602 |  |  | 2-31-10 |  |  | 和24線(4A24) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A24_79UL | 11KV和24線(4A24) 79RY U/L | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0603 |  |  | 2-31-11 |  |  | 和24線(4A24) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A24_LCO_TAP | 11KV和24線(4A24) LCO TAP | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0604 |  |  | 2-31-12 |  |  | 和25線(4A25) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A25_79UL | 11KV和25線(4A25) 79RY U/L | FEEDER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0605 |  |  | 2-31-13 |  |  | 和25線(4A25) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A25_LCO_TAP | 11KV和25線(4A25) LCO TAP | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0606 |  |  | 2-31-14 |  |  | 和26線(4A26) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A26_79UL | 11KV和26線(4A26) 79RY U/L | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0607 |  |  | 2-31-15 |  |  | 和26線(4A26) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A26_LCO_TAP | 11KV和26線(4A26) LCO TAP | FEEDER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0608 |  |  | 2-32-00 |  |  | 和27線(4A27) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A27_79UL | 11KV和27線(4A27) 79RY U/L | FEEDER | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0609 |  |  | 2-32-01 |  |  | 和27線(4A27) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A27_LCO_TAP | 11KV和27線(4A27) LCO TAP | FEEDER | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0610 |  |  | 2-32-02 |  |  | 和28線(4A28) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A28_79UL | 11KV和28線(4A28) 79RY U/L | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0611 |  |  | 2-32-03 |  |  | 和28線(4A28) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A28_LCO_TAP | 11KV和28線(4A28) LCO TAP | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 2-32-04 |  |  | 和29線(4A29) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A29_79UL | 11KV和29線(4A29) 79RY U/L | FEEDER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0613 |  |  | 2-32-05 |  |  | 和29線(4A29) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A29_LCO_TAP | 11KV和29線(4A29) LCO TAP | FEEDER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 2-32-06 |  |  | 和30線(4A30) 79S |  | 復閉電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A30_79UL | 11KV和30線(4A30) 79RY U/L | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0615 |  |  | 2-32-07 |  |  | 和30線(4A30) 51NS |  | 接地過流電驛 使用/閉鎖 |  |  | B2/D20_D1 | [8 empty] | 和順DS.4A30_LCO_TAP | 11KV和30線(4A30) LCO TAP | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0648 |  |  | 2-34-08 |  |  | 1500 50SA |  | 1500 50RY 測試/正常 |  |  | B2/D20_A1 | [8 empty] | 和順DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0649 |  |  | 2-34-09 |  |  | 25PFA |  | 同步電驛電源故障警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0650 |  |  | 2-34-10 |  |  | 25TA |  | 同步電驛延時警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0651 |  |  | 2-34-11 |  |  | ACB1 |  | 所內電源ACB1 |  |  | B3/D20_A1 | [8 empty] | 和順DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0652 |  |  | 2-34-12 |  |  | ACB2 |  | 所內電源ACB2 |  |  | B3/D20_A1 | [8 empty] | 和順DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0653 |  |  | 2-34-13 |  |  | ACB TIE |  | 所內電源ACB TIE |  |  | B3/D20_A1 | [8 empty] | 和順DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0654 |  |  | 2-34-14 |  |  | STUV |  | 所內電源欠壓警報 |  |  | ELEM/D20_A1 | [8 empty] | 和順DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0655 |  |  | 2-34-15 |  |  | 11KV SC 60A |  | SC 壓差警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.11KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Water1 | 第一段 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0656 |  |  | 2-35-00 |  |  | WP1 |  | 地下室第一水位警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.水位警報(1) | 地下室第一段水位警報 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0657 |  |  | 2-35-01 |  |  | 161KV GIS CBA |  | 161KV CB 重故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0658 |  |  | 2-35-02 |  |  | 161KV GIS CBF |  | 161KV CB 輕故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0659 |  |  | 2-35-03 |  |  | DCA |  | 直流 NFB 跳脫警報 |  |  | ELEM/D20_A1 | [8 empty] | 和順DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0660 |  |  | 2-35-04 |  |  | ACBA |  | 所內電源 ACB 跳脫警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0661 |  |  | 2-35-05 |  |  | CHG#1 |  | 充電機故障 (設備用) |  |  | B3/D20_A1 | [8 empty] | 和順DS.直流充電機故障 | 直流充電機故障 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0662 |  |  | 2-35-06 |  |  | DCE |  | DC 接地警報 |  |  | ELEM/D20_A1 | [8 empty] | 和順DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0663 |  |  | 2-35-07 |  |  | 11KV GIS CBA |  | 11/22KV CB 重故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0664 |  |  | 2-35-08 |  |  | 11KV GIS CBF |  | 11/22KV CB 輕故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0665 |  |  | 2-35-09 |  |  | 11KV GIS LOA |  | 11/22KV GIS 復閉失敗 |  |  | B3/D20_A1 | [8 empty] | 和順DS.11/23KV_LOA | 饋線復閉失敗閉鎖 | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Comm_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0666 |  |  | 2-35-10 |  |  | COMM S/L |  | 通訊處理單元 遙控/現場 |  |  | B3/D20_A1 | [8 empty] | 和順DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0667 |  |  | 2-35-11 |  |  | 無人化開關場照明 (A) |  | 無人化開關場照明 (A) |  |  | B3/D20_A1 | [8 empty] | 和順DS.開關場照明(A) | 開關場照明(A)景觀照明 | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0668 |  |  | 2-35-12 |  |  | 無人化開關場照明 (B) |  | 無人化開關場照明 (B) |  |  | B3/D20_A1 | [8 empty] | 和順DS.開關場照明(B) | 開關場照明(B)路燈照明 | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0669 |  |  | 2-35-13 |  |  | OWA1 |  | 集油池第一段水位警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.集油池水位(1) | 集油池第一段水位警報 | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0670 |  |  | 2-35-14 |  |  | OWA2 |  | 集油池第二段水位警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.集油池水位(2) | 集油池第二段水位警報 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Water2 | 第二段 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0671 |  |  | 2-35-15 |  |  | WP2 |  | 地下室第二段水位警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.水位警報(2) | 地下室第二段水位警報 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0672 |  |  | 2-36-00 |  |  | ACFA |  | 通訊設備 AC 電源故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0673 |  |  | 2-36-01 |  |  | CHG#2 |  | 充電機故障 (通訊用) |  |  | B3/D20_A1 | [8 empty] | 和順DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0676 |  |  | 2-36-04 |  |  | Locate Empty |  | 通訊室或控制室溫度警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.通訊機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0677 |  |  | 2-36-05 |  |  | PSA |  | 其他重故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0678 |  |  | 2-36-06 |  |  | PSF |  | 其他輕故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0679 |  |  | 2-36-07 |  |  | 門禁一 |  | 建築物門禁警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0680 |  |  | 2-36-08 |  |  | 門禁二 |  | 控制室大小 |  |  | B3/D20_A1 | [8 empty] | 和順DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0681 |  |  | 2-36-09 |  |  | 火災警報(1) |  | 火災警報(1)受信總機 |  |  | B3/D20_A1 | [8 empty] | 和順DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0682 |  |  | 2-36-10 |  |  | SCADA故障(SUPA) |  | LOCAL SCADA 故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.SCADA故障 | 變電所LOCAL SCADA故障 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | TCA |  |  | Status | 斷路器跳脫迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0683 |  |  | 2-36-11 |  |  | 161KV/22KV/11KV TCA |  | 跳脫迴路警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.TCA | 斷路器跳脫回路故障 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0684 |  |  | 2-36-12 |  |  | 161KB #1 BUS VUA |  | 衡相電驛警報 |  |  | B2/D20_A1 | [8 empty] | 和順DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0685 |  |  | 2-36-13 |  |  | 161KV #2 BUS VUA |  | 衡相電驛警報 |  |  | B2/D20_A1 | [8 empty] | 和順DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | OilLeak | 涵洞水泵警報 | Element | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0686 |  |  | 2-36-14 |  |  | SWP抽水泵故障警報 |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.涵洞水泵 | 涵洞水泵警報 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0687 |  |  | 2-36-15 |  |  | 161KV GIS COMT |  | 空壓機超時警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0688 |  |  | 2-37-00 |  |  | 11KV GIS COMT |  | 空壓機超時警報 |  |  | B3/D20_A1 | [8 empty] | 和順DS.11KV空壓機COMT | 11KV空壓機運轉超時警報 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0689 |  |  | 2-37-01 |  |  | OSCF |  | 示波器故障 |  |  | B3/D20_A1 | [8 empty] | 和順DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0690 |  |  | 2-37-02 |  |  | 門禁三 |  | 防盜,保全 |  |  | B3/D20_A1 | [8 empty] | 和順DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | GPSA |  |  | Status | GPS故障警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0691 |  |  | 2-37-03 |  |  | GPS校時來源 |  |  |  |  | B3/D20_A1 | [16 empty] | 535 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0692 |  |  | 2-37-04 |  |  | 緊急發電機運轉 |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | PMCC_R_L |  |  | Status | PMCC Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0693 |  |  | 2-37-05 |  |  | PMCC R/L |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.PMCC_IED_S/L | 11/23KV IED SUPY/LOCAL | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | MCC |  | Element | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0694 |  |  | 2-37-06 |  |  | MCC Comm. Trouble |  |  |  |  | B3/D20_A1 | [16 empty] | 538 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 0 |  | StaDev | 所內設施 |  | PMCC |  | Element | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0695 |  |  | 2-37-07 |  |  | PMCC Comm. Trouble |  |  |  |  | B3/D20_A1 | [16 empty] | 539 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 11 | 11kV | LBS210 | #1SC(210) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0696 | 697 |  | 2-37-08 | 2-37-09 |  | #1SC 210 LBS AS |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0698 | 699 |  | 2-37-10 | 2-37-11 |  | #2SC 220 LBS AS |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | LBS230 | #3SC(230) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0700 | 701 |  | 2-37-12 | 2-37-13 |  | #3SC 230 LBS AS |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | LBS240 | #4SC(240) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 0702 | 703 |  | 2-37-14 | 2-37-15 |  | #4SC 240 LBS AS |  |  |  |  | B3/D20_A1 | [8 empty] | 和順DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0197 | [8 empty] | kV_-18_18(-2000_2000) | not found | B3/D20_A1 | [8 empty] | 和順DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 544 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0194 | [8 empty] | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 545 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0195 | [8 empty] | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 546 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0196 | [8 empty] | A_-3000_3000(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 547 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0190 | [8 empty] | MW_-108_108(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 548 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0191 | [8 empty] | MVAR_-72_72(-2000_2000) |  | B3/D20_A1 | [8 empty] | 和順DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 549 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0198 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和51線KVAR | 23KV和51線 KVAR | FEEDER | [5 empty] | 550 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0199 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和51線A1 | 23KV和51線 R相AMP | FEEDER | [5 empty] | 551 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0200 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和51線A2 | 23KV和51線 S相AMP | FEEDER | [5 empty] | 552 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0201 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和51線A3 | 23KV和51線 T相AMP | FEEDER | [5 empty] | 553 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和51線A0 | 23KV和51線 N相AMP | FEEDER | [5 empty] | 554 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0203 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和52線KVAR | 23KV和52線 KVAR | FEEDER | [5 empty] | 555 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0204 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和52線A1 | 23KV和52線 R相AMP | FEEDER | [5 empty] | 556 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0205 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和52線A2 | 23KV和52線 S相AMP | FEEDER | [5 empty] | 557 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0206 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和52線A3 | 23KV和52線 T相AMP | FEEDER | [5 empty] | 558 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和52線A0 | 23KV和52線 N相AMP | FEEDER | [5 empty] | 559 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0208 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和53線KVAR | 23KV和53線 KVAR | FEEDER | [5 empty] | 560 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和53線A1 | 23KV和53線 R相AMP | FEEDER | [5 empty] | 561 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和53線A2 | 23KV和53線 S相AMP | FEEDER | [5 empty] | 562 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和53線A3 | 23KV和53線 T相AMP | FEEDER | [5 empty] | 563 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和53線A0 | 23KV和53線 N相AMP | FEEDER | [5 empty] | 564 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0213 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和54線KVAR | 23KV和54線 KVAR | FEEDER | [5 empty] | 565 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0214 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和54線A1 | 23KV和54線 R相AMP | FEEDER | [5 empty] | 566 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0215 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和54線A2 | 23KV和54線 S相AMP | FEEDER | [5 empty] | 567 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0216 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和54線A3 | 23KV和54線 T相AMP | FEEDER | [5 empty] | 568 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和54線A0 | 23KV和54線 N相AMP | FEEDER | [5 empty] | 569 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0218 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和55線KVAR | 23KV和55線 KVAR | FEEDER | [5 empty] | 570 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0219 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和55線A1 | 23KV和55線 R相AMP | FEEDER | [5 empty] | 571 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0220 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和55線A2 | 23KV和55線 S相AMP | FEEDER | [5 empty] | 572 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0221 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和55線A3 | 23KV和55線 T相AMP | FEEDER | [5 empty] | 573 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0222 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和55線A0 | 23KV和55線 N相AMP | FEEDER | [5 empty] | 574 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0223 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和56線KVAR | 23KV和56線 KVAR | FEEDER | [5 empty] | 575 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0224 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和56線A1 | 23KV和56線 R相AMP | FEEDER | [5 empty] | 576 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0225 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和56線A2 | 23KV和56線 S相AMP | FEEDER | [5 empty] | 577 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0226 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和56線A3 | 23KV和56線 T相AMP | FEEDER | [5 empty] | 578 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0227 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和56線A0 | 23KV和56線 N相AMP | FEEDER | [5 empty] | 579 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0228 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和57線KVAR | 23KV和57線 KVAR | FEEDER | [5 empty] | 580 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0229 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和57線A1 | 23KV和57線 R相AMP | FEEDER | [5 empty] | 581 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0230 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和57線A2 | 23KV和57線 S相AMP | FEEDER | [5 empty] | 582 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0231 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和57線A3 | 23KV和57線 T相AMP | FEEDER | [5 empty] | 583 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0232 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和57線A0 | 23KV和57線 N相AMP | FEEDER | [5 empty] | 584 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0233 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和58線KVAR | 23KV和58線 KVAR | FEEDER | [5 empty] | 585 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0234 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和58線A1 | 23KV和58線 R相AMP | FEEDER | [5 empty] | 586 |  |  |  |  | AI | [5 empty] | C06R450R | 405 | 406 | 450 | 600 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0235 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和58線A2 | 23KV和58線 S相AMP | FEEDER | [5 empty] | 587 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0236 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和58線A3 | 23KV和58線 T相AMP | FEEDER | [5 empty] | 588 |  |  |  |  | AI | [5 empty] | C06R0450 | 427.5 | 450 | 495 | 553.5 | 1.25 | -427.5 | -450 | -495 | -553.5 | 1 | 0.01 | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0237 | [8 empty] | A_-600_600(-2000_2000) |  | B2/D20_D1 | [8 empty] | 和順DS.和58線A0 | 23KV和58線 N相AMP | FEEDER | [5 empty] | 589 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 590 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_A1 | [8 empty] | 和順DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 591 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0088 | [9 empty] | not found | ELEM/D20_A1 | [8 empty] | 和順DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 | [10 empty] | B2/D20_A1 | [8 empty] | 和順DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 | [10 empty] | B2/D20_A1 | [8 empty] | 和順DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0536 | 537 | [9 empty] | B2/D20_A1 | [8 empty] | 和順DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0538 | 539 | [9 empty] | B2/D20_A1 | [8 empty] | 和順DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0380 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0386 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0387 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0388 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0389 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0390 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0391 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0392 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0381 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A51_DS | 4A51_DS (非取樣點) | FEEDER | [5 empty] | 608 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A51_ES | 4A51_ES (非取樣點) | FEEDER | [5 empty] | 609 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0254 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A51_CB | 4A51(23KV和51線) CB | FEEDER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0255 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A51_PHA | 23KV和51線(4A51) 相間RY | FEEDER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A51_GDA | 23KV和51線(4A51) 接地RY | FEEDER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0616 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A51_79UL | 23KV和51線(4A51) 79RY U/L | FEEDER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0617 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A51_LCO_TAP | 23KV和51線(4A51) LCO TAP | FEEDER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A52_DS | 4A52_DS (非取樣點) | FEEDER | [5 empty] | 615 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A52_ES | 4A52_ES (非取樣點) | FEEDER | [5 empty] | 616 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0257 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A52_CB | 4A52(23KV和52線) CB | FEEDER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A52_PHA | 23KV和52線(4A52) 相間RY | FEEDER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A52_GDA | 23KV和52線(4A52) 接地RY | FEEDER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0618 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A52_79UL | 23KV和52線(4A52) 79RY U/L | FEEDER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0619 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A52_LCO_TAP | 23KV和52線(4A52) LCO TAP | FEEDER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A53_DS | 4A53_DS (非取樣點) | FEEDER | [5 empty] | 622 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A53_ES | 4A53_ES (非取樣點) | FEEDER | [5 empty] | 623 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0260 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A53_CB | 4A53(23KV和53線) CB | FEEDER | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A53_PHA | 23KV和53線(4A53) 相間RY | FEEDER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A53_GDA | 23KV和53線(4A53) 接地RY | FEEDER | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0620 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A53_79UL | 23KV和53線(4A53) 79RY U/L | FEEDER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0621 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A53_LCO_TAP | 23KV和53線(4A53) LCO TAP | FEEDER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A54_DS | 4A54_DS (非取樣點) | FEEDER | [5 empty] | 629 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A54_ES | 4A54_ES (非取樣點) | FEEDER | [5 empty] | 630 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0263 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A54_CB | 4A54(23KV和54線) CB | FEEDER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A54_PHA | 23KV和54線(4A54) 相間RY | FEEDER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A54_GDA | 23KV和54線(4A54) 接地RY | FEEDER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0622 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A54_79UL | 23KV和54線(4A54) 79RY U/L | FEEDER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0623 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A54_LCO_TAP | 23KV和54線(4A54) LCO TAP | FEEDER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A55_DS | 4A55_DS (非取樣點) | FEEDER | [5 empty] | 636 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A55_ES | 4A55_ES (非取樣點) | FEEDER | [5 empty] | 637 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0266 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A55_CB | 4A55(23KV和55線) CB | FEEDER | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A55_PHA | 23KV和55線(4A55) 相間RY | FEEDER | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A55_GDA | 23KV和55線(4A55) 接地RY | FEEDER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0624 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A55_79UL | 23KV和55線(4A55) 79RY U/L | FEEDER | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0625 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A55_LCO_TAP | 23KV和55線(4A55) LCO TAP | FEEDER | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A56_DS | 4A56_DS (非取樣點) | FEEDER | [5 empty] | 643 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A56_ES | 4A56_ES (非取樣點) | FEEDER | [5 empty] | 644 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0269 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A56_CB | 4A56(23KV和56線) CB | FEEDER | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A56_PHA | 23KV和56線(4A56) 相間RY | FEEDER | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A56_GDA | 23KV和56線(4A56) 接地RY | FEEDER | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0626 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A56_79UL | 23KV和56線(4A56) 79RY U/L | FEEDER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0627 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A56_LCO_TAP | 23KV和56線(4A56) LCO TAP | FEEDER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A57_DS | 4A57_DS (非取樣點) | FEEDER | [5 empty] | 650 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A57_ES | 4A57_ES (非取樣點) | FEEDER | [5 empty] | 651 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0272 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A57_CB | 4A57(23KV和57線) CB | FEEDER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A57_PHA | 23KV和57線(4A57) 相間RY | FEEDER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A57_GDA | 23KV和57線(4A57) 接地RY | FEEDER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0628 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A57_79UL | 23KV和57線(4A57) 79RY U/L | FEEDER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0629 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A57_LCO_TAP | 23KV和57線(4A57) LCO TAP | FEEDER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A58_DS | 4A58_DS (非取樣點) | FEEDER | [5 empty] | 657 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A58_ES | 4A58_ES (非取樣點) | FEEDER | [5 empty] | 658 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/4A11/T1 |  |  | 0275 | [9 empty] | not found | B2/D20_D1 | [8 empty] | 和順DS.4A58_CB | 4A58(23KV和58線) CB | FEEDER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0276 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A58_PHA | 23KV和58線(4A58) 相間RY | FEEDER | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0277 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A58_GDA | 23KV和58線(4A58) 接地RY | FEEDER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0630 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A58_79UL | 23KV和58線(4A58) 79RY U/L | FEEDER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0631 | [10 empty] | B2/D20_D1 | [8 empty] | 和順DS.4A58_LCO_TAP | 23KV和58線(4A58) LCO TAP | FEEDER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.351 | 351 (非取樣點) | MTR | [5 empty] | 664 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.351E | 351E (非取樣點) | MTR | [5 empty] | 665 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  |  | 0096 | [9 empty] | not found | ELEM/D20_A1 | [8 empty] | 和順DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.350_PHA | 350開關箱IED RY PHA | OTHER | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 | [10 empty] | ELEM/D20_A1 | [8 empty] | 和順DS.350_81A | 350 #3DTR 81RY動作 | OTHER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 350 | #3DTR(350) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0383 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.350_81UL | 350 #3DTR 81RY U/L | OTHER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0384 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS |  |  | 3DTR | #3DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0385 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.251E | 251E (非取樣點) | SC | [5 empty] | 673 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | DS1 |  |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [16 empty] | 674 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | A/LBS250^C/5SC(A) |  |  | 0248 | [9 empty] | not found | B3/D20_A1 | [8 empty] | 和順DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0249 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0250 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | LBS250 | #5SC(250) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/250 | C/5SC(B) |  |  | 0704 | 705 | [9 empty] | B3/D20_A1 | [8 empty] | 和順DS.250_LBS | 250(23KV #5SC) LBS | SC | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [8 empty] | 和順DS.261E | 261E (非取樣點) | SC | [5 empty] | 679 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | D1 |  |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D20_A1 | [16 empty] | 680 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0251 | [9 empty] | not found | B3/D20_A1 | [8 empty] | 和順DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0252 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0253 | [10 empty] | B3/D20_A1 | [8 empty] | 和順DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0382 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D20 | 和順DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D20 | 和順DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0393 | [10 empty] | B1/D20_A1 | [8 empty] | 和順DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D20 | 和順DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D20_A1 | [12 empty] | 和順DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D20/161/1BUS/V; OPRD2: D20/161/2BUS/V
D20 | 和順DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D20_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D20/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D20 | 和順DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D20_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_3 | OPRD1: D20/161/1510/MW; OPRD2: D20/161/1520/MW; OPRD3: D20/161/1540/MW
D20 | 和順DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D20_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D20/0/CalcPoint/OPRN2_MW
D20 | 和順DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D20_A1 | [17 empty] | none
D20 | 和順DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D20_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D20/0/CalcPoint/OPRN1; OPRD2: D20/0/CalcPoint/OPRN2; OPRD3: D20/0/CalcPoint/PRFL_UL
D20 | 和順DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D20_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D20/11/310/I_R; OPRD2: D20/11/320/I_R
D20 | 和順DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D20_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D20/11/310/I_S; OPRD2: D20/11/320/I_S
D20 | 和順DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D20_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D20/11/310/I_T; OPRD2: D20/11/320/I_T
D20 | 和順DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D20_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D20/11/330/I_R; OPRD2: D20/11/340/I_R
D20 | 和順DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D20_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D20/11/330/I_S; OPRD2: D20/11/340/I_S
D20 | 和順DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D20_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D20/11/330/I_T; OPRD2: D20/11/340/I_T
D20 | 和順DS | 161 | 161kV | 1510 | 道爺~和順~新化線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D20_A1 | [12 empty] | 和順DS.1510_AMP | 道爺和順新化線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: D20/161/1510/MW; OPRD2: D20/161/1510/MVAR; OPRD3: D20/0/CalcPoint/Vbs4
D20 | 和順DS | 161 | 161kV | 1520 | 安南～和順線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D20_A1 | [12 empty] | 和順DS.1520_AMP | 安南和順線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: D20/161/1520/MW; OPRD2: D20/161/1520/MVAR; OPRD3: D20/0/CalcPoint/Vbs4
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D20_A1 | [12 empty] | 和順DS.1540_AMP | 和順公學二路 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: D20/161/1540/MW; OPRD2: D20/161/1540/MVAR; OPRD3: D20/0/CalcPoint/Vbs4
D20 | 和順DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D20_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D20/11/1ABUS/V
D20 | 和順DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D20_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D20/11/1BBUS/V
D20 | 和順DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D20_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D20/11/2ABUS/V
D20 | 和順DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D20_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D20/11/2BBUS/V
D20 | 和順DS | 22 | 22kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D20_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D20/22/3BUS/V
D20 | 和順DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D20_A1 | [12 empty] | 和順DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D20//1DTR(A)/SupLocal; OPRD2: D20//1DTR(A)/Tap Chan
D20 | 和順DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D20_A1 | [12 empty] | 和順DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D20//1DTR(B)/SupLocal; OPRD2: D20//1DTR(B)/Tap Chan
D20 | 和順DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D20_A1 | [12 empty] | 和順DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D20//2DTR(A)/SupLocal; OPRD2: D20//2DTR(A)/Tap Chan
D20 | 和順DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D20_A1 | [12 empty] | 和順DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D20//2DTR(B)/SupLocal; OPRD2: D20//2DTR(B)/Tap Chan
D20 | 和順DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D20_A1 | [12 empty] | 和順DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D20//3DTR/SupLocal; OPRD2: D20//3DTR/Tap Chan
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1ABUS/V; OPRD2: D20/11/4A11/I_R; OPRD3: D20/11/4A11/I_S; OPRD4: D20/11/4A11/I_T
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1ABUS/V; OPRD2: D20/11/4A12/I_R; OPRD3: D20/11/4A12/I_S; OPRD4: D20/11/4A12/I_T
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1ABUS/V; OPRD2: D20/11/4A13/I_R; OPRD3: D20/11/4A13/I_S; OPRD4: D20/11/4A13/I_T
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1ABUS/V; OPRD2: D20/11/4A14/I_R; OPRD3: D20/11/4A14/I_S; OPRD4: D20/11/4A14/I_T
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1ABUS/V; OPRD2: D20/11/4A15/I_R; OPRD3: D20/11/4A15/I_S; OPRD4: D20/11/4A15/I_T
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1BBUS/V; OPRD2: D20/11/4A16/I_R; OPRD3: D20/11/4A16/I_S; OPRD4: D20/11/4A16/I_T
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1BBUS/V; OPRD2: D20/11/4A17/I_R; OPRD3: D20/11/4A17/I_S; OPRD4: D20/11/4A17/I_T
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1BBUS/V; OPRD2: D20/11/4A18/I_R; OPRD3: D20/11/4A18/I_S; OPRD4: D20/11/4A18/I_T
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1BBUS/V; OPRD2: D20/11/4A19/I_R; OPRD3: D20/11/4A19/I_S; OPRD4: D20/11/4A19/I_T
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/1BBUS/V; OPRD2: D20/11/4A20/I_R; OPRD3: D20/11/4A20/I_S; OPRD4: D20/11/4A20/I_T
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2ABUS/V; OPRD2: D20/11/4A21/I_R; OPRD3: D20/11/4A21/I_S; OPRD4: D20/11/4A21/I_T
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2ABUS/V; OPRD2: D20/11/4A22/I_R; OPRD3: D20/11/4A22/I_S; OPRD4: D20/11/4A22/I_T
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2ABUS/V; OPRD2: D20/11/4A23/I_R; OPRD3: D20/11/4A23/I_S; OPRD4: D20/11/4A23/I_T
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2ABUS/V; OPRD2: D20/11/4A24/I_R; OPRD3: D20/11/4A24/I_S; OPRD4: D20/11/4A24/I_T
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2ABUS/V; OPRD2: D20/11/4A25/I_R; OPRD3: D20/11/4A25/I_S; OPRD4: D20/11/4A25/I_T
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2BBUS/V; OPRD2: D20/11/4A26/I_R; OPRD3: D20/11/4A26/I_S; OPRD4: D20/11/4A26/I_T
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2BBUS/V; OPRD2: D20/11/4A27/I_R; OPRD3: D20/11/4A27/I_S; OPRD4: D20/11/4A27/I_T
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2BBUS/V; OPRD2: D20/11/4A28/I_R; OPRD3: D20/11/4A28/I_S; OPRD4: D20/11/4A28/I_T
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2BBUS/V; OPRD2: D20/11/4A29/I_R; OPRD3: D20/11/4A29/I_S; OPRD4: D20/11/4A29/I_T
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/11/2BBUS/V; OPRD2: D20/11/4A30/I_R; OPRD3: D20/11/4A30/I_S; OPRD4: D20/11/4A30/I_T
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A51/I_R; OPRD3: D20/22/4A51/I_S; OPRD4: D20/22/4A51/I_T
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A52/I_R; OPRD3: D20/22/4A52/I_S; OPRD4: D20/22/4A52/I_T
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A53/I_R; OPRD3: D20/22/4A53/I_S; OPRD4: D20/22/4A53/I_T
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A54/I_R; OPRD3: D20/22/4A54/I_S; OPRD4: D20/22/4A54/I_T
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A55/I_R; OPRD3: D20/22/4A55/I_S; OPRD4: D20/22/4A55/I_T
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A56/I_R; OPRD3: D20/22/4A56/I_S; OPRD4: D20/22/4A56/I_T
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A57/I_R; OPRD3: D20/22/4A57/I_S; OPRD4: D20/22/4A57/I_T
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D20/22/3BUS/V; OPRD2: D20/22/4A58/I_R; OPRD3: D20/22/4A58/I_S; OPRD4: D20/22/4A58/I_T
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A11/kVA; OPRD2: D20/11/4A11/KVAR
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A12/kVA; OPRD2: D20/11/4A12/KVAR
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A13/kVA; OPRD2: D20/11/4A13/KVAR
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A14/kVA; OPRD2: D20/11/4A14/KVAR
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A15/kVA; OPRD2: D20/11/4A15/KVAR
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A16/kVA; OPRD2: D20/11/4A16/KVAR
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A17/kVA; OPRD2: D20/11/4A17/KVAR
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A18/kVA; OPRD2: D20/11/4A18/KVAR
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A19/kVA; OPRD2: D20/11/4A19/KVAR
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A20/kVA; OPRD2: D20/11/4A20/KVAR
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A21/kVA; OPRD2: D20/11/4A21/KVAR
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A22/kVA; OPRD2: D20/11/4A22/KVAR
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A23/kVA; OPRD2: D20/11/4A23/KVAR
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A24/kVA; OPRD2: D20/11/4A24/KVAR
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A25/kVA; OPRD2: D20/11/4A25/KVAR
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A26/kVA; OPRD2: D20/11/4A26/KVAR
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A27/kVA; OPRD2: D20/11/4A27/KVAR
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A28/kVA; OPRD2: D20/11/4A28/KVAR
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A29/kVA; OPRD2: D20/11/4A29/KVAR
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/11/4A30/kVA; OPRD2: D20/11/4A30/KVAR
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A51/kVA; OPRD2: D20/22/4A51/KVAR
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A52/kVA; OPRD2: D20/22/4A52/KVAR
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A53/kVA; OPRD2: D20/22/4A53/KVAR
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A54/kVA; OPRD2: D20/22/4A54/KVAR
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A55/kVA; OPRD2: D20/22/4A55/KVAR
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A56/kVA; OPRD2: D20/22/4A56/KVAR
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A57/kVA; OPRD2: D20/22/4A57/KVAR
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D20_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D20/22/4A58/kVA; OPRD2: D20/22/4A58/KVAR
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D20_A1 | [12 empty] | 和順DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D20/11/210/CB; OPRD2: 6.9; OPRD3: 0
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D20_A1 | [12 empty] | 和順DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D20/11/220/CB; OPRD2: 6.9; OPRD3: 0
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D20_A1 | [12 empty] | 和順DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D20/11/230/CB; OPRD2: 6.9; OPRD3: 0
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D20_A1 | [12 empty] | 和順DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D20/11/240/CB; OPRD2: 6.9; OPRD3: 0
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D20_A1 | [12 empty] | 和順DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_LBS_23 | LG_MVAR | sc_mvar | OPRD1: D20/22/250/CB; OPRD2: 13.8; OPRD3: 0
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D20_A1 | [15 empty] | SC_CAL_11 |  | sc_mvar | OPRD1: D20/22/260/CB; OPRD2: 13.8; OPRD3: 0
D20 | 和順DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D20_A1 | [12 empty] | 和順DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_44 | D20//1DTR/96D | D20//1DTR/63Q | D20//1DTR/96B2 | D20//1DTR/96PA | D20//1DTR/96B1 | D20//1DTR/TRA | D20//1DTR/87A | D20//1DTR(A)/51ZA | D20//1DTR(B)/51ZA | D20//2DTR/96PA | D20//2DTR/87A | D20//2DTR/96D | D20//2DTR/63Q | D20//2DTR/96B2 | D20//2DTR/TRA | D20//2DTR/96B1 | D20//2DTR(A)/51ZA | D20//2DTR(B)/51ZA | D20//3DTR/96B1 | D20//3DTR/96B2 | D20//3DTR/96D | D20//3DTR/87A | D20//3DTR/51ZA | D20//3DTR/TRA | D20//3DTR/96PA | D20//3DTR/63Q | D20/11/310/PHA | D20/11/310/GDA | D20/11/320/GDA | D20/11/320/PHA | D20/11/330/PHA | D20/11/330/GDA | D20/11/340/GDA | D20/11/340/PHA | D20/161/1750/PHA | D20/161/1750/GDA | D20/161/1760/PHA | D20/161/1760/GDA | D20/161/1770/PHA | D20/161/1770/GDA | D20/161/1BUS/87A | D20/161/2BUS/87A | D20/22/350/GDA | D20/22/350/PHA
D20 | 和順DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D20_A1 | [12 empty] | 和順DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D20//1DTR/TRF; OPRD2: D20//2DTR/TRF; OPRD3: D20//3DTR/TRF
D20 | 和順DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/161/1750/CB
D20 | 和順DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/11/310/CB
D20 | 和順DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/11/320/CB
D20 | 和順DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/161/1760/CB
D20 | 和順DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/11/330/CB
D20 | 和順DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/11/340/CB
D20 | 和順DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/0/StaDev/STUV
D20 | 和順DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/0/StaDev/DCA
D20 | 和順DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/0/StaDev/DCE
D20 | 和順DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/161/1770/CB
D20 | 和順DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/22/350/CB
D20 | 和順DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D20_D1 | [17 empty] | lamp2CC | OPRD1: D20/22/350/81A

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D20 | 和順DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 和順DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D20/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 和順DS.1510_AMP | 道爺和順新化線 AMP | LINE161 | D20/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 和順DS.1520_AMP | 安南和順線 AMP | LINE161 | D20/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 和順DS.1540_AMP | 和順公學二路 AMP | LINE161 | D20/161/1540/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D20 | 和順DS | 0 |  |  |  |  | 和11線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和11線KVA | 11KV和11線KVA | FEEDER |  |  | KVA_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和11線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和11線KW | 11KV和11線KW | FEEDER |  |  | KW_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和12線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和12線KVA | 11KV和12線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和12線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和12線KW | 11KV和12線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和13線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和13線KVA | 11KV和13線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和13線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和13線KW | 11KV和13線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和14線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和14線KVA | 11KV和14線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和14線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和14線KW | 11KV和14線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和15線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和15線KVA | 11KV和15線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和15線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和15線KW | 11KV和15線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和16線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和16線KVA | 11KV和16線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和16線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和16線KW | 11KV和16線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和17線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和17線KVA | 11KV和17線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和17線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和17線KW | 11KV和17線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和18線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和18線KVA | 11KV和18線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和18線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和18線KW | 11KV和18線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和19線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和19線KVA | 11KV和19線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和19線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和19線KW | 11KV和19線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和20線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和20線KVA | 11KV和20線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和20線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和20線KW | 11KV和20線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和21線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和21線KVA | 11KV和21線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和21線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和21線KW | 11KV和21線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和22線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和22線KVA | 11KV和22線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和22線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和22線KW | 11KV和22線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和23線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和23線KVA | 11KV和23線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和23線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和23線KW | 11KV和23線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和24線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和24線KVA | 11KV和24線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和24線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和24線KW | 11KV和24線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和25線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和25線KVA | 11KV和25線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和25線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和25線KW | 11KV和25線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和26線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和26線KVA | 11KV和26線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和26線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和26線KW | 11KV和26線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和27線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和27線KVA | 11KV和27線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和27線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和27線KW | 11KV和27線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和28線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和28線KVA | 11KV和28線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和28線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和28線KW | 11KV和28線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和29線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和29線KVA | 11KV和29線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和29線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和29線KW | 11KV和29線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和30線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和30線KVA | 11KV和30線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和30線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和30線KW | 11KV和30線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 47 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 53 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 56 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_PF | #1DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 66 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D20/11/210/MVAR |  | SC_LBS_11 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D20/11/220/MVAR |  | SC_LBS_11 |  |  | 69 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D20/11/230/MVAR |  | SC_LBS_11 |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D20/11/240/MVAR |  | SC_LBS_11 |  |  | 71 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | TRTOT | 和順主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 和順DS.TRTOT_MW | 和順主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 72 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | TRTOT | 和順主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 和順DS.TRTOT_MVAR | 和順主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 75 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D20 | 和順DS | 0 |  |  |  |  | 和51線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和51線KVA | 23KV和51線KVA | FEEDER |  |  | KVA_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和51線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和51線KW | 23KV和51線KW | FEEDER |  |  | KW_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和52線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和52線KVA | 23KV和52線KVA | FEEDER |  |  | KVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和52線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和52線KW | 23KV和52線KW | FEEDER |  |  | KW_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和53線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和53線KVA | 23KV和53線KVA | FEEDER |  |  | KVA_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和53線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和53線KW | 23KV和53線KW | FEEDER |  |  | KW_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和54線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和54線KVA | 23KV和54線KVA | FEEDER |  |  | KVA_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和54線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和54線KW | 23KV和54線KW | FEEDER |  |  | KW_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和55線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和55線KVA | 23KV和55線KVA | FEEDER |  |  | KVA_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和55線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和55線KW | 23KV和55線KW | FEEDER |  |  | KW_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和56線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和56線KVA | 23KV和56線KVA | FEEDER |  |  | KVA_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和56線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和56線KW | 23KV和56線KW | FEEDER |  |  | KW_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和57線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和57線KVA | 23KV和57線KVA | FEEDER |  |  | KVA_CAL |  |  | 89 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和57線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和57線KW | 23KV和57線KW | FEEDER |  |  | KW_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和58線KVA | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和58線KVA | 23KV和58線KVA | FEEDER |  |  | KVA_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  |  |  |  | 和58線KW | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.和58線KW | 23KV和58線KW | FEEDER |  |  | KW_CAL |  |  | 92 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 22 | 22kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 和順DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D20/22/250/MVAR |  | SC_LBS_23 |  |  | 93 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 94 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 95 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 96 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 97 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | COMM_S_L | 通訊處理單元 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.COMM_S/L_4 | 通訊處理單元 SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 98 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D20 | 和順DS | 0 |  | TCA | 斷路器跳脫回路故障 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 和順DS.TCA_4 | 斷路器跳脫回路故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 99 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 和順DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D20/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 100 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 和順DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D20/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 101 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510_AMP | 道爺和順新化線 | [27 empty] | ADCS_S | [8 empty] | 和順DS.1510_AMP_A | 道爺和順新化線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 161 | 161kV | 1520_AMP | 安南和順線 | [27 empty] | ADCS_S | [8 empty] | 和順DS.1520_AMP_A | 安南和順線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 161 | 161kV | 1540_AMP | 和順公學二路 | [27 empty] | ADCS_S | [8 empty] | 和順DS.1540_AMP_A | 和順公學二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D20//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D20//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D20//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D20//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 和順DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 111 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 和順DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 和順DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 和順DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 和順DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 和順DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 和順DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 和順DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 和順DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 119 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D20//3DTR/TR_PERM |  | DTR_PERM |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D20 | 和順DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0024 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D20/161/1BUS/V |  |  |  | DNP | 122 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0025 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D20/161/2BUS/V |  |  |  | DNP | 123 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D20 | 和順DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [14 empty] | 0051 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D20/11/1ABUS/V |  |  |  | DNP | 124 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [14 empty] | 0087 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D20/11/1BBUS/V |  |  |  | DNP | 125 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0118 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D20/11/2ABUS/V |  |  |  | DNP | 126 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0151 | [8 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D20/11/2BBUS/V |  |  |  | DNP | 127 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | MW | [14 empty] | 0002 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1510_MW | 道爺和順新化線 MW | LINE161 | D20/161/1510/MW |  |  |  | DNP | 128 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | MVAR | [14 empty] | 0003 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1510_MVAR | 道爺和順新化線 MVAR | LINE161 | D20/161/1510/MVAR |  |  |  | DNP | 129 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510LPD | 道爺和順新化線(1510) |  | V | [14 empty] | 0180 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1510LPD_KV | 道爺和順新化線(1510) LPD KV | LINE161 | D20/161/1510/V |  |  |  | DNP | 130 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | MW | [14 empty] | 0004 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1520_MW | 安南和順線 MW | LINE161 | D20/161/1520/MW |  |  |  | DNP | 131 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | MVAR | [14 empty] | 0005 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1520_MVAR | 安南和順線 MVAR | LINE161 | D20/161/1520/MVAR |  |  |  | DNP | 132 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1520LPD | 安南和順線(1520) |  | V | [14 empty] | 0181 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1520LPD_KV | 安南和順線(1520) LPD KV | LINE161 | D20/161/1520/V |  |  |  | DNP | 133 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | MW | [14 empty] | 0008 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1540_MW | 和順公學二路 MW | LINE161 | D20/161/1540/MW |  |  |  | DNP | 134 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | MVAR | [14 empty] | 0009 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1540_MVAR | 和順公學二路 MVAR | LINE161 | D20/161/1540/MVAR |  |  |  | DNP | 135 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1540LPD | 和順公學二路(1540) |  | V | [14 empty] | 0183 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1540LPD_KV | 和順公學二路(1540) LPD KV | LINE161 | D20/161/1540/V |  |  |  | DNP | 136 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D20 | 和順DS | 11 | 11kV | 和11線 | 和11線 |  | 和11線KVAR | [14 empty] | 0052 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和11線KVAR | 11KV和11線 KVAR | FEEDER | D20/11/4A11/KVAR |  |  |  | DNP | 137 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和11線 | 和11線 |  | 和11線A1 | [14 empty] | 0053 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和11線A1 | 11KV和11線 R相AMP | FEEDER | D20/11/4A11/I_R |  |  |  | DNP | 138 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和11線 | 和11線 |  | 和11線A2 | [14 empty] | 0054 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和11線A2 | 11KV和11線 S相AMP | FEEDER | D20/11/4A11/I_S |  |  |  | DNP | 139 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和11線 | 和11線 |  | 和11線A3 | [14 empty] | 0055 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和11線A3 | 11KV和11線 T相AMP | FEEDER | D20/11/4A11/I_T |  |  |  | DNP | 140 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和11線 | 和11線 |  | 和11線A0 | [14 empty] | 0056 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和11線A0 | 11KV和11線 N相AMP | FEEDER | D20/11/4A11/I_N |  |  |  | DNP | 141 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和12線 | 和12線 |  | 和12線KVAR | [14 empty] | 0057 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和12線KVAR | 11KV和12線 KVAR | FEEDER | D20/11/4A12/KVAR |  |  |  | DNP | 142 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和12線 | 和12線 |  | 和12線A1 | [14 empty] | 0058 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和12線A1 | 11KV和12線 R相AMP | FEEDER | D20/11/4A12/I_R |  |  |  | DNP | 143 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和12線 | 和12線 |  | 和12線A2 | [14 empty] | 0059 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和12線A2 | 11KV和12線 S相AMP | FEEDER | D20/11/4A12/I_S |  |  |  | DNP | 144 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和12線 | 和12線 |  | 和12線A3 | [14 empty] | 0060 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和12線A3 | 11KV和12線 T相AMP | FEEDER | D20/11/4A12/I_T |  |  |  | DNP | 145 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和12線 | 和12線 |  | 和12線A0 | [14 empty] | 0061 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和12線A0 | 11KV和12線 N相AMP | FEEDER | D20/11/4A12/I_N |  |  |  | DNP | 146 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和13線 | 和13線 |  | 和13線KVAR | [14 empty] | 0062 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和13線KVAR | 11KV和13線 KVAR | FEEDER | D20/11/4A13/KVAR |  |  |  | DNP | 147 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和13線 | 和13線 |  | 和13線A1 | [14 empty] | 0063 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和13線A1 | 11KV和13線 R相AMP | FEEDER | D20/11/4A13/I_R |  |  |  | DNP | 148 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和13線 | 和13線 |  | 和13線A2 | [14 empty] | 0066 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和13線A2 | 11KV和13線 S相AMP | FEEDER | D20/11/4A13/I_S |  |  |  | DNP | 149 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和13線 | 和13線 |  | 和13線A3 | [14 empty] | 0067 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和13線A3 | 11KV和13線 T相AMP | FEEDER | D20/11/4A13/I_T |  |  |  | DNP | 150 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和13線 | 和13線 |  | 和13線A0 | [14 empty] | 0068 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和13線A0 | 11KV和13線 N相AMP | FEEDER | D20/11/4A13/I_N |  |  |  | DNP | 151 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和14線 | 和14線 |  | 和14線KVAR | [14 empty] | 0069 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和14線KVAR | 11KV和14線 KVAR | FEEDER | D20/11/4A14/KVAR |  |  |  | DNP | 152 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和14線 | 和14線 |  | 和14線A1 | [14 empty] | 0070 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和14線A1 | 11KV和14線 R相AMP | FEEDER | D20/11/4A14/I_R |  |  |  | DNP | 153 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和14線 | 和14線 |  | 和14線A2 | [14 empty] | 0071 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和14線A2 | 11KV和14線 S相AMP | FEEDER | D20/11/4A14/I_S |  |  |  | DNP | 154 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和14線 | 和14線 |  | 和14線A3 | [14 empty] | 0072 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和14線A3 | 11KV和14線 T相AMP | FEEDER | D20/11/4A14/I_T |  |  |  | DNP | 155 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和14線 | 和14線 |  | 和14線A0 | [14 empty] | 0073 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和14線A0 | 11KV和14線 N相AMP | FEEDER | D20/11/4A14/I_N |  |  |  | DNP | 156 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和15線 | 和15線 |  | 和15線KVAR | [14 empty] | 0074 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和15線KVAR | 11KV和15線 KVAR | FEEDER | D20/11/4A15/KVAR |  |  |  | DNP | 157 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和15線 | 和15線 |  | 和15線A1 | [14 empty] | 0075 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和15線A1 | 11KV和15線 R相AMP | FEEDER | D20/11/4A15/I_R |  |  |  | DNP | 158 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和15線 | 和15線 |  | 和15線A2 | [14 empty] | 0076 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和15線A2 | 11KV和15線 S相AMP | FEEDER | D20/11/4A15/I_S |  |  |  | DNP | 159 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和15線 | 和15線 |  | 和15線A3 | [14 empty] | 0077 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和15線A3 | 11KV和15線 T相AMP | FEEDER | D20/11/4A15/I_T |  |  |  | DNP | 160 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和15線 | 和15線 |  | 和15線A0 | [14 empty] | 0078 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和15線A0 | 11KV和15線 N相AMP | FEEDER | D20/11/4A15/I_N |  |  |  | DNP | 161 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和16線 | 和16線 |  | 和16線KVAR | [14 empty] | 0088 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和16線KVAR | 11KV和16線 KVAR | FEEDER | D20/11/4A16/KVAR |  |  |  | DNP | 162 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和16線 | 和16線 |  | 和16線A1 | [14 empty] | 0089 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和16線A1 | 11KV和16線 R相AMP | FEEDER | D20/11/4A16/I_R |  |  |  | DNP | 163 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和16線 | 和16線 |  | 和16線A2 | [14 empty] | 0090 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和16線A2 | 11KV和16線 S相AMP | FEEDER | D20/11/4A16/I_S |  |  |  | DNP | 164 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和16線 | 和16線 |  | 和16線A3 | [14 empty] | 0091 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和16線A3 | 11KV和16線 T相AMP | FEEDER | D20/11/4A16/I_T |  |  |  | DNP | 165 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和16線 | 和16線 |  | 和16線A0 | [14 empty] | 0092 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和16線A0 | 11KV和16線 N相AMP | FEEDER | D20/11/4A16/I_N |  |  |  | DNP | 166 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和17線 | 和17線 |  | 和17線KVAR | [14 empty] | 0093 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和17線KVAR | 11KV和17線 KVAR | FEEDER | D20/11/4A17/KVAR |  |  |  | DNP | 167 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和17線 | 和17線 |  | 和17線A1 | [14 empty] | 0094 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和17線A1 | 11KV和17線 R相AMP | FEEDER | D20/11/4A17/I_R |  |  |  | DNP | 168 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和17線 | 和17線 |  | 和17線A2 | [14 empty] | 0095 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和17線A2 | 11KV和17線 S相AMP | FEEDER | D20/11/4A17/I_S |  |  |  | DNP | 169 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和17線 | 和17線 |  | 和17線A3 | [14 empty] | 0096 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和17線A3 | 11KV和17線 T相AMP | FEEDER | D20/11/4A17/I_T |  |  |  | DNP | 170 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和17線 | 和17線 |  | 和17線A0 | [14 empty] | 0097 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和17線A0 | 11KV和17線 N相AMP | FEEDER | D20/11/4A17/I_N |  |  |  | DNP | 171 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和18線 | 和18線 |  | 和18線KVAR | [14 empty] | 0098 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和18線KVAR | 11KV和18線 KVAR | FEEDER | D20/11/4A18/KVAR |  |  |  | DNP | 172 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和18線 | 和18線 |  | 和18線A1 | [14 empty] | 0099 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和18線A1 | 11KV和18線 R相AMP | FEEDER | D20/11/4A18/I_R |  |  |  | DNP | 173 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和18線 | 和18線 |  | 和18線A2 | [14 empty] | 0100 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和18線A2 | 11KV和18線 S相AMP | FEEDER | D20/11/4A18/I_S |  |  |  | DNP | 174 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和18線 | 和18線 |  | 和18線A3 | [14 empty] | 0101 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和18線A3 | 11KV和18線 T相AMP | FEEDER | D20/11/4A18/I_T |  |  |  | DNP | 175 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和18線 | 和18線 |  | 和18線A0 | [14 empty] | 0102 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和18線A0 | 11KV和18線 N相AMP | FEEDER | D20/11/4A18/I_N |  |  |  | DNP | 176 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和19線 | 和19線 |  | 和19線KVAR | [14 empty] | 0103 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和19線KVAR | 11KV和19線 KVAR | FEEDER | D20/11/4A19/KVAR |  |  |  | DNP | 177 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和19線 | 和19線 |  | 和19線A1 | [14 empty] | 0104 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和19線A1 | 11KV和19線 R相AMP | FEEDER | D20/11/4A19/I_R |  |  |  | DNP | 178 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和19線 | 和19線 |  | 和19線A2 | [14 empty] | 0105 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和19線A2 | 11KV和19線 S相AMP | FEEDER | D20/11/4A19/I_S |  |  |  | DNP | 179 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和19線 | 和19線 |  | 和19線A3 | [14 empty] | 0106 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和19線A3 | 11KV和19線 T相AMP | FEEDER | D20/11/4A19/I_T |  |  |  | DNP | 180 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和19線 | 和19線 |  | 和19線A0 | [14 empty] | 0107 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和19線A0 | 11KV和19線 N相AMP | FEEDER | D20/11/4A19/I_N |  |  |  | DNP | 181 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和20線 | 和20線 |  | 和20線KVAR | [14 empty] | 0108 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和20線KVAR | 11KV和20線 KVAR | FEEDER | D20/11/4A20/KVAR |  |  |  | DNP | 182 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和20線 | 和20線 |  | 和20線A1 | [14 empty] | 0109 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和20線A1 | 11KV和20線 R相AMP | FEEDER | D20/11/4A20/I_R |  |  |  | DNP | 183 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和20線 | 和20線 |  | 和20線A2 | [14 empty] | 0110 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和20線A2 | 11KV和20線 S相AMP | FEEDER | D20/11/4A20/I_S |  |  |  | DNP | 184 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和20線 | 和20線 |  | 和20線A3 | [14 empty] | 0111 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和20線A3 | 11KV和20線 T相AMP | FEEDER | D20/11/4A20/I_T |  |  |  | DNP | 185 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和20線 | 和20線 |  | 和20線A0 | [14 empty] | 0112 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和20線A0 | 11KV和20線 N相AMP | FEEDER | D20/11/4A20/I_N |  |  |  | DNP | 186 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和21線 | 和21線 |  | 和21線KVAR | [14 empty] | 0119 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和21線KVAR | 11KV和21線 KVAR | FEEDER | D20/11/4A21/KVAR |  |  |  | DNP | 187 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和21線 | 和21線 |  | 和21線A1 | [14 empty] | 0120 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和21線A1 | 11KV和21線 R相AMP | FEEDER | D20/11/4A21/I_R |  |  |  | DNP | 188 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和21線 | 和21線 |  | 和21線A2 | [14 empty] | 0121 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和21線A2 | 11KV和21線 S相AMP | FEEDER | D20/11/4A21/I_S |  |  |  | DNP | 189 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和21線 | 和21線 |  | 和21線A3 | [14 empty] | 0122 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和21線A3 | 11KV和21線 T相AMP | FEEDER | D20/11/4A21/I_T |  |  |  | DNP | 190 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和21線 | 和21線 |  | 和21線A0 | [14 empty] | 0123 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和21線A0 | 11KV和21線 N相AMP | FEEDER | D20/11/4A21/I_N |  |  |  | DNP | 191 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和22線 | 和22線 |  | 和22線KVAR | [14 empty] | 0124 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和22線KVAR | 11KV和22線 KVAR | FEEDER | D20/11/4A22/KVAR |  |  |  | DNP | 192 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和22線 | 和22線 |  | 和22線A1 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和22線A1 | 11KV和22線 R相AMP | FEEDER | D20/11/4A22/I_R |  |  |  | DNP | 193 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和22線 | 和22線 |  | 和22線A2 | [14 empty] | 0126 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和22線A2 | 11KV和22線 S相AMP | FEEDER | D20/11/4A22/I_S |  |  |  | DNP | 194 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和22線 | 和22線 |  | 和22線A3 | [14 empty] | 0127 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和22線A3 | 11KV和22線 T相AMP | FEEDER | D20/11/4A22/I_T |  |  |  | DNP | 195 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和22線 | 和22線 |  | 和22線A0 | [14 empty] | 0130 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和22線A0 | 11KV和22線 N相AMP | FEEDER | D20/11/4A22/I_N |  |  |  | DNP | 196 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和23線 | 和23線 |  | 和23線KVAR | [14 empty] | 0131 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和23線KVAR | 11KV和23線 KVAR | FEEDER | D20/11/4A23/KVAR |  |  |  | DNP | 197 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和23線 | 和23線 |  | 和23線A1 | [14 empty] | 0132 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和23線A1 | 11KV和23線 R相AMP | FEEDER | D20/11/4A23/I_R |  |  |  | DNP | 198 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和23線 | 和23線 |  | 和23線A2 | [14 empty] | 0133 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和23線A2 | 11KV和23線 S相AMP | FEEDER | D20/11/4A23/I_S |  |  |  | DNP | 199 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和23線 | 和23線 |  | 和23線A3 | [14 empty] | 0134 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和23線A3 | 11KV和23線 T相AMP | FEEDER | D20/11/4A23/I_T |  |  |  | DNP | 200 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和23線 | 和23線 |  | 和23線A0 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和23線A0 | 11KV和23線 N相AMP | FEEDER | D20/11/4A23/I_N |  |  |  | DNP | 201 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和24線 | 和24線 |  | 和24線KVAR | [14 empty] | 0136 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和24線KVAR | 11KV和24線 KVAR | FEEDER | D20/11/4A24/KVAR |  |  |  | DNP | 202 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和24線 | 和24線 |  | 和24線A1 | [14 empty] | 0137 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和24線A1 | 11KV和24線 R相AMP | FEEDER | D20/11/4A24/I_R |  |  |  | DNP | 203 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和24線 | 和24線 |  | 和24線A2 | [14 empty] | 0138 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和24線A2 | 11KV和24線 S相AMP | FEEDER | D20/11/4A24/I_S |  |  |  | DNP | 204 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和24線 | 和24線 |  | 和24線A3 | [14 empty] | 0139 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和24線A3 | 11KV和24線 T相AMP | FEEDER | D20/11/4A24/I_T |  |  |  | DNP | 205 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和24線 | 和24線 |  | 和24線A0 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和24線A0 | 11KV和24線 N相AMP | FEEDER | D20/11/4A24/I_N |  |  |  | DNP | 206 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和25線 | 和25線 |  | 和25線KVAR | [14 empty] | 0141 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和25線KVAR | 11KV和25線 KVAR | FEEDER | D20/11/4A25/KVAR |  |  |  | DNP | 207 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和25線 | 和25線 |  | 和25線A1 | [14 empty] | 0142 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和25線A1 | 11KV和25線 R相AMP | FEEDER | D20/11/4A25/I_R |  |  |  | DNP | 208 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和25線 | 和25線 |  | 和25線A2 | [14 empty] | 0143 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和25線A2 | 11KV和25線 S相AMP | FEEDER | D20/11/4A25/I_S |  |  |  | DNP | 209 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和25線 | 和25線 |  | 和25線A3 | [14 empty] | 0144 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和25線A3 | 11KV和25線 T相AMP | FEEDER | D20/11/4A25/I_T |  |  |  | DNP | 210 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和25線 | 和25線 |  | 和25線A0 | [14 empty] | 0145 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和25線A0 | 11KV和25線 N相AMP | FEEDER | D20/11/4A25/I_N |  |  |  | DNP | 211 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和26線 | 和26線 |  | 和26線KVAR | [14 empty] | 0152 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和26線KVAR | 11KV和26線 KVAR | FEEDER | D20/11/4A26/KVAR |  |  |  | DNP | 212 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和26線 | 和26線 |  | 和26線A1 | [14 empty] | 0153 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和26線A1 | 11KV和26線 R相AMP | FEEDER | D20/11/4A26/I_R |  |  |  | DNP | 213 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和26線 | 和26線 |  | 和26線A2 | [14 empty] | 0154 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和26線A2 | 11KV和26線 S相AMP | FEEDER | D20/11/4A26/I_S |  |  |  | DNP | 214 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和26線 | 和26線 |  | 和26線A3 | [14 empty] | 0155 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和26線A3 | 11KV和26線 T相AMP | FEEDER | D20/11/4A26/I_T |  |  |  | DNP | 215 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和26線 | 和26線 |  | 和26線A0 | [14 empty] | 0156 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和26線A0 | 11KV和26線 N相AMP | FEEDER | D20/11/4A26/I_N |  |  |  | DNP | 216 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和27線 | 和27線 |  | 和27線KVAR | [14 empty] | 0157 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和27線KVAR | 11KV和27線 KVAR | FEEDER | D20/11/4A27/KVAR |  |  |  | DNP | 217 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和27線 | 和27線 |  | 和27線A1 | [14 empty] | 0158 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和27線A1 | 11KV和27線 R相AMP | FEEDER | D20/11/4A27/I_R |  |  |  | DNP | 218 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和27線 | 和27線 |  | 和27線A2 | [14 empty] | 0159 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和27線A2 | 11KV和27線 S相AMP | FEEDER | D20/11/4A27/I_S |  |  |  | DNP | 219 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和27線 | 和27線 |  | 和27線A3 | [14 empty] | 0160 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和27線A3 | 11KV和27線 T相AMP | FEEDER | D20/11/4A27/I_T |  |  |  | DNP | 220 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和27線 | 和27線 |  | 和27線A0 | [14 empty] | 0161 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和27線A0 | 11KV和27線 N相AMP | FEEDER | D20/11/4A27/I_N |  |  |  | DNP | 221 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和28線 | 和28線 |  | 和28線KVAR | [14 empty] | 0162 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和28線KVAR | 11KV和28線 KVAR | FEEDER | D20/11/4A28/KVAR |  |  |  | DNP | 222 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和28線 | 和28線 |  | 和28線A1 | [14 empty] | 0163 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和28線A1 | 11KV和28線 R相AMP | FEEDER | D20/11/4A28/I_R |  |  |  | DNP | 223 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和28線 | 和28線 |  | 和28線A2 | [14 empty] | 0164 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和28線A2 | 11KV和28線 S相AMP | FEEDER | D20/11/4A28/I_S |  |  |  | DNP | 224 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和28線 | 和28線 |  | 和28線A3 | [14 empty] | 0165 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和28線A3 | 11KV和28線 T相AMP | FEEDER | D20/11/4A28/I_T |  |  |  | DNP | 225 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和28線 | 和28線 |  | 和28線A0 | [14 empty] | 0166 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和28線A0 | 11KV和28線 N相AMP | FEEDER | D20/11/4A28/I_N |  |  |  | DNP | 226 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和29線 | 和29線 |  | 和29線KVAR | [14 empty] | 0167 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和29線KVAR | 11KV和29線 KVAR | FEEDER | D20/11/4A29/KVAR |  |  |  | DNP | 227 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和29線 | 和29線 |  | 和29線A1 | [14 empty] | 0168 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和29線A1 | 11KV和29線 R相AMP | FEEDER | D20/11/4A29/I_R |  |  |  | DNP | 228 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和29線 | 和29線 |  | 和29線A2 | [14 empty] | 0169 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和29線A2 | 11KV和29線 S相AMP | FEEDER | D20/11/4A29/I_S |  |  |  | DNP | 229 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和29線 | 和29線 |  | 和29線A3 | [14 empty] | 0170 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和29線A3 | 11KV和29線 T相AMP | FEEDER | D20/11/4A29/I_T |  |  |  | DNP | 230 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和29線 | 和29線 |  | 和29線A0 | [14 empty] | 0171 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和29線A0 | 11KV和29線 N相AMP | FEEDER | D20/11/4A29/I_N |  |  |  | DNP | 231 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和30線 | 和30線 |  | 和30線KVAR | [14 empty] | 0172 | [8 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和30線KVAR | 11KV和30線 KVAR | FEEDER | D20/11/4A30/KVAR |  |  |  | DNP | 232 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和30線 | 和30線 |  | 和30線A1 | [14 empty] | 0173 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和30線A1 | 11KV和30線 R相AMP | FEEDER | D20/11/4A30/I_R |  |  |  | DNP | 233 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和30線 | 和30線 |  | 和30線A2 | [14 empty] | 0174 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和30線A2 | 11KV和30線 S相AMP | FEEDER | D20/11/4A30/I_S |  |  |  | DNP | 234 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和30線 | 和30線 |  | 和30線A3 | [14 empty] | 0175 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和30線A3 | 11KV和30線 T相AMP | FEEDER | D20/11/4A30/I_T |  |  |  | DNP | 235 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | 和30線 | 和30線 |  | 和30線A0 | [14 empty] | 0176 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和30線A0 | 11KV和30線 N相AMP | FEEDER | D20/11/4A30/I_N |  |  |  | DNP | 236 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0026 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.1500TIE_AMP | 1500TIE AMP | TIE | D20/161/1500/I_R |  |  |  | DNP | 237 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | _100 | 100 |  | I_R | [14 empty] | 0079 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D20/11/100/I_R |  |  |  | DNP | 238 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | _100 | 100 |  | I_S | [14 empty] | 0080 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D20/11/100/I_S |  |  |  | DNP | 239 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | _100 | 100 |  | I_T | [14 empty] | 0081 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D20/11/100/I_T |  |  |  | DNP | 240 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | _200 | 200 |  | I_R | [14 empty] | 0177 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D20/11/200/I_R |  |  |  | DNP | 241 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | _200 | 200 |  | I_S | [14 empty] | 0178 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D20/11/200/I_S |  |  |  | DNP | 242 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 11 | 11kV | _200 | 200 |  | I_T | [14 empty] | 0179 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D20/11/200/I_T |  |  |  | DNP | 243 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [14 empty] | 0046 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D20/11/310/KW |  |  |  | DNP | 244 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [14 empty] | 0047 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D20/11/310/KVAR |  |  |  | DNP | 245 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [14 empty] | 0048 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D20/11/310/I_R |  |  |  | DNP | 246 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [14 empty] | 0049 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D20/11/310/I_S |  |  |  | DNP | 247 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [14 empty] | 0050 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D20/11/310/I_T |  |  |  | DNP | 248 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [14 empty] | 0027 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR_OIL | #1DTR 油溫 | MTR | D20//1DTR/OilTemp |  |  |  | DNP | 249 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [14 empty] | 0028 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D20//1DTR(A)/CoilTemp |  |  |  | DNP | 250 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [14 empty] | 0030 |  | 0107 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D20//1DTR(A)/TapPosMv |  |  |  | DNP | 251 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [14 empty] | 0082 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D20/11/320/KW |  |  |  | DNP | 252 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [14 empty] | 0083 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D20/11/320/KVAR |  |  |  | DNP | 253 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [14 empty] | 0084 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D20/11/320/I_R |  |  |  | DNP | 254 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [14 empty] | 0085 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D20/11/320/I_S |  |  |  | DNP | 255 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [14 empty] | 0086 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D20/11/320/I_T |  |  |  | DNP | 256 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [14 empty] | 0029 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D20//1DTR(B)/CoilTemp |  |  |  | DNP | 257 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [14 empty] | 0031 |  | 0109 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D20//1DTR(B)/TapPosMv |  |  |  | DNP | 258 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0113 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D20/11/330/KW |  |  |  | DNP | 259 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0114 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D20/11/330/KVAR |  |  |  | DNP | 260 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0115 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D20/11/330/I_R |  |  |  | DNP | 261 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0116 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D20/11/330/I_S |  |  |  | DNP | 262 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0117 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D20/11/330/I_T |  |  |  | DNP | 263 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0032 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR_OIL | #2DTR 油溫 | MTR | D20//2DTR/OilTemp |  |  |  | DNP | 264 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [14 empty] | 0033 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D20//2DTR(A)/CoilTemp |  |  |  | DNP | 265 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [14 empty] | 0035 |  | 0111 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D20//2DTR(A)/TapPosMv |  |  |  | DNP | 266 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0146 | [8 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D20/11/340/KW |  |  |  | DNP | 267 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.054000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0147 | [8 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D20/11/340/KVAR |  |  |  | DNP | 268 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.036000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0148 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D20/11/340/I_R |  |  |  | DNP | 269 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0149 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D20/11/340/I_S |  |  |  | DNP | 270 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0150 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D20/11/340/I_T |  |  |  | DNP | 271 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [14 empty] | 0034 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D20//2DTR(B)/CoilTemp |  |  |  | DNP | 272 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [14 empty] | 0036 |  | 0113 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D20//2DTR(B)/TapPosMv |  |  |  | DNP | 273 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0023 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D20/0/StaDev/DCV_N |  |  |  | DNP | 274 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D20 | 和順DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0022 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D20/0/StaDev/DCV_P |  |  |  | DNP | 275 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI90%參考點 |  | ADCH1 | [14 empty] | 0001 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER | D20/0/RTU/ADCH1 |  |  |  | DNP | 276 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI90%參考點 |  | ADCH2 | [14 empty] | 0065 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER | D20/0/RTU/ADCH2 |  |  |  | DNP | 277 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI90%參考點 |  | ADCH3 | [14 empty] | 0129 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER | D20/0/RTU/ADCH3 |  |  |  | DNP | 278 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI90%參考點 |  | ADCH4 | [14 empty] | 0193 | [8 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER | D20/0/RTU/ADCH4 |  |  |  | DNP | 279 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI10%參考點 |  | ADCL1 | [14 empty] | 0000 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER | D20/0/RTU/ADCL1 |  |  |  | DNP | 280 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI10%參考點 |  | ADCL2 | [14 empty] | 0064 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER | D20/0/RTU/ADCL2 |  |  |  | DNP | 281 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI10%參考點 |  | ADCL3 | [14 empty] | 0128 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER | D20/0/RTU/ADCL3 |  |  |  | DNP | 282 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | AI | AI10%參考點 |  | ADCL4 | [14 empty] | 0192 | [8 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER | D20/0/RTU/ADCL4 |  |  |  | DNP | 283 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [14 empty] | 0190 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_MW | #3DTR二次側 MW | MTR | D20/22/350/KW |  |  |  | DNP | 284 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D20 | 和順DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [14 empty] | 0191 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D20/22/350/KVAR |  |  |  | DNP | 285 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D20 | 和順DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [14 empty] | 0194 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D20/22/350/I_R |  |  |  | DNP | 286 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [14 empty] | 0195 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D20/22/350/I_S |  |  |  | DNP | 287 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [14 empty] | 0196 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D20/22/350/I_T |  |  |  | DNP | 288 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [14 empty] | 0037 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_OIL | #3DTR 油溫 | MTR | D20//3DTR/OilTemp |  |  |  | DNP | 289 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [14 empty] | 0038 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_COIL | #3DTR 線溫 | MTR | D20//3DTR/CoilTemp |  |  |  | DNP | 290 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [14 empty] | 0039 |  | 0115 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 和順DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D20//3DTR/TapPosMv |  |  |  | DNP | 291 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D20 | 和順DS | 22 | 22kV | 3BUS | #3BUS |  | V | [14 empty] | 0197 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 和順DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D20/22/3BUS/V |  |  |  | DNP | 292 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D20 | 和順DS | 22 | 22kV | 和51線 | 和51線 |  | 和51線KVAR | [14 empty] | 0198 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和51線KVAR | 23KV和51線 KVAR | FEEDER | D20/22/4A51/KVAR |  |  |  | DNP | 293 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和51線 | 和51線 |  | 和51線A1 | [14 empty] | 0199 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和51線A1 | 23KV和51線 R相AMP | FEEDER | D20/22/4A51/I_R |  |  |  | DNP | 294 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和51線 | 和51線 |  | 和51線A2 | [14 empty] | 0200 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和51線A2 | 23KV和51線 S相AMP | FEEDER | D20/22/4A51/I_S |  |  |  | DNP | 295 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和51線 | 和51線 |  | 和51線A3 | [14 empty] | 0201 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和51線A3 | 23KV和51線 T相AMP | FEEDER | D20/22/4A51/I_T |  |  |  | DNP | 296 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和51線 | 和51線 |  | 和51線A0 | [14 empty] | 0202 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和51線A0 | 23KV和51線 N相AMP | FEEDER | D20/22/4A51/I_N |  |  |  | DNP | 297 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和52線 | 和52線 |  | 和52線KVAR | [14 empty] | 0203 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和52線KVAR | 23KV和52線 KVAR | FEEDER | D20/22/4A52/KVAR |  |  |  | DNP | 298 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和52線 | 和52線 |  | 和52線A1 | [14 empty] | 0204 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和52線A1 | 23KV和52線 R相AMP | FEEDER | D20/22/4A52/I_R |  |  |  | DNP | 299 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和52線 | 和52線 |  | 和52線A2 | [14 empty] | 0205 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和52線A2 | 23KV和52線 S相AMP | FEEDER | D20/22/4A52/I_S |  |  |  | DNP | 300 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和52線 | 和52線 |  | 和52線A3 | [14 empty] | 0206 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和52線A3 | 23KV和52線 T相AMP | FEEDER | D20/22/4A52/I_T |  |  |  | DNP | 301 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和52線 | 和52線 |  | 和52線A0 | [14 empty] | 0207 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和52線A0 | 23KV和52線 N相AMP | FEEDER | D20/22/4A52/I_N |  |  |  | DNP | 302 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和53線 | 和53線 |  | 和53線KVAR | [14 empty] | 0208 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和53線KVAR | 23KV和53線 KVAR | FEEDER | D20/22/4A53/KVAR |  |  |  | DNP | 303 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和53線 | 和53線 |  | 和53線A1 | [14 empty] | 0209 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和53線A1 | 23KV和53線 R相AMP | FEEDER | D20/22/4A53/I_R |  |  |  | DNP | 304 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和53線 | 和53線 |  | 和53線A2 | [14 empty] | 0210 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和53線A2 | 23KV和53線 S相AMP | FEEDER | D20/22/4A53/I_S |  |  |  | DNP | 305 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和53線 | 和53線 |  | 和53線A3 | [14 empty] | 0211 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和53線A3 | 23KV和53線 T相AMP | FEEDER | D20/22/4A53/I_T |  |  |  | DNP | 306 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和53線 | 和53線 |  | 和53線A0 | [14 empty] | 0212 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和53線A0 | 23KV和53線 N相AMP | FEEDER | D20/22/4A53/I_N |  |  |  | DNP | 307 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和54線 | 和54線 |  | 和54線KVAR | [14 empty] | 0213 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和54線KVAR | 23KV和54線 KVAR | FEEDER | D20/22/4A54/KVAR |  |  |  | DNP | 308 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和54線 | 和54線 |  | 和54線A1 | [14 empty] | 0214 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和54線A1 | 23KV和54線 R相AMP | FEEDER | D20/22/4A54/I_R |  |  |  | DNP | 309 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和54線 | 和54線 |  | 和54線A2 | [14 empty] | 0215 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和54線A2 | 23KV和54線 S相AMP | FEEDER | D20/22/4A54/I_S |  |  |  | DNP | 310 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和54線 | 和54線 |  | 和54線A3 | [14 empty] | 0216 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和54線A3 | 23KV和54線 T相AMP | FEEDER | D20/22/4A54/I_T |  |  |  | DNP | 311 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和54線 | 和54線 |  | 和54線A0 | [14 empty] | 0217 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和54線A0 | 23KV和54線 N相AMP | FEEDER | D20/22/4A54/I_N |  |  |  | DNP | 312 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和55線 | 和55線 |  | 和55線KVAR | [14 empty] | 0218 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和55線KVAR | 23KV和55線 KVAR | FEEDER | D20/22/4A55/KVAR |  |  |  | DNP | 313 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和55線 | 和55線 |  | 和55線A1 | [14 empty] | 0219 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和55線A1 | 23KV和55線 R相AMP | FEEDER | D20/22/4A55/I_R |  |  |  | DNP | 314 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和55線 | 和55線 |  | 和55線A2 | [14 empty] | 0220 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和55線A2 | 23KV和55線 S相AMP | FEEDER | D20/22/4A55/I_S |  |  |  | DNP | 315 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和55線 | 和55線 |  | 和55線A3 | [14 empty] | 0221 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和55線A3 | 23KV和55線 T相AMP | FEEDER | D20/22/4A55/I_T |  |  |  | DNP | 316 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和55線 | 和55線 |  | 和55線A0 | [14 empty] | 0222 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和55線A0 | 23KV和55線 N相AMP | FEEDER | D20/22/4A55/I_N |  |  |  | DNP | 317 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和56線 | 和56線 |  | 和56線KVAR | [14 empty] | 0223 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和56線KVAR | 23KV和56線 KVAR | FEEDER | D20/22/4A56/KVAR |  |  |  | DNP | 318 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和56線 | 和56線 |  | 和56線A1 | [14 empty] | 0224 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和56線A1 | 23KV和56線 R相AMP | FEEDER | D20/22/4A56/I_R |  |  |  | DNP | 319 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和56線 | 和56線 |  | 和56線A2 | [14 empty] | 0225 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和56線A2 | 23KV和56線 S相AMP | FEEDER | D20/22/4A56/I_S |  |  |  | DNP | 320 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和56線 | 和56線 |  | 和56線A3 | [14 empty] | 0226 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和56線A3 | 23KV和56線 T相AMP | FEEDER | D20/22/4A56/I_T |  |  |  | DNP | 321 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和56線 | 和56線 |  | 和56線A0 | [14 empty] | 0227 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和56線A0 | 23KV和56線 N相AMP | FEEDER | D20/22/4A56/I_N |  |  |  | DNP | 322 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和57線 | 和57線 |  | 和57線KVAR | [14 empty] | 0228 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和57線KVAR | 23KV和57線 KVAR | FEEDER | D20/22/4A57/KVAR |  |  |  | DNP | 323 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和57線 | 和57線 |  | 和57線A1 | [14 empty] | 0229 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和57線A1 | 23KV和57線 R相AMP | FEEDER | D20/22/4A57/I_R |  |  |  | DNP | 324 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和57線 | 和57線 |  | 和57線A2 | [14 empty] | 0230 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和57線A2 | 23KV和57線 S相AMP | FEEDER | D20/22/4A57/I_S |  |  |  | DNP | 325 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和57線 | 和57線 |  | 和57線A3 | [14 empty] | 0231 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和57線A3 | 23KV和57線 T相AMP | FEEDER | D20/22/4A57/I_T |  |  |  | DNP | 326 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和57線 | 和57線 |  | 和57線A0 | [14 empty] | 0232 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和57線A0 | 23KV和57線 N相AMP | FEEDER | D20/22/4A57/I_N |  |  |  | DNP | 327 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和58線 | 和58線 |  | 和58線KVAR | [14 empty] | 0233 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和58線KVAR | 23KV和58線 KVAR | FEEDER | D20/22/4A58/KVAR |  |  |  | DNP | 328 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和58線 | 和58線 |  | 和58線A1 | [14 empty] | 0234 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和58線A1 | 23KV和58線 R相AMP | FEEDER | D20/22/4A58/I_R |  |  |  | DNP | 329 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R450R | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和58線 | 和58線 |  | 和58線A2 | [14 empty] | 0235 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和58線A2 | 23KV和58線 S相AMP | FEEDER | D20/22/4A58/I_S |  |  |  | DNP | 330 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和58線 | 和58線 |  | 和58線A3 | [14 empty] | 0236 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和58線A3 | 23KV和58線 T相AMP | FEEDER | D20/22/4A58/I_T |  |  |  | DNP | 331 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | C06R0450 | 405.000000 | 405.000000 | 450.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 22 | 22kV | 和58線 | 和58線 |  | 和58線A0 | [14 empty] | 0237 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 和順DS.和58線A0 | 23KV和58線 N相AMP | FEEDER | D20/22/4A58/I_N |  |  |  | DNP | 332 | DNPAIPoint | DS050 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | PHA | [14 empty] | 0003 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1510_PHA | 道爺和順新化線(1510) 相間RY | LINE161 | D20/161/1510/PHA |  |  |  | DNP | 333 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | GDA | [14 empty] | 0004 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1510_GDA | 道爺和順新化線(1510) 接地RY | LINE161 | D20/161/1510/GDA |  |  |  | DNP | 334 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | 87A | [14 empty] | 0001 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1510_87A | 道爺和順新化線(1510) 87RY | LINE161 | D20/161/1510/87A1 |  |  |  | DNP | 335 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | 87UL | [14 empty] | 0323 |  | 0076 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1510_87UL | 道爺和順新化線(1510) 87RY U/L | LINE161 | D20/161/1510/87UL |  |  |  | DNP | 336 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | CB | [14 empty] | 0000 |  | 0001 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1510_CB | 1510(道爺和順新化線) CB | LINE161 | D20/161/1510/CB |  |  |  | DNP | 337 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | 79UL | [14 empty] | 0325 |  | 0078 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1510_79UL | 道爺和順新化線(1510) 79RY U/L | LINE161 | D20/161/1510/79UL |  |  |  | DNP | 338 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | DS1 | 1511 | [13 empty] | 0448 | 449 | 0120 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1511_DS | 1511(道爺和順新化線) DS | LINE161 | D20/161/1510/DS1 |  |  |  | DNP | 339 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | DS2 | 1512 | [13 empty] | 0450 | 451 | 0121 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1512_DS | 1512(道爺和順新化線) DS | LINE161 | D20/161/1510/DS2 |  |  |  | DNP | 340 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | DS3 | 1513 | [13 empty] | 0452 | 453 | 0122 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1513_DS | 1513(道爺和順新化線) DS | LINE161 | D20/161/1510/DS3 |  |  |  | DNP | 341 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | E3 | 1513E | [13 empty] | 0454 | 455 | 0123 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1513E_ES | 1513E(道爺和順新化線) ES | LINE161 | D20/161/1510/ES3 |  |  |  | DNP | 342 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | PHA | [14 empty] | 0008 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1520_PHA | 安南和順線(1520) 相間RY | LINE161 | D20/161/1520/PHA |  |  |  | DNP | 343 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | GDA | [14 empty] | 0009 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1520_GDA | 安南和順線(1520) 接地RY | LINE161 | D20/161/1520/GDA |  |  |  | DNP | 344 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | 87A | [14 empty] | 0006 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1520_87A | 安南和順線(1520) 87RY | LINE161 | D20/161/1520/87A1 |  |  |  | DNP | 345 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | 87UL | [14 empty] | 0326 |  | 0079 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1520_87UL | 安南和順線(1520) 87RY U/L | LINE161 | D20/161/1520/87UL |  |  |  | DNP | 346 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | CB | [14 empty] | 0005 |  | 0002 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1520_CB | 1520(安南和順線) CB | LINE161 | D20/161/1520/CB |  |  |  | DNP | 347 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | 79UL | [14 empty] | 0328 |  | 0081 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1520_79UL | 安南和順線(1520) 79RY U/L | LINE161 | D20/161/1520/79UL |  |  |  | DNP | 348 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | DS1 | 1521 | [13 empty] | 0456 | 457 | 0124 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1521_DS | 1521(安南和順線) DS | LINE161 | D20/161/1520/DS1 |  |  |  | DNP | 349 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | DS2 | 1522 | [13 empty] | 0458 | 459 | 0125 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1522_DS | 1522(安南和順線) DS | LINE161 | D20/161/1520/DS2 |  |  |  | DNP | 350 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | DS3 | 1523 | [13 empty] | 0460 | 461 | 0126 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1523_DS | 1523(安南和順線) DS | LINE161 | D20/161/1520/DS3 |  |  |  | DNP | 351 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | E3 | 1523E | [13 empty] | 0462 | 463 | 0127 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1523E_ES | 1523E(安南和順線) ES | LINE161 | D20/161/1520/ES3 |  |  |  | DNP | 352 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | PHA | [14 empty] | 0018 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1540_PHA | 和順公學二路(1540) 相間RY | LINE161 | D20/161/1540/PHA |  |  |  | DNP | 353 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | GDA | [14 empty] | 0019 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1540_GDA | 和順公學二路(1540) 接地RY | LINE161 | D20/161/1540/GDA |  |  |  | DNP | 354 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 87A | [14 empty] | 0016 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1540_87A | 和順公學二路(1540) 87RY | LINE161 | D20/161/1540/87A1 |  |  |  | DNP | 355 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 87UL | [14 empty] | 0332 |  | 0085 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1540_87UL | 和順公學二路(1540) 87RY U/L | LINE161 | D20/161/1540/87UL |  |  |  | DNP | 356 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | CB | [14 empty] | 0015 |  | 0004 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1540_CB | 1540(和順公學二路) CB | LINE161 | D20/161/1540/CB |  |  |  | DNP | 357 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | 79UL | [14 empty] | 0334 |  | 0087 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1540_79UL | 和順公學二路(1540) 79RY U/L | LINE161 | D20/161/1540/79UL |  |  |  | DNP | 358 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | DS1 | 1541 | [13 empty] | 0472 | 473 | 0132 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1541_DS | 1541(和順公學二路) DS | LINE161 | D20/161/1540/DS1 |  |  |  | DNP | 359 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | DS2 | 1542 | [13 empty] | 0474 | 475 | 0133 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1542_DS | 1542(和順公學二路) DS | LINE161 | D20/161/1540/DS2 |  |  |  | DNP | 360 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | DS3 | 1543 | [13 empty] | 0476 | 477 | 0134 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1543_DS | 1543(和順公學二路) DS | LINE161 | D20/161/1540/DS3 |  |  |  | DNP | 361 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | E3 | 1543E | [13 empty] | 0478 | 479 | 0135 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1543E_ES | 1543E(和順公學二路) ES | LINE161 | D20/161/1540/ES3 |  |  |  | DNP | 362 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | PHA | [14 empty] | 0164 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_PHA | 11KV和11線(4A11) 相間RY | FEEDER | D20/11/4A11/PHA |  |  |  | DNP | 363 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) |  | GDA | [14 empty] | 0165 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_GDA | 11KV和11線(4A11) 接地RY | FEEDER | D20/11/4A11/GDA |  |  |  | DNP | 364 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線(4A11) 79RY |  | 79UL | [14 empty] | 0576 |  | 0172 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_79UL | 11KV和11線(4A11) 79RY U/L | FEEDER | D20/11/4A11/79UL |  |  |  | DNP | 365 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A11_LCO | 和11線(4A11) LCO |  | TapPosMv | [14 empty] | 0577 |  | 0173 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_LCO_TAP | 11KV和11線(4A11) LCO TAP | FEEDER | D20/11/4A11/ADJ |  |  |  | DNP | 366 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A11 | 和11線 |  | CB | [14 empty] | 0163 |  | 0019 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_CB | 4A11(11KV和11線) CB | FEEDER | D20/11/4A11/CB |  |  |  | DNP | 367 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | PHA | [14 empty] | 0167 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_PHA | 11KV和12線(4A12) 相間RY | FEEDER | D20/11/4A12/PHA |  |  |  | DNP | 368 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) |  | GDA | [14 empty] | 0168 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_GDA | 11KV和12線(4A12) 接地RY | FEEDER | D20/11/4A12/GDA |  |  |  | DNP | 369 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線(4A12) 79RY |  | 79UL | [14 empty] | 0578 |  | 0174 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_79UL | 11KV和12線(4A12) 79RY U/L | FEEDER | D20/11/4A12/79UL |  |  |  | DNP | 370 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A12_LCO | 和12線(4A12) LCO |  | TapPosMv | [14 empty] | 0579 |  | 0175 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_LCO_TAP | 11KV和12線(4A12) LCO TAP | FEEDER | D20/11/4A12/ADJ |  |  |  | DNP | 371 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A12 | 和12線 |  | CB | [14 empty] | 0166 |  | 0020 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_CB | 4A12(11KV和12線) CB | FEEDER | D20/11/4A12/CB |  |  |  | DNP | 372 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | PHA | [14 empty] | 0170 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_PHA | 11KV和13線(4A13) 相間RY | FEEDER | D20/11/4A13/PHA |  |  |  | DNP | 373 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) |  | GDA | [14 empty] | 0171 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_GDA | 11KV和13線(4A13) 接地RY | FEEDER | D20/11/4A13/GDA |  |  |  | DNP | 374 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線(4A13) 79RY |  | 79UL | [14 empty] | 0580 |  | 0176 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_79UL | 11KV和13線(4A13) 79RY U/L | FEEDER | D20/11/4A13/79UL |  |  |  | DNP | 375 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A13_LCO | 和13線(4A13) LCO |  | TapPosMv | [14 empty] | 0581 |  | 0177 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_LCO_TAP | 11KV和13線(4A13) LCO TAP | FEEDER | D20/11/4A13/ADJ |  |  |  | DNP | 376 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A13 | 和13線 |  | CB | [14 empty] | 0169 |  | 0021 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_CB | 4A13(11KV和13線) CB | FEEDER | D20/11/4A13/CB |  |  |  | DNP | 377 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | PHA | [14 empty] | 0173 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_PHA | 11KV和14線(4A14) 相間RY | FEEDER | D20/11/4A14/PHA |  |  |  | DNP | 378 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) |  | GDA | [14 empty] | 0174 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_GDA | 11KV和14線(4A14) 接地RY | FEEDER | D20/11/4A14/GDA |  |  |  | DNP | 379 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線(4A14) 79RY |  | 79UL | [14 empty] | 0582 |  | 0178 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_79UL | 11KV和14線(4A14) 79RY U/L | FEEDER | D20/11/4A14/79UL |  |  |  | DNP | 380 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A14_LCO | 和14線(4A14) LCO |  | TapPosMv | [14 empty] | 0583 |  | 0179 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_LCO_TAP | 11KV和14線(4A14) LCO TAP | FEEDER | D20/11/4A14/ADJ |  |  |  | DNP | 381 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A14 | 和14線 |  | CB | [14 empty] | 0172 |  | 0022 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_CB | 4A14(11KV和14線) CB | FEEDER | D20/11/4A14/CB |  |  |  | DNP | 382 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | PHA | [14 empty] | 0176 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_PHA | 11KV和15線(4A15) 相間RY | FEEDER | D20/11/4A15/PHA |  |  |  | DNP | 383 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) |  | GDA | [14 empty] | 0177 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_GDA | 11KV和15線(4A15) 接地RY | FEEDER | D20/11/4A15/GDA |  |  |  | DNP | 384 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線(4A15) 79RY |  | 79UL | [14 empty] | 0584 |  | 0180 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_79UL | 11KV和15線(4A15) 79RY U/L | FEEDER | D20/11/4A15/79UL |  |  |  | DNP | 385 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A15_LCO | 和15線(4A15) LCO |  | TapPosMv | [14 empty] | 0585 |  | 0181 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_LCO_TAP | 11KV和15線(4A15) LCO TAP | FEEDER | D20/11/4A15/ADJ |  |  |  | DNP | 386 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A15 | 和15線 |  | CB | [14 empty] | 0175 |  | 0023 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_CB | 4A15(11KV和15線) CB | FEEDER | D20/11/4A15/CB |  |  |  | DNP | 387 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | PHA | [14 empty] | 0188 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_PHA | 11KV和16線(4A16) 相間RY | FEEDER | D20/11/4A16/PHA |  |  |  | DNP | 388 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) |  | GDA | [14 empty] | 0189 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_GDA | 11KV和16線(4A16) 接地RY | FEEDER | D20/11/4A16/GDA |  |  |  | DNP | 389 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線(4A16) 79RY |  | 79UL | [14 empty] | 0586 |  | 0182 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_79UL | 11KV和16線(4A16) 79RY U/L | FEEDER | D20/11/4A16/79UL |  |  |  | DNP | 390 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A16_LCO | 和16線(4A16) LCO |  | TapPosMv | [14 empty] | 0587 |  | 0183 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_LCO_TAP | 11KV和16線(4A16) LCO TAP | FEEDER | D20/11/4A16/ADJ |  |  |  | DNP | 391 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A16 | 和16線 |  | CB | [14 empty] | 0187 |  | 0029 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_CB | 4A16(11KV和16線) CB | FEEDER | D20/11/4A16/CB |  |  |  | DNP | 392 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | PHA | [14 empty] | 0191 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_PHA | 11KV和17線(4A17) 相間RY | FEEDER | D20/11/4A17/PHA |  |  |  | DNP | 393 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) |  | GDA | [14 empty] | 0192 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_GDA | 11KV和17線(4A17) 接地RY | FEEDER | D20/11/4A17/GDA |  |  |  | DNP | 394 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線(4A17) 79RY |  | 79UL | [14 empty] | 0588 |  | 0184 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_79UL | 11KV和17線(4A17) 79RY U/L | FEEDER | D20/11/4A17/79UL |  |  |  | DNP | 395 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A17_LCO | 和17線(4A17) LCO |  | TapPosMv | [14 empty] | 0589 |  | 0185 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_LCO_TAP | 11KV和17線(4A17) LCO TAP | FEEDER | D20/11/4A17/ADJ |  |  |  | DNP | 396 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A17 | 和17線 |  | CB | [14 empty] | 0190 |  | 0030 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_CB | 4A17(11KV和17線) CB | FEEDER | D20/11/4A17/CB |  |  |  | DNP | 397 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | PHA | [14 empty] | 0194 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_PHA | 11KV和18線(4A18) 相間RY | FEEDER | D20/11/4A18/PHA |  |  |  | DNP | 398 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) |  | GDA | [14 empty] | 0195 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_GDA | 11KV和18線(4A18) 接地RY | FEEDER | D20/11/4A18/GDA |  |  |  | DNP | 399 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線(4A18) 79RY |  | 79UL | [14 empty] | 0590 |  | 0186 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_79UL | 11KV和18線(4A18) 79RY U/L | FEEDER | D20/11/4A18/79UL |  |  |  | DNP | 400 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A18_LCO | 和18線(4A18) LCO |  | TapPosMv | [14 empty] | 0591 |  | 0187 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_LCO_TAP | 11KV和18線(4A18) LCO TAP | FEEDER | D20/11/4A18/ADJ |  |  |  | DNP | 401 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A18 | 和18線 |  | CB | [14 empty] | 0193 |  | 0031 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_CB | 4A18(11KV和18線) CB | FEEDER | D20/11/4A18/CB |  |  |  | DNP | 402 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | PHA | [14 empty] | 0197 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_PHA | 11KV和19線(4A19) 相間RY | FEEDER | D20/11/4A19/PHA |  |  |  | DNP | 403 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) |  | GDA | [14 empty] | 0198 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_GDA | 11KV和19線(4A19) 接地RY | FEEDER | D20/11/4A19/GDA |  |  |  | DNP | 404 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線(4A19) 79RY |  | 79UL | [14 empty] | 0592 |  | 0188 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_79UL | 11KV和19線(4A19) 79RY U/L | FEEDER | D20/11/4A19/79UL |  |  |  | DNP | 405 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A19_LCO | 和19線(4A19) LCO |  | TapPosMv | [14 empty] | 0593 |  | 0189 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_LCO_TAP | 11KV和19線(4A19) LCO TAP | FEEDER | D20/11/4A19/ADJ |  |  |  | DNP | 406 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A19 | 和19線 |  | CB | [14 empty] | 0196 |  | 0032 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_CB | 4A19(11KV和19線) CB | FEEDER | D20/11/4A19/CB |  |  |  | DNP | 407 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | PHA | [14 empty] | 0200 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_PHA | 11KV和20線(4A20) 相間RY | FEEDER | D20/11/4A20/PHA |  |  |  | DNP | 408 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) |  | GDA | [14 empty] | 0201 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_GDA | 11KV和20線(4A20) 接地RY | FEEDER | D20/11/4A20/GDA |  |  |  | DNP | 409 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線(4A20) 79RY |  | 79UL | [14 empty] | 0594 |  | 0190 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_79UL | 11KV和20線(4A20) 79RY U/L | FEEDER | D20/11/4A20/79UL |  |  |  | DNP | 410 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A20_LCO | 和20線(4A20) LCO |  | TapPosMv | [14 empty] | 0595 |  | 0191 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_LCO_TAP | 11KV和20線(4A20) LCO TAP | FEEDER | D20/11/4A20/ADJ |  |  |  | DNP | 411 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A20 | 和20線 |  | CB | [14 empty] | 0199 |  | 0033 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_CB | 4A20(11KV和20線) CB | FEEDER | D20/11/4A20/CB |  |  |  | DNP | 412 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | PHA | [14 empty] | 0208 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_PHA | 11KV和21線(4A21) 相間RY | FEEDER | D20/11/4A21/PHA |  |  |  | DNP | 413 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) |  | GDA | [14 empty] | 0209 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_GDA | 11KV和21線(4A21) 接地RY | FEEDER | D20/11/4A21/GDA |  |  |  | DNP | 414 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線(4A21) 79RY |  | 79UL | [14 empty] | 0596 |  | 0192 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_79UL | 11KV和21線(4A21) 79RY U/L | FEEDER | D20/11/4A21/79UL |  |  |  | DNP | 415 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A21_LCO | 和21線(4A21) LCO |  | TapPosMv | [14 empty] | 0597 |  | 0193 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_LCO_TAP | 11KV和21線(4A21) LCO TAP | FEEDER | D20/11/4A21/ADJ |  |  |  | DNP | 416 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A21 | 和21線 |  | CB | [14 empty] | 0207 |  | 0037 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_CB | 4A21(11KV和21線) CB | FEEDER | D20/11/4A21/CB |  |  |  | DNP | 417 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | PHA | [14 empty] | 0211 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_PHA | 11KV和22線(4A22) 相間RY | FEEDER | D20/11/4A22/PHA |  |  |  | DNP | 418 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) |  | GDA | [14 empty] | 0212 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_GDA | 11KV和22線(4A22) 接地RY | FEEDER | D20/11/4A22/GDA |  |  |  | DNP | 419 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線(4A22) 79RY |  | 79UL | [14 empty] | 0598 |  | 0194 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_79UL | 11KV和22線(4A22) 79RY U/L | FEEDER | D20/11/4A22/79UL |  |  |  | DNP | 420 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A22_LCO | 和22線(4A22) LCO |  | TapPosMv | [14 empty] | 0599 |  | 0195 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_LCO_TAP | 11KV和22線(4A22) LCO TAP | FEEDER | D20/11/4A22/ADJ |  |  |  | DNP | 421 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A22 | 和22線 |  | CB | [14 empty] | 0210 |  | 0038 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_CB | 4A22(11KV和22線) CB | FEEDER | D20/11/4A22/CB |  |  |  | DNP | 422 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | PHA | [14 empty] | 0214 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_PHA | 11KV和23線(4A23) 相間RY | FEEDER | D20/11/4A23/PHA |  |  |  | DNP | 423 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) |  | GDA | [14 empty] | 0215 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_GDA | 11KV和23線(4A23) 接地RY | FEEDER | D20/11/4A23/GDA |  |  |  | DNP | 424 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線(4A23) 79RY |  | 79UL | [14 empty] | 0600 |  | 0196 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_79UL | 11KV和23線(4A23) 79RY U/L | FEEDER | D20/11/4A23/79UL |  |  |  | DNP | 425 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A23_LCO | 和23線(4A23) LCO |  | TapPosMv | [14 empty] | 0601 |  | 0197 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_LCO_TAP | 11KV和23線(4A23) LCO TAP | FEEDER | D20/11/4A23/ADJ |  |  |  | DNP | 426 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A23 | 和23線 |  | CB | [14 empty] | 0213 |  | 0039 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_CB | 4A23(11KV和23線) CB | FEEDER | D20/11/4A23/CB |  |  |  | DNP | 427 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | PHA | [14 empty] | 0217 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_PHA | 11KV和24線(4A24) 相間RY | FEEDER | D20/11/4A24/PHA |  |  |  | DNP | 428 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) |  | GDA | [14 empty] | 0218 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_GDA | 11KV和24線(4A24) 接地RY | FEEDER | D20/11/4A24/GDA |  |  |  | DNP | 429 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線(4A24) 79RY |  | 79UL | [14 empty] | 0602 |  | 0198 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_79UL | 11KV和24線(4A24) 79RY U/L | FEEDER | D20/11/4A24/79UL |  |  |  | DNP | 430 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A24_LCO | 和24線(4A24) LCO |  | TapPosMv | [14 empty] | 0603 |  | 0199 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_LCO_TAP | 11KV和24線(4A24) LCO TAP | FEEDER | D20/11/4A24/ADJ |  |  |  | DNP | 431 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A24 | 和24線 |  | CB | [14 empty] | 0216 |  | 0040 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_CB | 4A24(11KV和24線) CB | FEEDER | D20/11/4A24/CB |  |  |  | DNP | 432 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | PHA | [14 empty] | 0220 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_PHA | 11KV和25線(4A25) 相間RY | FEEDER | D20/11/4A25/PHA |  |  |  | DNP | 433 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) |  | GDA | [14 empty] | 0221 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_GDA | 11KV和25線(4A25) 接地RY | FEEDER | D20/11/4A25/GDA |  |  |  | DNP | 434 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線(4A25) 79RY |  | 79UL | [14 empty] | 0604 |  | 0200 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_79UL | 11KV和25線(4A25) 79RY U/L | FEEDER | D20/11/4A25/79UL |  |  |  | DNP | 435 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A25_LCO | 和25線(4A25) LCO |  | TapPosMv | [14 empty] | 0605 |  | 0201 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_LCO_TAP | 11KV和25線(4A25) LCO TAP | FEEDER | D20/11/4A25/ADJ |  |  |  | DNP | 436 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A25 | 和25線 |  | CB | [14 empty] | 0219 |  | 0041 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_CB | 4A25(11KV和25線) CB | FEEDER | D20/11/4A25/CB |  |  |  | DNP | 437 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | PHA | [14 empty] | 0226 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_PHA | 11KV和26線(4A26) 相間RY | FEEDER | D20/11/4A26/PHA |  |  |  | DNP | 438 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) |  | GDA | [14 empty] | 0227 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_GDA | 11KV和26線(4A26) 接地RY | FEEDER | D20/11/4A26/GDA |  |  |  | DNP | 439 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線(4A26) 79RY |  | 79UL | [14 empty] | 0606 |  | 0202 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_79UL | 11KV和26線(4A26) 79RY U/L | FEEDER | D20/11/4A26/79UL |  |  |  | DNP | 440 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A26_LCO | 和26線(4A26) LCO |  | TapPosMv | [14 empty] | 0607 |  | 0203 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_LCO_TAP | 11KV和26線(4A26) LCO TAP | FEEDER | D20/11/4A26/ADJ |  |  |  | DNP | 441 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A26 | 和26線 |  | CB | [14 empty] | 0225 |  | 0045 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_CB | 4A26(11KV和26線) CB | FEEDER | D20/11/4A26/CB |  |  |  | DNP | 442 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | PHA | [14 empty] | 0229 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_PHA | 11KV和27線(4A27) 相間RY | FEEDER | D20/11/4A27/PHA |  |  |  | DNP | 443 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) |  | GDA | [14 empty] | 0230 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_GDA | 11KV和27線(4A27) 接地RY | FEEDER | D20/11/4A27/GDA |  |  |  | DNP | 444 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線(4A27) 79RY |  | 79UL | [14 empty] | 0608 |  | 0204 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_79UL | 11KV和27線(4A27) 79RY U/L | FEEDER | D20/11/4A27/79UL |  |  |  | DNP | 445 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A27_LCO | 和27線(4A27) LCO |  | TapPosMv | [14 empty] | 0609 |  | 0205 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_LCO_TAP | 11KV和27線(4A27) LCO TAP | FEEDER | D20/11/4A27/ADJ |  |  |  | DNP | 446 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A27 | 和27線 |  | CB | [14 empty] | 0228 |  | 0046 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_CB | 4A27(11KV和27線) CB | FEEDER | D20/11/4A27/CB |  |  |  | DNP | 447 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | PHA | [14 empty] | 0232 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_PHA | 11KV和28線(4A28) 相間RY | FEEDER | D20/11/4A28/PHA |  |  |  | DNP | 448 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) |  | GDA | [14 empty] | 0233 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_GDA | 11KV和28線(4A28) 接地RY | FEEDER | D20/11/4A28/GDA |  |  |  | DNP | 449 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線(4A28) 79RY |  | 79UL | [14 empty] | 0610 |  | 0206 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_79UL | 11KV和28線(4A28) 79RY U/L | FEEDER | D20/11/4A28/79UL |  |  |  | DNP | 450 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A28_LCO | 和28線(4A28) LCO |  | TapPosMv | [14 empty] | 0611 |  | 0207 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_LCO_TAP | 11KV和28線(4A28) LCO TAP | FEEDER | D20/11/4A28/ADJ |  |  |  | DNP | 451 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A28 | 和28線 |  | CB | [14 empty] | 0231 |  | 0047 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_CB | 4A28(11KV和28線) CB | FEEDER | D20/11/4A28/CB |  |  |  | DNP | 452 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | PHA | [14 empty] | 0235 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_PHA | 11KV和29線(4A29) 相間RY | FEEDER | D20/11/4A29/PHA |  |  |  | DNP | 453 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) |  | GDA | [14 empty] | 0236 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_GDA | 11KV和29線(4A29) 接地RY | FEEDER | D20/11/4A29/GDA |  |  |  | DNP | 454 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線(4A29) 79RY |  | 79UL | [14 empty] | 0612 |  | 0208 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_79UL | 11KV和29線(4A29) 79RY U/L | FEEDER | D20/11/4A29/79UL |  |  |  | DNP | 455 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A29_LCO | 和29線(4A29) LCO |  | TapPosMv | [14 empty] | 0613 |  | 0209 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_LCO_TAP | 11KV和29線(4A29) LCO TAP | FEEDER | D20/11/4A29/ADJ |  |  |  | DNP | 456 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A29 | 和29線 |  | CB | [14 empty] | 0234 |  | 0048 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_CB | 4A29(11KV和29線) CB | FEEDER | D20/11/4A29/CB |  |  |  | DNP | 457 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | PHA | [14 empty] | 0238 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_PHA | 11KV和30線(4A30) 相間RY | FEEDER | D20/11/4A30/PHA |  |  |  | DNP | 458 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) |  | GDA | [14 empty] | 0239 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_GDA | 11KV和30線(4A30) 接地RY | FEEDER | D20/11/4A30/GDA |  |  |  | DNP | 459 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線(4A30) 79RY |  | 79UL | [14 empty] | 0614 |  | 0210 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_79UL | 11KV和30線(4A30) 79RY U/L | FEEDER | D20/11/4A30/79UL |  |  |  | DNP | 460 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 11 | 11kV | 4A30_LCO | 和30線(4A30) LCO |  | TapPosMv | [14 empty] | 0615 |  | 0211 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_LCO_TAP | 11KV和30線(4A30) LCO TAP | FEEDER | D20/11/4A30/ADJ |  |  |  | DNP | 461 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 11 | 11kV | 4A30 | 和30線 |  | CB | [14 empty] | 0237 |  | 0049 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_CB | 4A30(11KV和30線) CB | FEEDER | D20/11/4A30/CB |  |  |  | DNP | 462 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0181 |  | 0025 | [8 empty] | ADCS_S | [8 empty] | 和順DS.100_CB | 100(TIE) CB | TIE | D20/11/100/CB |  |  |  | DNP | 463 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0182 | [10 empty] | ADCS_S | [8 empty] | 和順DS.100_51A | 11KV TIE(100) 51RY | TIE | D20/11/100/PHA |  |  |  | DNP | 464 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0183 | [10 empty] | ADCS_S | [8 empty] | 和順DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D20/11/100/GDA |  |  |  | DNP | 465 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0054 |  | 0011 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1500_CB | 1500(TIE) CB | TIE | D20/161/1500/CB |  |  |  | DNP | 466 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0055 | [10 empty] | 161KV_S | [8 empty] | 和順DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D20/161/1500/50A |  |  |  | DNP | 467 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0544 | 545 | 0168 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1501_DS | 1501(TIE) DS | TIE | D20/161/1500/DS1 |  |  |  | DNP | 468 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0546 | 547 | 0169 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1502_DS | 1502(TIE) DS | TIE | D20/161/1500/DS2 |  |  |  | DNP | 469 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0648 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D20/161/1500/50SA |  |  |  | DNP | 470 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0243 |  | 0051 | [8 empty] | ADCS_S | [8 empty] | 和順DS.200_CB | 200(TIE) CB | TIE | D20/11/200/CB |  |  |  | DNP | 471 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0244 | [10 empty] | ADCS_S | [8 empty] | 和順DS.200_51A | 11KV TIE(200) 51RY | TIE | D20/11/200/PHA |  |  |  | DNP | 472 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0245 | [10 empty] | ADCS_S | [8 empty] | 和順DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D20/11/200/GDA |  |  |  | DNP | 473 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0178 |  | 0024 | [8 empty] | ADCS_S | [8 empty] | 和順DS.390_CB | 390(#1SSTR) CB | OTHER | D20/11/390/CB |  |  |  | DNP | 474 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0179 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D20/11/390/PHA |  |  |  | DNP | 475 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0180 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D20/11/390/GDA |  |  |  | DNP | 476 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0240 |  | 0050 | [8 empty] | ADCS_S | [8 empty] | 和順DS.490_CB | 490(#2SSTR) CB | OTHER | D20/11/490/CB |  |  |  | DNP | 477 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0241 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D20/11/490/PHA |  |  |  | DNP | 478 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0242 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D20/11/490/GDA |  |  |  | DNP | 479 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [14 empty] | 0060 |  | 0012 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1750_CB | 1750(#1DTR) CB | MTR | D20/161/1750/CB |  |  |  | DNP | 480 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 310 | #1DTR(310) |  | CB | [14 empty] | 0067 |  | 0016 | [8 empty] | ADCS_S | [8 empty] | 和順DS.310_CB | 310(#1DTR) CB | MTR | D20/11/310/CB |  |  |  | DNP | 481 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 320 | #1DTR(320) |  | CB | [14 empty] | 0070 |  | 0026 | [8 empty] | ADCS_S | [8 empty] | 和順DS.320_CB | 320(#1DTR) CB | MTR | D20/11/320/CB |  |  |  | DNP | 482 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 51A | [14 empty] | 0065 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#1DTR_51A | #1DTR 51RY | MTR | D20/161/1750/PHA |  |  |  | DNP | 483 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 51NA | [14 empty] | 0066 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#1DTR_51NA | #1DTR 51N RY | MTR | D20/161/1750/GDA |  |  |  | DNP | 484 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [14 empty] | 0063 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D20//1DTR(A)/51ZA |  |  |  | DNP | 485 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 87A | [14 empty] | 0061 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#1DTR_87A | #1DTR 87RY | MTR | D20//1DTR/87A |  |  |  | DNP | 486 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 87UL | [14 empty] | 0356 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D20//1DTR/87UL |  |  |  | DNP | 487 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 96PA | [14 empty] | 0062 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D20//1DTR/96PA |  |  |  | DNP | 488 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 96D | [14 empty] | 0365 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_96D | #1DTR 96D RY | MTR | D20//1DTR/96D |  |  |  | DNP | 489 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 96P | [14 empty] | 0366 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_96P | #1DTR 96P RY | MTR | D20//1DTR/96P |  |  |  | DNP | 490 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 63Q | [14 empty] | 0367 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D20//1DTR/63Q |  |  |  | DNP | 491 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [14 empty] | 0363 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D20//1DTR/96B1 |  |  |  | DNP | 492 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [14 empty] | 0364 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D20//1DTR/96B2 |  |  |  | DNP | 493 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | TRA | [14 empty] | 0361 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_TRA | #1DTR 重故障 | MTR | D20//1DTR/TRA |  |  |  | DNP | 494 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR | #1DTR |  | TRF | [14 empty] | 0362 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D20//1DTR/TRF |  |  |  | DNP | 495 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [14 empty] | 0357 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D20//1DTR(A)/SupLocal |  |  |  | DNP | 496 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [14 empty] | 0358 |  | 0106 | [8 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D20//1DTR(A)/Tap Chan |  |  |  | DNP | 497 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [14 empty] | 0359 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D20//1DTR(B)/SupLocal |  |  |  | DNP | 498 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [14 empty] | 0360 |  | 0108 | [8 empty] | ADCS_S | [8 empty] | 和順DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D20//1DTR(B)/Tap Chan |  |  |  | DNP | 499 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [13 empty] | 0528 | 529 | 0160 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1751_DS | 1751(#1DTR) DS | MTR | D20/161/1750/DS1 |  |  |  | DNP | 500 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [13 empty] | 0530 | 531 | 0161 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1752_DS | 1752(#1DTR) DS | MTR | D20/161/1750/DS2 |  |  |  | DNP | 501 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0074 |  | 0013 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1760_CB | 1760(#2DTR) CB | MTR | D20/161/1760/CB |  |  |  | DNP | 502 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0081 |  | 0034 | [8 empty] | ADCS_S | [8 empty] | 和順DS.330_CB | 330(#2DTR) CB | MTR | D20/11/330/CB |  |  |  | DNP | 503 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0084 |  | 0042 | [8 empty] | ADCS_S | [8 empty] | 和順DS.340_CB | 340(#2DTR) CB | MTR | D20/11/340/CB |  |  |  | DNP | 504 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 51A | [14 empty] | 0079 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#2DTR_51A | #2DTR 51RY | MTR | D20/161/1760/PHA |  |  |  | DNP | 505 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 51NA | [14 empty] | 0080 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#2DTR_51NA | #2DTR 51N RY | MTR | D20/161/1760/GDA |  |  |  | DNP | 506 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0077 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D20//2DTR(A)/51ZA |  |  |  | DNP | 507 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0075 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#2DTR_87A | #2DTR 87RY | MTR | D20//2DTR/87A |  |  |  | DNP | 508 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 87UL | [14 empty] | 0368 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D20//2DTR/87UL |  |  |  | DNP | 509 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0076 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D20//2DTR/96PA |  |  |  | DNP | 510 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0377 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_96D | #2DTR 96D RY | MTR | D20//2DTR/96D |  |  |  | DNP | 511 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0378 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_96P | #2DTR 96P RY | MTR | D20//2DTR/96P |  |  |  | DNP | 512 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0379 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D20//2DTR/63Q |  |  |  | DNP | 513 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0375 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D20//2DTR/96B1 |  |  |  | DNP | 514 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0376 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D20//2DTR/96B2 |  |  |  | DNP | 515 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0373 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_TRA | #2DTR 重故障 | MTR | D20//2DTR/TRA |  |  |  | DNP | 516 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0374 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D20//2DTR/TRF |  |  |  | DNP | 517 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [14 empty] | 0369 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D20//2DTR(A)/SupLocal |  |  |  | DNP | 518 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [14 empty] | 0370 |  | 0110 | [8 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D20//2DTR(A)/Tap Chan |  |  |  | DNP | 519 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [14 empty] | 0371 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D20//2DTR(B)/SupLocal |  |  |  | DNP | 520 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [14 empty] | 0372 |  | 0112 | [8 empty] | ADCS_S | [8 empty] | 和順DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D20//2DTR(B)/Tap Chan |  |  |  | DNP | 521 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0532 | 533 | 0162 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1761_DS | 1761(#2DTR) DS | MTR | D20/161/1760/DS1 |  |  |  | DNP | 522 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0534 | 535 | 0163 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1762_DS | 1762(#2DTR) DS | MTR | D20/161/1760/DS2 |  |  |  | DNP | 523 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [14 empty] | 0160 |  | 0017 | [8 empty] | ADCS_S | [8 empty] | 和順DS.210_CB | 210(11KV #1SC) CB | SC | D20/11/210/CB |  |  |  | DNP | 524 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [14 empty] | 0161 | [10 empty] | ADCS_S | [8 empty] | 和順DS.210_SCA | 11KV #1SC 51,51N RY | SC | D20/11/210/SCA |  |  |  | DNP | 525 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [14 empty] | 0162 | [10 empty] | ADCS_S | [8 empty] | 和順DS.210_OUVA | 11KV #1SC 27,59RY(欠壓或過壓) | SC | D20/11/210/UVA |  |  |  | DNP | 526 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [14 empty] | 0696 | 697 | 0018 | [8 empty] | ADCS_S | [8 empty] | 和順DS.210_LBS | 210(11KV #1SC) LBS | SC | D20/11/210/LBS |  |  |  | DNP | 527 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [14 empty] | 0184 |  | 0027 | [8 empty] | ADCS_S | [8 empty] | 和順DS.220_CB | 220(11KV #2SC) CB | SC | D20/11/220/CB |  |  |  | DNP | 528 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [14 empty] | 0185 | [10 empty] | ADCS_S | [8 empty] | 和順DS.220_SCA | 11KV #2SC 51,51N RY | SC | D20/11/220/SCA |  |  |  | DNP | 529 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [14 empty] | 0186 | [10 empty] | ADCS_S | [8 empty] | 和順DS.220_OUVA | 11KV #2SC 27,59RY(欠壓或過壓) | SC | D20/11/220/UVA |  |  |  | DNP | 530 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [14 empty] | 0698 | 699 | 0028 | [8 empty] | ADCS_S | [8 empty] | 和順DS.220_LBS | 220(11KV #2SC) LBS | SC | D20/11/220/LBS |  |  |  | DNP | 531 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [14 empty] | 0204 |  | 0035 | [8 empty] | ADCS_S | [8 empty] | 和順DS.230_CB | 230(11KV #3SC) CB | SC | D20/11/230/CB |  |  |  | DNP | 532 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0205 | [10 empty] | ADCS_S | [8 empty] | 和順DS.230_SCA | 11KV #3SC 51,51N RY | SC | D20/11/230/SCA |  |  |  | DNP | 533 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0206 | [10 empty] | ADCS_S | [8 empty] | 和順DS.230_OUVA | 11KV #3SC 27,59RY(欠壓或過壓) | SC | D20/11/230/UVA |  |  |  | DNP | 534 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [14 empty] | 0700 | 701 | 0036 | [8 empty] | ADCS_S | [8 empty] | 和順DS.230_LBS | 230(11KV #3SC) LBS | SC | D20/11/230/LBS |  |  |  | DNP | 535 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [14 empty] | 0222 |  | 0043 | [8 empty] | ADCS_S | [8 empty] | 和順DS.240_CB | 240(11KV #4SC) CB | SC | D20/11/240/CB |  |  |  | DNP | 536 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0223 | [10 empty] | ADCS_S | [8 empty] | 和順DS.240_SCA | 11KV #4SC 51,51N RY | SC | D20/11/240/SCA |  |  |  | DNP | 537 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0224 | [10 empty] | ADCS_S | [8 empty] | 和順DS.240_OUVA | 11KV #4SC 27,59RY(欠壓或過壓) | SC | D20/11/240/UVA |  |  |  | DNP | 538 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [14 empty] | 0702 | 703 | 0044 | [8 empty] | ADCS_S | [8 empty] | 和順DS.240_LBS | 240(11KV #4SC) LBS | SC | D20/11/240/LBS |  |  |  | DNP | 539 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0684 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D20/161/1BUS/BUS_VUA |  |  |  | DNP | 540 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0050 | [10 empty] | 161KV_S | [8 empty] | 和順DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D20/161/1BUS/87A |  |  |  | DNP | 541 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0353 |  | 0170 | [8 empty] | ADCS_S | [8 empty] | 和順DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D20/161/1BUS/87UL |  |  |  | DNP | 542 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0685 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D20/161/2BUS/BUS_VUA |  |  |  | DNP | 543 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0051 | [10 empty] | 161KV_S | [8 empty] | 和順DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D20/161/2BUS/87A |  |  |  | DNP | 544 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0354 |  | 0171 | [8 empty] | ADCS_S | [8 empty] | 和順DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D20/161/2BUS/87UL |  |  |  | DNP | 545 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0663 | [10 empty] | ADCS_S | [8 empty] | 和順DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D20/0/ComPoint/CBA |  |  |  | DNP | 546 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0664 | [10 empty] | ADCS_S | [8 empty] | 和順DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D20/0/ComPoint/CBF |  |  |  | DNP | 547 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 11 | 11kV | _SC | 11/ SC |  | 60A | [14 empty] | 0655 | [10 empty] | ADCS_S | [8 empty] | 和順DS.11KV_SC_60A | 11/23KV SC 60A | OTHER | D20/11/ComPoint/60A |  |  |  | DNP | 548 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0657 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D20/161/ComPoint/CBA |  |  |  | DNP | 549 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0658 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D20/161/ComPoint/CBF |  |  |  | DNP | 550 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0056 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D20/161/ComPoint/RCA |  |  |  | DNP | 551 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV |  |  |  | COMT | [14 empty] | 0687 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D20/161/ComPoint/COMT |  |  |  | DNP | 552 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0320 |  | 0000 | [8 empty] | ADCS_S | [8 empty] | 和順DS.TEST_CB | TEST CB | OTHER | D20/0/RTU/Test_CB |  |  |  | DNP | 553 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0681 | [10 empty] | ADCS_S | [8 empty] | 和順DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D20/0/StaDev/Fire1 |  |  |  | DNP | 554 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 25PFA | [14 empty] | 0649 | [10 empty] | ADCS_S | [8 empty] | 和順DS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | D20/0/ComPoint/25PFA |  |  |  | DNP | 555 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 25TA | [14 empty] | 0650 | [10 empty] | ADCS_S | [8 empty] | 和順DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D20/0/ComPoint/25TA |  |  |  | DNP | 556 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | SUBA | [14 empty] | 0677 | [10 empty] | ADCS_S | [8 empty] | 和順DS.其他重故障 | 變電所內其他重故障 | OTHER | D20/0/StaDev/PSA |  |  |  | DNP | 557 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | SUBF | [14 empty] | 0678 | [10 empty] | ADCS_S | [8 empty] | 和順DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D20/0/StaDev/PSF |  |  |  | DNP | 558 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0651 |  | 0245 | [8 empty] | ADCS_S | [8 empty] | 和順DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D20/0/StaDev/ACB1 |  |  |  | DNP | 559 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ON/OFF | ON
D20 | 和順DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0652 |  | 0246 | [8 empty] | ADCS_S | [8 empty] | 和順DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D20/0/StaDev/ACB2 |  |  |  | DNP | 560 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ON/OFF | ON
D20 | 和順DS | 0 |  |  |  |  | ACBA | [14 empty] | 0660 | [10 empty] | ADCS_S | [8 empty] | 和順DS.所內電源ACBA | 所內電源故障警報 | OTHER | D20/0/StaDev/ACBA |  |  |  | DNP | 561 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0653 |  | 0247 | [8 empty] | ADCS_S | [8 empty] | 和順DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D20/0/StaDev/ACBT |  |  |  | DNP | 562 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ON/OFF | OFF
D20 | 和順DS | 0 |  |  |  |  | STUV | [14 empty] | 0654 | [10 empty] | ADCS_S | [8 empty] | 和順DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D20/0/StaDev/STUV |  |  |  | DNP | 563 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0661 | [10 empty] | ADCS_S | [8 empty] | 和順DS.直流充電機故障 | 直流充電機故障 | OTHER | D20/0/StaDev/CHG1 |  |  |  | DNP | 564 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | DCA | [14 empty] | 0659 | [10 empty] | ADCS_S | [8 empty] | 和順DS.直流電源DCA | 直流電源故障警報 | OTHER | D20/0/StaDev/DCA |  |  |  | DNP | 565 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | DCE | [14 empty] | 0662 | [10 empty] | ADCS_S | [8 empty] | 和順DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D20/0/StaDev/DCE |  |  |  | DNP | 566 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0673 | [10 empty] | ADCS_S | [8 empty] | 和順DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D20/0/StaDev/CHG2 |  |  |  | DNP | 567 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | CommACF | [14 empty] | 0672 | [10 empty] | ADCS_S | [8 empty] | 和順DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D20/0/StaDev/CommACF |  |  |  | DNP | 568 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | Door1 | [14 empty] | 0679 | [10 empty] | ADCS_S | [8 empty] | 和順DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D20/0/StaDev/Door1 |  |  |  | DNP | 569 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  |  |  |  | Door2 | [14 empty] | 0680 | [10 empty] | ADCS_S | [8 empty] | 和順DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D20/0/StaDev/Door2 |  |  |  | DNP | 570 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0667 | [10 empty] | ADCS_S | [8 empty] | 和順DS.開關場照明(A) | 開關場照明(A)景觀照明 | OTHER | D20/0/StaDev/Lights1 |  |  |  | DNP | 571 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ON/OFF | OFF
D20 | 和順DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0668 |  | 0249 | [8 empty] | ADCS_S | [8 empty] | 和順DS.開關場照明(B) | 開關場照明(B)路燈照明 | OTHER | D20/0/StaDev/Lights2 |  |  |  | DNP | 572 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ON/OFF | OFF
D20 | 和順DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0665 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.11/23KV_LOA | 饋線復閉失敗閉鎖 | OTHER | D20/0/ComPoint/LOA |  |  |  | DNP | 573 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 11KV空壓機COMT | [14 empty] | 0688 | [10 empty] | ADCS_S | [8 empty] | 和順DS.11KV空壓機COMT | 11KV空壓機運轉超時警報 | OTHER | D20/11/ComPoint/COMT |  |  |  | DNP | 574 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1510 | 道爺和順新化線(1510) |  | 87CFA | [14 empty] | 0400 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1510_87CFA | 道爺和順新化線(1510)RY通訊故障 | OTHER | D20/161/1510/87CFA |  |  |  | DNP | 575 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1510 | 道爺和順新化線(1510) |  | RYFA | [14 empty] | 0401 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1510_RYFA | 道爺和順新化線(1510)數位RY故障 | OTHER | D20/161/1510/RYFA |  |  |  | DNP | 576 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1520 | 安南和順線(1520) |  | 87CFA | [14 empty] | 0404 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1520_87CFA | 安南和順線(1520)87RY通訊故障 | OTHER | D20/161/1520/87CFA |  |  |  | DNP | 577 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1520 | 安南和順線(1520) |  | RYFA | [14 empty] | 0405 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1520_RYFA | 安南和順線(1520)數位電驛故障 | OTHER | D20/161/1520/RYFA |  |  |  | DNP | 578 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1540 | 和順公學二路(1540) |  | 87CFA | [14 empty] | 0412 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1540_87CFA | 和順公學二路(1540)87RY通訊故障 | OTHER | D20/161/1540/87CFA |  |  |  | DNP | 579 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 1540 | 和順公學二路(1540) |  | RYFA | [14 empty] | 0413 | [10 empty] | ADCS_S | [8 empty] | 和順DS.1540_RYFA | 和順公學二路(1540)數位電驛故障 | OTHER | D20/161/1540/RYFA |  |  |  | DNP | 580 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV |  |  |  | OSCA | [14 empty] | 0057 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D20/161/ComPoint/OSCA |  |  |  | DNP | 581 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 310 | #1DTR(310) |  | GDA | [14 empty] | 0069 | [10 empty] | ADCS_S | [8 empty] | 和順DS.310_GDA | 310開關箱IED RY GDA | OTHER | D20/11/310/GDA |  |  |  | DNP | 582 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [14 empty] | 0068 | [10 empty] | ADCS_S | [8 empty] | 和順DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D20/11/310/PHA |  |  |  | DNP | 583 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 320 | #1DTR(320) |  | GDA | [14 empty] | 0072 | [10 empty] | ADCS_S | [8 empty] | 和順DS.320_GDA | 320開關箱IED RY GDA | OTHER | D20/11/320/GDA |  |  |  | DNP | 584 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [14 empty] | 0071 | [10 empty] | ADCS_S | [8 empty] | 和順DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D20/11/320/PHA |  |  |  | DNP | 585 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0083 | [10 empty] | ADCS_S | [8 empty] | 和順DS.330_GDA | 330開關箱IED RY GDA | OTHER | D20/11/330/GDA |  |  |  | DNP | 586 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [14 empty] | 0082 | [10 empty] | ADCS_S | [8 empty] | 和順DS.330_PHA2 | 330開關箱IED RY PHA | OTHER | D20/11/330/PHA |  |  |  | DNP | 587 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0086 | [10 empty] | ADCS_S | [8 empty] | 和順DS.340_GDA | 340開關箱IED RY GDA | OTHER | D20/11/340/GDA |  |  |  | DNP | 588 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [14 empty] | 0085 | [10 empty] | ADCS_S | [8 empty] | 和順DS.340_PHA2 | 340開關箱IED RY PHA | OTHER | D20/11/340/PHA |  |  |  | DNP | 589 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [14 empty] | 0666 | [10 empty] | ADCS_S | [8 empty] | 和順DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | D20/0/StaDev/Comm_R_L |  |  |  | DNP | 590 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D20 | 和順DS | 161 | 161kV |  |  |  | MCC | [14 empty] | 0321 | [10 empty] | ADCS_S | [8 empty] | 和順DS.MCC故障 | 161KV IED故障 | OTHER | D20/0/StaDev/MCC |  |  |  | DNP | 591 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 11_ | 11/ |  | PMCC | [14 empty] | 0322 | [10 empty] | ADCS_S | [8 empty] | 和順DS.PMCC故障 | 11/23KV IED故障 | OTHER | D20/0/StaDev/PMCC |  |  |  | DNP | 592 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 變電所LOCAL | 變電所LOCAL |  | SCADAA | [14 empty] | 0682 | [10 empty] | ADCS_S | [8 empty] | 和順DS.SCADA故障 | 變電所LOCAL SCADA故障 | OTHER | D20/0/StaDev/SCADAA |  |  |  | DNP | 593 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | TCA | [14 empty] | 0683 | [10 empty] | ADCS_S | [8 empty] | 和順DS.TCA | 斷路器跳脫回路故障 | OTHER | D20/0/StaDev/TCA |  |  |  | DNP | 594 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0656 | [10 empty] | ADCS_S | [8 empty] | 和順DS.水位警報(1) | 地下室第一段水位警報 | OTHER | D20/0/StaDev/Water1 |  |  |  | DNP | 595 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0671 | [10 empty] | ADCS_S | [8 empty] | 和順DS.水位警報(2) | 地下室第二段水位警報 | OTHER | D20/0/StaDev/Water2 |  |  |  | DNP | 596 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 通訊機房溫度 | [14 empty] | 0676 | [10 empty] | ADCS_S | [8 empty] | 和順DS.通訊機房溫度 | 通訊室或控制室溫度警報 | OTHER | D20/0/StaDev/R_Temp |  |  |  | DNP | 597 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 集油池水位(1) | [14 empty] | 0669 | [10 empty] | ADCS_S | [8 empty] | 和順DS.集油池水位(1) | 集油池第一段水位警報 | OTHER | D20/0/StaDev/OilLeak1 |  |  |  | DNP | 598 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | 集油池水位(2) | [14 empty] | 0670 | [10 empty] | ADCS_S | [8 empty] | 和順DS.集油池水位(2) | 集油池第二段水位警報 | OTHER | D20/0/StaDev/OilLeak2 |  |  |  | DNP | 599 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0690 | [10 empty] | ADCS_S | [8 empty] | 和順DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D20/0/StaDev/Door3 |  |  |  | DNP | 600 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV |  |  |  | OSCF | [14 empty] | 0689 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D20/0/ComPoint/OSCF |  |  |  | DNP | 601 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | PMCC_IED | 11/ IED |  | SupLocal | [14 empty] | 0693 | [10 empty] | ADCS_S | [8 empty] | 和順DS.PMCC_IED_S/L | 11/23KV IED SUPY/LOCAL | OTHER | D20/0/StaDev/PMCC_R_L |  |  |  | DNP | 602 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D20 | 和順DS | 0 |  |  |  |  | 涵洞水泵 | [14 empty] | 0686 | [10 empty] | ADCS_S | [8 empty] | 和順DS.涵洞水泵 | 涵洞水泵警報 | OTHER | D20/0/StaDev/OilLeak |  |  |  | DNP | 603 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | BVS | BVS |  | RY | [14 empty] | 0441 | [10 empty] | ADCS_S | [8 empty] | 和順DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D20/0/ComPoint/GRZ100 |  |  |  | DNP | 604 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | LOCK/USE | USE
D20 | 和順DS | 0 |  |  |  |  | GEN | [14 empty] | 0692 | [10 empty] | ADCS_S | [8 empty] | 和順DS.GEN | 緊急發電機運轉 | OTHER | D20/0/StaDev/2A5Other |  |  |  | DNP | 605 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ON/OFF | OFF
D20 | 和順DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0443 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D20/161/ComPoint/12B_CTFA |  |  |  | DNP | 606 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0442 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D20/161/ComPoint/BUS_RYFA |  |  |  | DNP | 607 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0444 | [10 empty] | ADCS_S | [8 empty] | 和順DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D20/0/ComPoint/OLTC_A |  |  |  | DNP | 608 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [14 empty] | 0088 |  | 0014 | [8 empty] | 161KV_S | [8 empty] | 和順DS.1770_CB | 1770(#3DTR) CB | MTR | D20/161/1770/CB |  |  |  | DNP | 609 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 350 | #3DTR(350) |  | CB | [14 empty] | 0096 |  | 0052 | [8 empty] | ADCS_S | [8 empty] | 和順DS.350_CB | 350(#3DTR) CB | MTR | D20/22/350/CB |  |  |  | DNP | 610 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 51A | [14 empty] | 0092 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#3DTR_51A | #3DTR 51RY | MTR | D20/161/1770/PHA |  |  |  | DNP | 611 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 51NA | [14 empty] | 0093 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#3DTR_51NA | #3DTR 51N RY | MTR | D20/161/1770/GDA |  |  |  | DNP | 612 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [14 empty] | 0091 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D20//3DTR/51ZA |  |  |  | DNP | 613 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 87A | [14 empty] | 0089 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#3DTR_87A | #3DTR 87RY | MTR | D20//3DTR/87A |  |  |  | DNP | 614 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 96PA | [14 empty] | 0090 | [10 empty] | 161KV_S | [8 empty] | 和順DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D20//3DTR/96PA |  |  |  | DNP | 615 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 96D | [14 empty] | 0390 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_96D | #3DTR 96D RY | MTR | D20//3DTR/96D |  |  |  | DNP | 616 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 96P | [14 empty] | 0391 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_96P | #3DTR 96P RY | MTR | D20//3DTR/96P |  |  |  | DNP | 617 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 63Q | [14 empty] | 0392 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D20//3DTR/63Q |  |  |  | DNP | 618 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [14 empty] | 0388 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D20//3DTR/96B1 |  |  |  | DNP | 619 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [14 empty] | 0389 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D20//3DTR/96B2 |  |  |  | DNP | 620 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | TRA | [14 empty] | 0386 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_TRA | #3DTR 重故障 | MTR | D20//3DTR/TRA |  |  |  | DNP | 621 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | TRF | [14 empty] | 0387 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D20//3DTR/TRF |  |  |  | DNP | 622 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [14 empty] | 0384 | [10 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D20//3DTR/SupLocal |  |  |  | DNP | 623 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D20 | 和順DS | 0 |  | 3DTR | #3DTR |  | A_M | [14 empty] | 0385 |  | 0114 | [8 empty] | ADCS_S | [8 empty] | 和順DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D20//3DTR/Tap Chan |  |  |  | DNP | 624 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [13 empty] | 0536 | 537 | 0164 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1771_DS | 1771(#3DTR) DS | MTR | D20/161/1770/DS1 |  |  |  | DNP | 625 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [13 empty] | 0538 | 539 | 0165 | [8 empty] | ADCS_S | [8 empty] | 和順DS.1772_DS | 1772(#3DTR) DS | MTR | D20/161/1770/DS2 |  |  |  | DNP | 626 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D20 | 和順DS | 161 | 161kV | 1613DTR | #3DTR |  | 187UL | [14 empty] | 0380 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | D20//3DTR/87UL1 |  |  |  | DNP | 627 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1613DTR | #3DTR |  | 287UL | [14 empty] | 0381 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | D20//3DTR/87UL2 |  |  |  | DNP | 628 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1613DTR | #3DTR |  | 51Z_UL | [14 empty] | 0382 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | D20//3DTR/51Z_UL |  |  |  | DNP | 629 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 161 | 161kV | 1613DTR | #3DTR |  | DTR_86A | [14 empty] | 0094 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER | D20//3DTR/DTR_86A |  |  |  | DNP | 630 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 161 | 161kV | 1613DTR | #3DTR |  | RYFA | [14 empty] | 0393 | [10 empty] | ADCS_S | [8 empty] | 和順DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | D20//3DTR/RYFA |  |  |  | DNP | 631 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 350 | #3DTR(350) |  | 81A | [14 empty] | 0095 | [10 empty] | ADCS_S | [8 empty] | 和順DS.350_81A | 350 #3DTR 81RY動作 | OTHER | D20/22/350/81A |  |  |  | DNP | 632 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 350 | #3DTR(350) |  | 81UL | [14 empty] | 0383 | [10 empty] | ADCS_S | [8 empty] | 和順DS.350_81UL | 350 #3DTR 81RY U/L | OTHER | D20/22/350/81UL |  |  |  | DNP | 633 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 0 |  | 350 | #3DTR(350) |  | GDA | [14 empty] | 0098 | [10 empty] | ADCS_S | [8 empty] | 和順DS.350_GDA | 350開關箱IED RY GDA | OTHER | D20/22/350/GDA |  |  |  | DNP | 634 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 0 |  | 350 | #3DTR(350) |  | PHA | [14 empty] | 0097 | [10 empty] | ADCS_S | [8 empty] | 和順DS.350_PHA | 350開關箱IED RY PHA | OTHER | D20/22/350/PHA |  |  |  | DNP | 635 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [14 empty] | 0248 |  | 0053 | [8 empty] | ADCS_S | [8 empty] | 和順DS.250_CB | 250(23KV #5SC) CB | SC | D20/22/250/CB |  |  |  | DNP | 636 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [14 empty] | 0249 | [10 empty] | ADCS_S | [8 empty] | 和順DS.250_SCA | 23KV #5SC 51,51N RY | SC | D20/22/250/SCA |  |  |  | DNP | 637 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [14 empty] | 0250 | [10 empty] | ADCS_S | [8 empty] | 和順DS.250_OUVA | 23KV #5SC 27,59RY(欠壓或過壓) | SC | D20/22/250/UVA |  |  |  | DNP | 638 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 250 | #5SC(250) |  | LBS | [14 empty] | 0704 | 705 | 0250 | [8 empty] | ADCS_S | [8 empty] | 和順DS.250_LBS | 250(23KV #5SC) LBS | SC | D20/22/250/LBS |  |  |  | DNP | 639 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [14 empty] | 0251 |  | 0054 | [8 empty] | ADCS_S | [8 empty] | 和順DS.260_CB | 260(23KV #6SC) CB | SC | D20/22/260/CB |  |  |  | DNP | 640 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [14 empty] | 0252 | [10 empty] | ADCS_S | [8 empty] | 和順DS.260_SCA | 23KV #6SC 51,51N RY | SC | D20/22/260/SCA |  |  |  | DNP | 641 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [14 empty] | 0253 | [10 empty] | ADCS_S | [8 empty] | 和順DS.260_OUVA | 23KV #6SC 27,59RY(欠壓或過壓) | SC | D20/22/260/UVA |  |  |  | DNP | 642 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | PHA | [14 empty] | 0255 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_PHA | 23KV和51線(4A51) 相間RY | FEEDER | D20/22/4A51/PHA |  |  |  | DNP | 643 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) |  | GDA | [14 empty] | 0256 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_GDA | 23KV和51線(4A51) 接地RY | FEEDER | D20/22/4A51/GDA |  |  |  | DNP | 644 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線(4A51) 79RY |  | 79UL | [14 empty] | 0616 |  | 0212 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_79UL | 23KV和51線(4A51) 79RY U/L | FEEDER | D20/22/4A51/79UL |  |  |  | DNP | 645 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A51_LCO | 和51線(4A51) LCO |  | TapPosMv | [14 empty] | 0617 |  | 0213 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_LCO_TAP | 23KV和51線(4A51) LCO TAP | FEEDER | D20/22/4A51/ADJ |  |  |  | DNP | 646 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A51 | 和51線 |  | CB | [14 empty] | 0254 |  | 0055 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_CB | 4A51(23KV和51線) CB | FEEDER | D20/22/4A51/CB |  |  |  | DNP | 647 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | PHA | [14 empty] | 0258 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_PHA | 23KV和52線(4A52) 相間RY | FEEDER | D20/22/4A52/PHA |  |  |  | DNP | 648 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) |  | GDA | [14 empty] | 0259 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_GDA | 23KV和52線(4A52) 接地RY | FEEDER | D20/22/4A52/GDA |  |  |  | DNP | 649 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線(4A52) 79RY |  | 79UL | [14 empty] | 0618 |  | 0214 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_79UL | 23KV和52線(4A52) 79RY U/L | FEEDER | D20/22/4A52/79UL |  |  |  | DNP | 650 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A52_LCO | 和52線(4A52) LCO |  | TapPosMv | [14 empty] | 0619 |  | 0215 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_LCO_TAP | 23KV和52線(4A52) LCO TAP | FEEDER | D20/22/4A52/ADJ |  |  |  | DNP | 651 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A52 | 和52線 |  | CB | [14 empty] | 0257 |  | 0056 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_CB | 4A52(23KV和52線) CB | FEEDER | D20/22/4A52/CB |  |  |  | DNP | 652 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | PHA | [14 empty] | 0261 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_PHA | 23KV和53線(4A53) 相間RY | FEEDER | D20/22/4A53/PHA |  |  |  | DNP | 653 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) |  | GDA | [14 empty] | 0262 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_GDA | 23KV和53線(4A53) 接地RY | FEEDER | D20/22/4A53/GDA |  |  |  | DNP | 654 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線(4A53) 79RY |  | 79UL | [14 empty] | 0620 |  | 0216 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_79UL | 23KV和53線(4A53) 79RY U/L | FEEDER | D20/22/4A53/79UL |  |  |  | DNP | 655 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A53_LCO | 和53線(4A53) LCO |  | TapPosMv | [14 empty] | 0621 |  | 0217 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_LCO_TAP | 23KV和53線(4A53) LCO TAP | FEEDER | D20/22/4A53/ADJ |  |  |  | DNP | 656 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A53 | 和53線 |  | CB | [14 empty] | 0260 |  | 0057 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_CB | 4A53(23KV和53線) CB | FEEDER | D20/22/4A53/CB |  |  |  | DNP | 657 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | PHA | [14 empty] | 0264 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_PHA | 23KV和54線(4A54) 相間RY | FEEDER | D20/22/4A54/PHA |  |  |  | DNP | 658 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) |  | GDA | [14 empty] | 0265 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_GDA | 23KV和54線(4A54) 接地RY | FEEDER | D20/22/4A54/GDA |  |  |  | DNP | 659 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線(4A54) 79RY |  | 79UL | [14 empty] | 0622 |  | 0218 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_79UL | 23KV和54線(4A54) 79RY U/L | FEEDER | D20/22/4A54/79UL |  |  |  | DNP | 660 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A54_LCO | 和54線(4A54) LCO |  | TapPosMv | [14 empty] | 0623 |  | 0219 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_LCO_TAP | 23KV和54線(4A54) LCO TAP | FEEDER | D20/22/4A54/ADJ |  |  |  | DNP | 661 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A54 | 和54線 |  | CB | [14 empty] | 0263 |  | 0058 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_CB | 4A54(23KV和54線) CB | FEEDER | D20/22/4A54/CB |  |  |  | DNP | 662 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | PHA | [14 empty] | 0267 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_PHA | 23KV和55線(4A55) 相間RY | FEEDER | D20/22/4A55/PHA |  |  |  | DNP | 663 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) |  | GDA | [14 empty] | 0268 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_GDA | 23KV和55線(4A55) 接地RY | FEEDER | D20/22/4A55/GDA |  |  |  | DNP | 664 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線(4A55) 79RY |  | 79UL | [14 empty] | 0624 |  | 0220 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_79UL | 23KV和55線(4A55) 79RY U/L | FEEDER | D20/22/4A55/79UL |  |  |  | DNP | 665 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A55_LCO | 和55線(4A55) LCO |  | TapPosMv | [14 empty] | 0625 |  | 0221 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_LCO_TAP | 23KV和55線(4A55) LCO TAP | FEEDER | D20/22/4A55/ADJ |  |  |  | DNP | 666 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A55 | 和55線 |  | CB | [14 empty] | 0266 |  | 0059 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_CB | 4A55(23KV和55線) CB | FEEDER | D20/22/4A55/CB |  |  |  | DNP | 667 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | PHA | [14 empty] | 0270 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_PHA | 23KV和56線(4A56) 相間RY | FEEDER | D20/22/4A56/PHA |  |  |  | DNP | 668 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) |  | GDA | [14 empty] | 0271 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_GDA | 23KV和56線(4A56) 接地RY | FEEDER | D20/22/4A56/GDA |  |  |  | DNP | 669 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線(4A56) 79RY |  | 79UL | [14 empty] | 0626 |  | 0222 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_79UL | 23KV和56線(4A56) 79RY U/L | FEEDER | D20/22/4A56/79UL |  |  |  | DNP | 670 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A56_LCO | 和56線(4A56) LCO |  | TapPosMv | [14 empty] | 0627 |  | 0223 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_LCO_TAP | 23KV和56線(4A56) LCO TAP | FEEDER | D20/22/4A56/ADJ |  |  |  | DNP | 671 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A56 | 和56線 |  | CB | [14 empty] | 0269 |  | 0060 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_CB | 4A56(23KV和56線) CB | FEEDER | D20/22/4A56/CB |  |  |  | DNP | 672 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | PHA | [14 empty] | 0273 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_PHA | 23KV和57線(4A57) 相間RY | FEEDER | D20/22/4A57/PHA |  |  |  | DNP | 673 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) |  | GDA | [14 empty] | 0274 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_GDA | 23KV和57線(4A57) 接地RY | FEEDER | D20/22/4A57/GDA |  |  |  | DNP | 674 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線(4A57) 79RY |  | 79UL | [14 empty] | 0628 |  | 0224 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_79UL | 23KV和57線(4A57) 79RY U/L | FEEDER | D20/22/4A57/79UL |  |  |  | DNP | 675 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A57_LCO | 和57線(4A57) LCO |  | TapPosMv | [14 empty] | 0629 |  | 0225 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_LCO_TAP | 23KV和57線(4A57) LCO TAP | FEEDER | D20/22/4A57/ADJ |  |  |  | DNP | 676 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A57 | 和57線 |  | CB | [14 empty] | 0272 |  | 0061 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_CB | 4A57(23KV和57線) CB | FEEDER | D20/22/4A57/CB |  |  |  | DNP | 677 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | PHA | [14 empty] | 0276 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_PHA | 23KV和58線(4A58) 相間RY | FEEDER | D20/22/4A58/PHA |  |  |  | DNP | 678 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) |  | GDA | [14 empty] | 0277 | [10 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_GDA | 23KV和58線(4A58) 接地RY | FEEDER | D20/22/4A58/GDA |  |  |  | DNP | 679 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線(4A58) 79RY |  | 79UL | [14 empty] | 0630 |  | 0226 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_79UL | 23KV和58線(4A58) 79RY U/L | FEEDER | D20/22/4A58/79UL |  |  |  | DNP | 680 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | USE
D20 | 和順DS | 22 | 22kV | 4A58_LCO | 和58線(4A58) LCO |  | TapPosMv | [14 empty] | 0631 |  | 0227 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_LCO_TAP | 23KV和58線(4A58) LCO TAP | FEEDER | D20/22/4A58/ADJ |  |  |  | DNP | 681 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D20 | 和順DS | 22 | 22kV | 4A58 | 和58線 |  | CB | [14 empty] | 0275 |  | 0062 | [8 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_CB | 4A58(23KV和58線) CB | FEEDER | D20/22/4A58/CB |  |  |  | DNP | 682 | DNPDIPoint | DS050 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 和順DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 683 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 和順DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 684 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 和順DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 685 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 和順DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 686 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 22 | 22kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 和順DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 687 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1510LE | 1510LE (非取樣點) | LINE161 | D20/161/1510/LE0 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1510 | 道爺和順新化線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1510BE | 1510BE (非取樣點) | LINE161 | D20/161/1510/BE0 |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1520LE | 1520LE (非取樣點) | LINE161 | D20/161/1520/LE0 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1520 | 安南和順線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1520BE | 1520BE (非取樣點) | LINE161 | D20/161/1520/BE0 |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1540LE | 1540LE (非取樣點) | LINE161 | D20/161/1540/LE0 |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1540 | 和順公學二路(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1540BE | 1540BE (非取樣點) | LINE161 | D20/161/1540/BE0 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A11 | 4A11_DS |  | DS1 | 4A11_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_DS | 4A11_DS (非取樣點) | FEEDER | D20/11/4A11/DS |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A11 | 4A11_ES |  | A110 | 4A11_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A11_ES | 4A11_ES (非取樣點) | FEEDER | D20/11/4A11/ES |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A12 | 4A12_DS |  | DS1 | 4A12_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_DS | 4A12_DS (非取樣點) | FEEDER | D20/11/4A12/DS |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A12 | 4A12_ES |  | A120 | 4A12_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A12_ES | 4A12_ES (非取樣點) | FEEDER | D20/11/4A12/ES |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A13 | 4A13_DS |  | DS1 | 4A13_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_DS | 4A13_DS (非取樣點) | FEEDER | D20/11/4A13/DS |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A13 | 4A13_ES |  | A130 | 4A13_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A13_ES | 4A13_ES (非取樣點) | FEEDER | D20/11/4A13/ES |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A14 | 4A14_DS |  | DS1 | 4A14_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_DS | 4A14_DS (非取樣點) | FEEDER | D20/11/4A14/DS |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A14 | 4A14_ES |  | A140 | 4A14_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A14_ES | 4A14_ES (非取樣點) | FEEDER | D20/11/4A14/ES |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A15 | 4A15_DS |  | DS1 | 4A15_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_DS | 4A15_DS (非取樣點) | FEEDER | D20/11/4A15/DS |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A15 | 4A15_ES |  | A150 | 4A15_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A15_ES | 4A15_ES (非取樣點) | FEEDER | D20/11/4A15/ES |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A16 | 4A16_DS |  | DS1 | 4A16_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_DS | 4A16_DS (非取樣點) | FEEDER | D20/11/4A16/DS |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A16 | 4A16_ES |  | A160 | 4A16_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A16_ES | 4A16_ES (非取樣點) | FEEDER | D20/11/4A16/ES |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A17 | 4A17_DS |  | DS1 | 4A17_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_DS | 4A17_DS (非取樣點) | FEEDER | D20/11/4A17/DS |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A17 | 4A17_ES |  | A170 | 4A17_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A17_ES | 4A17_ES (非取樣點) | FEEDER | D20/11/4A17/ES |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A18 | 4A18_DS |  | DS1 | 4A18_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_DS | 4A18_DS (非取樣點) | FEEDER | D20/11/4A18/DS |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A18 | 4A18_ES |  | A180 | 4A18_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A18_ES | 4A18_ES (非取樣點) | FEEDER | D20/11/4A18/ES |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A19 | 4A19_DS |  | DS1 | 4A19_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_DS | 4A19_DS (非取樣點) | FEEDER | D20/11/4A19/DS |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A19 | 4A19_ES |  | A190 | 4A19_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A19_ES | 4A19_ES (非取樣點) | FEEDER | D20/11/4A19/ES |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A20 | 4A20_DS |  | DS1 | 4A20_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_DS | 4A20_DS (非取樣點) | FEEDER | D20/11/4A20/DS |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A20 | 4A20_ES |  | A200 | 4A20_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A20_ES | 4A20_ES (非取樣點) | FEEDER | D20/11/4A20/ES |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A21 | 4A21_DS |  | DS1 | 4A21_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_DS | 4A21_DS (非取樣點) | FEEDER | D20/11/4A21/DS |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A21 | 4A21_ES |  | A210 | 4A21_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A21_ES | 4A21_ES (非取樣點) | FEEDER | D20/11/4A21/ES |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A22 | 4A22_DS |  | DS1 | 4A22_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_DS | 4A22_DS (非取樣點) | FEEDER | D20/11/4A22/DS |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A22 | 4A22_ES |  | A220 | 4A22_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A22_ES | 4A22_ES (非取樣點) | FEEDER | D20/11/4A22/ES |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A23 | 4A23_DS |  | DS1 | 4A23_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_DS | 4A23_DS (非取樣點) | FEEDER | D20/11/4A23/DS |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A23 | 4A23_ES |  | A230 | 4A23_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A23_ES | 4A23_ES (非取樣點) | FEEDER | D20/11/4A23/ES |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A24 | 4A24_DS |  | DS1 | 4A24_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_DS | 4A24_DS (非取樣點) | FEEDER | D20/11/4A24/DS |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A24 | 4A24_ES |  | A240 | 4A24_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A24_ES | 4A24_ES (非取樣點) | FEEDER | D20/11/4A24/ES |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A25 | 4A25_DS |  | DS1 | 4A25_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_DS | 4A25_DS (非取樣點) | FEEDER | D20/11/4A25/DS |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A25 | 4A25_ES |  | A250 | 4A25_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A25_ES | 4A25_ES (非取樣點) | FEEDER | D20/11/4A25/ES |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A26 | 4A26_DS |  | DS1 | 4A26_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_DS | 4A26_DS (非取樣點) | FEEDER | D20/11/4A26/DS |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A26 | 4A26_ES |  | A260 | 4A26_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A26_ES | 4A26_ES (非取樣點) | FEEDER | D20/11/4A26/ES |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A27 | 4A27_DS |  | DS1 | 4A27_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_DS | 4A27_DS (非取樣點) | FEEDER | D20/11/4A27/DS |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A27 | 4A27_ES |  | A270 | 4A27_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A27_ES | 4A27_ES (非取樣點) | FEEDER | D20/11/4A27/ES |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A28 | 4A28_DS |  | DS1 | 4A28_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_DS | 4A28_DS (非取樣點) | FEEDER | D20/11/4A28/DS |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A28 | 4A28_ES |  | A280 | 4A28_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A28_ES | 4A28_ES (非取樣點) | FEEDER | D20/11/4A28/ES |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A29 | 4A29_DS |  | DS1 | 4A29_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_DS | 4A29_DS (非取樣點) | FEEDER | D20/11/4A29/DS |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A29 | 4A29_ES |  | A290 | 4A29_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A29_ES | 4A29_ES (非取樣點) | FEEDER | D20/11/4A29/ES |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A30 | 4A30_DS |  | DS1 | 4A30_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_DS | 4A30_DS (非取樣點) | FEEDER | D20/11/4A30/DS |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A30 | 4A30_ES |  | A300 | 4A30_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A30_ES | 4A30_ES (非取樣點) | FEEDER | D20/11/4A30/ES |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_S | [8 empty] | 和順DS.101E | 101E (非取樣點) | TIE | D20/11/100/E1 |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_S | [8 empty] | 和順DS.102E | 102E (非取樣點) | TIE | D20/11/100/E2 |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 和順DS.101 | 101 (非取樣點) | TIE | D20/11/100/D1 |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 和順DS.102 | 102 (非取樣點) | TIE | D20/11/100/D2 |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 和順DS.1501E | 1501E (非取樣點) | TIE | D20/161/1500/E1 |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 和順DS.1502E | 1502E (非取樣點) | TIE | D20/161/1500/E2 |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_S | [8 empty] | 和順DS.201E | 201E (非取樣點) | TIE | D20/11/200/E1 |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_S | [8 empty] | 和順DS.202E | 202E (非取樣點) | TIE | D20/11/200/E2 |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 和順DS.201 | 201 (非取樣點) | TIE | D20/11/200/D1 |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 和順DS.202 | 202 (非取樣點) | TIE | D20/11/200/D2 |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 和順DS.391 | 391 (非取樣點) | OTHER | D20/11/390/D1 |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 和順DS.391E | 391E (非取樣點) | OTHER | D20/11/390/E1 |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 和順DS.491 | 491 (非取樣點) | OTHER | D20/11/490/D1 |  |  |  |  | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 和順DS.491E | 491E (非取樣點) | OTHER | D20/11/490/E1 |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1750TE | 1750TE (非取樣點) | MTR | D20/161/1750/TE0 |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1750BE | 1750BE (非取樣點) | MTR | D20/161/1750/BE0 |  |  |  |  | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 和順DS.311 | 311 (非取樣點) | MTR | D20/11/310/D1 |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 和順DS.311E | 311E (非取樣點) | MTR | D20/11/310/E1 |  |  |  |  | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 和順DS.321 | 321 (非取樣點) | MTR | D20/11/320/D1 |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 和順DS.321E | 321E (非取樣點) | MTR | D20/11/320/E1 |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1760TE | 1760TE (非取樣點) | MTR | D20/161/1760/TE0 |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1760BE | 1760BE (非取樣點) | MTR | D20/161/1760/BE0 |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 和順DS.331 | 331 (非取樣點) | MTR | D20/11/330/D1 |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 和順DS.331E | 331E (非取樣點) | MTR | D20/11/330/E1 |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 和順DS.341 | 341 (非取樣點) | MTR | D20/11/340/D1 |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 和順DS.341E | 341E (非取樣點) | MTR | D20/11/340/E1 |  |  |  |  | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 和順DS.211E | 211E (非取樣點) | SC | D20/11/210/E1 |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 和順DS.211 | 211 (非取樣點) | SC | D20/11/210/D1 |  |  |  |  | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 和順DS.221E | 221E (非取樣點) | SC | D20/11/220/E1 |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 和順DS.221 | 221 (非取樣點) | SC | D20/11/220/D1 |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 和順DS.231E | 231E (非取樣點) | SC | D20/11/230/E1 |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 和順DS.231 | 231 (非取樣點) | SC | D20/11/230/D1 |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 和順DS.241E | 241E (非取樣點) | SC | D20/11/240/E1 |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 和順DS.241 | 241 (非取樣點) | SC | D20/11/240/D1 |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 和順DS.15B1E | 15B1E (非取樣點) | BUS | D20/161/161B1E/E1 |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 和順DS.15B2E | 15B2E (非取樣點) | BUS | D20/161/161B2E/E2 |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 和順DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 770 | NotelDIPoint | [38 empty] | START/STOP | STOP
D20 | 和順DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 和順DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 和順DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 和順DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 和順DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 和順DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 和順DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1770TE | 1770TE (非取樣點) | MTR | D20/161/1770/TE0 |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.1770BE | 1770BE (非取樣點) | MTR | D20/161/1770/BE0 |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 和順DS.351 | 351 (非取樣點) | MTR | D20/22/350/D1 |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 和順DS.351E | 351E (非取樣點) | MTR | D20/22/350/E1 |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 和順DS.251E | 251E (非取樣點) | SC | D20/22/250/E1 |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 和順DS.251 | 251 (非取樣點) | SC | [5 empty] | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 和順DS.261E | 261E (非取樣點) | SC | D20/22/260/E1 |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 和順DS.261 | 261 (非取樣點) | SC | [5 empty] | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A51 | 4A51_DS |  | DS1 | 4A51_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_DS | 4A51_DS (非取樣點) | FEEDER | D20/22/4A51/DS |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A51 | 4A51_ES |  | A510 | 4A51_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A51_ES | 4A51_ES (非取樣點) | FEEDER | D20/22/4A51/ES |  |  |  |  | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A52 | 4A52_DS |  | DS1 | 4A52_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_DS | 4A52_DS (非取樣點) | FEEDER | D20/22/4A52/DS |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A52 | 4A52_ES |  | A520 | 4A52_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A52_ES | 4A52_ES (非取樣點) | FEEDER | D20/22/4A52/ES |  |  |  |  | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A53 | 4A53_DS |  | DS1 | 4A53_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_DS | 4A53_DS (非取樣點) | FEEDER | D20/22/4A53/DS |  |  |  |  | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A53 | 4A53_ES |  | A530 | 4A53_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A53_ES | 4A53_ES (非取樣點) | FEEDER | D20/22/4A53/ES |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A54 | 4A54_DS |  | DS1 | 4A54_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_DS | 4A54_DS (非取樣點) | FEEDER | D20/22/4A54/DS |  |  |  |  | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A54 | 4A54_ES |  | A540 | 4A54_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A54_ES | 4A54_ES (非取樣點) | FEEDER | D20/22/4A54/ES |  |  |  |  | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A55 | 4A55_DS |  | DS1 | 4A55_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_DS | 4A55_DS (非取樣點) | FEEDER | D20/22/4A55/DS |  |  |  |  | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A55 | 4A55_ES |  | A550 | 4A55_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A55_ES | 4A55_ES (非取樣點) | FEEDER | D20/22/4A55/ES |  |  |  |  | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A56 | 4A56_DS |  | DS1 | 4A56_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_DS | 4A56_DS (非取樣點) | FEEDER | D20/22/4A56/DS |  |  |  |  | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A56 | 4A56_ES |  | A560 | 4A56_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A56_ES | 4A56_ES (非取樣點) | FEEDER | D20/22/4A56/ES |  |  |  |  | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A57 | 4A57_DS |  | DS1 | 4A57_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_DS | 4A57_DS (非取樣點) | FEEDER | D20/22/4A57/DS |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A57 | 4A57_ES |  | A570 | 4A57_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A57_ES | 4A57_ES (非取樣點) | FEEDER | D20/22/4A57/ES |  |  |  |  | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 4A58 | 4A58_DS |  | DS1 | 4A58_DS | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_DS | 4A58_DS (非取樣點) | FEEDER | D20/22/4A58/DS |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 4A58 | 4A58_ES |  | A580 | 4A58_ES | [24 empty] | DDCS4_1 | [8 empty] | 和順DS.4A58_ES | 4A58_ES (非取樣點) | FEEDER | D20/22/4A58/ES |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 3 | #3 |  | BE | #3_BE | [24 empty] | ADCS_S | [8 empty] | 和順DS.#3_BE | #3 BE(非取樣點) | OTHER | [5 empty] | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D20 | 和順DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 和順DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D20 | 和順DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_S | [8 empty] | 和順DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo