## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.310_DS | 310_DS (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.310_ES | 310_ES (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_A1 | [8 empty] | 台西DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.330_DS | 330_DS (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.330_ES | 330_ES (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.320_DS | 320_DS (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.320_ES | 320_ES (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.340_DS | 340_DS (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.340_ES | 340_ES (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP21_DS | XP21_DS (非取樣點) | FEEDER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP21_ES | XP21_ES (非取樣點) | FEEDER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP22_DS | XP22_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP22_ES | XP22_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP23_DS | XP23_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP23_ES | XP23_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP24_DS | XP24_DS (非取樣點) | FEEDER | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP24_ES | XP24_ES (非取樣點) | FEEDER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP25_DS | XP25_DS (非取樣點) | FEEDER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP25_ES | XP25_ES (非取樣點) | FEEDER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP26_DS | XP26_DS (非取樣點) | FEEDER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP26_ES | XP26_ES (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | DS1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.100_DS | 100_DS (非取樣點) | TIE | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP34_DS | XP34_DS (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP34_ES | XP34_ES (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP33_DS | XP33_DS (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP33_ES | XP33_ES (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP32_DS | XP32_DS (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP32_ES | XP32_ES (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP31_DS | XP31_DS (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP31_ES | XP31_ES (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP30_DS | XP30_DS (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP30_ES | XP30_ES (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP29_DS | XP29_DS (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP29_ES | XP29_ES (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP28_DS | XP28_DS (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP28_ES | XP28_ES (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP27_DS | XP27_DS (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP27_ES | XP27_ES (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | DS1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.200_DS | 200_DS (非取樣點) | TIE | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP35_DS | XP35_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP35_ES | XP35_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP36_DS | XP36_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP36_ES | XP36_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP37_DS | XP37_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP37_ES | XP37_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP38_DS | XP38_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP38_ES | XP38_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP39_DS | XP39_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP39_ES | XP39_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP40_DS | XP40_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D21_D1 | [8 empty] | 台西DS.XP40_ES | XP40_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D21_A1 | [8 empty] | 台西DS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1BUS | #1BUS |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aahz | B2/D21_A1 | [8 empty] | 台西DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 2BUS | #2BUS |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aahz | B2/D21_A1 | [8 empty] | 台西DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 80 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 81 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D21_A1 | [8 empty] | 台西DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 82 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D21 | 台西DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D21_A1 | [8 empty] | 台西DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 83 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1560 | MW | 北港台西線 1560 瓦 | MW_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_MW | 北港台西線 MW | LINE161 | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1560 | MVAR | 北港台西線 1560 乏 | MVAR_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_MVAR | 北港台西線 MVAR | LINE161 | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1550 | MW | 雲林台西雲高線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_MW | 雲林台西雲高線 MW | LINE161 | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1550 | MVAR | 雲林台西雲高線 1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_MVAR | 雲林台西雲高線 MVAR | LINE161 | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1510 | MW | 台西六輕紅線 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1510_MW | 塑化紅線 MW | LINE161 | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1510 | MVAR | 台西六輕紅線 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1510_MVAR | 塑化紅線 MVAR | LINE161 | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1520 | MW | 台西六輕白線 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1520_MW | 塑化白線 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1520 | MVAR | 台西六輕白線 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1520_MVAR | 塑化白線 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | DCV | 65 | DC-P電壓 | kV_-150_150(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | DCV | -65 | DC-N電壓 | kV_-150_150(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1500 | A | 161KV TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | #1ATR | ℃ | #1ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | #1BTR | ℃ | #1BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 台西DS.TEST_CB | TEST CB | OTHER | [5 empty] | 98 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04D21/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1560 | ON/OFF | 北港台西線 1560 CB |  | aaba | B2/D21_A1 | [8 empty] | 台西DS.1560_CB | 1560(北港台西線) CB | LINE161 | [5 empty] | 99 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #2ATR | ℃ | #2ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #2BTR | ℃ | #2BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D21TN06/T2 |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1550 | ON/OFF | 雲林台西雲高線 1550 CB |  | aaca | B2/D21_A1 | [8 empty] | 台西DS.1550_CB | 1550(雲林台西雲高線) CB | LINE161 | [5 empty] | 103 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0010 |  | 0003 | 1-01-02 |  | 1-03 | 1510 | ON/OFF | 台西六輕紅線 1510 CB |  | aafa | B2/D21_A1 | [8 empty] | 台西DS.1510_CB | 1510(塑化紅線) CB | LINE161 | [5 empty] | 104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #3DTR | ℃ | #3DTR 油溫 |  |  | B1/D21_A1 | [16 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #3DTR | ℃ | #3DTR 線溫 |  |  | B1/D21_A1 | [16 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0015 |  | 0004 | 1-01-07 |  | 1-04 | 1520 | ON/OFF | 台西六輕白線 1520 CB |  | aaga | B2/D21_A1 | [8 empty] | 台西DS.1520_CB | 1520(塑化白線) CB | LINE161 | [5 empty] | 107 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 310 | MW | #1DTR 1A 310 瓦 | MW_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 310 | MVAR | #1DTR 1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 310R | A | #1DTR 1A 310 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 310S | A | #1DTR 1A 310 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 310T | A | #1DTR 1A 310 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F1 | MVAR | F1 台一線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台一線KVAR | 11KV台一線 KVAR | FEEDER | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F1 | A | F1 台一線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台一線A1 | 11KV台一線 R相AMP | FEEDER | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F1 | A | F1 台一線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台一線A2 | 11KV台一線 S相AMP | FEEDER | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F1 | A | F1 台一線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台一線A3 | 11KV台一線 T相AMP | FEEDER | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F2 | MVAR | F2 台二線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台二線KVAR | 11KV台二線 KVAR | FEEDER | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F2 | A | F2 台二線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台二線A1 | 11KV台二線 R相AMP | FEEDER | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F2 | A | F2 台二線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台二線A2 | 11KV台二線 S相AMP | FEEDER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F2 | A | F2 台二線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台二線A3 | 11KV台二線 T相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F3 | MVAR | F3 台三線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台三線KVAR | 11KV台三線 KVAR | FEEDER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F3 | A | F3 台三線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台三線A1 | 11KV台三線 R相AMP | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F3 | A | F3 台三線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台三線A2 | 11KV台三線 S相AMP | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F3 | A | F3 台三線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台三線A3 | 11KV台三線 T相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F4 | MVAR | F4 台四線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台四線KVAR | 11KV台四線 KVAR | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F4 | A | F4 台四線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台四線A1 | 11KV台四線 R相AMP | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F4 | A | F4 台四線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台四線A2 | 11KV台四線 S相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F4 | A | F4 台四線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台四線A3 | 11KV台四線 T相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F5 | MVAR | F5 台五線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台五線KVAR | 11KV台五線 KVAR | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F5 | A | F5 台五線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台五線A1 | 11KV台五線 R相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F5 | A | F5 台五線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台五線A2 | 11KV台五線 S相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | F5 | A | F5 台五線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台五線A3 | 11KV台五線 T相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | F6 | MVAR | F6 台六線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台六線KVAR | 11KV台六線 KVAR | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | F6 | A | F6 台六線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台六線A1 | 11KV台六線 R相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | F6 | A | F6 台六線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台六線A2 | 11KV台六線 S相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | F6 | A | F6 台六線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台六線A3 | 11KV台六線 T相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0072 |  |  | 1-C8 |  |  | #1A BUS | KV | #1DTR 1A 310 BUS電壓 | kV_-9_9(-2000_2000) | aaa | B3/D21_A1 | [8 empty] | 台西DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 100 | A | #1TIE 100 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 100 | A | #1TIE 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 100 | A | #1TIE 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 330 | MW | #2DTR 2A 330 瓦 | MW_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 330 | MVAR | #2DTR 2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 330 | A | #2DTR 2A 330 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 330 | A | #2DTR 2A 330 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 330 | A | #2DTR 2A 330 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F7 | MW | F7 台十四線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台14線KVAR | 11KV台14線 KVAR | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F7 | A | F7 台十四線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台14線A1 | 11KV台14線 R相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F7 | A | F7 台十四線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台14線A2 | 11KV台14線 S相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F7 | A | F7 台十四線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台14線A3 | 11KV台14線 T相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F8 | MVAR | F8 台十三線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台13線KVAR | 11KV台13線 KVAR | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F8 | A | F8 台十三線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台13線A1 | 11KV台13線 R相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F8 | A | F8 台十三線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台13線A2 | 11KV台13線 S相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F8 | A | F8 台十三線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台13線A3 | 11KV台13線 T相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F9 | MVAR | F9 台十二線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台12線KVAR | 11KV台12線 KVAR | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F9 | A | F9 台十二線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台12線A1 | 11KV台12線 R相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F9 | A | F9 台十二線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台12線A2 | 11KV台12線 S相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F9 | A | F9 台十二線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台12線A3 | 11KV台12線 T相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F10 | MVAR | F10 台十一線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台11線KVAR | 11KV台11線 KVAR | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F10 | A | F10 台十一線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台11線A1 | 11KV台11線 R相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F10 | A | F10 台十一線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台11線A2 | 11KV台11線 S相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F10 | A | F10 台十一線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台11線A3 | 11KV台11線 T相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0097 |  |  | 1-E1 |  |  | #2A BUS | KV | #2DTR 2A 330 BUS電壓 | kV_-9_9(-2000_2000) | aba | B3/D21_A1 | [8 empty] | 台西DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 320 | MW | #1DTR 1B 320 瓦 | MW_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 320 | MVAR | #1DTR 1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 320 | A | #1DTR 1B 320 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 320 | A | #1DTR 1B 320 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 320 | A | #1DTR 1B 320 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | F11 | MVAR | F11 台十線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台十線KVAR | 11KV台十線 KVAR | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F11 | A | F11 台十線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台十線A1 | 11KV台十線 R相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F11 | A | F11 台十線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台十線A2 | 11KV台十線 S相AMP | FEEDER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F11 | A | F11 台十線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台十線A3 | 11KV台十線 T相AMP | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F12 | MVAR | F12 台九線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台九線KVAR | 11KV台九線 KVAR | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F12 | A | F12 台九線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台九線A1 | 11KV台九線 R相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F12 | A | F12 台九線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台九線A2 | 11KV台九線 S相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F12 | A | F12 台九線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台九線A3 | 11KV台九線 T相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F13 | MVAR | F13 台八線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台八線KVAR | 11KV台八線 KVAR | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F13 | A | F13 台八線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台八線A1 | 11KV台八線 R相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F13 | A | F13 台八線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台八線A2 | 11KV台八線 S相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F13 | A | F13 台八線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台八線A3 | 11KV台八線 T相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F14 | MVAR | F14 台七線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台七線KVAR | 11KV台七線 KVAR | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F14 | A | F14 台七線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台七線A1 | 11KV台七線 R相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F14 | A | F14 台七線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台七線A2 | 11KV台七線 S相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F14 | A | F14 台七線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台七線A3 | 11KV台七線 T相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0119 |  |  | 1-F7 |  |  | #1B BUS | KV | #1DTR 1B 320 BUS電壓 | kV_-9_9(-2000_2000) | baa | B3/D21_A1 | [8 empty] | 台西DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 200 | A | #2TIE 200 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 200 | A | #2TIE 200 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 200 | A | #2TIE 200 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C20R1200 | 1140 | 1200 | 1320 | 1476 | 2.27 | -1140 | -1200 | -1320 | -1476 | 1 | 0.01 | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 340 | MW | #2DTR 2B 340 瓦 | MW_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 340 | MVAR | #2DTR 2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 340 | A | #2DTR 2B 340 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 340 | A | #2DTR 2B 340 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 340 | A | #2DTR 2B 340 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | F15 | MVAR | F15 台十五線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台15線KVAR | 11KV台15線 KVAR | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | F15 | A | F15 台十五線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台15線A1 | 11KV台15線 R相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F15 | A | F15 台十五線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台15線A2 | 11KV台15線 S相AMP | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F15 | A | F15 台十五線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台15線A3 | 11KV台15線 T相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F16 | MVAR | F16 台十六線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台16線KVAR | 11KV台16線 KVAR | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F16 | A | F16 台十六線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台16線A1 | 11KV台16線 R相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F16 | A | F16 台十六線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台16線A2 | 11KV台16線 S相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F16 | A | F16 台十六線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台16線A3 | 11KV台16線 T相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F17 | MVAR | F17 台十七線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台17線KVAR | 11KV台17線 KVAR | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F17 | A | F17 台十七線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台17線A1 | 11KV台17線 R相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F17 | A | F17 台十七線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台17線A2 | 11KV台17線 S相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | F17 | A | F17 台十七線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台17線A3 | 11KV台17線 T相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | F18 | MVAR | F18 台十八線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台18線KVAR | 11KV台18線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | F18 | A | F18 台十八線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台18線A1 | 11KV台18線 R相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | F18 | A | F18 台十八線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台18線A2 | 11KV台18線 S相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | F18 | A | F18 台十八線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台18線A3 | 11KV台18線 T相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | F19 | MVAR | F19 台十九線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台19線KVAR | 11KV台19線 KVAR | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | F19 | A | F19 台十九線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台19線A1 | 11KV台19線 R相AMP | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | F19 | A | F19 台十九線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台19線A2 | 11KV台19線 S相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | F19 | A | F19 台十九線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台19線A3 | 11KV台19線 T相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | F20 | MVAR | F20 台二十線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台20線KVAR | 11KV台20線 KVAR | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F20 | A | F20 台二十線 R相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台20線A1 | 11KV台20線 R相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F20 | A | F20 台二十線 S相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台20線A2 | 11KV台20線 S相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F20 | A | F20 台二十線 T相電流 | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台20線A3 | 11KV台20線 T相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0155 |  |  | 2-9B |  |  | #2B BUS | KV | #2DTR 2B 340 BUS電壓 | kV_-9_9(-2000_2000) | bba | B3/D21_A1 | [8 empty] | 台西DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 台一線 | A | 台一線F1 XP21 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台一線A0 | 11KV台一線 N相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 台二線 | A | 台二線F2 XP22 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台二線A0 | 11KV台二線 N相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 台三線 | A | 台三線F3 XP23 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台三線A0 | 11KV台三線 N相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 台四線 | A | 台四線F4 XP24 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台四線A0 | 11KV台四線 N相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 台五線 | A | 台五線F5 XP25 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台五線A0 | 11KV台五線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 台六線 | A | 台六線F6 XP26 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台六線A0 | 11KV台六線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 台七線 | A | 台七線F14 XP27 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台七線A0 | 11KV台七線 N相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 台八線 | A | 台八線F13 XP28 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台八線A0 | 11KV台八線 N相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 台九線 | A | 台九線F12 XP29 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台九線A0 | 11KV台九線 N相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 台十線 | A | 台十線F11 XP30 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台十線A0 | 11KV台十線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 台十一線 | A | 台十一線F10 XP31 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台11線A0 | 11KV台11線 N相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 台十二線 | A | 台十二線F9 XP32 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台12線A0 | 11KV台12線 N相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 台十三線 | A | 台十三線F8 XP33 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台13線A0 | 11KV台13線 N相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 台十四線 | A | 台十四線F7 XP34 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台14線A0 | 11KV台14線 N相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 台十五線 | A | 台十五線F15 XP35 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台15線A0 | 11KV台15線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 台十六線 | A | 台十六線F16 XP36 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台16線A0 | 11KV台16線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 台十七線 | A | 台十七線F17 XP37 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台17線A0 | 11KV台17線 N相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 台十八線 | A | 台十八線F18 XP38 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台18線A0 | 11KV台18線 N相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 台十九線 | A | 台十九線F19 XP39 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台19線A0 | 11KV台19線 N相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 台二十線 | A | 台二十線F20 XP40 A(N) | A_-600_600(-2000_2000) |  | B2/D21_D1 | [8 empty] | 台西DS.台20線A0 | 11KV台20線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | OilPreR1 |  |  | MvMoment | R相正導油壓 |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 1560 | KG | 北港台西線 1560 R1相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_OF_R1 | 北港台西線 R1相 油壓 | OTHER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | OilPreR2 |  |  | MvMoment | R相副導油壓 |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 1560 | KG | 北港台西線 1560 R2相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_OF_R2 | 北港台西線 R2相 油壓 | OTHER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | OilPreS1 |  |  | MvMoment | S相正導油壓 |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 1560 | KG | 北港台西線 1560 S1相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_OF_S1 | 北港台西線 S1相 油壓 | OTHER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | OilPreS2 |  |  | MvMoment | S相副導油壓 |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 1560 | KG | 北港台西線 1560 S2相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_OF_S2 | 北港台西線 S2相 油壓 | OTHER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | OilPreT1 |  |  | MvMoment | T相正導油壓 |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 1560 | KG | 北港台西線 1560 T1相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_OF_T1 | 北港台西線 T1相 油壓 | OTHER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | OilPreT2 |  |  | MvMoment | T相副導油壓 |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 1560 | KG | 北港台西線 1560 T2相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1560_OF_T2 | 北港台西線 T2相 油壓 | OTHER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | OilPreR1 |  |  | MvMoment | R相正導油壓 |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 1550 | KG | 雲林台西雲高線 1550 R1相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_OF_R1 | 雲林台西雲高線 R1相 油壓 | OTHER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | OilPreR2 |  |  | MvMoment | R相副導油壓 |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 1550 | KG | 雲林台西雲高線 1550 R2相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_OF_R2 | 雲林台西雲高線 R2相 油壓 | OTHER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | OilPreS1 |  |  | MvMoment | S相正導油壓 |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 1550 | KG | 雲林台西雲高線 1550 S1相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_OF_S1 | 雲林台西雲高線 S1相 油壓 | OTHER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | OilPreS2 |  |  | MvMoment | S相副導油壓 |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 1550 | KG | 雲林台西雲高線 1550 S2相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_OF_S2 | 雲林台西雲高線 S2相 油壓 | OTHER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | OilPreT1 |  |  | MvMoment | T相正導油壓 |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 1550 | KG | 雲林台西雲高線 1550 T1相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_OF_T1 | 雲林台西雲高線 T1相 油壓 | OTHER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | OilPreT2 |  |  | MvMoment | T相副導油壓 |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 1550 | KG | 雲林台西雲高線 1550 T2相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D21_A1 | [8 empty] | 台西DS.1550_OF_T2 | 雲林台西雲高線 T2相 油壓 | OTHER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 10 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0009 | 1-05-00 |  | 1-09 | 1500 | ON/OFF | 161KV TIE 1500 CB |  | aaez | B2/D21_A1 | [8 empty] | 台西DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1560 | 87A1 | 北港台西線 1560 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_87A1 | 北港台西線(1560) #1 87RY | LINE161 | [5 empty] | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 1560 | 87A2 | 北港台西線 1560 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_87A2 | 北港台西線(1560) #2 87RY | LINE161 | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1560 | PHA | 北港台西線 1560 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_PHA | 北港台西線(1560) 相間RY | LINE161 | [5 empty] | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1560 | GDA | 北港台西線 1560 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_GDA | 北港台西線(1560) 接地RY | LINE161 | [5 empty] | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0045 |  | 0010 | 1-05-05 |  | 1-0A | 1750 | ON/OFF | #1DTR 1750 CB |  | aaab | ELEM/D21_A1 | [8 empty] | 台西DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1550 | 87A1 | 雲林台西雲高線 1550 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_87A1 | 雲林台西雲高線(1550) #1 87RY | LINE161 | [5 empty] | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1550 | 87A2 | 雲林台西雲高線 1550 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_87A2 | 雲林台西雲高線(1550) #2 87RY | LINE161 | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1550 | PHA | 雲林台西雲高線 1550 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_PHA | 雲林台西雲高線(1550) 相間RY | LINE161 | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1550 | GDA | 雲林台西雲高線 1550 CB |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_GDA | 雲林台西雲高線(1550) 接地RY | LINE161 | [5 empty] | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0055 |  | 0011 | 1-06-07 |  | 1-0B | 1760 | ON/OFF | #2DTR 1760 CB |  | aadb | ELEM/D21_A1 | [8 empty] | 台西DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1510 | 85A | 台西六輕紅線 1510 85A |  |  | B2/D21_A1 | [8 empty] | 台西DS.1510_85A | 塑化紅線(1510) 85RY | LINE161 | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1510 | PHA | 台西六輕紅線 1510 PHA |  |  | B2/D21_A1 | [8 empty] | 台西DS.1510_PHA | 塑化紅線(1510) 相間RY | LINE161 | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1510 | GDA | 台西六輕紅線 1510 GDA |  |  | B2/D21_A1 | [8 empty] | 台西DS.1510_GDA | 塑化紅線(1510) 接地RY | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbD | B/1Bus | B/2Bus | T/3DTR |  | 0065 |  | 0012 | 1-08-01 |  | 1-0C | 1770 | ON/OFF | #3DTR 1770 CB |  | aa | ELEM/D21_A1 | [16 empty] | 268 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1520 | 85A | 台西六輕白線 1520 85A |  |  | B2/D21_A1 | [8 empty] | 台西DS.1520_85A | 塑化白線(1520) 85RY | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1520 | PHA | 台西六輕白線 1520 PHA |  |  | B2/D21_A1 | [8 empty] | 台西DS.1520_PHA | 塑化白線(1520) 相間RY | LINE161 | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1520 | GDA | 台西六輕白線 1520 GDA |  |  | B2/D21_A1 | [8 empty] | 台西DS.1520_GDA | 塑化白線(1520) 接地RY | LINE161 | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | T/1DTR(A) |  |  | 0051 |  | 0016 | 1-06-03 |  | 1-10 | 310 | ON/OFF | #1DTR 1A 310 CB |  | aaca | ELEM/D21_A1 | [8 empty] | 台西DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1500 | 50A | 161KV TIE 1500 50A |  |  | B2/D21_A1 | [8 empty] | 台西DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D21_A1 | [8 empty] | 台西DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D21_A1 | [8 empty] | 台西DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 161 kV | RCA | 復閉電驛動作警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | C/1SC |  |  | 0146 |  | 0018 | 2-02-02 |  | 1-12 | Locate Empty |  |  |  | aadb | B3/D21_A1 | [8 empty] | 台西DS.210_CB_1 | 210(11KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 277 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1DTR | 87A | #1DTR 87A |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1DTR | 51ZA | #1DTR 51ZA |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 1750 | PHA(51A) | #1DTR 1750 PHA |  |  | B2/D21_A1 | [8 empty] | 台西DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | 1750 | GDA(51NA) | #1DTR 1750 GDA |  |  | B2/D21_A1 | [8 empty] | 台西DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/XP21/T1 |  |  | 0128 |  | 0019 | 2-00-00 |  | 1-13 | Locate Empty |  |  |  | aaeb | B2/D21_D1 | [8 empty] | 台西DS.XP21_CB | XP21(11KV台一線) CB | FEEDER | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 310 | PHA | #1DTR 1A 310 PHA |  |  | B3/D21_A1 | [8 empty] | 台西DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #1DTR | A/N | #1DTR 86A |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_86A | #1DTR 86A | OTHER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #2DTR | A/N | #2DTR 86A |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_86A | #2DTR 86A | OTHER | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/XP22/T1 |  |  | 0131 |  | 0020 | 2-00-03 |  | 1-14 | Locate Empty |  |  |  | aafb | B2/D21_D1 | [8 empty] | 台西DS.XP22_CB | XP22(11KV台二線) CB | FEEDER | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #2DTR | 87A | #2DTR 87A |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #2DTR | 51ZA | #2DTR 51ZA |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | 1760 | PHA | #2DTR 1760 PHA |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 1760 | GDA | #2DTR 1760 GDA |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/XP23/T1 |  |  | 0134 |  | 0021 | 2-00-06 |  | 1-15 | Locate Empty |  |  |  | aagb | B2/D21_D1 | [8 empty] | 台西DS.XP23_CB | XP23(11KV台三線) CB | FEEDER | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 330 | PHA | #2DTR 2A 330 PHA |  |  | B3/D21_A1 | [8 empty] | 台西DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/XP24/T1 |  |  | 0137 |  | 0022 | 2-01-01 |  | 1-16 | Locate Empty |  |  |  | aahb | B2/D21_D1 | [8 empty] | 台西DS.XP24_CB | XP24(11KV台四線) CB | FEEDER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 320 | PHA | #1DTR 1B 320 PHA |  |  | B3/D21_A1 | [8 empty] | 台西DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/XP25/T1 |  |  | 0140 |  | 0023 | 2-01-04 |  | 1-17 | Locate Empty |  |  |  | aaib | B2/D21_D1 | [8 empty] | 台西DS.XP25_CB | XP25(11KV台五線) CB | FEEDER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #3DTR | 87A | #3DTR 87A |  |  | B1/D21_A1 | [16 empty] | 298 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #3DTR | 96PA | #3DTR 機械保護動作(96PA) |  |  | B1/D21_A1 | [16 empty] | 299 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #3DTR | 51Z | #3DTR 51ZA |  |  | B1/D21_A1 | [16 empty] | 300 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 1770 | PHA | #3DTR 1770 PHA |  |  | B1/D21_A1 | [16 empty] | 301 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 1770 | GDA | #3DTR 1770 GDA |  |  | B1/D21_A1 | [16 empty] | 302 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/XP26/T1 |  |  | 0143 |  | 0024 | 2-01-07 |  | 1-18 | Locate Empty |  |  |  | aajb | B2/D21_D1 | [8 empty] | 台西DS.XP26_CB | XP26(11KV台六線) CB | FEEDER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 340 | PHA | #2DTR 2B 340 PHA |  |  | B3/D21_A1 | [8 empty] | 台西DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D21_A1 | [8 empty] | 台西DS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D21_A1 | [16 empty] | 306 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | C/2SC |  |  | 0149 |  | 0025 | 2-02-05 |  | 1-19 | Locate Empty |  |  |  | aakb | B3/D21_A1 | [8 empty] | 台西DS.220_CB_1 | 220(11KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 307 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 2-00-01 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP21_PHA | 11KV台一線(XP21) 相間RY | FEEDER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 2-00-02 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP21_GDA | 11KV台一線(XP21) 接地RY | FEEDER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1ABus | B/2ABus |  |  | 0152 |  | 0026 | 2-03-00 |  | 1-1A | Locate Empty |  |  |  | aalb | B3/D21_A1 | [16 empty] | 310 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 2-00-04 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP22_PHA | 11KV台二線(XP22) 相間RY | FEEDER | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 2-00-05 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP22_GDA | 11KV台二線(XP22) 接地RY | FEEDER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/XP34/T1 |  |  | 0155 |  | 0027 | 2-03-03 |  | 1-1B | Locate Empty |  |  |  | abab | B2/D21_D1 | [8 empty] | 台西DS.XP34_CB | XP34(11KV台14線) CB | FEEDER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 2-00-07 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP23_PHA | 11KV台三線(XP23) 相間RY | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 2-01-00 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP23_GDA | 11KV台三線(XP23) 接地RY | FEEDER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/XP33/T1 |  |  | 0158 |  | 0028 | 2-03-06 |  | 1-1C | Locate Empty |  |  |  | abbb | B2/D21_D1 | [8 empty] | 台西DS.XP33_CB | XP33(11KV台13線) CB | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 2-01-02 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP24_PHA | 11KV台四線(XP24) 相間RY | FEEDER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 2-01-03 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP24_GDA | 11KV台四線(XP24) 接地RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/XP32/T1 |  |  | 0161 |  | 0029 | 1-14-01 |  | 1-1D | F9 | ON/OFF | F9 CB 台十二線 |  | abcb | B2/D21_D1 | [8 empty] | 台西DS.XP32_CB | XP32(11KV台12線) CB | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 2-01-05 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP25_PHA | 11KV台五線(XP25) 相間RY | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 2-01-06 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP25_GDA | 11KV台五線(XP25) 接地RY | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/XP31/T1 |  |  | 0164 |  | 0030 | 1-14-04 |  | 1-1E | F10 | ON/OFF | F10 CB 台十一線 |  | abdb | B2/D21_D1 | [8 empty] | 台西DS.XP31_CB | XP31(11KV台11線) CB | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 2-02-00 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP26_PHA | 11KV台六線(XP26) 相間RY | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 2-02-01 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP26_GDA | 11KV台六線(XP26) 接地RY | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | C/4SC |  |  | 0167 |  | 0031 | 1-14-07 |  | 1-1F | 240 | ON/OFF | #2BSC 240CB |  | abeb | B3/D21_A1 | [8 empty] | 台西DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0147 |  |  | 2-02-03 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0148 |  |  | 2-02-04 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | T/2DTR(A) |  |  | 0061 |  | 0032 | 1-07-05 |  | 1-20 | 330 | ON/OFF | #2DTR 2A 330 CB |  | abfa | ELEM/D21_A1 | [8 empty] | 台西DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0150 |  |  | 2-02-06 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0151 |  |  | 2-02-07 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | T/1DTR(B) |  |  | 0063 |  | 0033 | 1-07-07 |  | 1-21 | 320 | ON/OFF | #1DTR 1B 320 CB |  | baba | ELEM/D21_A1 | [8 empty] | 台西DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 2-03-01 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [16 empty] | 332 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 2-03-02 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [16 empty] | 333 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | C/3SC |  |  | 0182 |  | 0034 | 1-16-06 |  | 1-22 | 230 | ON/OFF | #2ASC 230CB |  | bacb | B3/D21_A1 | [8 empty] | 台西DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 2-03-04 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP34_PHA | 11KV台14線(XP34) 相間RY | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 2-03-05 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP34_GDA | 11KV台14線(XP34) 接地RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/XP30/T1 |  |  | 0170 |  | 0035 | 1-15-02 |  | 1-23 | F11 | ON/OFF | F11 CB 台十線 |  | badb | B2/D21_D1 | [8 empty] | 台西DS.XP30_CB | XP30(11KV台十線) CB | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 2-03-07 |  |  | Locate Empty |  |  |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP33_PHA | 11KV台13線(XP33) 相間RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F8 | 51NA | F8 GDA 台十三線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP33_GDA | 11KV台13線(XP33) 接地RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/XP29/T1 |  |  | 0173 |  | 0036 | 1-15-05 |  | 1-24 | F12 | ON/OFF | F12 CB 台九線 |  | baeb | B2/D21_D1 | [8 empty] | 台西DS.XP29_CB | XP29(11KV台九線) CB | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F9 | 51A | F9 PHA 台十二線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP32_PHA | 11KV台12線(XP32) 相間RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F9 | 51NA | F9 GDA 台十二線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP32_GDA | 11KV台12線(XP32) 接地RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/XP28/T1 |  |  | 0176 |  | 0037 | 1-16-00 |  | 1-25 | F13 | ON/OFF | F13 CB 台八線 |  | bafb | B2/D21_D1 | [8 empty] | 台西DS.XP28_CB | XP28(11KV台八線) CB | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F10 | 51A | F10 PHA 台十一線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP31_PHA | 11KV台11線(XP31) 相間RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F10 | 51NA | F10 GDA 台十一線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP31_GDA | 11KV台11線(XP31) 接地RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/XP27/T1 |  |  | 0179 |  | 0038 | 1-16-03 |  | 1-26 | F14 | ON/OFF | F14 CB 台七線 |  | bagb | B2/D21_D1 | [8 empty] | 台西DS.XP27_CB | XP27(11KV台七線) CB | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 240 | 51/51A | #2BSC 240 SCA 51+51N |  |  | B3/D21_A1 | [8 empty] | 台西DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 240 | 27/59 A | #2BSC 240 UVA 27+59 |  |  | B3/D21_A1 | [8 empty] | 台西DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdr | B/1BBus | B/2BBus |  |  | 0185 |  | 0039 | 1-17-01 |  | 1-27 | 200 | ON/OFF | #2TIE 200CB |  | bahb | B3/D21_A1 | [8 empty] | 台西DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | F11 | PHA | F11 PHA 台十線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP30_PHA | 11KV台十線(XP30) 相間RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | F11 | GDA | F11 GDA 台十線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP30_GDA | 11KV台十線(XP30) 接地RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | C/6SC |  |  | 0206 |  | 0040 | 1-19-06 |  | 1-28 | 260 | ON/OFF | #3BSC 260CB |  | bbab | B3/D21_A1 | [8 empty] | 台西DS.260_CB | 260(11KV #6SC) CB | SC | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F12 | 51A | F12 PHA 台九線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP29_PHA | 11KV台九線(XP29) 相間RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F12 | 51NA | F12 GDA 台九線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP29_GDA | 11KV台九線(XP29) 接地RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/XP35/T1 |  |  | 0188 |  | 0042 | 1-17-04 |  | 1-2A | F15 | ON/OFF | F15 CB 台十五線 |  | bbbb | B2/D21_D1 | [8 empty] | 台西DS.XP35_CB | XP35(11KV台15線) CB | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F13 | 51A | F13 PHA 台八線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP28_PHA | 11KV台八線(XP28) 相間RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F13 | 51NA | F13 GDA 台八線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP28_GDA | 11KV台八線(XP28) 接地RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/XP36/T1 |  |  | 0191 |  | 0043 | 1-17-07 |  | 1-2B | F16 | ON/OFF | F16 CB 台十六線 |  | bbcb | B2/D21_D1 | [8 empty] | 台西DS.XP36_CB | XP36(11KV台16線) CB | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | F14 | 51A | F14 PHA 台七線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP27_PHA | 11KV台七線(XP27) 相間RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | F14 | 51NA | F14 GDA 台七線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP27_GDA | 11KV台七線(XP27) 接地RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/XP37/T1 |  |  | 0194 |  | 0044 | 1-18-02 |  | 1-2C | F17 | ON/OFF | F17 CB 台十七線 |  | bbdb | B2/D21_D1 | [8 empty] | 台西DS.XP37_CB | XP37(11KV台17線) CB | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 230 | 51/51A | #2ASC 230 SCA 51+51N |  |  | B3/D21_A1 | [8 empty] | 台西DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | 230 | 27/59 A | #2ASC 230 UVA 27+59 |  |  | B3/D21_A1 | [8 empty] | 台西DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/XP38/T1 |  |  | 0197 |  | 0045 | 1-18-05 |  | 1-2D | F18 | ON/OFF | F18 CB 台十八線 |  | bbeb | B2/D21_D1 | [8 empty] | 台西DS.XP38_CB | XP38(11KV台18線) CB | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 200 | 51A | #2TIE 200 PHA |  |  | B3/D21_A1 | [8 empty] | 台西DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | 200 | 51NA | #2TIE 200 GDA |  |  | B3/D21_A1 | [8 empty] | 台西DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/XP39/T1 |  |  | 0200 |  | 0046 | 1-19-00 |  | 1-2E | F19 | ON/OFF | F19 CB 台十九線 |  | bbfb | B2/D21_D1 | [8 empty] | 台西DS.XP39_CB | XP39(11KV台19線) CB | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | F15 | 51A | F15 PHA 台十五線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP35_PHA | 11KV台15線(XP35) 相間RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | F15 | 51NA | F15 GDA 台十五線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP35_GDA | 11KV台15線(XP35) 接地RY | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/XP40/T1 |  |  | 0203 |  | 0047 | 1-19-03 |  | 1-2F | F20 | ON/OFF | F20 CB 台二十線 |  | bbgb | B2/D21_D1 | [8 empty] | 台西DS.XP40_CB | XP40(11KV台20線) CB | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | F16 | 51A | F16 PHA 台十六線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP36_PHA | 11KV台16線(XP36) 相間RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | F16 | 51NA | F16 GDA 台十六線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP36_GDA | 11KV台16線(XP36) 接地RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | C/5SC |  |  | 0209 |  | 0048 | 1-1A-01 |  | 1-30 | 250 | ON/OFF | #3ASC 250CB |  | bbhb | B3/D21_A1 | [8 empty] | 台西DS.250_CB | 250(11KV #5SC) CB | SC | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | F17 | 51A | F17 PHA 台十七線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP37_PHA | 11KV台17線(XP37) 相間RY | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | F17 | 51NA | F17 GDA 台十七線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP37_GDA | 11KV台17線(XP37) 接地RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | T/2DTR(B) |  |  | 0071 |  | 0049 | 1-08-07 |  | 1-31 | 340 | ON/OFF | #2DTR 2B 340 CB |  | bbia | ELEM/D21_A1 | [8 empty] | 台西DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | F18 | 51A | F18 PHA 台十八線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP38_PHA | 11KV台18線(XP38) 相間RY | FEEDER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | F18 | 51NA | F18 GDA 台十八線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP38_GDA | 11KV台18線(XP38) 接地RY | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0844 |  | 0054 | 2-34-12 |  | 1-36 | F1 | ON/OFF | F1 台一線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP21_ADJ | 11KV台一線(XP21) LCO分流器 U/L | FEEDER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | F19 | 51A | F19 PHA 台十九線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP39_PHA | 11KV台19線(XP39) 相間RY | FEEDER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | F19 | 51NA | F19 GDA 台十九線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP39_GDA | 11KV台19線(XP39) 接地RY | FEEDER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0845 |  | 0055 | 2-34-13 |  | 1-37 | F2 | ON/OFF | F2 台二線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP22_ADJ | 11KV台二線(XP22) LCO分流器 U/L | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | F20 | 51A | F20 PHA 台二十線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP40_PHA | 11KV台20線(XP40) 相間RY | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | F20 | 51NA | F20 GDA 台二十線 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP40_GDA | 11KV台20線(XP40) 接地RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0846 |  | 0056 | 2-34-14 |  | 1-38 | F3 | ON/OFF | F3 台三線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP23_ADJ | 11KV台三線(XP23) LCO分流器 U/L | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | 260 | 51/51A | #3BSC 260 SCA 51+51N |  |  | B3/D21_A1 | [8 empty] | 台西DS.260_SCA | 11KV #6SC 51,51N RY | SC | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | 260 | 27/59 A | #3BSC 260 UVA 27+59 |  |  | B3/D21_A1 | [8 empty] | 台西DS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0847 |  | 0057 | 2-34-15 |  | 1-39 | F4 | ON/OFF | F4 台四線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP24_ADJ | 11KV台四線(XP24) LCO分流器 U/L | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | 250 | 51/51NA | #3ASC 250 SCA 51+51N |  |  | B3/D21_A1 | [8 empty] | 台西DS.250_SCA | 11KV #5SC 51,51N RY | SC | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | 250 | 27/59 A | #3ASC 250 UVA 無設備 |  |  | B3/D21_A1 | [8 empty] | 台西DS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0848 |  | 0058 | 2-35-00 |  | 1-3A | F5 | ON/OFF | F5 台五線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP25_ADJ | 11KV台五線(XP25) LCO分流器 U/L | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU | L/R | L/R STATUS |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0849 |  | 0059 | 2-35-01 |  | 1-3B | F6 | ON/OFF | F6 台六線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP26_ADJ | 11KV台六線(XP26) LCO分流器 U/L | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0850 |  | 0060 | 2-35-02 |  | 1-3C | F7 | ON/OFF | F7 台十四線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP34_ADJ | 11KV台14線(XP34) LCO分流器 U/L | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0851 |  | 0061 | 2-35-03 |  | 1-3D | F8 | ON/OFF | F8 台十三線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP33_ADJ | 11KV台13線(XP33) LCO分流器 U/L | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0852 |  | 0062 | 2-35-04 |  | 1-3E | F9 | ON/OFF | F9 台十二線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP32_ADJ | 11KV台12線(XP32) LCO分流器 U/L | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 1550 | 87CFA | 雲林台西雲高線 87RY通訊故障 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_87CFA | 雲林台西雲高線(1550)RY通訊故障 | OTHER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-30-14 |  |  | 1550 | RYFA | 雲林台西雲高線數位電驛故障 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_RYFA | 雲林台西雲高線(1550)數位RY故障 | OTHER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0527 |  |  | 1-30-15 |  |  | 1560 | 87CFA | 北港台西線 87RY通訊故障 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_87CFA | 北港台西線(1560)87RY通訊故障 | OTHER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | 1560 | RYFA | 北港台西線數位電驛故障 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_RYFA | 北港台西線(1560)數位電驛故障 | OTHER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0853 |  | 0063 | 2-35-05 |  | 1-3F | F10 | ON/OFF | F10 台十一線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP31_ADJ | 11KV台11線(XP31) LCO分流器 U/L | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0064 | 1-30-02 |  | 1-40 | 1560 | USE/LOCK | 北港台西線 1560 87RY UL2 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_87UL2 | 北港台西線(1560) #2 87RY U/L | LINE161 | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D21_A1 | [8 empty] | 台西DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D21 | 台西DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA | 161KV BUS |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0065 | 1-30-03 |  | 1-41 | 1560 | USE/LOCK | 北港台西線 1560 79RY U/L |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_79UL | 北港台西線(1560) 79RY U/L | LINE161 | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0066 | 1-30-04 |  | 1-42 | 1550 | USE/LOCK | 雲林台西雲高線 1550 87RY UL2 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_87UL2 | 雲林台西雲高線(1550)#287RY U/L | LINE161 | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  | 0067 | 1-30-05 |  | 1-43 | 1550 | USE/LOCK | 雲林台西雲高線 1550 79RY U/L |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_79UL | 雲林台西雲高線(1550) 79RY U/L | LINE161 | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | #1DTR | USE/LOCK | #1DTR. 數位電驛故障 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | 85UL1 | 請TPC確認 | INSERT | Status | 第1具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  | 0068 | 1-30-06 |  | 1-44 | 1510 | USE/LOCK | 台西六輕紅線 1510 685M U/L |  |  | B2/D21_A1 | [8 empty] | 台西DS.1510_85U1 | 塑化紅線(1510) 85RY(M) U/L | LINE161 | [5 empty] | 410 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | 85UL2 | 請TPC確認 | INSERT | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  | 0069 | 1-30-07 |  | 1-45 | 1510 | USE/LOCK | 台西六輕紅線 1510 685B U/L |  |  | B2/D21_A1 | [8 empty] | 台西DS.1510_85U2 | 塑化紅線(1510) 85RY(B) U/L | LINE161 | [5 empty] | 411 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | 85UL1 | 請TPC確認 | INSERT | Status | 第1具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0520 |  | 0070 | 1-30-08 |  | 1-46 | 1520 | USE/LOCK | 台西六輕白線 1520 885M U/L |  |  | B2/D21_A1 | [8 empty] | 台西DS.1520_85U1 | 塑化白線(1520) 85RY(M) U/L | LINE161 | [5 empty] | 412 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | #2DTR | USE/LOCK | #2DTR. 數位電驛故障 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0542 |  |  | 1-31-14 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0543 |  |  | 1-31-15 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | 85UL2 | 請TPC確認 | INSERT | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0521 |  | 0071 | 1-30-09 |  | 1-47 | 1520 | USE/LOCK | 台西六輕白線 1520 885B U/L |  |  | B2/D21_A1 | [8 empty] | 台西DS.1520_85U2 | 塑化白線(1520) 85RY(B) U/L | LINE161 | [5 empty] | 416 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0529 |  | 0076 | 1-31-01 |  | 1-4C | 1550 | USE/LOCK | 雲林台西雲高線 1550 87RY UL1 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1550_87UL1 | 雲林台西雲高線(1550)#187RY U/L | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | #1ATR | 遙控/現場 | #1ATR OLTC S/L |  | c | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0077 | 1-31-02 |  | 1-4D | 1560 | USE/LOCK | 北港台西線 1560 87RY UL1 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1560_87UL1 | 北港台西線(1560) #1 87RY U/L | LINE161 | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0557 |  |  | 1-32-13 |  |  | #1DTR | TRA | #1DTR 重故障 |  | a | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | #1DTR | TRF | #1DTR 輕故障 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | #1BTR | 遙控/現場 | #1BTR OLTC S/L |  | b | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0078 | 1-32-08 |  | 1-4E | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D21_A1 | [8 empty] | 台西DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | #2ATR | 遙控/現場 | #2ATR OLTC S/L |  | c | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0079 | 1-32-09 |  | 1-4F | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D21_A1 | [8 empty] | 台西DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0564 |  |  | 1-33-04 |  |  | #2DTR | TRA | #2DTR 重故障 |  | a | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #2DTR | TRF | #2DTR 輕故障 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | #2BTR | 遙控/現場 | #2BTR OLTC S/L |  | b | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0080 | 1-31-06 |  | 1-50 | #1DTR | USE/LOCK | #1DTR. #1 87RY U/L |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | #3DTR | ON/OFF | #3DTR 87 閉鎖開關 |  |  | B1/D21_A1 | [16 empty] | 430 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | #3DTR | 遙控/現場 | #3DTR OLTC S/L |  |  | B1/D21_A1 | [16 empty] | 431 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  | 0081 | 1-31-07 |  | 1-51 | #1DTR | USE/LOCK | #1DTR. #2 87RY U/L |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | #3DTR | TRA | #3DTR 重故障 |  | a | B1/D21_A1 | [16 empty] | 433 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | #3DTR | TRF | #3DTR 輕故障 |  |  | B1/D21_A1 | [16 empty] | 434 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0768 |  |  | 2-30-00 |  |  | #1DTR | ON/OFF | #1DTR 96P |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0769 |  |  | 2-30-01 |  |  | #1DTR | ON/OFF | #1DTR 96D |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 2-30-02 |  |  | #1DTR | ON/OFF | #1DTR 96B1 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0771 |  |  | 2-30-03 |  |  | #1DTR | ON/OFF | #1DTR 96B2 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0772 |  |  | 2-30-04 |  |  | #1DTR | ON/OFF | #1DTR 63Q |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0773 |  |  | 2-30-05 |  |  | #2DTR | ON/OFF | #2DTR 96P |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0774 |  |  | 2-30-06 |  |  | #2DTR | ON/OFF | #2DTR 96D |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0775 |  |  | 2-30-07 |  |  | #2DTR | ON/OFF | #2DTR 96B1 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0776 |  |  | 2-30-08 |  |  | #2DTR | ON/OFF | #2DTR 96B2 |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0777 |  |  | 2-30-09 |  |  | #2DTR | ON/OFF | #2DTR 63Q |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0536 |  | 0082 | 1-31-08 |  | 1-52 | #1DTR | USE/LOCK | #1DTR. 51Z U/L |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0083 | 1-31-10 |  | 1-53 | #2DTR | USE/LOCK | #2DTR. #1 87RY U/L |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0084 | 1-31-11 |  | 1-54 | #2DTR | USE/LOCK | #2DTR. #2 87RY U/L |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0540 |  | 0085 | 1-31-12 |  | 1-55 | #2DTR | USE/LOCK | #2DTR. 51Z U/L |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0854 |  | 0086 | 2-35-06 |  | 1-56 | F11 | ON/OFF | F11 台十線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP30_ADJ | 11KV台十線(XP30) LCO分流器 U/L | FEEDER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0855 |  | 0087 | 2-35-07 |  | 1-57 | F12 | ON/OFF | F12 台九線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP29_ADJ | 11KV台九線(XP29) LCO分流器 U/L | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0856 |  | 0088 | 2-35-08 |  | 1-58 | F13 | ON/OFF | F13 台八線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP28_ADJ | 11KV台八線(XP28) LCO分流器 U/L | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0857 |  | 0089 | 2-35-09 |  | 1-59 | F14 | ON/OFF | F14 台七線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP27_ADJ | 11KV台七線(XP27) LCO分流器 U/L | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0858 |  | 0090 | 2-35-10 |  | 1-5A | F15 | ON/OFF | F15 台十五線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP35_ADJ | 11KV台15線(XP35) LCO分流器 U/L | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0859 |  | 0091 | 2-35-11 |  | 1-5B | F16 | ON/OFF | F16 台十六線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP36_ADJ | 11KV台16線(XP36) LCO分流器 U/L | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0860 |  | 0092 | 2-35-12 |  | 1-5C | F17 | ON/OFF | F17 台十七線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP37_ADJ | 11KV台17線(XP37) LCO分流器 U/L | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0861 |  | 0093 | 2-35-13 |  | 1-5D | F18 | ON/OFF | F18 台十八線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP38_ADJ | 11KV台18線(XP38) LCO分流器 U/L | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0862 |  | 0094 | 2-35-14 |  | 1-5E | F19 | ON/OFF | F19 台十九線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP39_ADJ | 11KV台19線(XP39) LCO分流器 U/L | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0863 |  | 0095 | 2-35-15 |  | 1-5F | F20 | ON/OFF | F20 台二十線 LCO 分流器 |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP40_ADJ | 11KV台20線(XP40) LCO分流器 U/L | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D21 | 台西DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0096 | 1-32-12 |  | 1-60 | #1ATR | OLTC A/M | #1ATR OLTC A/M |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D21 | 台西DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0024 |  | 0097 | 1-98 |  | 1-61 | #1ATR | 升/降 | #1ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 460 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0560 |  | 0098 | 1-33-00 |  | 1-62 | #1BTR | OLTC A/M | #1BTR OLTC A/M |  |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D21 | 台西DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0025 |  | 0099 | 1-99 |  | 1-63 | #1BTR | 升/降 | #1BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 462 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0563 |  | 0100 | 1-33-03 |  | 1-64 | #2ATR | OLTC A/M | #2ATR OLTC A/M |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D21 | 台西DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  | 0101 | 1-9D |  | 1-65 | #2ATR | 升/降 | #2ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 464 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0567 |  | 0102 | 1-33-07 |  | 1-66 | #2BTR | OLTC A/M | #2BTR OLTC A/M |  |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D21 | 台西DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0030 |  | 0103 | 1-9E |  | 1-67 | #2BTR | 升/降 | #2BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D21_A1 | [8 empty] | 台西DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 466 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0570 |  | 0104 | 1-33-10 |  | 1-68 | #3DTR | OLTC A/M | #3DTR OLTC A/M |  |  | B1/D21_A1 | [16 empty] | 467 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  | 0105 | 1-A2 |  | 1-69 | #3DTR | 升/降 | #3DTR TAP位置 |  |  | B1/D21_A1 | [16 empty] | 468 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | DS1 | 1561 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0576 | 577 | 0112 | 1-34-00 | 1-34-01 | 1-70 | 1561 | ON | 北港台西線 1561 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1561_DS | 1561(北港台西線) DS | LINE161 | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | DS2 | 1562 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0578 | 579 | 0113 | 1-34-02 | 1-34-03 | 1-71 | 1562 | ON | 北港台西線 1562ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1562_DS | 1562(北港台西線) DS | LINE161 | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 11 | 11kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-32-04 |  |  | 60Ry | A/N | 11KV SC 60A |  |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_SC_60A | 11KV SC 60A | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 2-32-05 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D21_A1 | [8 empty] | 台西DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 2-32-06 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D21_A1 | [8 empty] | 台西DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Water1 | 0.5M水位警報 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0807 |  |  | 2-32-07 |  |  | 地下室 | A/N | 地下室 0.5M 水位警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Water2 | 1M水位警報 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0808 |  |  | 2-32-08 |  |  | 地下室 | A/N | 地下室 1M 水位警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0809 |  |  | 2-32-09 |  |  | 冷氣機 | ON/OFF | 冷氣機跳脫 |  |  | B3/D21_A1 | [8 empty] | 台西DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-32-10 |  |  | 火災警報(1) | ON/OFF | 火災警報(1)受信總機 |  |  | B3/D21_A1 | [8 empty] | 台西DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 2-32-11 |  |  | 火災警報(2) | ON/OFF | 火災警報(2) |  |  | B3/D21_A1 | [8 empty] | 台西DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | 火災警報(3) | ON/OFF | 火災警報(3) |  |  | B3/D21_A1 | [8 empty] | 台西DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0813 |  |  | 2-32-13 |  |  | Locate Empty | ON/OFF | 無人化防盜(1) 保全 |  |  | B3/D21_A1 | [8 empty] | 台西DS.無人化防盜(1) | 無人化防盜(1)保全控制室 | OTHER | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0814 |  |  | 2-32-14 |  |  | Locate Empty | ON/OFF | 無人化防盜(2) |  |  | B3/D21_A1 | [8 empty] | 台西DS.無人化防盜(2) | 無人化防盜(2)保全圍牆 | OTHER | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0815 |  |  | 2-32-15 |  |  | Locate Empty | ON/OFF | 無人化防盜(3) |  |  | B3/D21_A1 | [8 empty] | 台西DS.無人化防盜(3) | 無人化防盜(3) | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Door1 | 大小門門禁 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | Locate Empty | ON/OFF | 無人化防盜(1) 大小門門禁 |  |  | B3/D21_A1 | [8 empty] | 台西DS.無人化門禁(1) | 無人化門禁(1)建物大門 | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | Locate Empty | ON/OFF | 無人化防盜(2)控制室門禁 |  |  | B3/D21_A1 | [8 empty] | 台西DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | Locate Empty | ON/OFF | 無人化防盜(3) |  |  | B3/D21_A1 | [8 empty] | 台西DS.無人化門禁(3) | 無人化門禁(3) | OTHER | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | DS3 | 1563 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0580 | 581 | 0114 | 1-34-04 | 1-34-05 | 1-72 | 1563 | ON | 北港台西線 1563ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1563_DS | 1563(北港台西線) DS | LINE161 | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0582 | 583 | 0115 | 1-34-06 | 1-34-07 | 1-73 | 1563E | ON | 北港台西線 1563E ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1563E_ES | 1563E(北港台西線) ES | LINE161 | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 2-33-05 |  |  | OPA | ON/OFF | OPA 充油電纜 |  |  | B3/D21_A1 | [8 empty] | 台西DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0584 | 585 | 0116 | 1-34-08 | 1-34-09 | 1-74 | 1551 | ON | 雲林台西雲高線 1551 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1551_DS | 1551(雲林台西雲高線) DS | LINE161 | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0586 | 587 | 0117 | 1-34-10 | 1-34-11 | 1-75 | 1552 | ON | 雲林台西雲高線 1552 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1552_DS | 1552(雲林台西雲高線) DS | LINE161 | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 2-33-08 |  |  | Locate Empty | ON/OFF | 所內欠壓 |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 2-33-09 |  |  | VUA | ON/OFF | VUA1 |  |  | B2/D21_A1 | [8 empty] | 台西DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 2-33-10 |  |  | VUA | ON/OFF | VUA2 |  |  | B2/D21_A1 | [8 empty] | 台西DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 2-33-11 |  |  | DCA | ON/OFF | DCA 直流電源故障 |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-33-12 |  |  | CHG1 | ON/OFF | CHG1 充電機故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 2-33-13 |  |  | CHG2 | ON/OFF | 通訊充電機故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 2-33-14 |  |  | DCE | ON/OFF | DCE 直流接地 |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 2-33-15 |  |  | 空壓機 | ON/OFF | 161KV 空壓機超時 |  |  | B3/D21_A1 | [8 empty] | 台西DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0832 |  |  | 2-34-00 |  |  | 161KV | CBA | 161KV CB重故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0833 |  |  | 2-34-01 |  |  | 161KV | CBF | 161KV CB輕故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0834 |  |  | 2-34-02 |  |  | 11KV | CBA | 11KV CB重故障 |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.11KV_CBA | 11KV斷路器重故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0835 |  |  | 2-34-03 |  |  | 11KV | CBF | 11KV CB輕故障 |  |  | ELEM/D21_A1 | [8 empty] | 台西DS.11KV_CBF | 11KV斷路器輕故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 2-34-04 |  |  | ACBA | ON/OFF | ACB警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 2-34-05 |  |  | Locate Empty | ON/OFF | 其他重故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0838 |  |  | 2-34-06 |  |  | Locate Empty | ON/OFF | 其他輕故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0839 |  |  | 2-34-07 |  |  | 集油池 | OWA | 集油池警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 2-34-08 |  |  | Locate Empty | ON/OFF | 通訊設備 AC故障 |  |  | B3/D21_A1 | [8 empty] | 台西DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 2-34-11 |  |  | Locate Empty | ON/OFF | 通信室溫控警報 |  |  | B3/D21_A1 | [8 empty] | 台西DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0588 | 589 | 0118 | 1-34-12 | 1-34-13 | 1-76 | 1553 | ON | 雲林台西雲高線 1553 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1553_DS | 1553(雲林台西雲高線) DS | LINE161 | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0590 | 591 | 0119 | 1-34-14 | 1-34-15 | 1-77 | 1553E | ON | 雲林台西雲高線 1553E ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1553E_ES | 1553E(雲林台西雲高線) ES | LINE161 | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | DS1 | 1511 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0592 | 593 | 0120 | 1-35-00 | 1-35-01 | 1-78 | 1511 | ON | 台西六輕紅線 1511 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1511_DS | 1511(塑化紅線) DS | LINE161 | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | DS2 | 1512 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0594 | 595 | 0121 | 1-35-02 | 1-35-03 | 1-79 | 1512 | ON | 台西六輕紅線 1512 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1512_DS | 1512(塑化紅線) DS | LINE161 | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | DS3 | 1513 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0596 | 597 | 0122 | 1-35-04 | 1-35-05 | 1-7A | 1513 | ON | 台西六輕紅線 1513 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1513_DS | 1513(塑化紅線) DS | LINE161 | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0598 | 599 | 0123 | 1-35-06 | 1-35-07 | 1-7B | 1513E | ON | 台西六輕紅線 1513E ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1513E_ES | 1513E(塑化紅線) ES | LINE161 | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | DS1 | 1521 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0600 | 601 | 0124 | 1-35-08 | 1-35-09 | 1-7C | 1521 | ON | 台西六輕白線 1521 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1521_DS | 1521(塑化白線) DS | LINE161 | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | DS2 | 1522 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0602 | 603 | 0125 | 1-35-10 | 1-35-11 | 1-7D | 1522 | ON | 台西六輕白線 1522 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1522_DS | 1522(塑化白線) DS | LINE161 | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | DS3 | 1523 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0604 | 605 | 0126 | 1-35-12 | 1-35-13 | 1-7E | 1523 | ON | 台西六輕白線 1523 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1523_DS | 1523(塑化白線) DS | LINE161 | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0606 | 607 | 0127 | 1-35-14 | 1-35-15 | 1-7F | 1523E | ON | 台西六輕白線 1523E ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1523E_ES | 1523E(塑化白線) ES | LINE161 | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0144 | 2-38-00 | 2-38-01 | 2-10 | 1501 | ON | 161KV 1501 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0145 | 2-38-02 | 2-38-03 | 2-11 | 1502 | ON | 161KV 1502 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0146 | 2-38-04 | 2-38-05 | 2-12 | 1751 | ON | #1DTR 1751 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0902 | 903 | 0147 | 2-38-06 | 2-38-07 | 2-13 | 1752 | ON | #1DTR 1752 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0148 | 2-38-08 | 2-38-09 | 2-14 | 1761 | ON | #2DTR 1761 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0149 | 2-38-10 | 2-38-11 | 2-15 | 1762 | ON | #2DTR 1762 ABS |  |  | B2/D21_A1 | [8 empty] | 台西DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0150 | 2-38-12 | 2-38-13 | 2-16 | 1771 | ON | #3DTR 1771 ABS |  |  | B2/D21_A1 | [16 empty] | 525 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0910 | 911 | 0151 | 2-38-14 | 2-38-15 | 2-17 | 1772 | ON | #3DTR 1772 ABS |  |  | B2/D21_A1 | [16 empty] | 526 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0822 |  | 0156 | 2-33-06 |  | 2-1C | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/D21_A1 | [8 empty] | 台西DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0823 |  | 0157 | 2-33-07 |  | 2-1D | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/D21_A1 | [8 empty] | 台西DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0819 |  | 0158 | 2-33-03 |  | 2-1E | Locate Empty | ON/OFF | 開關場照明(A) |  |  | B3/D21_A1 | [8 empty] | 台西DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D21 | 台西DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0820 |  | 0159 | 2-33-04 |  | 2-1F | Locate Empty | ON/OFF | 開關場照明(B) |  |  | B3/D21_A1 | [8 empty] | 台西DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0160 | 2-30-10 |  | 2-20 | F1 | USE/LOCK | F1 台一線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP21_79UL | 11KV台一線(XP21) 79RY U/L | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0161 | 2-30-11 |  | 2-21 | F2 | USE/LOCK | F2 台二線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP22_79UL | 11KV台二線(XP22) 79RY U/L | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  | 0162 | 2-30-12 |  | 2-22 | F3 | USE/LOCK | F3 台三線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP23_79UL | 11KV台三線(XP23) 79RY U/L | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0163 | 2-30-13 |  | 2-23 | F4 | USE/LOCK | F4 台四線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP24_79UL | 11KV台四線(XP24) 79RY U/L | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0164 | 2-30-14 |  | 2-24 | F5 | USE/LOCK | F5 台五線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP25_79UL | 11KV台五線(XP25) 79RY U/L | FEEDER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  | 0165 | 2-30-15 |  | 2-25 | F6 | USE/LOCK | F6 台六線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP26_79UL | 11KV台六線(XP26) 79RY U/L | FEEDER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0784 |  | 0166 | 2-31-00 |  | 2-26 | 210 | A/M | #1A 210 SC Q-CTL A/M |  |  | B3/D21_A1 | [8 empty] | 台西DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0785 |  | 0167 | 2-31-01 |  | 2-27 | 210 | A/M | #1B 220 SC Q-CTL A/M |  |  | B3/D21_A1 | [8 empty] | 台西DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0168 | 2-31-02 |  | 2-28 | F7 | USE/LOCK | F7 台十四線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP34_79UL | 11KV台14線(XP34) 79RY U/L | FEEDER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  | 0169 | 2-31-03 |  | 2-29 | F8 | USE/LOCK | F8 台十三線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP33_79UL | 11KV台13線(XP33) 79RY U/L | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  | 0170 | 2-31-04 |  | 2-2A | F9 | USE/LOCK | F9 台十二線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP32_79UL | 11KV台12線(XP32) 79RY U/L | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0171 | 2-31-05 |  | 2-2B | F10 | USE/LOCK | F10 台十一線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP31_79UL | 11KV台11線(XP31) 79RY U/L | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0790 |  | 0172 | 2-31-06 |  | 2-2C | 240 | A/M | #2B 240 SC Q-CTL A/M |  |  | B3/D21_A1 | [8 empty] | 台西DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0173 | 2-31-07 |  | 2-2D | F11 | USE/LOCK | F11 台十線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP30_79UL | 11KV台十線(XP30) 79RY U/L | FEEDER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0174 | 2-31-08 |  | 2-2E | F12 | USE/LOCK | F12 台九線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP29_79UL | 11KV台九線(XP29) 79RY U/L | FEEDER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0175 | 2-31-09 |  | 2-2F | F13 | USE/LOCK | F13 台八線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP28_79UL | 11KV台八線(XP28) 79RY U/L | FEEDER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0176 | 2-31-10 |  | 2-30 | F14 | USE/LOCK | F14 台七線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP27_79UL | 11KV台七線(XP27) 79RY U/L | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0795 |  | 0177 | 2-31-11 |  | 2-31 | 230 | A/M | #2A 230 SC Q-CTL A/M |  |  | B3/D21_A1 | [8 empty] | 台西DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0796 |  | 0178 | 2-31-12 |  | 2-32 | F15 | USE/LOCK | F15 台十五線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP35_79UL | 11KV台15線(XP35) 79RY U/L | FEEDER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0797 |  | 0179 | 2-31-13 |  | 2-33 | F16 | USE/LOCK | F16 台十六線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP36_79UL | 11KV台16線(XP36) 79RY U/L | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0180 | 2-31-14 |  | 2-34 | F17 | USE/LOCK | F17 台十七線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP37_79UL | 11KV台17線(XP37) 79RY U/L | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  | 0181 | 2-31-15 |  | 2-35 | F18 | USE/LOCK | F18 台十八線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP38_79UL | 11KV台18線(XP38) 79RY U/L | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCH4 |  | INSERT | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 553 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | RTU | RTU |  | ADCL4 |  | INSERT | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D21_A1 | [8 empty] | 台西DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 554 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0182 | 2-32-00 |  | 2-36 | F19 | USE/LOCK | F19 台十九線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP39_79UL | 11KV台19線(XP39) 79RY U/L | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0183 | 2-32-01 |  | 2-37 | F20 | USE/LOCK | F20 台二十線 79RY U/L |  |  | B2/D21_D1 | [8 empty] | 台西DS.XP40_79UL | 11KV台20線(XP40) 79RY U/L | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0802 |  | 0184 | 2-32-02 |  | 2-38 | 260 | A/M | #3B 260 SC Q-CTL A/M |  |  | B3/D21_A1 | [8 empty] | 台西DS.260_A/M | 11KV #6SC 乏控器 A/M | SC | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0803 |  | 0185 | 2-32-03 |  | 2-39 | 250 | A/M | #3A 250 SC Q-CTL A/M |  |  | B3/D21_A1 | [8 empty] | 台西DS.250_A/M | 11KV #5SC 乏控器 A/M | SC | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 310 | #1DTR(310) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.310_GDA | 11KV 310(#1ADTR) 51N RY | OTHER | [5 empty] | 559 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 320 | #1DTR(320) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.320_GDA | 11KV 320(#1BDTR) 51N RY | OTHER | [5 empty] | 560 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 330 | #2DTR(330) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.330_GDA | 11KV 330(#2ADTR) 51N RY | OTHER | [5 empty] | 561 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 340 | #2DTR(340) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.340_GDA | 11KV 340(#2BDTR) 51N RY | OTHER | [5 empty] | 562 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | ComPoint |  |  | LOA | 請TPC確認 | INSERT | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_LOA | 11KV饋線復閉失敗 | OTHER | [5 empty] | 563 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | ComPoint |  |  | RYFA | 請TPC確認 | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | Locate Empty |  |  |  |  | B3/D21_A1 | [8 empty] | 台西DS.11KV_RYFA | 11KV IED故障 | OTHER | [5 empty] | 564 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D21 | 台西DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D21_A1 | [12 empty] | 台西DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D21/161/1BUS/V; OPRD2: D21/161/2BUS/V
D21 | 台西DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D21_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D21/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D21 | 台西DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D21_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D21/161/1510/MW; OPRD2: D21/161/1520/MW; OPRD3: D21/161/1550/MW; OPRD4: D21/161/1560/MW
D21 | 台西DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D21_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D21/0/CalcPoint/OPRN2_MW
D21 | 台西DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D21_A1 | [17 empty] | none
D21 | 台西DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D21_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D21/0/CalcPoint/OPRN1; OPRD2: D21/0/CalcPoint/OPRN2; OPRD3: D21/0/CalcPoint/PRFL_UL
D21 | 台西DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D21_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D21/11/310/I_R; OPRD2: D21/11/320/I_R
D21 | 台西DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D21_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D21/11/310/I_S; OPRD2: D21/11/320/I_S
D21 | 台西DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D21_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D21/11/310/I_T; OPRD2: D21/11/320/I_T
D21 | 台西DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D21_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D21/11/330/I_R; OPRD2: D21/11/340/I_R
D21 | 台西DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D21_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D21/11/330/I_S; OPRD2: D21/11/340/I_S
D21 | 台西DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D21_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D21/11/330/I_T; OPRD2: D21/11/340/I_T
D21 | 台西DS | 161 | 161kV | 1510 | 台西六輕紅線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D21_A1 | [12 empty] | 台西DS.1510_AMP | 塑化紅線 AMP | LINE161 | AMP_CAL | C20R1200 | amp_cal | OPRD1: D21/161/1510/MW; OPRD2: D21/161/1510/MVAR; OPRD3: D21/0/CalcPoint/Vbs4
D21 | 台西DS | 161 | 161kV | 1520 | 台西六輕白線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D21_A1 | [12 empty] | 台西DS.1520_AMP | 塑化白線 AMP | LINE161 | AMP_CAL | C20R1200 | amp_cal | OPRD1: D21/161/1520/MW; OPRD2: D21/161/1520/MVAR; OPRD3: D21/0/CalcPoint/Vbs4
D21 | 台西DS | 161 | 161kV | 1550 | 雲林~台西~雲高線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D21_A1 | [12 empty] | 台西DS.1550_AMP | 雲林台西雲高線 AMP | LINE161 | AMP_CAL | C20R1017 | amp_cal | OPRD1: D21/161/1550/MW; OPRD2: D21/161/1550/MVAR; OPRD3: D21/0/CalcPoint/Vbs4
D21 | 台西DS | 161 | 161kV | 1560 | 北港～台西線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D21_A1 | [12 empty] | 台西DS.1560_AMP | 北港台西線 AMP | LINE161 | AMP_CAL | C20R1200 | amp_cal | OPRD1: D21/161/1560/MW; OPRD2: D21/161/1560/MVAR; OPRD3: D21/0/CalcPoint/Vbs4
D21 | 台西DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D21_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D21/11/1ABUS/V
D21 | 台西DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D21_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D21/11/1BBUS/V
D21 | 台西DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D21_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D21/11/2ABUS/V
D21 | 台西DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D21_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D21/11/2BBUS/V
D21 | 台西DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D21_A1 | [12 empty] | 台西DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D21//1DTR(A)/SupLocal; OPRD2: D21//1DTR(A)/Tap Chan
D21 | 台西DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D21_A1 | [12 empty] | 台西DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D21//1DTR(B)/SupLocal; OPRD2: D21//1DTR(B)/Tap Chan
D21 | 台西DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D21_A1 | [12 empty] | 台西DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D21//2DTR(A)/SupLocal; OPRD2: D21//2DTR(A)/Tap Chan
D21 | 台西DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D21_A1 | [12 empty] | 台西DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D21//2DTR(B)/SupLocal; OPRD2: D21//2DTR(B)/Tap Chan
D21 | 台西DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D21_A1 | [15 empty] | DTR_PERM |  | dtr_perm | OPRD1: D21//3DTR/SupLocal; OPRD2: D21//3DTR/Tap Chan
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1ABUS/V; OPRD2: D21/11/XP21/I_R; OPRD3: D21/11/XP21/I_S; OPRD4: D21/11/XP21/I_T
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1ABUS/V; OPRD2: D21/11/XP22/I_R; OPRD3: D21/11/XP22/I_S; OPRD4: D21/11/XP22/I_T
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1ABUS/V; OPRD2: D21/11/XP23/I_R; OPRD3: D21/11/XP23/I_S; OPRD4: D21/11/XP23/I_T
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1ABUS/V; OPRD2: D21/11/XP24/I_R; OPRD3: D21/11/XP24/I_S; OPRD4: D21/11/XP24/I_T
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1ABUS/V; OPRD2: D21/11/XP25/I_R; OPRD3: D21/11/XP25/I_S; OPRD4: D21/11/XP25/I_T
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1ABUS/V; OPRD2: D21/11/XP26/I_R; OPRD3: D21/11/XP26/I_S; OPRD4: D21/11/XP26/I_T
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1BBUS/V; OPRD2: D21/11/XP27/I_R; OPRD3: D21/11/XP27/I_S; OPRD4: D21/11/XP27/I_T
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1BBUS/V; OPRD2: D21/11/XP28/I_R; OPRD3: D21/11/XP28/I_S; OPRD4: D21/11/XP28/I_T
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1BBUS/V; OPRD2: D21/11/XP29/I_R; OPRD3: D21/11/XP29/I_S; OPRD4: D21/11/XP29/I_T
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/1BBUS/V; OPRD2: D21/11/XP30/I_R; OPRD3: D21/11/XP30/I_S; OPRD4: D21/11/XP30/I_T
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2ABUS/V; OPRD2: D21/11/XP31/I_R; OPRD3: D21/11/XP31/I_S; OPRD4: D21/11/XP31/I_T
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2ABUS/V; OPRD2: D21/11/XP32/I_R; OPRD3: D21/11/XP32/I_S; OPRD4: D21/11/XP32/I_T
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2ABUS/V; OPRD2: D21/11/XP33/I_R; OPRD3: D21/11/XP33/I_S; OPRD4: D21/11/XP33/I_T
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2ABUS/V; OPRD2: D21/11/XP34/I_R; OPRD3: D21/11/XP34/I_S; OPRD4: D21/11/XP34/I_T
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2BBUS/V; OPRD2: D21/11/XP35/I_R; OPRD3: D21/11/XP35/I_S; OPRD4: D21/11/XP35/I_T
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2BBUS/V; OPRD2: D21/11/XP36/I_R; OPRD3: D21/11/XP36/I_S; OPRD4: D21/11/XP36/I_T
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2BBUS/V; OPRD2: D21/11/XP37/I_R; OPRD3: D21/11/XP37/I_S; OPRD4: D21/11/XP37/I_T
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2BBUS/V; OPRD2: D21/11/XP38/I_R; OPRD3: D21/11/XP38/I_S; OPRD4: D21/11/XP38/I_T
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2BBUS/V; OPRD2: D21/11/XP39/I_R; OPRD3: D21/11/XP39/I_S; OPRD4: D21/11/XP39/I_T
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D21/11/2BBUS/V; OPRD2: D21/11/XP40/I_R; OPRD3: D21/11/XP40/I_S; OPRD4: D21/11/XP40/I_T
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP21/kVA; OPRD2: D21/11/XP21/KVAR
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP22/kVA; OPRD2: D21/11/XP22/KVAR
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP23/kVA; OPRD2: D21/11/XP23/KVAR
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP24/kVA; OPRD2: D21/11/XP24/KVAR
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP25/kVA; OPRD2: D21/11/XP25/KVAR
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP26/kVA; OPRD2: D21/11/XP26/KVAR
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP27/kVA; OPRD2: D21/11/XP27/KVAR
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP28/kVA; OPRD2: D21/11/XP28/KVAR
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP29/kVA; OPRD2: D21/11/XP29/KVAR
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP30/kVA; OPRD2: D21/11/XP30/KVAR
D21 | 台西DS | 11 | 11kV | XP31 | 台十一線(XP31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP31/kVA; OPRD2: D21/11/XP31/KVAR
D21 | 台西DS | 11 | 11kV | XP32 | 台十二線(XP32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP32/kVA; OPRD2: D21/11/XP32/KVAR
D21 | 台西DS | 11 | 11kV | XP33 | 台十三線(XP33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP33/kVA; OPRD2: D21/11/XP33/KVAR
D21 | 台西DS | 11 | 11kV | XP34 | 台十四線(XP34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP34/kVA; OPRD2: D21/11/XP34/KVAR
D21 | 台西DS | 11 | 11kV | XP35 | 台十五線(XP35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP35/kVA; OPRD2: D21/11/XP35/KVAR
D21 | 台西DS | 11 | 11kV | XP36 | 台十六線(XP36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP36/kVA; OPRD2: D21/11/XP36/KVAR
D21 | 台西DS | 11 | 11kV | XP37 | 台十七線(XP37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP37/kVA; OPRD2: D21/11/XP37/KVAR
D21 | 台西DS | 11 | 11kV | XP38 | 台十八線(XP38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP38/kVA; OPRD2: D21/11/XP38/KVAR
D21 | 台西DS | 11 | 11kV | XP39 | 台十九線(XP39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP39/kVA; OPRD2: D21/11/XP39/KVAR
D21 | 台西DS | 11 | 11kV | XP40 | 台二十線(XP40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D21_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D21/11/XP40/kVA; OPRD2: D21/11/XP40/KVAR
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D21_A1 | [12 empty] | 台西DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D21/11/210/CB; OPRD2: 6.9; OPRD3: 0
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D21_A1 | [12 empty] | 台西DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D21/11/220/CB; OPRD2: 6.9; OPRD3: 0
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D21_A1 | [12 empty] | 台西DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D21/11/230/CB; OPRD2: 6.9; OPRD3: 0
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D21_A1 | [12 empty] | 台西DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D21/11/240/CB; OPRD2: 6.9; OPRD3: 0
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D21_A1 | [12 empty] | 台西DS.250_SC_MVAR | 11KV#5SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D21/11/250/CB; OPRD2: 6.9; OPRD3: 0
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D21_A1 | [12 empty] | 台西DS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D21/11/260/CB; OPRD2: 6.9; OPRD3: 0
D21 | 台西DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D21_A1 | [12 empty] | 台西DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_36 | D21//1DTR/96B1 | D21//1DTR/96D | D21//1DTR/96B2 | D21//1DTR/63Q | D21//1DTR/51ZA | D21//1DTR/TRA | D21//1DTR/87A | D21//1DTR/96PA | D21//2DTR/PHA | D21//2DTR/GDA | D21//2DTR/TRA | D21//2DTR/96B1 | D21//2DTR/96B2 | D21//2DTR/63Q | D21//2DTR/96D | D21//2DTR/96PA | D21//2DTR/51ZA | D21//2DTR/87A | D21//3DTR/TRA | D21//3DTR/GDA | D21//3DTR/96PA | D21//3DTR/87A | D21//3DTR/51ZA | D21//3DTR/PHA | D21/11/310/PHA | D21/11/310/GDA | D21/11/320/PHA | D21/11/320/GDA | D21/11/330/GDA | D21/11/330/PHA | D21/11/340/PHA | D21/11/340/GDA | D21/161/1750/GDA | D21/161/1750/PHA | D21/161/1BUS/87A | D21/161/2BUS/87A
D21 | 台西DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D21_A1 | [12 empty] | 台西DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_3 | OPRD1: D21//1DTR/TRF; OPRD2: D21//2DTR/TRF; OPRD3: D21//3DTR/TRF
D21 | 台西DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/161/1750/CB
D21 | 台西DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/161/1760/CB
D21 | 台西DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/161/1770/CB
D21 | 台西DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/11/310/CB
D21 | 台西DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/11/330/CB
D21 | 台西DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/11/320/CB
D21 | 台西DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/11/340/CB
D21 | 台西DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/0/RTU/RTU_R_L
D21 | 台西DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/0/StaDev/PMA
D21 | 台西DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/0/StaDev/STUV
D21 | 台西DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/0/StaDev/DCA
D21 | 台西DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/0/StaDev/DCE
D21 | 台西DS | 11 | 11kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/11/ComPoint/CBA
D21 | 台西DS | 11 | 11kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D21_D1 | [17 empty] | lamp2CC | OPRD1: D21/11/ComPoint/CBF

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D21 | 台西DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 台西DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D21/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 台西DS.1510_AMP | 塑化紅線 AMP | LINE161 | D21/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 台西DS.1520_AMP | 塑化白線 AMP | LINE161 | D21/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | I | [25 empty] | ADCS_N | [8 empty] | 台西DS.1550_AMP | 雲林台西雲高線 AMP | LINE161 | D21/161/1550/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1017 | 915.000000 | 915.000000 | 1017.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | I | [25 empty] | ADCS_N | [8 empty] | 台西DS.1560_AMP | 北港台西線 AMP | LINE161 | D21/161/1560/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D21 | 台西DS | 0 |  |  |  |  | 台11線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台11線KVA | 11KV台11線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台11線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台11線KW | 11KV台11線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台12線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台12線KVA | 11KV台12線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台12線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台12線KW | 11KV台12線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台13線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台13線KVA | 11KV台13線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台13線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台13線KW | 11KV台13線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台14線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台14線KVA | 11KV台14線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台14線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台14線KW | 11KV台14線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台15線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台15線KVA | 11KV台15線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台15線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台15線KW | 11KV台15線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台16線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台16線KVA | 11KV台16線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台16線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台16線KW | 11KV台16線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台17線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台17線KVA | 11KV台17線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台17線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台17線KW | 11KV台17線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台18線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台18線KVA | 11KV台18線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台18線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台18線KW | 11KV台18線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台19線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台19線KVA | 11KV台19線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台19線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台19線KW | 11KV台19線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台20線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台20線KVA | 11KV台20線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台20線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台20線KW | 11KV台20線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台一線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台一線KVA | 11KV台一線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台一線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台一線KW | 11KV台一線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台七線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台七線KVA | 11KV台七線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台七線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台七線KW | 11KV台七線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台九線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台九線KVA | 11KV台九線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台九線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台九線KW | 11KV台九線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台二線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台二線KVA | 11KV台二線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台二線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台二線KW | 11KV台二線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台八線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台八線KVA | 11KV台八線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台八線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台八線KW | 11KV台八線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台十線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台十線KVA | 11KV台十線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台十線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台十線KW | 11KV台十線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台三線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台三線KVA | 11KV台三線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台三線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台三線KW | 11KV台三線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台五線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台五線KVA | 11KV台五線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台五線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台五線KW | 11KV台五線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台六線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台六線KVA | 11KV台六線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台六線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台六線KW | 11KV台六線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台四線KVA | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台四線KVA | 11KV台四線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  |  |  |  | 台四線KW | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.台四線KW | 11KV台四線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D21/11/210/MVAR |  | SC_CAL_11 |  |  | 47 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D21/11/220/MVAR |  | SC_CAL_11 |  |  | 48 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D21/11/230/MVAR |  | SC_CAL_11 |  |  | 49 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D21/11/240/MVAR |  | SC_CAL_11 |  |  | 50 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.250_SC_MVAR | 11KV#5SC MVAR | SC | D21/11/250/MVAR |  | SC_CAL_11 |  |  | 51 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.260_SC_MVAR | 11KV#6SC MVAR | SC | D21/11/260/MVAR |  | SC_CAL_11 |  |  | 52 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | TRTOT | 台西主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 台西DS.TRTOT_MW | 台西主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | TRTOT | 台西主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 台西DS.TRTOT_MVAR | 台西主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 56 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 59 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 62 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 65 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 70 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 74 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D21 | 台西DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.1750_CB_1 | 1750(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.310_CB_1 | 310(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.320_CB_1 | 320(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.330_CB_1 | 330(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.340_CB_1 | 340(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.210_CB_1 | 210(11KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.220_CB_1 | 220(11KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.230_CB_1 | 230(11KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.240_CB_1 | 240(11KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 250_CB | #5SC(250_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.250_CB_1 | 250(11KV #5SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 260_CB | #6SC(260_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.260_CB_1 | 260(11KV #6SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | _CBA | 斷路器重故障點燈(_CBA) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.11KV_CBA_1 | 11KV斷路器重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 87 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | _CBF | 斷路器輕故障(_CBF) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.11KV_CBF_1 | 11KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 88 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | RTU_S_L | RTU |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.RTU_S/L_1 | RTU SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 89 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D21 | 台西DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 台西DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D21/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 90 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 台西DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D21/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510_AMP | 塑化紅線 | [27 empty] | ADCS_N | [8 empty] | 台西DS.1510_AMP_A | 塑化紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 161 | 161kV | 1520_AMP | 塑化白線 | [27 empty] | ADCS_N | [8 empty] | 台西DS.1520_AMP_A | 塑化白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 161 | 161kV | 1550_AMP | 雲林台西雲高線 | [27 empty] | ADCS_N | [8 empty] | 台西DS.1550_AMP_A | 雲林台西雲高線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 161 | 161kV | 1560_AMP | 北港台西線 | [27 empty] | ADCS_N | [8 empty] | 台西DS.1560_AMP_A | 北港台西線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 台西DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 98 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 99 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 200_CB | 200(200_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.200_CB_1 | 200 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D21//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D21//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D21//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D21//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.#1DTR_MVA_1 | #1DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 1DTR_MVA | #1DTR(B) | [27 empty] | DDCS1_2 | [8 empty] | 台西DS.#1DTR_MVA_2 | #1DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 台西DS.#2DTR_MVA_1 | #2DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_2 | [8 empty] | 台西DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 台西DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 台西DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 台西DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 台西DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 台西DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 台西DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D21 | 台西DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 台西DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 台西DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 118 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D21/0/RTU/ADCH1 |  |  |  | CDC | 119 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D21/0/RTU/ADCH2 |  |  |  | CDC | 120 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D21/0/RTU/ADCH3 |  |  |  | CDC | 121 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D21/0/RTU/ADCH4 |  |  |  | CDC | 122 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D21/0/RTU/ADCL1 |  |  |  | CDC | 123 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D21/0/RTU/ADCL2 |  |  |  | CDC | 124 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D21/0/RTU/ADCL3 |  |  |  | CDC | 125 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D21/0/RTU/ADCL4 |  |  |  | CDC | 126 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D21/161/1BUS/V |  |  |  | CDC | 127 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D21 | 台西DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D21/161/2BUS/V |  |  |  | CDC | 128 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D21 | 台西DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-C8 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D21/11/1ABUS/V |  |  |  | CDC | 129 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-F7 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D21/11/1BBUS/V |  |  |  | CDC | 130 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-E1 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D21/11/2ABUS/V |  |  |  | CDC | 131 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-9B | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D21/11/2BBUS/V |  |  |  | CDC | 132 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1510_MW | 塑化紅線 MW | LINE161 | D21/161/1510/MW |  |  |  | CDC | 133 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1510_MVAR | 塑化紅線 MVAR | LINE161 | D21/161/1510/MVAR |  |  |  | CDC | 134 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1520_MW | 塑化白線 MW | LINE161 | D21/161/1520/MW |  |  |  | CDC | 135 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1520_MVAR | 塑化白線 MVAR | LINE161 | D21/161/1520/MVAR |  |  |  | CDC | 136 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_MW | 雲林台西雲高線 MW | LINE161 | D21/161/1550/MW |  |  |  | CDC | 137 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_MVAR | 雲林台西雲高線 MVAR | LINE161 | D21/161/1550/MVAR |  |  |  | CDC | 138 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_MW | 北港台西線 MW | LINE161 | D21/161/1560/MW |  |  |  | CDC | 139 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_MVAR | 北港台西線 MVAR | LINE161 | D21/161/1560/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台11線 | 台11線 |  | 台11線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台11線KVAR | 11KV台11線 KVAR | FEEDER | D21/11/XP31/KVAR |  |  |  | CDC | 141 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台11線A1 | 11KV台11線 R相AMP | FEEDER | D21/11/XP31/I_R |  |  |  | CDC | 142 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台11線A2 | 11KV台11線 S相AMP | FEEDER | D21/11/XP31/I_S |  |  |  | CDC | 143 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台11線A3 | 11KV台11線 T相AMP | FEEDER | D21/11/XP31/I_T |  |  |  | CDC | 144 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台12線 | 台12線 |  | 台12線KVAR | [17 empty] | 1-D9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台12線KVAR | 11KV台12線 KVAR | FEEDER | D21/11/XP32/KVAR |  |  |  | CDC | 145 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A1 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台12線A1 | 11KV台12線 R相AMP | FEEDER | D21/11/XP32/I_R |  |  |  | CDC | 146 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A2 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台12線A2 | 11KV台12線 S相AMP | FEEDER | D21/11/XP32/I_S |  |  |  | CDC | 147 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A3 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台12線A3 | 11KV台12線 T相AMP | FEEDER | D21/11/XP32/I_T |  |  |  | CDC | 148 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台13線 | 台13線 |  | 台13線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台13線KVAR | 11KV台13線 KVAR | FEEDER | D21/11/XP33/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台13線A1 | 11KV台13線 R相AMP | FEEDER | D21/11/XP33/I_R |  |  |  | CDC | 150 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台13線A2 | 11KV台13線 S相AMP | FEEDER | D21/11/XP33/I_S |  |  |  | CDC | 151 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台13線A3 | 11KV台13線 T相AMP | FEEDER | D21/11/XP33/I_T |  |  |  | CDC | 152 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台14線 | 台14線 |  | 台14線KVAR | [17 empty] | 1-D1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台14線KVAR | 11KV台14線 KVAR | FEEDER | D21/11/XP34/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A1 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台14線A1 | 11KV台14線 R相AMP | FEEDER | D21/11/XP34/I_R |  |  |  | CDC | 154 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A2 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台14線A2 | 11KV台14線 S相AMP | FEEDER | D21/11/XP34/I_S |  |  |  | CDC | 155 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A3 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台14線A3 | 11KV台14線 T相AMP | FEEDER | D21/11/XP34/I_T |  |  |  | CDC | 156 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台15線 | 台15線 |  | 台15線KVAR | [17 empty] | 2-83 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台15線KVAR | 11KV台15線 KVAR | FEEDER | D21/11/XP35/KVAR |  |  |  | CDC | 157 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A1 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台15線A1 | 11KV台15線 R相AMP | FEEDER | D21/11/XP35/I_R |  |  |  | CDC | 158 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A2 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台15線A2 | 11KV台15線 S相AMP | FEEDER | D21/11/XP35/I_S |  |  |  | CDC | 159 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A3 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台15線A3 | 11KV台15線 T相AMP | FEEDER | D21/11/XP35/I_T |  |  |  | CDC | 160 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台16線 | 台16線 |  | 台16線KVAR | [17 empty] | 2-87 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台16線KVAR | 11KV台16線 KVAR | FEEDER | D21/11/XP36/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A1 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台16線A1 | 11KV台16線 R相AMP | FEEDER | D21/11/XP36/I_R |  |  |  | CDC | 162 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A2 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台16線A2 | 11KV台16線 S相AMP | FEEDER | D21/11/XP36/I_S |  |  |  | CDC | 163 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A3 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台16線A3 | 11KV台16線 T相AMP | FEEDER | D21/11/XP36/I_T |  |  |  | CDC | 164 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台17線 | 台17線 |  | 台17線KVAR | [17 empty] | 2-8B | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台17線KVAR | 11KV台17線 KVAR | FEEDER | D21/11/XP37/KVAR |  |  |  | CDC | 165 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A1 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台17線A1 | 11KV台17線 R相AMP | FEEDER | D21/11/XP37/I_R |  |  |  | CDC | 166 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A2 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台17線A2 | 11KV台17線 S相AMP | FEEDER | D21/11/XP37/I_S |  |  |  | CDC | 167 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A3 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台17線A3 | 11KV台17線 T相AMP | FEEDER | D21/11/XP37/I_T |  |  |  | CDC | 168 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台18線 | 台18線 |  | 台18線KVAR | [17 empty] | 2-8F | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台18線KVAR | 11KV台18線 KVAR | FEEDER | D21/11/XP38/KVAR |  |  |  | CDC | 169 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A1 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台18線A1 | 11KV台18線 R相AMP | FEEDER | D21/11/XP38/I_R |  |  |  | CDC | 170 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A2 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台18線A2 | 11KV台18線 S相AMP | FEEDER | D21/11/XP38/I_S |  |  |  | CDC | 171 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A3 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台18線A3 | 11KV台18線 T相AMP | FEEDER | D21/11/XP38/I_T |  |  |  | CDC | 172 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台19線 | 台19線 |  | 台19線KVAR | [17 empty] | 2-93 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台19線KVAR | 11KV台19線 KVAR | FEEDER | D21/11/XP39/KVAR |  |  |  | CDC | 173 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A1 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台19線A1 | 11KV台19線 R相AMP | FEEDER | D21/11/XP39/I_R |  |  |  | CDC | 174 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A2 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台19線A2 | 11KV台19線 S相AMP | FEEDER | D21/11/XP39/I_S |  |  |  | CDC | 175 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A3 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台19線A3 | 11KV台19線 T相AMP | FEEDER | D21/11/XP39/I_T |  |  |  | CDC | 176 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台20線 | 台20線 |  | 台20線KVAR | [17 empty] | 2-97 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台20線KVAR | 11KV台20線 KVAR | FEEDER | D21/11/XP40/KVAR |  |  |  | CDC | 177 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A1 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台20線A1 | 11KV台20線 R相AMP | FEEDER | D21/11/XP40/I_R |  |  |  | CDC | 178 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A2 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台20線A2 | 11KV台20線 S相AMP | FEEDER | D21/11/XP40/I_S |  |  |  | CDC | 179 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A3 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台20線A3 | 11KV台20線 T相AMP | FEEDER | D21/11/XP40/I_T |  |  |  | CDC | 180 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台一線 | 台一線 |  | 台一線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台一線KVAR | 11KV台一線 KVAR | FEEDER | D21/11/XP21/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台一線 | 台一線 |  | 台一線A1 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台一線A1 | 11KV台一線 R相AMP | FEEDER | D21/11/XP21/I_R |  |  |  | CDC | 182 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台一線 | 台一線 |  | 台一線A2 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台一線A2 | 11KV台一線 S相AMP | FEEDER | D21/11/XP21/I_S |  |  |  | CDC | 183 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台一線 | 台一線 |  | 台一線A3 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台一線A3 | 11KV台一線 T相AMP | FEEDER | D21/11/XP21/I_T |  |  |  | CDC | 184 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台七線 | 台七線 |  | 台七線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台七線KVAR | 11KV台七線 KVAR | FEEDER | D21/11/XP27/KVAR |  |  |  | CDC | 185 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台七線 | 台七線 |  | 台七線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台七線A1 | 11KV台七線 R相AMP | FEEDER | D21/11/XP27/I_R |  |  |  | CDC | 186 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台七線 | 台七線 |  | 台七線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台七線A2 | 11KV台七線 S相AMP | FEEDER | D21/11/XP27/I_S |  |  |  | CDC | 187 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台七線 | 台七線 |  | 台七線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台七線A3 | 11KV台七線 T相AMP | FEEDER | D21/11/XP27/I_T |  |  |  | CDC | 188 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台九線 | 台九線 |  | 台九線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台九線KVAR | 11KV台九線 KVAR | FEEDER | D21/11/XP29/KVAR |  |  |  | CDC | 189 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台九線 | 台九線 |  | 台九線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台九線A1 | 11KV台九線 R相AMP | FEEDER | D21/11/XP29/I_R |  |  |  | CDC | 190 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台九線 | 台九線 |  | 台九線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台九線A2 | 11KV台九線 S相AMP | FEEDER | D21/11/XP29/I_S |  |  |  | CDC | 191 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台九線 | 台九線 |  | 台九線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台九線A3 | 11KV台九線 T相AMP | FEEDER | D21/11/XP29/I_T |  |  |  | CDC | 192 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台二線 | 台二線 |  | 台二線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台二線KVAR | 11KV台二線 KVAR | FEEDER | D21/11/XP22/KVAR |  |  |  | CDC | 193 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台二線 | 台二線 |  | 台二線A1 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台二線A1 | 11KV台二線 R相AMP | FEEDER | D21/11/XP22/I_R |  |  |  | CDC | 194 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台二線 | 台二線 |  | 台二線A2 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台二線A2 | 11KV台二線 S相AMP | FEEDER | D21/11/XP22/I_S |  |  |  | CDC | 195 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台二線 | 台二線 |  | 台二線A3 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台二線A3 | 11KV台二線 T相AMP | FEEDER | D21/11/XP22/I_T |  |  |  | CDC | 196 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台八線 | 台八線 |  | 台八線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台八線KVAR | 11KV台八線 KVAR | FEEDER | D21/11/XP28/KVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台八線 | 台八線 |  | 台八線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台八線A1 | 11KV台八線 R相AMP | FEEDER | D21/11/XP28/I_R |  |  |  | CDC | 198 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台八線 | 台八線 |  | 台八線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台八線A2 | 11KV台八線 S相AMP | FEEDER | D21/11/XP28/I_S |  |  |  | CDC | 199 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台八線 | 台八線 |  | 台八線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台八線A3 | 11KV台八線 T相AMP | FEEDER | D21/11/XP28/I_T |  |  |  | CDC | 200 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台十線 | 台十線 |  | 台十線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台十線KVAR | 11KV台十線 KVAR | FEEDER | D21/11/XP30/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台十線 | 台十線 |  | 台十線A1 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台十線A1 | 11KV台十線 R相AMP | FEEDER | D21/11/XP30/I_R |  |  |  | CDC | 202 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台十線 | 台十線 |  | 台十線A2 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台十線A2 | 11KV台十線 S相AMP | FEEDER | D21/11/XP30/I_S |  |  |  | CDC | 203 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台十線 | 台十線 |  | 台十線A3 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台十線A3 | 11KV台十線 T相AMP | FEEDER | D21/11/XP30/I_T |  |  |  | CDC | 204 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台三線 | 台三線 |  | 台三線KVAR | [17 empty] | 1-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台三線KVAR | 11KV台三線 KVAR | FEEDER | D21/11/XP23/KVAR |  |  |  | CDC | 205 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台三線 | 台三線 |  | 台三線A1 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台三線A1 | 11KV台三線 R相AMP | FEEDER | D21/11/XP23/I_R |  |  |  | CDC | 206 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台三線 | 台三線 |  | 台三線A2 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台三線A2 | 11KV台三線 S相AMP | FEEDER | D21/11/XP23/I_S |  |  |  | CDC | 207 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台三線 | 台三線 |  | 台三線A3 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台三線A3 | 11KV台三線 T相AMP | FEEDER | D21/11/XP23/I_T |  |  |  | CDC | 208 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台五線 | 台五線 |  | 台五線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台五線KVAR | 11KV台五線 KVAR | FEEDER | D21/11/XP25/KVAR |  |  |  | CDC | 209 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台五線 | 台五線 |  | 台五線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台五線A1 | 11KV台五線 R相AMP | FEEDER | D21/11/XP25/I_R |  |  |  | CDC | 210 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台五線 | 台五線 |  | 台五線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台五線A2 | 11KV台五線 S相AMP | FEEDER | D21/11/XP25/I_S |  |  |  | CDC | 211 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台五線 | 台五線 |  | 台五線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台五線A3 | 11KV台五線 T相AMP | FEEDER | D21/11/XP25/I_T |  |  |  | CDC | 212 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台六線 | 台六線 |  | 台六線KVAR | [17 empty] | 1-C4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台六線KVAR | 11KV台六線 KVAR | FEEDER | D21/11/XP26/KVAR |  |  |  | CDC | 213 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台六線 | 台六線 |  | 台六線A1 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台六線A1 | 11KV台六線 R相AMP | FEEDER | D21/11/XP26/I_R |  |  |  | CDC | 214 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台六線 | 台六線 |  | 台六線A2 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台六線A2 | 11KV台六線 S相AMP | FEEDER | D21/11/XP26/I_S |  |  |  | CDC | 215 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台六線 | 台六線 |  | 台六線A3 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台六線A3 | 11KV台六線 T相AMP | FEEDER | D21/11/XP26/I_T |  |  |  | CDC | 216 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台四線 | 台四線 |  | 台四線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台四線KVAR | 11KV台四線 KVAR | FEEDER | D21/11/XP24/KVAR |  |  |  | CDC | 217 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台四線 | 台四線 |  | 台四線A1 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台四線A1 | 11KV台四線 R相AMP | FEEDER | D21/11/XP24/I_R |  |  |  | CDC | 218 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台四線 | 台四線 |  | 台四線A2 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台四線A2 | 11KV台四線 S相AMP | FEEDER | D21/11/XP24/I_S |  |  |  | CDC | 219 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台四線 | 台四線 |  | 台四線A3 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台四線A3 | 11KV台四線 T相AMP | FEEDER | D21/11/XP24/I_T |  |  |  | CDC | 220 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-94 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1500TIE_AMP | 1500TIE AMP | TIE | D21/161/1500/I_R |  |  |  | CDC | 221 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-91 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D21/0/StaDev/DCV_N |  |  |  | CDC | 222 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D21 | 台西DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-90 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D21/0/StaDev/DCV_P |  |  |  | CDC | 223 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台十線 | 台十線 |  | 台十線A0 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台十線A0 | 11KV台十線 N相AMP | FEEDER | D21/11/XP30/I_N |  |  |  | CDC | 224 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D21/11/100/I_R |  |  |  | CDC | 225 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D21/11/100/I_S |  |  |  | CDC | 226 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D21/11/100/I_T |  |  |  | CDC | 227 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-F8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D21/11/200/I_R |  |  |  | CDC | 228 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-F9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D21/11/200/I_S |  |  |  | CDC | 229 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-FA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D21/11/200/I_T |  |  |  | CDC | 230 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D21/11/310/KW |  |  |  | CDC | 231 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D21/11/310/KVAR |  |  |  | CDC | 232 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D21/11/310/I_R |  |  |  | CDC | 233 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D21/11/310/I_S |  |  |  | CDC | 234 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D21/11/310/I_T |  |  |  | CDC | 235 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-95 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR_OIL | #1DTR 油溫 | MTR | D21//1DTR/OilTemp |  |  |  | CDC | 236 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-96 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D21//1DTR(A)/CoilTemp |  |  |  | CDC | 237 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-98 |  | 1-61 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D21//1DTR(A)/TapPosMv |  |  |  | CDC | 238 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-E2 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D21/11/320/KW |  |  |  | CDC | 239 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-E3 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D21/11/320/KVAR |  |  |  | CDC | 240 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-E4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D21/11/320/I_R |  |  |  | CDC | 241 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D21/11/320/I_S |  |  |  | CDC | 242 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D21/11/320/I_T |  |  |  | CDC | 243 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-97 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D21//1DTR(B)/CoilTemp |  |  |  | CDC | 244 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-99 |  | 1-63 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D21//1DTR(B)/TapPosMv |  |  |  | CDC | 245 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D21/11/330/KW |  |  |  | CDC | 246 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D21/11/330/KVAR |  |  |  | CDC | 247 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D21/11/330/I_R |  |  |  | CDC | 248 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D21/11/330/I_S |  |  |  | CDC | 249 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D21/11/330/I_T |  |  |  | CDC | 250 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR_OIL | #2DTR 油溫 | MTR | D21//2DTR/OilTemp |  |  |  | CDC | 251 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D21//2DTR(A)/CoilTemp |  |  |  | CDC | 252 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9D |  | 1-65 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D21//2DTR(A)/TapPosMv |  |  |  | CDC | 253 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 1-FB | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D21/11/340/KW |  |  |  | CDC | 254 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 1-FC | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D21/11/340/KVAR |  |  |  | CDC | 255 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 1-FD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D21/11/340/I_R |  |  |  | CDC | 256 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 1-FE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D21/11/340/I_S |  |  |  | CDC | 257 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 1-FF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D21/11/340/I_T |  |  |  | CDC | 258 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D21//2DTR(B)/CoilTemp |  |  |  | CDC | 259 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9E |  | 1-67 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D21//2DTR(B)/TapPosMv |  |  |  | CDC | 260 | GENERICAIPoint | DS035_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D21 | 台西DS | 11 | 11kV | 台11線 | 台11線 |  | 台11線A0 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台11線A0 | 11KV台11線 N相AMP | FEEDER | D21/11/XP31/I_N |  |  |  | CDC | 261 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台12線 | 台12線 |  | 台12線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台12線A0 | 11KV台12線 N相AMP | FEEDER | D21/11/XP32/I_N |  |  |  | CDC | 262 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台13線 | 台13線 |  | 台13線A0 | [17 empty] | 2-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台13線A0 | 11KV台13線 N相AMP | FEEDER | D21/11/XP33/I_N |  |  |  | CDC | 263 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台14線 | 台14線 |  | 台14線A0 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台14線A0 | 11KV台14線 N相AMP | FEEDER | D21/11/XP34/I_N |  |  |  | CDC | 264 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台15線 | 台15線 |  | 台15線A0 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台15線A0 | 11KV台15線 N相AMP | FEEDER | D21/11/XP35/I_N |  |  |  | CDC | 265 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台16線 | 台16線 |  | 台16線A0 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台16線A0 | 11KV台16線 N相AMP | FEEDER | D21/11/XP36/I_N |  |  |  | CDC | 266 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台17線 | 台17線 |  | 台17線A0 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台17線A0 | 11KV台17線 N相AMP | FEEDER | D21/11/XP37/I_N |  |  |  | CDC | 267 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台18線 | 台18線 |  | 台18線A0 | [17 empty] | 2-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台18線A0 | 11KV台18線 N相AMP | FEEDER | D21/11/XP38/I_N |  |  |  | CDC | 268 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台19線 | 台19線 |  | 台19線A0 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台19線A0 | 11KV台19線 N相AMP | FEEDER | D21/11/XP39/I_N |  |  |  | CDC | 269 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台20線 | 台20線 |  | 台20線A0 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台20線A0 | 11KV台20線 N相AMP | FEEDER | D21/11/XP40/I_N |  |  |  | CDC | 270 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台一線 | 台一線 |  | 台一線A0 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台一線A0 | 11KV台一線 N相AMP | FEEDER | D21/11/XP21/I_N |  |  |  | CDC | 271 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台七線 | 台七線 |  | 台七線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台七線A0 | 11KV台七線 N相AMP | FEEDER | D21/11/XP27/I_N |  |  |  | CDC | 272 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台九線 | 台九線 |  | 台九線A0 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台九線A0 | 11KV台九線 N相AMP | FEEDER | D21/11/XP29/I_N |  |  |  | CDC | 273 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台二線 | 台二線 |  | 台二線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台二線A0 | 11KV台二線 N相AMP | FEEDER | D21/11/XP22/I_N |  |  |  | CDC | 274 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台八線 | 台八線 |  | 台八線A0 | [17 empty] | 2-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台八線A0 | 11KV台八線 N相AMP | FEEDER | D21/11/XP28/I_N |  |  |  | CDC | 275 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台三線 | 台三線 |  | 台三線A0 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台三線A0 | 11KV台三線 N相AMP | FEEDER | D21/11/XP23/I_N |  |  |  | CDC | 276 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台五線 | 台五線 |  | 台五線A0 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台五線A0 | 11KV台五線 N相AMP | FEEDER | D21/11/XP25/I_N |  |  |  | CDC | 277 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台六線 | 台六線 |  | 台六線A0 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台六線A0 | 11KV台六線 N相AMP | FEEDER | D21/11/XP26/I_N |  |  |  | CDC | 278 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 台四線 | 台四線 |  | 台四線A0 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.台四線A0 | 11KV台四線 N相AMP | FEEDER | D21/11/XP24/I_N |  |  |  | CDC | 279 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 0 |  | 1550_OF | 雲林台西雲高線 |  | R1 | [17 empty] | 2-C8 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_OF_R1 | 雲林台西雲高線 R1相 油壓 | OTHER | D21/161/1550/OilPreR1 |  |  |  | CDC | 280 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1550_OF | 雲林台西雲高線 |  | R2 | [17 empty] | 2-C9 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_OF_R2 | 雲林台西雲高線 R2相 油壓 | OTHER | D21/161/1550/OilPreR2 |  |  |  | CDC | 281 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1550_OF | 雲林台西雲高線 |  | S1 | [17 empty] | 2-CA | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_OF_S1 | 雲林台西雲高線 S1相 油壓 | OTHER | D21/161/1550/OilPreS1 |  |  |  | CDC | 282 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1550_OF | 雲林台西雲高線 |  | S2 | [17 empty] | 2-CB | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_OF_S2 | 雲林台西雲高線 S2相 油壓 | OTHER | D21/161/1550/OilPreS2 |  |  |  | CDC | 283 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1550_OF | 雲林台西雲高線 |  | T1 | [17 empty] | 2-CC | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_OF_T1 | 雲林台西雲高線 T1相 油壓 | OTHER | D21/161/1550/OilPreT1 |  |  |  | CDC | 284 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1550_OF | 雲林台西雲高線 |  | T2 | [17 empty] | 2-CD | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1550_OF_T2 | 雲林台西雲高線 T2相 油壓 | OTHER | D21/161/1550/OilPreT2 |  |  |  | CDC | 285 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1560_OF | 北港台西線 |  | R1 | [17 empty] | 2-C2 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_OF_R1 | 北港台西線 R1相 油壓 | OTHER | D21/161/1560/OilPreR1 |  |  |  | CDC | 286 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1560_OF | 北港台西線 |  | R2 | [17 empty] | 2-C3 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_OF_R2 | 北港台西線 R2相 油壓 | OTHER | D21/161/1560/OilPreR2 |  |  |  | CDC | 287 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1560_OF | 北港台西線 |  | S1 | [17 empty] | 2-C4 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_OF_S1 | 北港台西線 S1相 油壓 | OTHER | D21/161/1560/OilPreS1 |  |  |  | CDC | 288 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1560_OF | 北港台西線 |  | S2 | [17 empty] | 2-C5 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_OF_S2 | 北港台西線 S2相 油壓 | OTHER | D21/161/1560/OilPreS2 |  |  |  | CDC | 289 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1560_OF | 北港台西線 |  | T1 | [17 empty] | 2-C6 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_OF_T1 | 北港台西線 T1相 油壓 | OTHER | D21/161/1560/OilPreT1 |  |  |  | CDC | 290 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 0 |  | 1560_OF | 北港台西線 |  | T2 | [17 empty] | 2-C7 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_N | [8 empty] | 台西DS.1560_OF_T2 | 北港台西線 T2相 油壓 | OTHER | D21/161/1560/OilPreT2 |  |  |  | CDC | 291 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 10.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 禾風線 | 禾風線 |  | 禾風線KVAR | [17 empty] | 2-B5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.禾風線KVAR | 11KV禾風線 KVAR | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D21 | 台西DS | 11 | 11kV | 禾風線 | 禾風線 |  | 禾風線A1 | [17 empty] | 2-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.禾風線A1 | 11KV禾風線 R相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 禾風線 | 禾風線 |  | 禾風線A2 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.禾風線A2 | 11KV禾風線 S相AMP | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 禾風線 | 禾風線 |  | 禾風線A3 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.禾風線A3 | 11KV禾風線 T相AMP | FEEDER |  |  |  |  | CDC | 295 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D21 | 台西DS | 11 | 11kV | 禾風線 | 禾風線 |  | V | [17 empty] | 2-B9 | [5 empty] | kV_-18_18(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.禾風線_KV | 11KV禾風線 KV | OTHER |  |  |  |  | CDC | 296 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D21 | 台西DS | 11 | 11kV | 禾風線 | 禾風線 |  | 禾風線KW | [17 empty] | 2-B4 | [5 empty] | KW_-10800_10800(-2000_2000) |  | DDCS1_2 | [8 empty] | 台西DS.禾風線KW | 11KV禾風線 KW | OTHER |  |  |  |  | CDC | 297 | GENERICAIPoint | DS035_L2 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 5.400000 | 0.010000
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1510_PHA | 塑化紅線(1510) 相間RY | LINE161 | D21/161/1510/PHA |  |  |  | CDC | 298 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1510_GDA | 塑化紅線(1510) 接地RY | LINE161 | D21/161/1510/GDA |  |  |  | CDC | 299 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | 85A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1510_85A | 塑化紅線(1510) 85RY | LINE161 | D21/161/1510/85A |  |  |  | CDC | 300 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | 85U1 | [17 empty] | 1-30-06 |  | 1-44 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1510_85U1 | 塑化紅線(1510) 85RY(M) U/L | LINE161 | D21/161/1510/85UL1 |  |  |  | CDC | 301 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | 85U2 | [17 empty] | 1-30-07 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1510_85U2 | 塑化紅線(1510) 85RY(B) U/L | LINE161 | D21/161/1510/85UL2 |  |  |  | CDC | 302 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 台西DS.1510_CB | 1510(塑化紅線) CB | LINE161 | D21/161/1510/CB |  |  |  | CDC | 303 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | DS1 | 1511 | [16 empty] | 1-35-00 | 1-35-01 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1511_DS | 1511(塑化紅線) DS | LINE161 | D21/161/1510/DS1 |  |  |  | CDC | 304 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | DS2 | 1512 | [16 empty] | 1-35-02 | 1-35-03 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1512_DS | 1512(塑化紅線) DS | LINE161 | D21/161/1510/DS2 |  |  |  | CDC | 305 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | DS3 | 1513 | [16 empty] | 1-35-04 | 1-35-05 | 1-7A | [5 empty] | ADCS_N | [8 empty] | 台西DS.1513_DS | 1513(塑化紅線) DS | LINE161 | D21/161/1510/DS3 |  |  |  | CDC | 306 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | E3 | 1513E | [16 empty] | 1-35-06 | 1-35-07 | 1-7B | [5 empty] | ADCS_N | [8 empty] | 台西DS.1513E_ES | 1513E(塑化紅線) ES | LINE161 | D21/161/1510/ES3 |  |  |  | CDC | 307 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1520_PHA | 塑化白線(1520) 相間RY | LINE161 | D21/161/1520/PHA |  |  |  | CDC | 308 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1520_GDA | 塑化白線(1520) 接地RY | LINE161 | D21/161/1520/GDA |  |  |  | CDC | 309 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | 85A | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1520_85A | 塑化白線(1520) 85RY | LINE161 | D21/161/1520/85A |  |  |  | CDC | 310 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | 85U1 | [17 empty] | 1-30-08 |  | 1-46 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1520_85U1 | 塑化白線(1520) 85RY(M) U/L | LINE161 | D21/161/1520/85UL1 |  |  |  | CDC | 311 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | 85U2 | [17 empty] | 1-30-09 |  | 1-47 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1520_85U2 | 塑化白線(1520) 85RY(B) U/L | LINE161 | D21/161/1520/85UL2 |  |  |  | CDC | 312 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 台西DS.1520_CB | 1520(塑化白線) CB | LINE161 | D21/161/1520/CB |  |  |  | CDC | 313 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | DS1 | 1521 | [16 empty] | 1-35-08 | 1-35-09 | 1-7C | [5 empty] | ADCS_N | [8 empty] | 台西DS.1521_DS | 1521(塑化白線) DS | LINE161 | D21/161/1520/DS1 |  |  |  | CDC | 314 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | DS2 | 1522 | [16 empty] | 1-35-10 | 1-35-11 | 1-7D | [5 empty] | ADCS_N | [8 empty] | 台西DS.1522_DS | 1522(塑化白線) DS | LINE161 | D21/161/1520/DS2 |  |  |  | CDC | 315 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | DS3 | 1523 | [16 empty] | 1-35-12 | 1-35-13 | 1-7E | [5 empty] | ADCS_N | [8 empty] | 台西DS.1523_DS | 1523(塑化白線) DS | LINE161 | D21/161/1520/DS3 |  |  |  | CDC | 316 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | E3 | 1523E | [16 empty] | 1-35-14 | 1-35-15 | 1-7F | [5 empty] | ADCS_N | [8 empty] | 台西DS.1523E_ES | 1523E(塑化白線) ES | LINE161 | D21/161/1520/ES3 |  |  |  | CDC | 317 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1550_PHA | 雲林台西雲高線(1550) 相間RY | LINE161 | D21/161/1550/PHA |  |  |  | CDC | 318 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1550_GDA | 雲林台西雲高線(1550) 接地RY | LINE161 | D21/161/1550/GDA |  |  |  | CDC | 319 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 台西DS.1550_CB | 1550(雲林台西雲高線) CB | LINE161 | D21/161/1550/CB |  |  |  | CDC | 320 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | DS1 | 1551 | [16 empty] | 1-34-08 | 1-34-09 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1551_DS | 1551(雲林台西雲高線) DS | LINE161 | D21/161/1550/DS1 |  |  |  | CDC | 321 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | DS2 | 1552 | [16 empty] | 1-34-10 | 1-34-11 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1552_DS | 1552(雲林台西雲高線) DS | LINE161 | D21/161/1550/DS2 |  |  |  | CDC | 322 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | DS3 | 1553 | [16 empty] | 1-34-12 | 1-34-13 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1553_DS | 1553(雲林台西雲高線) DS | LINE161 | D21/161/1550/DS3 |  |  |  | CDC | 323 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | E3 | 1553E | [16 empty] | 1-34-14 | 1-34-15 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1553E_ES | 1553E(雲林台西雲高線) ES | LINE161 | D21/161/1550/ES3 |  |  |  | CDC | 324 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1560_PHA | 北港台西線(1560) 相間RY | LINE161 | D21/161/1560/PHA |  |  |  | CDC | 325 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1560_GDA | 北港台西線(1560) 接地RY | LINE161 | D21/161/1560/GDA |  |  |  | CDC | 326 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 台西DS.1560_CB | 1560(北港台西線) CB | LINE161 | D21/161/1560/CB |  |  |  | CDC | 327 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | DS1 | 1561 | [16 empty] | 1-34-00 | 1-34-01 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1561_DS | 1561(北港台西線) DS | LINE161 | D21/161/1560/DS1 |  |  |  | CDC | 328 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | DS2 | 1562 | [16 empty] | 1-34-02 | 1-34-03 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1562_DS | 1562(北港台西線) DS | LINE161 | D21/161/1560/DS2 |  |  |  | CDC | 329 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | DS3 | 1563 | [16 empty] | 1-34-04 | 1-34-05 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1563_DS | 1563(北港台西線) DS | LINE161 | D21/161/1560/DS3 |  |  |  | CDC | 330 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | E3 | 1563E | [16 empty] | 1-34-06 | 1-34-07 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1563E_ES | 1563E(北港台西線) ES | LINE161 | D21/161/1560/ES3 |  |  |  | CDC | 331 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | PHA | [17 empty] | 1-10-01 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_PHA | 11KV台一線(XP21) 相間RY | FEEDER | D21/11/XP21/PHA |  |  |  | CDC | 332 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_GDA | 11KV台一線(XP21) 接地RY | FEEDER | D21/11/XP21/GDA |  |  |  | CDC | 333 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-20 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_79UL | 11KV台一線(XP21) 79RY U/L | FEEDER | D21/11/XP21/79UL |  |  |  | CDC | 334 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP21 | 台一線(XP21) LCO分流器 |  | ADJ | [17 empty] | 2-34-12 |  | 1-36 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_ADJ | 11KV台一線(XP21) LCO分流器 U/L | FEEDER | D21/11/XP21/ADJ |  |  |  | CDC | 335 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP21 | XP21(11KV台一線) |  | CB | [17 empty] | 1-10-00 |  | 1-13 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_CB | XP21(11KV台一線) CB | FEEDER | D21/11/XP21/CB |  |  |  | CDC | 336 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_PHA | 11KV台二線(XP22) 相間RY | FEEDER | D21/11/XP22/PHA |  |  |  | CDC | 337 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_GDA | 11KV台二線(XP22) 接地RY | FEEDER | D21/11/XP22/GDA |  |  |  | CDC | 338 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-21 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_79UL | 11KV台二線(XP22) 79RY U/L | FEEDER | D21/11/XP22/79UL |  |  |  | CDC | 339 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP22 | 台二線(XP22) LCO分流器 |  | ADJ | [17 empty] | 2-34-13 |  | 1-37 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_ADJ | 11KV台二線(XP22) LCO分流器 U/L | FEEDER | D21/11/XP22/ADJ |  |  |  | CDC | 340 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP22 | XP22(11KV台二線) |  | CB | [17 empty] | 1-10-03 |  | 1-14 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_CB | XP22(11KV台二線) CB | FEEDER | D21/11/XP22/CB |  |  |  | CDC | 341 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_PHA | 11KV台三線(XP23) 相間RY | FEEDER | D21/11/XP23/PHA |  |  |  | CDC | 342 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_GDA | 11KV台三線(XP23) 接地RY | FEEDER | D21/11/XP23/GDA |  |  |  | CDC | 343 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-22 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_79UL | 11KV台三線(XP23) 79RY U/L | FEEDER | D21/11/XP23/79UL |  |  |  | CDC | 344 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP23 | 台三線(XP23) LCO分流器 |  | ADJ | [17 empty] | 2-34-14 |  | 1-38 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_ADJ | 11KV台三線(XP23) LCO分流器 U/L | FEEDER | D21/11/XP23/ADJ |  |  |  | CDC | 345 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP23 | XP23(11KV台三線) |  | CB | [17 empty] | 1-10-06 |  | 1-15 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_CB | XP23(11KV台三線) CB | FEEDER | D21/11/XP23/CB |  |  |  | CDC | 346 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_PHA | 11KV台四線(XP24) 相間RY | FEEDER | D21/11/XP24/PHA |  |  |  | CDC | 347 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_GDA | 11KV台四線(XP24) 接地RY | FEEDER | D21/11/XP24/GDA |  |  |  | CDC | 348 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) 79RY |  | 79UL | [17 empty] | 2-30-13 |  | 2-23 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_79UL | 11KV台四線(XP24) 79RY U/L | FEEDER | D21/11/XP24/79UL |  |  |  | CDC | 349 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP24 | 台四線(XP24) LCO分流器 |  | ADJ | [17 empty] | 2-34-15 |  | 1-39 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_ADJ | 11KV台四線(XP24) LCO分流器 U/L | FEEDER | D21/11/XP24/ADJ |  |  |  | CDC | 350 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP24 | XP24(11KV台四線) |  | CB | [17 empty] | 1-11-01 |  | 1-16 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_CB | XP24(11KV台四線) CB | FEEDER | D21/11/XP24/CB |  |  |  | CDC | 351 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_PHA | 11KV台五線(XP25) 相間RY | FEEDER | D21/11/XP25/PHA |  |  |  | CDC | 352 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_GDA | 11KV台五線(XP25) 接地RY | FEEDER | D21/11/XP25/GDA |  |  |  | CDC | 353 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-24 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_79UL | 11KV台五線(XP25) 79RY U/L | FEEDER | D21/11/XP25/79UL |  |  |  | CDC | 354 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP25 | 台五線(XP25) LCO分流器 |  | ADJ | [17 empty] | 2-35-00 |  | 1-3A | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_ADJ | 11KV台五線(XP25) LCO分流器 U/L | FEEDER | D21/11/XP25/ADJ |  |  |  | CDC | 355 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP25 | XP25(11KV台五線) |  | CB | [17 empty] | 1-11-04 |  | 1-17 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_CB | XP25(11KV台五線) CB | FEEDER | D21/11/XP25/CB |  |  |  | CDC | 356 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | PHA | [17 empty] | 1-12-00 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_PHA | 11KV台六線(XP26) 相間RY | FEEDER | D21/11/XP26/PHA |  |  |  | CDC | 357 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) |  | GDA | [17 empty] | 1-12-01 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_GDA | 11KV台六線(XP26) 接地RY | FEEDER | D21/11/XP26/GDA |  |  |  | CDC | 358 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) 79RY |  | 79UL | [17 empty] | 2-30-15 |  | 2-25 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_79UL | 11KV台六線(XP26) 79RY U/L | FEEDER | D21/11/XP26/79UL |  |  |  | CDC | 359 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP26 | 台六線(XP26) LCO分流器 |  | ADJ | [17 empty] | 2-35-01 |  | 1-3B | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_ADJ | 11KV台六線(XP26) LCO分流器 U/L | FEEDER | D21/11/XP26/ADJ |  |  |  | CDC | 360 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP26 | XP26(11KV台六線) |  | CB | [17 empty] | 1-11-07 |  | 1-18 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_CB | XP26(11KV台六線) CB | FEEDER | D21/11/XP26/CB |  |  |  | CDC | 361 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | PHA | [17 empty] | 1-16-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_PHA | 11KV台七線(XP27) 相間RY | FEEDER | D21/11/XP27/PHA |  |  |  | CDC | 362 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) |  | GDA | [17 empty] | 1-16-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_GDA | 11KV台七線(XP27) 接地RY | FEEDER | D21/11/XP27/GDA |  |  |  | CDC | 363 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-30 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_79UL | 11KV台七線(XP27) 79RY U/L | FEEDER | D21/11/XP27/79UL |  |  |  | CDC | 364 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP27 | 台七線(XP27) LCO分流器 |  | ADJ | [17 empty] | 2-35-09 |  | 1-59 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_ADJ | 11KV台七線(XP27) LCO分流器 U/L | FEEDER | D21/11/XP27/ADJ |  |  |  | CDC | 365 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP27 | XP27(11KV台七線) |  | CB | [17 empty] | 1-16-03 |  | 1-26 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_CB | XP27(11KV台七線) CB | FEEDER | D21/11/XP27/CB |  |  |  | CDC | 366 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_PHA | 11KV台八線(XP28) 相間RY | FEEDER | D21/11/XP28/PHA |  |  |  | CDC | 367 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_GDA | 11KV台八線(XP28) 接地RY | FEEDER | D21/11/XP28/GDA |  |  |  | CDC | 368 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 2-2F | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_79UL | 11KV台八線(XP28) 79RY U/L | FEEDER | D21/11/XP28/79UL |  |  |  | CDC | 369 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP28 | 台八線(XP28) LCO分流器 |  | ADJ | [17 empty] | 2-35-08 |  | 1-58 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_ADJ | 11KV台八線(XP28) LCO分流器 U/L | FEEDER | D21/11/XP28/ADJ |  |  |  | CDC | 370 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP28 | XP28(11KV台八線) |  | CB | [17 empty] | 1-16-00 |  | 1-25 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_CB | XP28(11KV台八線) CB | FEEDER | D21/11/XP28/CB |  |  |  | CDC | 371 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_PHA | 11KV台九線(XP29) 相間RY | FEEDER | D21/11/XP29/PHA |  |  |  | CDC | 372 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_GDA | 11KV台九線(XP29) 接地RY | FEEDER | D21/11/XP29/GDA |  |  |  | CDC | 373 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-2E | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_79UL | 11KV台九線(XP29) 79RY U/L | FEEDER | D21/11/XP29/79UL |  |  |  | CDC | 374 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP29 | 台九線(XP29) LCO分流器 |  | ADJ | [17 empty] | 2-35-07 |  | 1-57 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_ADJ | 11KV台九線(XP29) LCO分流器 U/L | FEEDER | D21/11/XP29/ADJ |  |  |  | CDC | 375 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP29 | XP29(11KV台九線) |  | CB | [17 empty] | 1-15-05 |  | 1-24 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_CB | XP29(11KV台九線) CB | FEEDER | D21/11/XP29/CB |  |  |  | CDC | 376 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | PHA | [17 empty] | 1-15-03 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_PHA | 11KV台十線(XP30) 相間RY | FEEDER | D21/11/XP30/PHA |  |  |  | CDC | 377 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) |  | GDA | [17 empty] | 1-15-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_GDA | 11KV台十線(XP30) 接地RY | FEEDER | D21/11/XP30/GDA |  |  |  | CDC | 378 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 2-2D | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_79UL | 11KV台十線(XP30) 79RY U/L | FEEDER | D21/11/XP30/79UL |  |  |  | CDC | 379 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP30 | 台十線(XP30) LCO分流器 |  | ADJ | [17 empty] | 2-35-06 |  | 1-56 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_ADJ | 11KV台十線(XP30) LCO分流器 U/L | FEEDER | D21/11/XP30/ADJ |  |  |  | CDC | 380 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP30 | XP30(11KV台十線) |  | CB | [17 empty] | 1-15-02 |  | 1-23 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_CB | XP30(11KV台十線) CB | FEEDER | D21/11/XP30/CB |  |  |  | CDC | 381 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP31 | 台11線(XP31) |  | PHA | [17 empty] | 1-14-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_PHA | 11KV台11線(XP31) 相間RY | FEEDER | D21/11/XP31/PHA |  |  |  | CDC | 382 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP31 | 台11線(XP31) |  | GDA | [17 empty] | 1-14-06 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_GDA | 11KV台11線(XP31) 接地RY | FEEDER | D21/11/XP31/GDA |  |  |  | CDC | 383 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP31 | 台11線(XP31) 79RY |  | 79UL | [17 empty] | 2-31-05 |  | 2-2B | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_79UL | 11KV台11線(XP31) 79RY U/L | FEEDER | D21/11/XP31/79UL |  |  |  | CDC | 384 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP31 | 台11線(XP31) LCO分流器 |  | ADJ | [17 empty] | 2-35-05 |  | 1-3F | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_ADJ | 11KV台11線(XP31) LCO分流器 U/L | FEEDER | D21/11/XP31/ADJ |  |  |  | CDC | 385 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP31 | XP31(11KV台11線) |  | CB | [17 empty] | 1-14-04 |  | 1-1E | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_CB | XP31(11KV台11線) CB | FEEDER | D21/11/XP31/CB |  |  |  | CDC | 386 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP32 | 台12線(XP32) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_PHA | 11KV台12線(XP32) 相間RY | FEEDER | D21/11/XP32/PHA |  |  |  | CDC | 387 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP32 | 台12線(XP32) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_GDA | 11KV台12線(XP32) 接地RY | FEEDER | D21/11/XP32/GDA |  |  |  | CDC | 388 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP32 | 台12線(XP32) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-2A | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_79UL | 11KV台12線(XP32) 79RY U/L | FEEDER | D21/11/XP32/79UL |  |  |  | CDC | 389 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP32 | 台12線(XP32) LCO分流器 |  | ADJ | [17 empty] | 2-35-04 |  | 1-3E | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_ADJ | 11KV台12線(XP32) LCO分流器 U/L | FEEDER | D21/11/XP32/ADJ |  |  |  | CDC | 390 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP32 | XP32(11KV台12線) |  | CB | [17 empty] | 1-14-01 |  | 1-1D | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_CB | XP32(11KV台12線) CB | FEEDER | D21/11/XP32/CB |  |  |  | CDC | 391 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP33 | 台13線(XP33) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_PHA | 11KV台13線(XP33) 相間RY | FEEDER | D21/11/XP33/PHA |  |  |  | CDC | 392 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP33 | 台13線(XP33) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_GDA | 11KV台13線(XP33) 接地RY | FEEDER | D21/11/XP33/GDA |  |  |  | CDC | 393 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP33 | 台13線(XP33) 79RY |  | 79UL | [17 empty] | 2-31-03 |  | 2-29 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_79UL | 11KV台13線(XP33) 79RY U/L | FEEDER | D21/11/XP33/79UL |  |  |  | CDC | 394 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP33 | 台13線(XP33) LCO分流器 |  | ADJ | [17 empty] | 2-35-03 |  | 1-3D | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_ADJ | 11KV台13線(XP33) LCO分流器 U/L | FEEDER | D21/11/XP33/ADJ |  |  |  | CDC | 395 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP33 | XP33(11KV台13線) |  | CB | [17 empty] | 1-13-06 |  | 1-1C | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_CB | XP33(11KV台13線) CB | FEEDER | D21/11/XP33/CB |  |  |  | CDC | 396 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP34 | 台14線(XP34) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_PHA | 11KV台14線(XP34) 相間RY | FEEDER | D21/11/XP34/PHA |  |  |  | CDC | 397 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP34 | 台14線(XP34) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_GDA | 11KV台14線(XP34) 接地RY | FEEDER | D21/11/XP34/GDA |  |  |  | CDC | 398 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP34 | 台14線(XP34) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-28 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_79UL | 11KV台14線(XP34) 79RY U/L | FEEDER | D21/11/XP34/79UL |  |  |  | CDC | 399 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP34 | 台14線(XP34) LCO分流器 |  | ADJ | [17 empty] | 2-35-02 |  | 1-3C | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_ADJ | 11KV台14線(XP34) LCO分流器 U/L | FEEDER | D21/11/XP34/ADJ |  |  |  | CDC | 400 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP34 | XP34(11KV台14線) |  | CB | [17 empty] | 1-13-03 |  | 1-1B | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_CB | XP34(11KV台14線) CB | FEEDER | D21/11/XP34/CB |  |  |  | CDC | 401 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP35 | 台15線(XP35) |  | PHA | [17 empty] | 1-17-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_PHA | 11KV台15線(XP35) 相間RY | FEEDER | D21/11/XP35/PHA |  |  |  | CDC | 402 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP35 | 台15線(XP35) |  | GDA | [17 empty] | 1-17-06 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_GDA | 11KV台15線(XP35) 接地RY | FEEDER | D21/11/XP35/GDA |  |  |  | CDC | 403 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP35 | 台15線(XP35) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-32 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_79UL | 11KV台15線(XP35) 79RY U/L | FEEDER | D21/11/XP35/79UL |  |  |  | CDC | 404 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP35 | 台15線(XP35) LCO分流器 |  | ADJ | [17 empty] | 2-35-10 |  | 1-5A | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_ADJ | 11KV台15線(XP35) LCO分流器 U/L | FEEDER | D21/11/XP35/ADJ |  |  |  | CDC | 405 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP35 | XP35(11KV台15線) |  | CB | [17 empty] | 1-17-04 |  | 1-2A | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_CB | XP35(11KV台15線) CB | FEEDER | D21/11/XP35/CB |  |  |  | CDC | 406 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP36 | 台16線(XP36) |  | PHA | [17 empty] | 1-18-00 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_PHA | 11KV台16線(XP36) 相間RY | FEEDER | D21/11/XP36/PHA |  |  |  | CDC | 407 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP36 | 台16線(XP36) |  | GDA | [17 empty] | 1-18-01 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_GDA | 11KV台16線(XP36) 接地RY | FEEDER | D21/11/XP36/GDA |  |  |  | CDC | 408 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP36 | 台16線(XP36) 79RY |  | 79UL | [17 empty] | 2-31-13 |  | 2-33 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_79UL | 11KV台16線(XP36) 79RY U/L | FEEDER | D21/11/XP36/79UL |  |  |  | CDC | 409 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP36 | 台16線(XP36) LCO分流器 |  | ADJ | [17 empty] | 2-35-11 |  | 1-5B | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_ADJ | 11KV台16線(XP36) LCO分流器 U/L | FEEDER | D21/11/XP36/ADJ |  |  |  | CDC | 410 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP36 | XP36(11KV台16線) |  | CB | [17 empty] | 1-17-07 |  | 1-2B | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_CB | XP36(11KV台16線) CB | FEEDER | D21/11/XP36/CB |  |  |  | CDC | 411 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP37 | 台17線(XP37) |  | PHA | [17 empty] | 1-18-03 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_PHA | 11KV台17線(XP37) 相間RY | FEEDER | D21/11/XP37/PHA |  |  |  | CDC | 412 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP37 | 台17線(XP37) |  | GDA | [17 empty] | 1-18-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_GDA | 11KV台17線(XP37) 接地RY | FEEDER | D21/11/XP37/GDA |  |  |  | CDC | 413 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP37 | 台17線(XP37) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-34 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_79UL | 11KV台17線(XP37) 79RY U/L | FEEDER | D21/11/XP37/79UL |  |  |  | CDC | 414 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP37 | 台17線(XP37) LCO分流器 |  | ADJ | [17 empty] | 2-35-12 |  | 1-5C | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_ADJ | 11KV台17線(XP37) LCO分流器 U/L | FEEDER | D21/11/XP37/ADJ |  |  |  | CDC | 415 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP37 | XP37(11KV台17線) |  | CB | [17 empty] | 1-18-02 |  | 1-2C | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_CB | XP37(11KV台17線) CB | FEEDER | D21/11/XP37/CB |  |  |  | CDC | 416 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP38 | 台18線(XP38) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_PHA | 11KV台18線(XP38) 相間RY | FEEDER | D21/11/XP38/PHA |  |  |  | CDC | 417 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP38 | 台18線(XP38) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_GDA | 11KV台18線(XP38) 接地RY | FEEDER | D21/11/XP38/GDA |  |  |  | CDC | 418 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP38 | 台18線(XP38) 79RY |  | 79UL | [17 empty] | 2-31-15 |  | 2-35 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_79UL | 11KV台18線(XP38) 79RY U/L | FEEDER | D21/11/XP38/79UL |  |  |  | CDC | 419 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP38 | 台18線(XP38) LCO分流器 |  | ADJ | [17 empty] | 2-35-13 |  | 1-5D | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_ADJ | 11KV台18線(XP38) LCO分流器 U/L | FEEDER | D21/11/XP38/ADJ |  |  |  | CDC | 420 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP38 | XP38(11KV台18線) |  | CB | [17 empty] | 1-18-05 |  | 1-2D | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_CB | XP38(11KV台18線) CB | FEEDER | D21/11/XP38/CB |  |  |  | CDC | 421 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP39 | 台19線(XP39) |  | PHA | [17 empty] | 1-19-01 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_PHA | 11KV台19線(XP39) 相間RY | FEEDER | D21/11/XP39/PHA |  |  |  | CDC | 422 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP39 | 台19線(XP39) |  | GDA | [17 empty] | 1-19-02 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_GDA | 11KV台19線(XP39) 接地RY | FEEDER | D21/11/XP39/GDA |  |  |  | CDC | 423 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP39 | 台19線(XP39) 79RY |  | 79UL | [17 empty] | 2-32-00 |  | 2-36 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_79UL | 11KV台19線(XP39) 79RY U/L | FEEDER | D21/11/XP39/79UL |  |  |  | CDC | 424 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP39 | 台19線(XP39) LCO分流器 |  | ADJ | [17 empty] | 2-35-14 |  | 1-5E | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_ADJ | 11KV台19線(XP39) LCO分流器 U/L | FEEDER | D21/11/XP39/ADJ |  |  |  | CDC | 425 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP39 | XP39(11KV台19線) |  | CB | [17 empty] | 1-19-00 |  | 1-2E | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_CB | XP39(11KV台19線) CB | FEEDER | D21/11/XP39/CB |  |  |  | CDC | 426 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | XP40 | 台20線(XP40) |  | PHA | [17 empty] | 1-19-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_PHA | 11KV台20線(XP40) 相間RY | FEEDER | D21/11/XP40/PHA |  |  |  | CDC | 427 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP40 | 台20線(XP40) |  | GDA | [17 empty] | 1-19-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_GDA | 11KV台20線(XP40) 接地RY | FEEDER | D21/11/XP40/GDA |  |  |  | CDC | 428 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | XP40 | 台20線(XP40) 79RY |  | 79UL | [17 empty] | 2-32-01 |  | 2-37 | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_79UL | 11KV台20線(XP40) 79RY U/L | FEEDER | D21/11/XP40/79UL |  |  |  | CDC | 429 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV | XP40 | 台20線(XP40) LCO分流器 |  | ADJ | [17 empty] | 2-35-15 |  | 1-5F | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_ADJ | 11KV台20線(XP40) LCO分流器 U/L | FEEDER | D21/11/XP40/ADJ |  |  |  | CDC | 430 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D21 | 台西DS | 11 | 11kV | XP40 | XP40(11KV台20線) |  | CB | [17 empty] | 1-19-03 |  | 1-2F | [5 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_CB | XP40(11KV台20線) CB | FEEDER | D21/11/XP40/CB |  |  |  | CDC | 431 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-05-00 |  | 1-09 | [5 empty] | 161KV_N | [8 empty] | 台西DS.1500_CB | 1500(TIE) CB | TIE | D21/161/1500/CB |  |  |  | CDC | 432 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-05-01 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D21/161/1500/50A |  |  |  | CDC | 433 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-38-00 | 2-38-01 | 2-10 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1501_DS | 1501(TIE) DS | TIE | D21/161/1500/DS1 |  |  |  | CDC | 434 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-38-02 | 2-38-03 | 2-11 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1502_DS | 1502(TIE) DS | TIE | D21/161/1500/DS2 |  |  |  | CDC | 435 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-05-05 |  | 1-0A | [5 empty] | 161KV_N | [8 empty] | 台西DS.1750_CB | 1750(#1DTR) CB | MTR | D21/161/1750/CB |  |  |  | CDC | 436 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-06-03 |  | 1-10 | [5 empty] | ADCS_N | [8 empty] | 台西DS.310_CB | 310(#1DTR) CB | MTR | D21/11/310/CB |  |  |  | CDC | 437 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-07-07 |  | 1-21 | [5 empty] | ADCS_N | [8 empty] | 台西DS.320_CB | 320(#1DTR) CB | MTR | D21/11/320/CB |  |  |  | CDC | 438 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.310_51A | #1DTR二次側(310) 51RY | MTR | D21/11/310/PHA |  |  |  | CDC | 439 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.320_51A | #1DTR二次側(320) 51RY | MTR | D21/11/320/PHA |  |  |  | CDC | 440 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-38-04 | 2-38-05 | 2-12 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1751_DS | 1751(#1DTR) DS | MTR | D21/161/1750/DS1 |  |  |  | CDC | 441 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 2-38-06 | 2-38-07 | 2-13 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1752_DS | 1752(#1DTR) DS | MTR | D21/161/1750/DS2 |  |  |  | CDC | 442 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-06-07 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 台西DS.1760_CB | 1760(#2DTR) CB | MTR | D21/161/1760/CB |  |  |  | CDC | 443 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-07-05 |  | 1-20 | [5 empty] | ADCS_N | [8 empty] | 台西DS.330_CB | 330(#2DTR) CB | MTR | D21/11/330/CB |  |  |  | CDC | 444 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-08-07 |  | 1-31 | [5 empty] | ADCS_N | [8 empty] | 台西DS.340_CB | 340(#2DTR) CB | MTR | D21/11/340/CB |  |  |  | CDC | 445 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-07-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.330_51A | #2DTR二次側(330) 51RY | MTR | D21/11/330/PHA |  |  |  | CDC | 446 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-09-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.340_51A | #2DTR二次側(340) 51RY | MTR | D21/11/340/PHA |  |  |  | CDC | 447 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-38-08 | 2-38-09 | 2-14 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1761_DS | 1761(#2DTR) DS | MTR | D21/161/1760/DS1 |  |  |  | CDC | 448 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 2-38-10 | 2-38-11 | 2-15 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1762_DS | 1762(#2DTR) DS | MTR | D21/161/1760/DS2 |  |  |  | CDC | 449 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-12-02 |  | 1-12 | [5 empty] | ADCS_N | [8 empty] | 台西DS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 450 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-31-00 |  | 2-26 | [5 empty] | ADCS_N | [8 empty] | 台西DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | D21/11/210/SC_A_M |  |  |  | CDC | 451 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-12-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.210_SCA | 11KV #1SC 51,51N RY | SC | D21/11/210/SCA |  |  |  | CDC | 452 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-12-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D21/11/210/UVA |  |  |  | CDC | 453 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-12-05 |  | 1-19 | [5 empty] | ADCS_N | [8 empty] | 台西DS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 454 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-31-01 |  | 2-27 | [5 empty] | ADCS_N | [8 empty] | 台西DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D21/11/220/SC_A_M |  |  |  | CDC | 455 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-12-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.220_SCA | 11KV #2SC 51,51N RY | SC | D21/11/220/SCA |  |  |  | CDC | 456 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-12-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D21/11/220/UVA |  |  |  | CDC | 457 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-16-06 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 台西DS.230_CB | 230(11KV #3SC) CB | SC | D21/11/230/CB |  |  |  | CDC | 458 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-11 |  | 2-31 | [5 empty] | ADCS_N | [8 empty] | 台西DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | D21/11/230/SC_A_M |  |  |  | CDC | 459 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-16-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.230_SCA | 11KV #3SC 51,51N RY | SC | D21/11/230/SCA |  |  |  | CDC | 460 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-17-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D21/11/230/UVA |  |  |  | CDC | 461 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-14-07 |  | 1-1F | [5 empty] | ADCS_N | [8 empty] | 台西DS.240_CB | 240(11KV #4SC) CB | SC | D21/11/240/CB |  |  |  | CDC | 462 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-31-06 |  | 2-2C | [5 empty] | ADCS_N | [8 empty] | 台西DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | D21/11/240/SC_A_M |  |  |  | CDC | 463 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-15-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.240_SCA | 11KV #4SC 51,51N RY | SC | D21/11/240/SCA |  |  |  | CDC | 464 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-15-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D21/11/240/UVA |  |  |  | CDC | 465 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-1A-01 |  | 1-30 | [5 empty] | ADCS_N | [8 empty] | 台西DS.250_CB | 250(11KV #5SC) CB | SC | D21/11/250/CB |  |  |  | CDC | 466 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-32-03 |  | 2-39 | [5 empty] | ADCS_N | [8 empty] | 台西DS.250_A/M | 11KV #5SC 乏控器 A/M | SC | D21/11/250/SC_A_M |  |  |  | CDC | 467 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-1A-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.250_SCA | 11KV #5SC 51,51N RY | SC | D21/11/250/SCA |  |  |  | CDC | 468 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-1A-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | D21/11/250/UVA |  |  |  | CDC | 469 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-19-06 |  | 1-28 | [5 empty] | ADCS_N | [8 empty] | 台西DS.260_CB | 260(11KV #6SC) CB | SC | D21/11/260/CB |  |  |  | CDC | 470 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-32-02 |  | 2-38 | [5 empty] | ADCS_N | [8 empty] | 台西DS.260_A/M | 11KV #6SC 乏控器 A/M | SC | D21/11/260/SC_A_M |  |  |  | CDC | 471 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-19-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.260_SCA | 11KV #6SC 51,51N RY | SC | D21/11/260/SCA |  |  |  | CDC | 472 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-1A-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | D21/11/260/UVA |  |  |  | CDC | 473 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D21/161/1BUS/BUS_VUA |  |  |  | CDC | 474 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-05-02 | [7 empty] | 161KV_N | [8 empty] | 台西DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D21/161/1BUS/87A |  |  |  | CDC | 475 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-4E | [5 empty] | ADCS_N | [8 empty] | 台西DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D21/161/1BUS/87UL |  |  |  | CDC | 476 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D21/161/2BUS/BUS_VUA |  |  |  | CDC | 477 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 台西DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D21/161/2BUS/87A |  |  |  | CDC | 478 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-09 |  | 1-4F | [5 empty] | ADCS_N | [8 empty] | 台西DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D21/161/2BUS/87UL |  |  |  | CDC | 479 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 11 | 11kV |  |  |  | CBA | [17 empty] | 2-34-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.11KV_CBA | 11KV斷路器重故障 | OTHER | D21/11/ComPoint/CBA |  |  |  | CDC | 480 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV |  |  |  | CBF | [17 empty] | 2-34-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.11KV_CBF | 11KV斷路器輕故障 | OTHER | D21/11/ComPoint/CBF |  |  |  | CDC | 481 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-34-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D21/161/ComPoint/CBA |  |  |  | CDC | 482 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-34-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D21/161/ComPoint/CBF |  |  |  | CDC | 483 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 2-33-15 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D21/0/ComPoint/COMT |  |  |  | CDC | 484 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | OSCA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.OSC啟動 | 示波器啟動警報 | OTHER | D21/161/ComPoint/OSCA |  |  |  | CDC | 485 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D21/0/RTU/RTU_R_L |  |  |  | CDC | 486 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D21 | 台西DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 台西DS.TEST_CB | TEST CB | OTHER | D21/0/RTU/Test_CB |  |  |  | CDC | 487 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-32-10 | [7 empty] | ADCS_N | [8 empty] | 台西DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D21/0/StaDev/Fire1 |  |  |  | CDC | 488 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | Fire2 | [17 empty] | 2-32-11 | [7 empty] | ADCS_N | [8 empty] | 台西DS.火災警報(2) | 火災警報(2) | OTHER | D21/0/StaDev/Fire2 |  |  |  | CDC | 489 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | Fire3 | [17 empty] | 2-32-12 | [7 empty] | ADCS_N | [8 empty] | 台西DS.火災警報(3) | 火災警報(3) | OTHER | D21/0/StaDev/Fire3 |  |  |  | CDC | 490 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | OPA | [17 empty] | 2-33-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D21/0/ComPoint/OPA |  |  |  | CDC | 491 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | SUBA | [17 empty] | 2-34-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.其他重故障 | 變電所內其他重故障 | OTHER | D21/0/StaDev/PSA |  |  |  | CDC | 492 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | SUBF | [17 empty] | 2-34-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D21/0/StaDev/PSF |  |  |  | CDC | 493 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-33-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D21/0/StaDev/ACB1 |  |  |  | CDC | 494 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D21 | 台西DS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-33-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D21/0/StaDev/ACB2 |  |  |  | CDC | 495 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D21 | 台西DS | 0 |  |  |  |  | ACBA | [17 empty] | 2-34-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.所內電源ACBA | 所內電源故障警報 | OTHER | D21/0/StaDev/ACBA |  |  |  | CDC | 496 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | STUV | [17 empty] | 2-33-08 | [7 empty] | ADCS_N | [8 empty] | 台西DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D21/0/StaDev/STUV |  |  |  | CDC | 497 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-11 | [7 empty] | ADCS_N | [8 empty] | 台西DS.直流電源DCA | 直流電源故障警報 | OTHER | D21/0/StaDev/DCA |  |  |  | CDC | 498 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | DCE | [17 empty] | 2-33-14 | [7 empty] | ADCS_N | [8 empty] | 台西DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D21/0/StaDev/DCE |  |  |  | CDC | 499 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | OilLeak | [17 empty] | 2-34-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D21/0/StaDev/OilLeak1 |  |  |  | CDC | 500 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | CommACF | [17 empty] | 2-34-08 | [7 empty] | ADCS_N | [8 empty] | 台西DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D21/0/StaDev/CommACF |  |  |  | CDC | 501 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-13 | [7 empty] | ADCS_N | [8 empty] | 台西DS.無人化防盜(1) | 無人化防盜(1)保全控制室 | OTHER | D21/0/StaDev/Burglar1 |  |  |  | CDC | 502 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | Burglar2 | [17 empty] | 2-32-14 | [7 empty] | ADCS_N | [8 empty] | 台西DS.無人化防盜(2) | 無人化防盜(2)保全圍牆 | OTHER | D21/0/StaDev/Burglar2 |  |  |  | CDC | 503 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | Burglar3 | [17 empty] | 2-32-15 | [7 empty] | ADCS_N | [8 empty] | 台西DS.無人化防盜(3) | 無人化防盜(3) | OTHER | D21/0/StaDev/Burglar3 |  |  |  | CDC | 504 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | Door1 | [17 empty] | 2-33-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.無人化門禁(1) | 無人化門禁(1)建物大門 | OTHER | D21/0/StaDev/Door1 |  |  |  | CDC | 505 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  |  |  |  | Door2 | [17 empty] | 2-33-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D21/0/StaDev/Door2 |  |  |  | CDC | 506 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  |  |  |  | Door3 | [17 empty] | 2-33-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.無人化門禁(3) | 無人化門禁(3) | OTHER | D21/0/StaDev/Door3 |  |  |  | CDC | 507 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-33-03 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 台西DS.開關場照明(A) | 開關場照明(A) | OTHER | D21/0/StaDev/Lights1 |  |  |  | CDC | 508 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D21 | 台西DS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-33-04 |  | 2-1F | [5 empty] | ADCS_N | [8 empty] | 台西DS.開關場照明(B) | 開關場照明(B) | OTHER | D21/0/StaDev/Lights2 |  |  |  | CDC | 509 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D21 | 台西DS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 2-32-09 | [7 empty] | ADCS_N | [8 empty] | 台西DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | D21/0/StaDev/AIRCON |  |  |  | CDC | 510 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D21 | 台西DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-32-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.水位警報(1) | 地下室水位警報(1) | OTHER | D21/0/StaDev/Water1 |  |  |  | CDC | 511 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-32-08 | [7 empty] | ADCS_N | [8 empty] | 台西DS.水位警報(2) | 地下室水位警報(2) | OTHER | D21/0/StaDev/Water2 |  |  |  | CDC | 512 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-33-12 | [7 empty] | ADCS_N | [8 empty] | 台西DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D21/0/StaDev/CHG1 |  |  |  | CDC | 513 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-33-13 | [7 empty] | ADCS_N | [8 empty] | 台西DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D21/0/StaDev/CHG2 |  |  |  | CDC | 514 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-32-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D21/161/1500/50SA |  |  |  | CDC | 515 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-13-00 |  | 1-1A | [5 empty] | ADCS_N | [8 empty] | 台西DS.100_CB | 100(TIE) CB | TIE |  |  |  |  | CDC | 516 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-13-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.100_51A | 11KV TIE(100) 51RY | TIE |  |  |  |  | CDC | 517 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-13-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.100_51NA | 11KV TIE(100) 51N RY | TIE |  |  |  |  | CDC | 518 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-17-01 |  | 1-27 | [5 empty] | ADCS_N | [8 empty] | 台西DS.200_CB | 200(TIE) CB | TIE | D21/11/200/CB |  |  |  | CDC | 519 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-17-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.200_51A | 11KV TIE(200) 51RY | TIE | D21/11/200/PHA |  |  |  | CDC | 520 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-17-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D21/11/200/GDA |  |  |  | CDC | 521 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#1DTR_51A | #1DTR 51RY | MTR | D21/161/1750/PHA |  |  |  | CDC | 522 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-06-02 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#1DTR_51NA | #1DTR 51N RY | MTR | D21/161/1750/GDA |  |  |  | CDC | 523 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-06-00 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D21//1DTR/51ZA |  |  |  | CDC | 524 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-05-06 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#1DTR_87A | #1DTR 87RY | MTR | D21//1DTR/87A |  |  |  | CDC | 525 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-05-07 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D21//1DTR/96PA |  |  |  | CDC | 526 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 2-30-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_96D | #1DTR 96D RY | MTR | D21//1DTR/96D |  |  |  | CDC | 527 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 2-30-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_96P | #1DTR 96P RY | MTR | D21//1DTR/96P |  |  |  | CDC | 528 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 2-30-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D21//1DTR/63Q |  |  |  | CDC | 529 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 2-30-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D21//1DTR/96B1 |  |  |  | CDC | 530 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 2-30-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D21//1DTR/96B2 |  |  |  | CDC | 531 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-13 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_TRA | #1DTR 重故障 | MTR | D21//1DTR/TRA |  |  |  | CDC | 532 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D21//1DTR/TRF |  |  |  | CDC | 533 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D21//1DTR(A)/SupLocal |  |  |  | CDC | 534 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-32-12 |  | 1-60 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D21//1DTR(A)/Tap Chan |  |  |  | CDC | 535 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D21//1DTR(B)/SupLocal |  |  |  | CDC | 536 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-33-00 |  | 1-62 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D21//1DTR(B)/Tap Chan |  |  |  | CDC | 537 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#2DTR_51A | #2DTR 51RY | MTR | D21//2DTR/PHA |  |  |  | CDC | 538 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#2DTR_51NA | #2DTR 51N RY | MTR | D21//2DTR/GDA |  |  |  | CDC | 539 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-07-02 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D21//2DTR/51ZA |  |  |  | CDC | 540 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-00 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#2DTR_87A | #2DTR 87RY | MTR | D21//2DTR/87A |  |  |  | CDC | 541 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-07-01 | [7 empty] | 161KV_N | [8 empty] | 台西DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D21//2DTR/96PA |  |  |  | CDC | 542 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-30-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_96D | #2DTR 96D RY | MTR | D21//2DTR/96D |  |  |  | CDC | 543 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-30-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_96P | #2DTR 96P RY | MTR | D21//2DTR/96P |  |  |  | CDC | 544 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-30-09 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D21//2DTR/63Q |  |  |  | CDC | 545 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-30-07 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D21//2DTR/96B1 |  |  |  | CDC | 546 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-30-08 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D21//2DTR/96B2 |  |  |  | CDC | 547 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_TRA | #2DTR 重故障 | MTR | D21//2DTR/TRA |  |  |  | CDC | 548 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D21//2DTR/TRF |  |  |  | CDC | 549 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-33-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D21//2DTR(A)/SupLocal |  |  |  | CDC | 550 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-33-03 |  | 1-64 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D21//2DTR(A)/Tap Chan |  |  |  | CDC | 551 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-33-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D21//2DTR(B)/SupLocal |  |  |  | CDC | 552 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D21 | 台西DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-33-07 |  | 1-66 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D21//2DTR(B)/Tap Chan |  |  |  | CDC | 553 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D21 | 台西DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 台西DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D21/0/StaDev/R_Temp |  |  |  | CDC | 554 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-32-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D21/161/ComPoint/OSCF |  |  |  | CDC | 555 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | _SC | SC |  | 60A | [17 empty] | 2-32-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.11KV_SC_60A | 11KV SC 60A | OTHER | D21/11/ComPoint/60A |  |  |  | CDC | 556 | GENERICDIPoint | DS035_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | 79UL | [17 empty] | 1-30-03 |  | 1-41 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1560_79UL | 北港台西線(1560) 79RY U/L | LINE161 | D21/161/1560/79UL |  |  |  | CDC | 557 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | 87A2 | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1550_87A2 | 雲林台西雲高線(1550) #2 87RY | LINE161 | D21/161/1550/87A2 |  |  |  | CDC | 558 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | 87A1 | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1550_87A1 | 雲林台西雲高線(1550) #1 87RY | LINE161 | D21/161/1550/87A1 |  |  |  | CDC | 559 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | 1_87UL2 | [17 empty] | 1-30-04 |  | 1-42 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1550_87UL2 | 雲林台西雲高線(1550)#287RY U/L | LINE161 | D21/161/1550/1_87UL2 |  |  |  | CDC | 560 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | 1_87UL1 | [17 empty] | 1-31-01 |  | 1-4C | [5 empty] | ADCS_N | [8 empty] | 台西DS.1550_87UL1 | 雲林台西雲高線(1550)#187RY U/L | LINE161 | D21/161/1550/1_87UL1 |  |  |  | CDC | 561 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 1550 | 雲林台西雲高線(1550) |  | 87CFA | [17 empty] | 1-30-13 | [7 empty] | ADCS_N | [8 empty] | 台西DS.1550_87CFA | 雲林台西雲高線(1550)RY通訊故障 | OTHER | D21/161/1550/87CFA |  |  |  | CDC | 562 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1550 | 雲林台西雲高線(1550) |  | RYFA | [17 empty] | 1-30-14 | [7 empty] | ADCS_N | [8 empty] | 台西DS.1550_RYFA | 雲林台西雲高線(1550)數位RY故障 | OTHER | D21/161/1550/RYFA |  |  |  | CDC | 563 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | 79UL | [17 empty] | 1-30-05 |  | 1-43 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1550_79UL | 雲林台西雲高線(1550) 79RY U/L | LINE161 | D21/161/1550/79UL |  |  |  | CDC | 564 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-05-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D21/0/ComPoint/RCA |  |  |  | CDC | 565 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | 87A2 | [17 empty] | 1-00-02 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1560_87A2 | 北港台西線(1560) #2 87RY | LINE161 | D21/161/1560/87A2 |  |  |  | CDC | 566 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | 87A1 | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 台西DS.1560_87A1 | 北港台西線(1560) #1 87RY | LINE161 | D21/161/1560/87A1 |  |  |  | CDC | 567 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | 1_87UL2 | [17 empty] | 1-30-02 |  | 1-40 | [5 empty] | ADCS_N | [8 empty] | 台西DS.1560_87UL2 | 北港台西線(1560) #2 87RY U/L | LINE161 | D21/161/1560/1_87UL2 |  |  |  | CDC | 568 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | 1_87UL1 | [17 empty] | 1-31-02 |  | 1-4D | [5 empty] | ADCS_N | [8 empty] | 台西DS.1560_87UL1 | 北港台西線(1560) #1 87RY U/L | LINE161 | D21/161/1560/1_87UL1 |  |  |  | CDC | 569 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 1560 | 北港台西線(1560) |  | 87CFA | [17 empty] | 1-30-15 | [7 empty] | ADCS_N | [8 empty] | 台西DS.1560_87CFA | 北港台西線(1560)87RY通訊故障 | OTHER | D21/161/1560/87CFA |  |  |  | CDC | 570 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1560 | 北港台西線(1560) |  | RYFA | [17 empty] | 1-31-00 | [7 empty] | ADCS_N | [8 empty] | 台西DS.1560_RYFA | 北港台西線(1560)數位電驛故障 | OTHER | D21/161/1560/RYFA |  |  |  | CDC | 571 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | GEN | [17 empty] | 1-31-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.GEN | 緊急發電機運轉 | OTHER | D21/0/StaDev/1A5Other |  |  |  | CDC | 572 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D21 | 台西DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-31-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D21/161/ComPoint/12B_CTFA |  |  |  | CDC | 573 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-31-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D21/161/ComPoint/BUS_RYFA |  |  |  | CDC | 574 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [17 empty] | 1-31-08 |  | 1-52 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | D21//1DTR/51Z_UL |  |  |  | CDC | 575 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [17 empty] | 1-06-05 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_86A | #1DTR 86A | OTHER | D21//1DTR/DTR_86A |  |  |  | CDC | 576 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [17 empty] | 1-31-06 |  | 1-50 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | D21//1DTR/1_87UL1 |  |  |  | CDC | 577 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [17 empty] | 1-31-07 |  | 1-51 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | D21//1DTR/1_87UL2 |  |  |  | CDC | 578 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 1DTR | #1DTR |  | RYFA | [17 empty] | 1-31-09 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | D21//1DTR/RYFA |  |  |  | CDC | 579 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 1-31-12 |  | 1-55 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | D21//2DTR/51Z_UL |  |  |  | CDC | 580 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 1-06-06 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_86A | #2DTR 86A | OTHER | D21//2DTR/DTR_86A |  |  |  | CDC | 581 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 1-31-10 |  | 1-53 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | D21//2DTR/1_87UL1 |  |  |  | CDC | 582 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 1-31-11 |  | 1-54 | [5 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | D21//2DTR/1_87UL2 |  |  |  | CDC | 583 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D21 | 台西DS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 台西DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | D21//2DTR/RYFA |  |  |  | CDC | 584 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  |  |  |  | PMA | [17 empty] | 1-31-14 | [7 empty] | ADCS_N | [8 empty] | 台西DS.PMA | 電力量測表計故障 | OTHER | D21/0/StaDev/PMA |  |  |  | CDC | 585 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-31-15 | [7 empty] | ADCS_N | [8 empty] | 台西DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D21/0/ComPoint/OLTC_A |  |  |  | CDC | 586 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-09-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.310_GDA | 11KV 310(#1ADTR) 51N RY | OTHER | D21/11/310/GDA |  |  |  | CDC | 587 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-09-02 | [7 empty] | ADCS_N | [8 empty] | 台西DS.320_GDA | 11KV 320(#1BDTR) 51N RY | OTHER | D21/11/320/GDA |  |  |  | CDC | 588 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | ADCS_N | [8 empty] | 台西DS.330_GDA | 11KV 330(#2ADTR) 51N RY | OTHER | D21/11/330/GDA |  |  |  | CDC | 589 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-09-04 | [7 empty] | ADCS_N | [8 empty] | 台西DS.340_GDA | 11KV 340(#2BDTR) 51N RY | OTHER | D21/11/340/GDA |  |  |  | CDC | 590 | GENERICDIPoint | DS035_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV |  |  |  | LOA | [17 empty] | 1-32-00 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.11KV_LOA | 11KV饋線復閉失敗 | OTHER | D21/11/ComPoint/LOA |  |  |  | CDC | 591 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV |  |  |  | RYFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_N | [8 empty] | 台西DS.11KV_RYFA | 11KV IED故障 | OTHER | D21/11/ComPoint/RYFA |  |  |  | CDC | 592 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | 59V0 | [17 empty] | 1-33-13 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_59V0 | 禾風風力 59V0 | OTHER |  |  |  |  | CDC | 593 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | CB | [17 empty] | 1-32-02 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_CB | 禾風風力 CB | OTHER |  |  |  |  | CDC | 594 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | DS1 | HEFENG | [16 empty] | 1-32-03 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_DS | 禾風風力 DS | OTHER |  |  |  |  | CDC | 595 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | LE0 | HEFENG | [16 empty] | 1-32-04 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_ES | 禾風風力 ES | OTHER |  |  |  |  | CDC | 596 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | GDA | [17 empty] | 1-32-06 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_GDA | 禾風風力 GDA | OTHER |  |  |  |  | CDC | 597 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | PHA | [17 empty] | 1-32-05 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_PHA | 禾風風力 PHA | OTHER |  |  |  |  | CDC | 598 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 0 |  | HEFENG | 禾風風力 |  | UVA | [17 empty] | 1-32-07 | [7 empty] | DDCS1_2 | [8 empty] | 台西DS.HEFENG_UVA | 禾風風力 UVA(27+59) | OTHER |  |  |  |  | CDC | 599 | GENERICDIPoint | DS035_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D21 | 台西DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 台西DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 600 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 台西DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 601 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 台西DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 602 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 台西DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 603 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 台西DS.250_SC_CAP | 11KV#5SC 容量 | SC | [5 empty] | 604 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 台西DS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 605 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 027 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_027 | 台西DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 606 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 028 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_028 | 台西DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 607 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 029 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_029 | 台西DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 608 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 030 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_030 | 台西DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 609 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 031 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_031 | 台西DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 610 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 032 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_032 | 台西DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 611 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 033 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_033 | 台西DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 612 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 0 |  | TRD | 台西DS |  | 034 | [25 empty] | TRAIN_AD | [8 empty] | 台西DS.TRD_034 | 台西DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 613 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1510LE | 1510LE (非取樣點) | LINE161 | D21/161/1510/LE0 |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1510 | 塑化紅線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1510BE | 1510BE (非取樣點) | LINE161 | D21/161/1510/BE0 |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1520LE | 1520LE (非取樣點) | LINE161 | D21/161/1520/LE0 |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1520 | 塑化白線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1520BE | 1520BE (非取樣點) | LINE161 | D21/161/1520/BE0 |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1550LE | 1550LE (非取樣點) | LINE161 | D21/161/1550/LE0 |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1550 | 雲林台西雲高線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1550BE | 1550BE (非取樣點) | LINE161 | D21/161/1550/BE0 |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1560LE | 1560LE (非取樣點) | LINE161 | D21/161/1560/LE0 |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1560 | 北港台西線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1560BE | 1560BE (非取樣點) | LINE161 | D21/161/1560/BE0 |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP21 | XP21_DS |  | DS1 | XP21_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_DS | XP21_DS (非取樣點) | FEEDER | D21/11/XP21/DS |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP21 | XP21_ES |  | LE0 | XP21_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP21_ES | XP21_ES (非取樣點) | FEEDER | D21/11/XP21/ES |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP22 | XP22_DS |  | DS1 | XP22_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_DS | XP22_DS (非取樣點) | FEEDER | D21/11/XP22/DS |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP22 | XP22_ES |  | LE0 | XP22_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP22_ES | XP22_ES (非取樣點) | FEEDER | D21/11/XP22/ES |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP23 | XP23_DS |  | DS1 | XP23_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_DS | XP23_DS (非取樣點) | FEEDER | D21/11/XP23/DS |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP23 | XP23_ES |  | LE0 | XP23_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP23_ES | XP23_ES (非取樣點) | FEEDER | D21/11/XP23/ES |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP24 | XP24_DS |  | DS1 | XP24_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_DS | XP24_DS (非取樣點) | FEEDER | D21/11/XP24/DS |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP24 | XP24_ES |  | LE0 | XP24_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP24_ES | XP24_ES (非取樣點) | FEEDER | D21/11/XP24/ES |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP25 | XP25_DS |  | DS1 | XP25_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_DS | XP25_DS (非取樣點) | FEEDER | D21/11/XP25/DS |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP25 | XP25_ES |  | LE0 | XP25_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP25_ES | XP25_ES (非取樣點) | FEEDER | D21/11/XP25/ES |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP26 | XP26_DS |  | DS1 | XP26_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_DS | XP26_DS (非取樣點) | FEEDER | D21/11/XP26/DS |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP26 | XP26_ES |  | LE0 | XP26_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP26_ES | XP26_ES (非取樣點) | FEEDER | D21/11/XP26/ES |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP27 | XP27_DS |  | DS1 | XP27_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_DS | XP27_DS (非取樣點) | FEEDER | D21/11/XP27/DS |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP27 | XP27_ES |  | LE0 | XP27_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP27_ES | XP27_ES (非取樣點) | FEEDER | D21/11/XP27/ES |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP28 | XP28_DS |  | DS1 | XP28_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_DS | XP28_DS (非取樣點) | FEEDER | D21/11/XP28/DS |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP28 | XP28_ES |  | LE0 | XP28_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP28_ES | XP28_ES (非取樣點) | FEEDER | D21/11/XP28/ES |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP29 | XP29_DS |  | DS1 | XP29_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_DS | XP29_DS (非取樣點) | FEEDER | D21/11/XP29/DS |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP29 | XP29_ES |  | LE0 | XP29_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP29_ES | XP29_ES (非取樣點) | FEEDER | D21/11/XP29/ES |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP30 | XP30_DS |  | DS1 | XP30_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_DS | XP30_DS (非取樣點) | FEEDER | D21/11/XP30/DS |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP30 | XP30_ES |  | LE0 | XP30_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP30_ES | XP30_ES (非取樣點) | FEEDER | D21/11/XP30/ES |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP31 | XP31_DS |  | DS1 | XP31_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_DS | XP31_DS (非取樣點) | FEEDER | D21/11/XP31/DS |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP31 | XP31_ES |  | LE0 | XP31_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP31_ES | XP31_ES (非取樣點) | FEEDER | D21/11/XP31/ES |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP32 | XP32_DS |  | DS1 | XP32_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_DS | XP32_DS (非取樣點) | FEEDER | D21/11/XP32/DS |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP32 | XP32_ES |  | LE0 | XP32_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP32_ES | XP32_ES (非取樣點) | FEEDER | D21/11/XP32/ES |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP33 | XP33_DS |  | DS1 | XP33_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_DS | XP33_DS (非取樣點) | FEEDER | D21/11/XP33/DS |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP33 | XP33_ES |  | LE0 | XP33_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP33_ES | XP33_ES (非取樣點) | FEEDER | D21/11/XP33/ES |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP34 | XP34_DS |  | DS1 | XP34_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_DS | XP34_DS (非取樣點) | FEEDER | D21/11/XP34/DS |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP34 | XP34_ES |  | LE0 | XP34_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP34_ES | XP34_ES (非取樣點) | FEEDER | D21/11/XP34/ES |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP35 | XP35_DS |  | DS1 | XP35_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_DS | XP35_DS (非取樣點) | FEEDER | D21/11/XP35/DS |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP35 | XP35_ES |  | LE0 | XP35_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP35_ES | XP35_ES (非取樣點) | FEEDER | D21/11/XP35/ES |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP36 | XP36_DS |  | DS1 | XP36_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_DS | XP36_DS (非取樣點) | FEEDER | D21/11/XP36/DS |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP36 | XP36_ES |  | LE0 | XP36_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP36_ES | XP36_ES (非取樣點) | FEEDER | D21/11/XP36/ES |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP37 | XP37_DS |  | DS1 | XP37_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_DS | XP37_DS (非取樣點) | FEEDER | D21/11/XP37/DS |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP37 | XP37_ES |  | LE0 | XP37_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP37_ES | XP37_ES (非取樣點) | FEEDER | D21/11/XP37/ES |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP38 | XP38_DS |  | DS1 | XP38_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_DS | XP38_DS (非取樣點) | FEEDER | D21/11/XP38/DS |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP38 | XP38_ES |  | LE0 | XP38_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP38_ES | XP38_ES (非取樣點) | FEEDER | D21/11/XP38/ES |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP39 | XP39_DS |  | DS1 | XP39_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_DS | XP39_DS (非取樣點) | FEEDER | D21/11/XP39/DS |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP39 | XP39_ES |  | LE0 | XP39_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP39_ES | XP39_ES (非取樣點) | FEEDER | D21/11/XP39/ES |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | XP40 | XP40_DS |  | DS1 | XP40_DS | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_DS | XP40_DS (非取樣點) | FEEDER | D21/11/XP40/DS |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | XP40 | XP40_ES |  | LE0 | XP40_ES | [24 empty] | DDCS1_2 | [8 empty] | 台西DS.XP40_ES | XP40_ES (非取樣點) | FEEDER | D21/11/XP40/ES |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 台西DS.1501E | 1501E (非取樣點) | TIE | D21/161/1500/E1 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 台西DS.1502E | 1502E (非取樣點) | TIE | D21/161/1500/E2 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1750TE | 1750TE (非取樣點) | MTR | D21/161/1750/TE0 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1750BE | 1750BE (非取樣點) | MTR | D21/161/1750/BE0 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 310 | #1DTR(310) |  | DS1 | 310_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.310_DS | 310_DS (非取樣點) | MTR | D21/11/310/DS |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 310 | #1DTR(310) |  | LE0 | 310_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.310_ES | 310_ES (非取樣點) | MTR | D21/11/310/ES |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 320 | #1DTR(320) |  | DS1 | 320_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.320_DS | 320_DS (非取樣點) | MTR | D21/11/320/DS |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 320 | #1DTR(320) |  | LE0 | 320_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.320_ES | 320_ES (非取樣點) | MTR | D21/11/320/ES |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1760TE | 1760TE (非取樣點) | MTR | D21/161/1760/TE0 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 台西DS.1760BE | 1760BE (非取樣點) | MTR | D21/161/1760/BE0 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 330 | #2DTR(330) |  | DS1 | 330_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.330_DS | 330_DS (非取樣點) | MTR | D21/11/330/DS |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 330 | #2DTR(330) |  | LE0 | 330_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.330_ES | 330_ES (非取樣點) | MTR | D21/11/330/ES |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 340 | #2DTR(340) |  | DS1 | 340_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.340_DS | 340_DS (非取樣點) | MTR | D21/11/340/DS |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 340 | #2DTR(340) |  | LE0 | 340_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.340_ES | 340_ES (非取樣點) | MTR | D21/11/340/ES |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.210_ES | 210_ES (非取樣點) | SC | D21/11/210/ES |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 210 | #1SC(210) |  | SC0 | 210SC | [24 empty] | ADCS_N | [8 empty] | 台西DS.210SC_ES | 210SC_ES (非取樣點) | SC | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.210_DS | 210_DS (非取樣點) | SC | D21/11/210/DS |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.220_ES | 220_ES (非取樣點) | SC | D21/11/220/ES |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 220 | #2SC(220) |  | SC0 | 220SC | [24 empty] | ADCS_N | [8 empty] | 台西DS.220SC_ES | 220SC_ES (非取樣點) | SC | [5 empty] | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.220_DS | 220_DS (非取樣點) | SC | D21/11/220/DS |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.230_ES | 230_ES (非取樣點) | SC | D21/11/230/ES |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 230 | #3SC(230) |  | SC0 | 230SC | [24 empty] | ADCS_N | [8 empty] | 台西DS.230SC_ES | 230SC_ES (非取樣點) | SC | [5 empty] | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.230_DS | 230_DS (非取樣點) | SC | D21/11/230/DS |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.240_ES | 240_ES (非取樣點) | SC | D21/11/240/ES |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 240 | #4SC(240) |  | SC0 | 240SC | [24 empty] | ADCS_N | [8 empty] | 台西DS.240SC_ES | 240SC_ES (非取樣點) | SC | [5 empty] | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.240_DS | 240_DS (非取樣點) | SC | D21/11/240/DS |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.250_ES | 250_ES (非取樣點) | SC | D21/11/250/ES |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_N | [8 empty] | 台西DS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.250_DS | 250_DS (非取樣點) | SC | D21/11/250/DS |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_N | [8 empty] | 台西DS.260_ES | 260_ES (非取樣點) | SC | D21/11/260/ES |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_N | [8 empty] | 台西DS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.260_DS | 260_DS (非取樣點) | SC | D21/11/260/DS |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 台西DS.15B1E | 15B1E (非取樣點) | BUS | D21/161/1BUS/BE1 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 台西DS.15B2E | 15B2E (非取樣點) | BUS | D21/161/2BUS/BE2 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D21 | 台西DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 台西DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 696 | NotelDIPoint | [38 empty] | START/STOP | STOP
D21 | 台西DS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_N | [8 empty] | 台西DS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_N | [8 empty] | 台西DS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_N | [8 empty] | 台西DS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_N | [8 empty] | 台西DS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 100 | TIE(100) |  | DS1 | 100_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.100_DS | 100_DS (非取樣點) | TIE | D21/11/100/DS |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 200 | TIE(200) |  | DS1 | 200_DS | [24 empty] | ADCS_N | [8 empty] | 台西DS.200_DS | 200_DS (非取樣點) | TIE | D21/11/200/DS |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 台西DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 台西DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 台西DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D21 | 台西DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 台西DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo