## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.311 | 311 (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.311E | 311E (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.321 | 321 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.321E | 321E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 四湖DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.211E | 211E (非取樣點) | SC | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.211 | 211 (非取樣點) | SC | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_DS | XQ21_DS (非取樣點) | FEEDER | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_ES | XQ21_ES (非取樣點) | FEEDER | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_DS | XQ22_DS (非取樣點) | FEEDER | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_ES | XQ22_ES (非取樣點) | FEEDER | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_DS | XQ23_DS (非取樣點) | FEEDER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_ES | XQ23_ES (非取樣點) | FEEDER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_DS | XQ24_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_ES | XQ24_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_DS | XQ25_DS (非取樣點) | FEEDER | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_ES | XQ25_ES (非取樣點) | FEEDER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.101 | 101 (非取樣點) | TIE | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.102 | 102 (非取樣點) | TIE | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.221E | 221E (非取樣點) | SC | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.221 | 221 (非取樣點) | SC | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_DS | XQ26_DS (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_ES | XQ26_ES (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_DS | XQ27_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_ES | XQ27_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_DS | XQ28_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_ES | XQ28_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_DS | XQ29_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_ES | XQ29_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_DS | XQ30_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_ES | XQ30_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.201 | 201 (非取樣點) | TIE | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.202 | 202 (非取樣點) | TIE | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_DS | XQ31_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_ES | XQ31_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_DS | XQ32_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_ES | XQ32_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_DS | XQ33_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_ES | XQ33_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.231E | 231E (非取樣點) | SC | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.231 | 231 (非取樣點) | SC | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_DS | XQ34_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_ES | XQ34_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_DS | XQ35_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_ES | XQ35_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.301 | 301 (非取樣點) | TIE | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_DS | XQ36_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_ES | XQ36_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_DS | XQ37_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_ES | XQ37_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.241E | 241E (非取樣點) | SC | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.241 | 241 (非取樣點) | SC | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_DS | XQ38_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_ES | XQ38_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_DS | XQ39_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_ES | XQ39_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_DS | XQ40_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_ES | XQ40_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.401 | 401 (非取樣點) | TIE | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D22_A1 | [8 empty] | 四湖DS.401E | 401E(非取樣點) | OTHER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D22_A1 | [8 empty] | 四湖DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D22_A1 | [8 empty] | 四湖DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D22_A1 | [8 empty] | 四湖DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D22 | 四湖DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D22_A1 | [8 empty] | 四湖DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1510 | MW | 北港四湖一路 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_MW | 北港四湖一路 MW | LINE161 | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1510 | MVAR | 北港四湖一路 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_MVAR | 北港四湖一路 MVAR | LINE161 | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1520 | MW | 北港四湖二路 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_MW | 北港四湖二路 MW | LINE161 | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1520 | MVAR | 北港四湖二路 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_MVAR | 北港四湖二路 MVAR | LINE161 | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1530 | MW | 湖風四湖線 1530瓦 | MW_-560_560(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_MW | 湖風四湖線 MW | LINE161 | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1530 | MVAR | 湖風四湖線 1530乏 | MVAR_-560_560(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_MVAR | 湖風四湖線 MVAR | LINE161 | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 161KV TIE | A | 161KV TIE 1500 A | A_-2000_2000(-2000_2000) |  | B2/D22_A1 | [8 empty] | 四湖DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | #1ATR | ℃ | #1ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | #1BTR | ℃ | #1BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0022 |  | 0079 | 1-96 |  | 1-4F | #1ATR | 升/降 | #1ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0023 |  | 0081 | 1-97 |  | 1-51 | #1BTR | 升/降 | #1BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #2ATR | ℃ | #2ATR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2BTR | ℃ | #2BTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0027 |  | 0083 | 1-9B |  | 1-53 | #2ATR | 升/降 | #2ATR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  | 0085 | 1-9C |  | 1-55 | #2BTR | 升/降 | #2BTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0034 |  |  | 1-A2 |  |  | #1APT | KV | #1APT 電壓 | kV_-9_9(-2000_2000) | aaa | B3/D22_A1 | [8 empty] | 四湖DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | D1A | MW | D1A 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | D1A | MVAR | D1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | D1A | A | D1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | D1A | A | D1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | D1A | A | D1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | F1 | KVAR | F1 XQ21 飛一線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛一線KVAR | 11KV飛一線 KVAR | FEEDER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | F1 | A | F1 XQ21 飛一線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛一線A1 | 11KV飛一線 R相AMP | FEEDER | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | F1 | A | F1 XQ21 飛一線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛一線A2 | 11KV飛一線 S相AMP | FEEDER | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | F1 | A | F1 XQ21 飛一線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛一線A3 | 11KV飛一線 T相AMP | FEEDER | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | F1 | A | F1 XQ21 飛一線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛一線A0 | 11KV飛一線 N相AMP | FEEDER | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | F2 | KVAR | F2 XQ22 飛二線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二線KVAR | 11KV飛二線 KVAR | FEEDER | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | F2 | A | F2 XQ22 飛二線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二線A1 | 11KV飛二線 R相AMP | FEEDER | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | F2 | A | F2 XQ22 飛二線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二線A2 | 11KV飛二線 S相AMP | FEEDER | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | F2 | A | F2 XQ22 飛二線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二線A3 | 11KV飛二線 T相AMP | FEEDER | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | F2 | A | F2 XQ22 飛二線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二線A0 | 11KV飛二線 N相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | F3 | KVAR | F3 XQ23 飛三線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛三線KVAR | 11KV飛三線 KVAR | FEEDER | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | F3 | A | F3 XQ23 飛三線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛三線A1 | 11KV飛三線 R相AMP | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | F3 | A | F3 XQ23 飛三線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛三線A2 | 11KV飛三線 S相AMP | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | F3 | A | F3 XQ23 飛三線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛三線A3 | 11KV飛三線 T相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | F3 | A | F3 XQ23 飛三線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛三線A0 | 11KV飛三線 N相AMP | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | F4 | KVAR | F4 XQ24 飛四線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛四線KVAR | 11KV飛四線 KVAR | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | F4 | A | F4 XQ24 飛四線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛四線A1 | 11KV飛四線 R相AMP | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | F4 | A | F4 XQ24 飛四線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛四線A2 | 11KV飛四線 S相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | F4 | A | F4 XQ24 飛四線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛四線A3 | 11KV飛四線 T相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | F4 | A | F4 XQ24 飛四線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛四線A0 | 11KV飛四線 N相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | F5 | KVAR | F5 XQ25 飛五線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛五線KVAR | 11KV飛五線 KVAR | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | F5 | A | F5 XQ25 飛五線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛五線A1 | 11KV飛五線 R相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | F5 | A | F5 XQ25 飛五線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛五線A2 | 11KV飛五線 S相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | F5 | A | F5 XQ25 飛五線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛五線A3 | 11KV飛五線 T相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | F5 | A | F5 XQ25 飛五線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛五線A0 | 11KV飛五線 N相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #1ATIE | A | #1A 100 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #1ATIE | A | #1A 100 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #1ATIE | A | #1A 100 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0070 |  |  | 1-C6 |  |  | #1BPT | KV | #1BPT 電壓 | kV_-9_9(-2000_2000) | baa | B3/D22_A1 | [8 empty] | 四湖DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | D1B | MW | D1B 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | D1B | MVAR | D1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | D1B | A | D1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | D1B | A | D1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | D1B | A | D1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | F6 | KVAR | F6 XQ26 飛六線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛六線KVAR | 11KV飛六線 KVAR | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | F6 | A | F6 XQ26 飛六線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛六線A1 | 11KV飛六線 R相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | F6 | A | F6 XQ26 飛六線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛六線A2 | 11KV飛六線 S相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | F6 | A | F6 XQ26 飛六線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛六線A3 | 11KV飛六線 T相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | F6 | A | F6 XQ26 飛六線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛六線A0 | 11KV飛六線 N相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | F7 | KVAR | F7 XQ27 飛七線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛七線KVAR | 11KV飛七線 KVAR | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | F7 | A | F7 XQ27 飛七線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛七線A1 | 11KV飛七線 R相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | F7 | A | F7 XQ27 飛七線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛七線A2 | 11KV飛七線 S相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | F7 | A | F7 XQ27 飛七線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛七線A3 | 11KV飛七線 T相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | F7 | A | F7 XQ27 飛七線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛七線A0 | 11KV飛七線 N相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | F8 | KVAR | F8 XQ28 飛八線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛八線KVAR | 11KV飛八線 KVAR | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | F8 | A | F8 XQ28 飛八線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛八線A1 | 11KV飛八線 R相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | F8 | A | F8 XQ28 飛八線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛八線A2 | 11KV飛八線 S相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | F8 | A | F8 XQ28 飛八線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛八線A3 | 11KV飛八線 T相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | F8 | A | F8 XQ28 飛八線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛八線A0 | 11KV飛八線 N相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | F9 | KVAR | F9 XQ29 飛九線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛九線KVAR | 11KV飛九線 KVAR | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | F9 | A | F9 XQ29 飛九線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛九線A1 | 11KV飛九線 R相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | F9 | A | F9 XQ29 飛九線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛九線A2 | 11KV飛九線 S相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | F9 | A | F9 XQ29 飛九線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛九線A3 | 11KV飛九線 T相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | F9 | A | F9 XQ29 飛九線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛九線A0 | 11KV飛九線 N相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | F10 | KVAR | F10 XQ30 飛十線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十線KVAR | 11KV飛十線 KVAR | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | F10 | A | F10 XQ30 飛十線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十線A1 | 11KV飛十線 R相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | F10 | A | F10 XQ30 飛十線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十線A2 | 11KV飛十線 S相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | F10 | A | F10 XQ30 飛十線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十線A3 | 11KV飛十線 T相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | F10 | A | F10 XQ30 飛十線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十線A0 | 11KV飛十線 N相AMP | FEEDER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | #1BTIE | A | #1BITE 200 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #1BTIE | A | #1BITE 200 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #1BTIE | A | #1BITE 200 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | F11 | KVAR | F11 XQ31 飛十一線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十一線KVAR | 11KV飛十一線 KVAR | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | F11 | A | F11 XQ31 飛十一線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十一線A1 | 11KV飛十一線 R相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | F11 | A | F11 XQ31 飛十一線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十一線A2 | 11KV飛十一線 S相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | F11 | A | F11 XQ31 飛十一線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十一線A3 | 11KV飛十一線 T相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | F11 | A | F11 XQ31 飛十一線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十一線A0 | 11KV飛十一線 N相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | F12 | KVAR | F12 XQ32 飛十二線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十二線KVAR | 11KV飛十二線 KVAR | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | F12 | A | F12 XQ32 飛十二線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十二線A1 | 11KV飛十二線 R相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | F12 | A | F12 XQ32 飛十二線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十二線A2 | 11KV飛十二線 S相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | F12 | A | F12 XQ32 飛十二線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十二線A3 | 11KV飛十二線 T相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | F12 | A | F12 XQ32 飛十二線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十二線A0 | 11KV飛十二線 N相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | F13 | KVAR | F13 XQ33 飛十三線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十三線KVAR | 11KV飛十三線 KVAR | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | F13 | A | F13 XQ33 飛十三線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十三線A1 | 11KV飛十三線 R相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | F13 | A | F13 XQ33 飛十三線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十三線A2 | 11KV飛十三線 S相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | F13 | A | F13 XQ33 飛十三線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十三線A3 | 11KV飛十三線 T相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | F13 | A | F13 XQ33 飛十三線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十三線A0 | 11KV飛十三線 N相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | D2A1 | MW | D2A1 330A1 瓦 |  |  | B3/D22_A1 | [16 empty] | 190 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | D2A1 | MVAR | D2A1 330A1 乏 |  |  | B3/D22_A1 | [16 empty] | 191 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | D2A1 | A | D2A1 330A1 R相電流 |  |  | B3/D22_A1 | [16 empty] | 192 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | D2A1 | A | D2A1 330A1 S相電流 |  |  | B3/D22_A1 | [16 empty] | 193 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | D2A1 | A | D2A1 330A1 T相電流 |  |  | B3/D22_A1 | [16 empty] | 194 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D22 | 四湖DS | 11 | 11kV | 2A1BUS | #2A1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0124 |  |  | 1-FC |  |  | #2A1PT | KV | #2A1PT 電壓 | kV_-9_9(-2000_2000) | aba | B3/D22_A1 | [8 empty] | 四湖DS.11KV#2A1BUS_KV | 11KV #2A1BUS KV | BUS | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 2A2BUS | #2A2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0125 |  |  | 1-FD |  |  | #2A2PT | KV | #2A2PT 電壓 | kV_-9_9(-2000_2000) | aca | B3/D22_A1 | [8 empty] | 四湖DS.11KV#2A2BUS_KV | 11KV #2A2BUS KV | BUS | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | D2A2 | MW | D2A2 330A2 瓦 | MW_-54_54(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | D2A2 | MVAR | D2A2 330A2 乏 | MVAR_-36_36(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | D2A2 | A | D2A2 330A2 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | D2A2 | A | D2A2 330A2 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | D2A2 | A | D2A2 330A2 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | F14 | KVAR | F14 XQ34 飛十四線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十四線KVAR | 11KV飛十四線 KVAR | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | F14 | A | F14 XQ34 飛十四線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十四線A1 | 11KV飛十四線 R相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | F14 | A | F14 XQ34 飛十四線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十四線A2 | 11KV飛十四線 S相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | F14 | A | F14 XQ34 飛十四線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十四線A3 | 11KV飛十四線 T相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | F14 | A | F14 XQ34 飛十四線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十四線A0 | 11KV飛十四線 N相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | F15 | KVAR | F15 XQ35 飛十五線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十五線KVAR | 11KV飛十五線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | F15 | A | F15 XQ35 飛十五線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十五線A1 | 11KV飛十五線 R相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | F15 | A | F15 XQ35 飛十五線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十五線A2 | 11KV飛十五線 S相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | F15 | A | F15 XQ35 飛十五線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十五線A3 | 11KV飛十五線 T相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | F15 | A | F15 XQ35 飛十五線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十五線A0 | 11KV飛十五線 N相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | #2ATIE |  | #2A 300 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_300_A1 | 11KV 300 R相AMP | TIE | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | #2ATIE |  | #2A 300 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_300_A2 | 11KV 300 S相AMP | TIE | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | #2ATIE |  | #2A 300 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_300_A3 | 11KV 300 T相AMP | TIE | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | F16 | KVAR | F16 XQ36 飛十六線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十六線KVAR | 11KV飛十六線 KVAR | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | F16 | A | F16 XQ36 飛十六線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十六線A1 | 11KV飛十六線 R相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | F16 | A | F16 XQ36 飛十六線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十六線A2 | 11KV飛十六線 S相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | F16 | A | F16 XQ36 飛十六線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十六線A3 | 11KV飛十六線 T相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | F16 | A | F16 XQ36 飛十六線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十六線A0 | 11KV飛十六線 N相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | F17 | KVAR | F17 XQ37 飛十七線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十七線KVAR | 11KV飛十七線 KVAR | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | F17 | A | F17 XQ37 飛十七線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十七線A1 | 11KV飛十七線 R相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | F17 | A | F17 XQ37 飛十七線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十七線A2 | 11KV飛十七線 S相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | F17 | A | F17 XQ37 飛十七線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十七線A3 | 11KV飛十七線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | F17 | A | F17 XQ37 飛十七線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十七線A0 | 11KV飛十七線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | D2B1 | MW | D2B1 340B1 瓦 |  |  | B3/D22_A1 | [16 empty] | 227 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | D2B1 | MVAR | D2B1 340B1 乏 |  |  | B3/D22_A1 | [16 empty] | 228 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | D2B1 | A | D2B1 340B1 R相電流 |  |  | B3/D22_A1 | [16 empty] | 229 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | D2B1 | A | D2B1 340B1 S相電流 |  |  | B3/D22_A1 | [16 empty] | 230 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | D2B1 | A | D2B1 340B1 T相電流 |  |  | B3/D22_A1 | [16 empty] | 231 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D22 | 四湖DS | 11 | 11kV | 2B1BUS | #2B1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0161 |  |  | 2-A1 |  |  | #2B1PT | KV | #2B1PT 電壓 | kV_-9_9(-2000_2000) | bba | B3/D22_A1 | [8 empty] | 四湖DS.11KV#2B1BUS_KV | 11KV #2B1BUS KV | BUS | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 2B2BUS | #2B2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0162 |  |  | 2-A2 |  |  | #2B2PT | KV | #2B2PT 電壓 | kV_-9_9(-2000_2000) | bca | B3/D22_A1 | [8 empty] | 四湖DS.11KV#2B2BUS_KV | 11KV #2B2BUS KV | BUS | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | D2B2 | MW | D2B2 340B2 瓦 | MW_-54_54(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | D2B2 | MVAR | D2B2 340B2 乏 | MVAR_-36_36(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | D2B2 | A | D2B2 340B2 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | D2B2 | A | D2B2 340B2 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | D2B2 | A | D2B2 340B2 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F18 | KVAR | F18 XQ38 飛十八線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十八線KVAR | 11KV飛十八線 KVAR | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F18 | A | F18 XQ38 飛十八線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十八線A1 | 11KV飛十八線 R相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F18 | A | F18 XQ38 飛十八線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十八線A2 | 11KV飛十八線 S相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F18 | A | F18 XQ38 飛十八線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十八線A3 | 11KV飛十八線 T相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | F18 | A | F18 XQ38 飛十八線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十八線A0 | 11KV飛十八線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | F19 | KVAR | F19 XQ39 飛十九線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十九線KVAR | 11KV飛十九線 KVAR | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | F19 | A | F19 XQ39 飛十九線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十九線A1 | 11KV飛十九線 R相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | F19 | A | F19 XQ39 飛十九線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十九線A2 | 11KV飛十九線 S相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | F19 | A | F19 XQ39 飛十九線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十九線A3 | 11KV飛十九線 T相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | F19 | A | F19 XQ39 飛十九線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛十九線A0 | 11KV飛十九線 N相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | F20 | KVAR | F20 XQ40 飛二十線 乏 | KVAR_-9000_9000(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二十線KVAR | 11KV飛二十線 KVAR | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 9 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | F20 | A | F20 XQ40 飛二十線 R相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二十線A1 | 11KV飛二十線 R相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C05R480R | 432 | 433 | 480 | 500 | 1.45 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | F20 | A | F20 XQ40 飛二十線 S相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二十線A2 | 11KV飛二十線 S相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | F20 | A | F20 XQ40 飛二十線 T相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二十線A3 | 11KV飛二十線 T相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C05R0480 | 456 | 480 | 500 | 501 | 1.45 | -456 | -480 | -500 | -501 | 1 | 0.01 | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | F20 | A | F20 XQ40 飛二十線 N相電流 | A_-500_500(-2000_2000) |  | B2/D22_D1 | [8 empty] | 四湖DS.飛二十線A0 | 11KV飛二十線 N相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | #2BTIE | A | #2BTIE 400 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | #2BTIE | A | #2BTIE 400 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | #2BTIE | A | #2BTIE 400T相電流 | A_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.4 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0250 |  |  | 2-FA |  |  | DC | V | DC P-G 電壓 | kV_-150_150(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0251 |  |  | 2-FB |  |  | DC | V | DC N-G 電壓 | kV_-150_150(-2000_2000) |  | B3/D22_A1 | [8 empty] | 四湖DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0254 |  |  | 2-FE |  |  | 1530 | V | 湖風G/S湖風四湖線 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D22_A1 | [8 empty] | 湖風GS.1530LPD_KV | 湖風四湖線(1530) LPD KV | LINE161 | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/W01D22/T2 |  | 0010 |  | 0003 | 1-01-02 |  | 1-03 | 1530 | ON/OFF | 湖風四湖線 CB |  | aaga | B2/D22_A1 | [8 empty] | 四湖DS.1530_CB | 1530(湖風四湖線) CB | LINE161 | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1530 | 87A | 湖風四湖線 87A |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_87A | 湖風四湖線(1530) 87RY | LINE161 | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04D221/T2 |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1510 | ON/OFF | 北港四湖一路 1510 CB |  | aaca | B2/D22_A1 | [8 empty] | 四湖DS.1510_CB | 1510(北港四湖一路) CB | LINE161 | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1510 | 87A1 | 北港四湖一路 1510 87A1 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_87A1 | 北港四湖一路(1510)第一套87RY | OTHER | [5 empty] | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 1510 | 87A2 | 北港四湖一路 1510 87A2 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_87A2 | 北港四湖一路(1510)第二套87RY | OTHER | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1510 | PHA | 北港四湖一路 1510 PHA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_PHA | 北港四湖一路(1510) 相間RY | LINE161 | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1510 | GDA | 北港四湖一路 1510 GDA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_GDA | 北港四湖一路(1510) 接地RY | LINE161 | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04D222/T2 |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1520 | ON/OFF | 北港四湖二路 1520 CB |  | aada | B2/D22_A1 | [8 empty] | 四湖DS.1520_CB | 1520(北港四湖二路) CB | LINE161 | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | 87A1 | 北港四湖二路 1520 87A1 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_87A1 | 北港四湖二路(1520)第一套87RY | OTHER | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1520 | 87A2 | 北港四湖二路 1520 87A2 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_87A2 | 北港四湖二路(1520)第二套87RY | OTHER | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1520 | PHA | 北港四湖二路 1520 PHA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_PHA | 北港四湖二路(1520) 相間RY | LINE161 | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1520 | GDA | 北港四湖二路 1520GDA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_GDA | 北港四湖二路(1520) 接地RY | LINE161 | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1530 | PHA | 湖風四湖線 PHA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_PHA | 湖風四湖線(1530) 相間RY | LINE161 | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1530 | GDA | 湖風四湖線 GDA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_GDA | 湖風四湖線(1530) 接地RY | LINE161 | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  | 0068 | 1-30-06 |  | 1-44 | 1530 | USE/LOCK | 湖風四湖線 87RY U/L |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_87UL | 湖風四湖線(1530) 87RY U/L | LINE161 | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  | 0069 | 1-30-07 |  | 1-45 | 1530 | USE/LOCK | 湖風四湖線 79RY U/L |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_79UL | 湖風四湖線(1530) 79RY U/L | LINE161 | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0036 |  | 0008 | 1-04-04 |  | 1-08 | 161KV TIE | ON/OFF | 161KV TIE 1500 CB |  | aaez | B2/D22_A1 | [8 empty] | 四湖DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 161KV TIE | 50A | 161KV TIE 1500 50 A |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D22_A1 | [8 empty] | 四湖DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D22_A1 | [8 empty] | 四湖DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | RCA | ON/OFF | RCA 復閉電驛警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0042 |  | 0009 | 1-05-02 |  | 1-09 | #1DTR | ON/OFF | #1DTR 1750 CB |  | aabb | ELEM/D22_A1 | [8 empty] | 四湖DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | #1DTR | 87A | #1DTR 87A |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #1DTR | 51ZA | #1DTR 51ZA |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1DTR | PHA | #1DTR 1750 PHA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1DTR | GDA | #1DTR 1750 GDA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0050 |  | 0012 | 1-06-02 |  | 1-0C | D1A | ON/OFF | D1A 310 CB |  | aaba | ELEM/D22_A1 | [8 empty] | 四湖DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 1_PHA |  |  | Status | 第1套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | D1A | PHA | D1A 310 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | D1A | GDA | D1A 310 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0053 |  | 0021 | 1-06-05 |  | 1-15 | D1B | ON/OFF | D1B 320 CB |  | baca | ELEM/D22_A1 | [8 empty] | 四湖DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 1_PHA |  |  | Status | 第1套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | D1B | PHA | D1B 320 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | D1B | GDA | D1B 320 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.320_GDA | 320開關箱IED RY GDA | OTHER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0056 |  | 0010 | 1-07-00 |  | 1-0A | #2DTR | ON/OFF | #2DTR 1760 CB |  | aafb | ELEM/D22_A1 | [8 empty] | 四湖DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #2DTR | 87A | #2DTR 87A |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #2DTR | 51ZA | #2DTR 51ZA |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #2DTR | PHA | #2DTR 1760 PHA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | #2DTR | GDA | #2DTR 1760 GDA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A1Bus | A/330A2^T/2DTR(A) |  |  | 0066 |  | 0033 | 1-08-02 |  | 1-21 | D2A1 | ON/OFF | D2A1 330A1 CB |  | abea | ELEM/D22_A1 | [8 empty] | 四湖DS.330A1_CB | 330A1(#2DTR) CB | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | DS1 | 331A1 | ADD | Status | DS1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0066 |  | 0033 | 1-08-02 |  | 1-21 | D2A1 | ON/OFF | D2A1 330A1 CB |  | abea | ELEM/D22_A1 | [8 empty] | 四湖DS.330A1_CB | 330A1(#2DTR) CB | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | E1 | 331A1E | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0066 |  | 0033 | 1-08-02 |  | 1-21 | D2A1 | ON/OFF | D2A1 330A1 CB |  | abea | ELEM/D22_A1 | [8 empty] | 四湖DS.330A1_CB | 330A1(#2DTR) CB | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | 1_PHA |  |  | Status | 第1套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | D2A1 | PHA | D2A1 330A1 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.330A1_PHA2 | 330A1開關箱IED RY PHA | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | D2A1 | GDA | D2A1 330A1 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.330A1_GDA | 330A1開關箱IED RY GDA | OTHER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A2Bus | A/330A1^T/2DTR(A) |  |  | 0069 |  | 0034 | 1-08-05 |  | 1-22 | D2A2 | ON/OFF | D2A2 330A2 CB |  | acba | ELEM/D22_A1 | [8 empty] | 四湖DS.330A2_CB | 330A2(#2DTR) CB | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | DS1 | 331A2 | ADD | Status | DS1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0069 |  | 0034 | 1-08-05 |  | 1-22 | D2A2 | ON/OFF | D2A2 330A2 CB |  | acba | ELEM/D22_A1 | [8 empty] | 四湖DS.330A2_CB | 330A2(#2DTR) CB | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | E1 | 331A2E | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0069 |  | 0034 | 1-08-05 |  | 1-22 | D2A2 | ON/OFF | D2A2 330A2 CB |  | acba | ELEM/D22_A1 | [8 empty] | 四湖DS.330A2_CB | 330A2(#2DTR) CB | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | 1_PHA |  |  | Status | 第1套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | D2A2 | PHA | D2A2 330A2 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.330A2_PHA2 | 330A2開關箱IED RY PHA | OTHER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | D2A2 | GDA | D2A2 330A2 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.330A2_GDA | 330A2開關箱IED RY GDA | OTHER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B1Bus | A/340B2^T/2DTR(B) |  |  | 0072 |  | 0041 | 1-09-00 |  | 1-29 | D2B1 | ON/OFF | D2B1 340B1 CB |  | bbca | ELEM/D22_A1 | [8 empty] | 四湖DS.340B1_CB | 340B1(#2DTR) CB | MTR | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | DS1 |  | ADD | Status | DS1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0072 |  | 0041 | 1-09-00 |  | 1-29 | D2B1 | ON/OFF | D2B1 340B1 CB |  | bbca | ELEM/D22_A1 | [8 empty] | 四湖DS.340B1_CB | 340B1(#2DTR) CB | MTR | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | E1 |  | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0072 |  | 0041 | 1-09-00 |  | 1-29 | D2B1 | ON/OFF | D2B1 340B1 CB |  | bbca | ELEM/D22_A1 | [8 empty] | 四湖DS.340B1_CB | 340B1(#2DTR) CB | MTR | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | 1_PHA |  |  | Status | 第1套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | D2B1 | PHA | D2B1 340B1 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.340B1_PHA2 | 340B1開關箱IED RY PHA | OTHER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | D2B1 | GDA | D2B1 340B1 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.340B1_GDA | 340B1開關箱IED RY GDA | OTHER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B2Bus | A/340B1^T/2DTR(B) |  |  | 0075 |  | 0042 | 1-09-03 |  | 1-2A | D2B2 | ON/OFF | D2B2 340B2 CB |  | bcba | ELEM/D22_A1 | [8 empty] | 四湖DS.340B2_CB | 340B2(#2DTR) CB | MTR | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | DS1 |  | ADD | Status | DS1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0075 |  | 0042 | 1-09-03 |  | 1-2A | D2B2 | ON/OFF | D2B2 340B2 CB |  | bcba | ELEM/D22_A1 | [8 empty] | 四湖DS.340B2_CB | 340B2(#2DTR) CB | MTR | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | E1 |  | ADD | Status | E1 | Close/Open | Y | 1 | DI-SP | [6 empty] | 0075 |  | 0042 | 1-09-03 |  | 1-2A | D2B2 | ON/OFF | D2B2 340B2 CB |  | bcba | ELEM/D22_A1 | [8 empty] | 四湖DS.340B2_CB | 340B2(#2DTR) CB | MTR | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | 1_PHA |  |  | Status | 第1套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | D2B2 | PHA | D2B2 340B2 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.340B2_PHA2 | 340B2開關箱IED RY PHA | OTHER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | D2B2 | GDA | D2B2 340B2 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.340B2_GDA | 340B2開關箱IED RY GDA | OTHER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D22_A1 | [16 empty] | 314 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | 1530 | ON/OFF | 湖風四湖線 87CFA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_87CFA | 湖風四湖線(1530)87RY通訊故障 | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | 1530 | ON/OFF | 湖風四湖線 RYFA |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1530_RYFA | 湖風四湖線(1530)數位電驛故障 | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | DS1 | 1531 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | 629 | 0100 | 1-37-04 | 1-37-05 | 1-64 | 1531 | ON | 湖風四湖線 1531 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1531_DS | 1531(湖風四湖線) DS | LINE161 | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | DS2 | 1532 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0630 | 631 | 0101 | 1-37-06 | 1-37-07 | 1-65 | 1532 | ON | 湖風四湖線 1532 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1532_DS | 1532(湖風四湖線) DS | LINE161 | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | DS3 | 1533 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0632 | 633 | 0102 | 1-37-08 | 1-37-09 | 1-66 | 1533 | ON | 湖風四湖線 1533 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1533_DS | 1533(湖風四湖線) DS | LINE161 | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0634 | 635 | 0103 | 1-37-10 | 1-37-11 | 1-67 | 1533E | ON | 湖風四湖線 1533E ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1533E_ES | 1533E(湖風四湖線) ES | LINE161 | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | #1DTR | A/N | #1DTR 86A |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_86A | #1DTR 86A | OTHER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | #2DTR | A/N | #2DTR 86A |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_86A | #2DTR 86A | OTHER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0128 |  | 0013 | 1-10-00 |  | 1-0D | #1ASC | ON/OFF | #1A 210 SC CB |  | aacb | B3/D22_A1 | [8 empty] | 四湖DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | #1ASC | SCA | #1A 210 SC SCA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | #1ASC | UVA | #1A 210 SC UVA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XQ21/T1 |  |  | 0131 |  | 0014 | 1-10-03 |  | 1-0E | F1 | ON/OFF | F1 XQ21 飛一線 CB |  | aadb | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_CB | XQ21(11KV飛一線) CB | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 |  |  | 1-10-04 |  |  | F1 | PHA | F1 XQ21 飛一線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_PHA | 11KV飛一線(XQ21) 相間RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | F1 | GDA | F1 XQ21 飛一線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_GDA | 11KV飛一線(XQ21) 接地RY | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XQ22/T1 |  |  | 0134 |  | 0015 | 1-10-06 |  | 1-0F | F2 | ON/OFF | F2 XQ22 飛二線 CB |  | aaeb | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_CB | XQ22(11KV飛二線) CB | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | F2 | PHA | F2 XQ22 飛二線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_PHA | 11KV飛二線(XQ22) 相間RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | F2 | GDA | F2 XQ22 飛二線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_GDA | 11KV飛二線(XQ22) 接地RY | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XQ23/T1 |  |  | 0137 |  | 0016 | 1-11-01 |  | 1-10 | F3 | ON/OFF | F3 XQ23 飛三線 CB |  | aafb | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_CB | XQ23(11KV飛三線) CB | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | F3 | PHA | F3 XQ23 飛三線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_PHA | 11KV飛三線(XQ23) 相間RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | F3 | GDA | F3 XQ23 飛三線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_GDA | 11KV飛三線(XQ23) 接地RY | FEEDER | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XQ24/T1 |  |  | 0140 |  | 0017 | 1-11-04 |  | 1-11 | F4 | ON/OFF | F4 XQ24 飛四線 CB |  | aagb | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_CB | XQ24(11KV飛四線) CB | FEEDER | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | F4 | PHA | F4 XQ24 飛四線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_PHA | 11KV飛四線(XQ24) 相間RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | F4 | GDA | F4 XQ24 飛四線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_GDA | 11KV飛四線(XQ24) 接地RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XQ25/T1 |  |  | 0143 |  | 0018 | 1-11-07 |  | 1-12 | F5 | ON/OFF | F5 XQ25 飛五線 CB |  | aahb | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_CB | XQ25(11KV飛五線) CB | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | F5 | PHA | F5 XQ25 飛五線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_PHA | 11KV飛五線(XQ25) 相間RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | F5 | GDA | F5 XQ25 飛五線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_GDA | 11KV飛五線(XQ25) 接地RY | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2A1Bus |  |  | 0146 |  | 0019 | 1-12-02 |  | 1-13 | #1ATIE | ON/OFF | #1A 100 TIE CB |  | aaib | B3/D22_A1 | [8 empty] | 四湖DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | #1ATIE | PHA | #1A 100 TIE PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 1-12-04 |  |  | #1ATIE | GDA | #1A 100 TIE GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1SSTR |  |  | 0149 |  | 0020 | 1-12-05 |  | 1-14 | #1SSTR | ON/OFF | #1SSTR 390 CB |  | baab | B3/D22_A1 | [8 empty] | 四湖DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | #1SSTR | PHA | #1SSTR 390 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | #1SSTR | GDA | #1SSTR 390 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0152 |  | 0022 | 1-13-00 |  | 1-16 | #1BSC | ON/OFF | #1BSC 220 CB |  | badb | B3/D22_A1 | [8 empty] | 四湖DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | #1BSC | SCA | #1BSC 220 SCA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | #1BSC | UVA | #1BSC 220 UVA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XQ26/T1 |  |  | 0155 |  | 0023 | 1-13-03 |  | 1-17 | F6 | ON/OFF | F6 XQ26 飛六線 CB |  | baeb | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_CB | XQ26(11KV飛六線) CB | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | F6 | PHA | F6 XQ26 飛六線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_PHA | 11KV飛六線(XQ26) 相間RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | F6 | GDA | F6 XQ26 飛六線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_GDA | 11KV飛六線(XQ26) 接地RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XQ27/T1 |  |  | 0158 |  | 0024 | 1-13-06 |  | 1-18 | F7 | ON/OFF | F7 XQ27 飛七線 CB |  | bafb | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_CB | XQ27(11KV飛七線) CB | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | F7 | PHA | F7 XQ27 飛七線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_PHA | 11KV飛七線(XQ27) 相間RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | F7 | GDA | F7 XQ27 飛七線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_GDA | 11KV飛七線(XQ27) 接地RY | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XQ28/T1 |  |  | 0161 |  | 0025 | 1-14-01 |  | 1-19 | F8 | ON/OFF | F8 XQ28 飛八線 CB |  | bagb | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_CB | XQ28(11KV飛八線) CB | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | F8 | PHA | F8 XQ28 飛八線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_PHA | 11KV飛八線(XQ28) 相間RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | F8 | GDA | F8 XQ28 飛八線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_GDA | 11KV飛八線(XQ28) 接地RY | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XQ29/T1 |  |  | 0164 |  | 0026 | 1-14-04 |  | 1-1A | F9 | ON/OFF | F9 XQ29 飛九線 CB |  | bahb | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_CB | XQ29(11KV飛九線) CB | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | F9 | PHA | F9 XQ29 飛九線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_PHA | 11KV飛九線(XQ29) 相間RY | FEEDER | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | F9 | GDA | F9 XQ29 飛九線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_GDA | 11KV飛九線(XQ29) 接地RY | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XQ30/T1 |  |  | 0167 |  | 0027 | 1-14-07 |  | 1-1B | F10 | ON/OFF | F10 XQ30 飛十線 CB |  | baib | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_CB | XQ30(11KV飛十線) CB | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | F10 | PHA | F10 XQ30 飛十線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_PHA | 11KV飛十線(XQ30) 相間RY | FEEDER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | F10 | GDA | F10 XQ30 飛十線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_GDA | 11KV飛十線(XQ30) 接地RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BBus | B/2B1Bus |  |  | 0170 |  | 0028 | 1-15-02 |  | 1-1C | #1BTIE | ON/OFF | #1BTIE 200 CB |  | bajb | B3/D22_A1 | [8 empty] | 四湖DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | #1BTIE | PHA | #1BTIE 200 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | #1BTIE | GDA | #1BTIE 200 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A1Bus | L/XQ31/T1 |  |  | 0173 |  | 0029 | 1-15-05 |  | 1-1D | F11 | ON/OFF | F11 XQ31 飛十一線 CB |  | abab | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_CB | XQ31(11KV飛十一線) CB | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | F11 | PHA | F11 XQ31 飛十一線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_PHA | 11KV飛十一線(XQ31) 相間RY | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | F11 | GDA | F11 XQ31 飛十一線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_GDA | 11KV飛十一線(XQ31) 接地RY | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A1Bus | L/XQ32/T1 |  |  | 0176 |  | 0030 | 1-16-00 |  | 1-1E | F12 | ON/OFF | F12 XQ32 飛十二線 CB |  | abbb | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_CB | XQ32(11KV飛十二線) CB | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | F12 | PHA | F12 XQ32 飛十二線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_PHA | 11KV飛十二線(XQ32) 相間RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | F12 | GDA | F12 XQ32 飛十二線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_GDA | 11KV飛十二線(XQ32) 接地RY | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A1Bus | L/XQ33/T1 |  |  | 0179 |  | 0031 | 1-16-03 |  | 1-1F | F13 | ON/OFF | F13 XQ33 飛十三線 CB |  | abcb | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_CB | XQ33(11KV飛十三線) CB | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | F13 | PHA | F13 XQ33 飛十三線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_PHA | 11KV飛十三線(XQ33) 相間RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | F13 | GDA | F13 XQ33 飛十三線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_GDA | 11KV飛十三線(XQ33) 接地RY | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A1Bus | C/3SC |  |  | 0182 |  | 0032 | 1-16-06 |  | 1-20 | #2ASC | ON/OFF | #2ASC 230 CB |  | abdb | B3/D22_A1 | [8 empty] | 四湖DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | #2ASC | SCA | #2ASC 230 SCA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | #2ASC | UVA | #2ASC 230 UVA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A2Bus | T/2SSTR |  |  | 0185 |  | 0035 | 1-17-01 |  | 1-23 | #2SSTR | ON/OFF | #2SSTR 490 CB |  | accb | B3/D22_A1 | [8 empty] | 四湖DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | #2SSTR | PHA | #2SSTR 490 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | #2SSTR | GDA | #2SSTR 490 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A2Bus | L/XQ34/T1 |  |  | 0188 |  | 0036 | 1-17-04 |  | 1-24 | F14 | ON/OFF | F14 XQ34 飛十四線 CB |  | acdb | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_CB | XQ34(11KV飛十四線) CB | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | F14 | PHA | F14 XQ34 飛十四線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_PHA | 11KV飛十四線(XQ34) 相間RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | F14 | GDA | F14 XQ34 飛十四線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_GDA | 11KV飛十四線(XQ34) 接地RY | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2A2Bus | L/XQ35/T1 |  |  | 0191 |  | 0037 | 1-17-07 |  | 1-25 | F15 | ON/OFF | F15 XQ35 飛十五線 CB |  | aceb | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_CB | XQ35(11KV飛十五線) CB | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | F15 | PHA | F15 XQ35 飛十五線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_PHA | 11KV飛十五線(XQ35) 相間RY | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | F15 | GDA | F15 XQ35 飛十五線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_GDA | 11KV飛十五線(XQ35) 接地RY | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2A2Bus | A/100/N1 |  |  | 0194 |  | 0038 | 1-18-02 |  | 1-26 | #2ATIE | ON/OFF | #2ATIE 300 CB |  | acfb | B3/D22_A1 | [8 empty] | 四湖DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | #2ATIE | PHA | #2ATIE 300 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.300_51A | 11KV TIE(300) 51RY | TIE | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | #2ATIE | GDA | #2ATIE 300 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.300_51NA | 11KV TIE(300) 51N RY | TIE | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B1Bus | L/XQ36/T1 |  |  | 0197 |  | 0039 | 1-18-05 |  | 1-27 | F16 | ON/OFF | F16 XQ36 飛十六線 CB |  | bbab | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_CB | XQ36(11KV飛十六線) CB | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | F16 | PHA | F16 XQ36 飛十六線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_PHA | 11KV飛十六線(XQ36) 相間RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | F16 | GDA | F16 XQ36 飛十六線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_GDA | 11KV飛十六線(XQ36) 接地RY | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B1Bus | L/XQ37/T1 |  |  | 0200 |  | 0040 | 1-19-00 |  | 1-28 | F17 | ON/OFF | F17 XQ37 飛十七線 CB |  | bbbb | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_CB | XQ37(11KV飛十七線) CB | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | F17 | PHA | F17 XQ37 飛十七線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_PHA | 11KV飛十七線(XQ37) 相間RY | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | F17 | GDA | F17 XQ37 飛十七線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_GDA | 11KV飛十七線(XQ37) 接地RY | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B2Bus | C/4SC |  |  | 0203 |  | 0043 | 1-19-03 |  | 1-2B | #2BSC | ON/OFF | #2BSC 240 CB |  | bccb | B3/D22_A1 | [8 empty] | 四湖DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | #2BSC | SCA | #2BSC 240 SCA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | #2BSC | UVA | #2BSC 240 UVA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B2Bus | L/XQ38/T1 |  |  | 0206 |  | 0044 | 1-19-06 |  | 1-2C | F18 | ON/OFF | F18 XQ38 飛十八線 CB |  | bcdb | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_CB | XQ38(11KV飛十八線) CB | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | F18 | PHA | F18 XQ38 飛十八線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_PHA | 11KV飛十八線(XQ38) 相間RY | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-1A-00 |  |  | F18 | GDA | F18 XQ38 飛十八線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_GDA | 11KV飛十八線(XQ38) 接地RY | FEEDER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B2Bus | L/XQ39/T1 |  |  | 0209 |  | 0045 | 1-1A-01 |  | 1-2D | F19 | ON/OFF | F19 XQ39 飛十九線 CB |  | bceb | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_CB | XQ39(11KV飛十九線) CB | FEEDER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | F19 | PHA | F19 XQ39 飛十九線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_PHA | 11KV飛十九線(XQ39) 相間RY | FEEDER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | F19 | GDA | F19 XQ39 飛十九線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_GDA | 11KV飛十九線(XQ39) 接地RY | FEEDER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2B2Bus | L/XQ40/T1 |  |  | 0212 |  | 0046 | 1-1A-04 |  | 1-2E | F20 | ON/OFF | F20 XQ40 飛二十線 CB |  | bcfb | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_CB | XQ40(11KV飛二十線) CB | FEEDER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | F20 | PHA | F20 XQ40 飛二十線 PHA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_PHA | 11KV飛二十線(XQ40) 相間RY | FEEDER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | F20 | GDA | F20 XQ40 飛二十線 GDA |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_GDA | 11KV飛二十線(XQ40) 接地RY | FEEDER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2B2Bus | A/200/N1 |  |  | 0215 |  | 0047 | 1-1A-07 |  | 1-2F | #2BTIE | ON/OFF | #2BTIE 400 CB |  | bcgb | B3/D22_A1 | [8 empty] | 四湖DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | #2BTIE | PHA | #2BTIE 400 PHA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.400_51A | 11KV TIE(400) 51RY | TIE | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | #2BTIE | GDA | #2BTIE 400 GDA |  |  | B3/D22_A1 | [8 empty] | 四湖DS.400_51NA | 11KV TIE(400) 51N RY | TIE | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線( XQ21) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  | 0208 | 1-1F-06 |  | 2-50 | F1 | 81A | F1 XQ21 飛一線 81 RY 動作 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.81RY_A/S(1) | 飛一線(XQ21)低頻電驛動作/復歸 | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線( XQ22) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0255 |  | 0209 | 1-1F-07 |  | 2-51 | F2 | 81A | F2 XQ22 飛二線 81 RY 動作 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.81RY_A/S(2) | 飛二線(XQ22)低頻電驛動作/復歸 | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線( XQ23) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  | 0210 | 2-00-00 |  | 2-52 | F3 | 81A | F3 XQ23 飛三線 81 RY 動作 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.81RY_A/S(3) | 飛三線(XQ23)低頻電驛動作/復歸 | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線( XQ26) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  | 0211 | 2-00-01 |  | 2-53 | F6 | 81A | F6 XQ26 飛六線 81 RY 動作 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.81RY_A/S(4) | 飛六線(XQ26)低頻電驛動作/復歸 | OTHER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線( XQ37) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | F17 | 81A | F17 XQ37 飛十七線 81 RY 動作 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.81RY_A/S(5) | XQ37低頻電驛動作/復歸 | OTHER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D22 | 四湖DS | 11 | 11kV | ComPoint |  |  | 81AS1 | XQ30、XQ36、XQ38、XQ39、XQ40 |  | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | F10、16、18、19、20 | 81A | 飛十、十六、十八、十九、二十線 81 RY 動作 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.81RY_A/S(6) | XQ(30 36 38-40)低頻RY動作/復歸 | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D22 | 四湖DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | Test CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 四湖DS.TEST_CB | TEST CB | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | Locate Empty | L/R | L/R STATUS |  |  | ELEM/D22_A1 | [8 empty] | 四湖DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0064 | 1-30-02 |  | 1-40 | 1510 | USE/LOCK | 北港四湖一路 1510 87RY UL1 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_87UL1 | 北港四湖一路(1510)#1 87RY U/L | OTHER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0065 | 1-30-03 |  | 1-41 | 1510 | USE/LOCK | 北港四湖一路 1510 79RY U/L |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_79UL | 北港四湖一路(1510) 79RY U/L | LINE161 | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0066 | 1-30-04 |  | 1-42 | 1520 | USE/LOCK | 北港四湖二路 1520 87RY UL1 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_87UL1 | 北港四湖二路(1520)#1 87RY U/L | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  | 0067 | 1-30-05 |  | 1-43 | 1520 | USE/LOCK | 北港四湖二路 1520 79RY U/L |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_79UL | 北港四湖二路(1520) 79RY U/L | LINE161 | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0252 |  |  | 2-FC |  |  | 1530 | MW | 湖風G/S湖風四湖線 1530瓦 | MW_-560_560(-2000_2000) |  | B1/W01_A1 | [8 empty] | 湖風GS.1530_MW | 湖風四湖線 MW | LINE161 | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0253 |  |  | 2-FD |  |  | 1530 | MVAR | 湖風G/S湖風四湖線 1530乏 | MVAR_-560_560(-2000_2000) |  | B1/W01_A1 | [8 empty] | 湖風GS.1530_MVAR | 湖風四湖線 MVAR | LINE161 | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | #1ATR | 遙控/現場 | #1ATR OLTC S/L |  | c | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0078 | 1-31-02 |  | 1-4E | #1ATR | OLTC A/M | #1ATR OLTC A/M |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0531 |  |  | 1-31-03 |  |  | #1DTR | TRA | #1DTR 重故障 |  | a | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | #1DTR | TRF | #1DTR 輕故障 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | #1BTR | 遙控/現場 | #1BTR OLTC S/L |  | b | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0080 | 1-31-06 |  | 1-50 | #1BTR | OLTC A/M | #1BTR OLTC A/M |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D22 | 四湖DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | #2ATR | 遙控/現場 | #2ATR OLTC S/L |  | c | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0537 |  | 0082 | 1-31-09 |  | 1-52 | #2ATR | OLTC A/M | #2ATR OLTC A/M |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0538 |  |  | 1-31-10 |  |  | #2DTR | TRA | #2DTR 重故障 |  | a | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0539 |  |  | 1-31-11 |  |  | #2DTR | TRF | #2DTR 輕故障 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | #2BTR | 遙控/現場 | #2BTR OLTC S/L |  | b | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0541 |  | 0084 | 1-31-13 |  | 1-54 | #2BTR | OLTC A/M | #2BTR OLTC A/M |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D22 | 四湖DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0549 |  | 0076 | 1-32-05 |  | 1-4C | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D22_A1 | [8 empty] | 四湖DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0550 |  | 0077 | 1-32-06 |  | 1-4D | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D22_A1 | [8 empty] | 四湖DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | 1510 | 87CFA | 北港四湖一路 1510 87Ry 通訊故障 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_87CFA | 北港四湖一路(1510)87RY通訊故障 | OTHER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | 1510 | RYFA | 北港四湖一路 1510 數位電驛故障 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_RYFA | 北港四湖一路(1510)數位電驛故障 | OTHER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | 1520 | 87CFA | 北港四湖二路 1520 87Ry 通訊故障 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_87CFA | 北港四湖二路(1520)87RY通訊故障 | OTHER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | 1520 | RYFA | 北港四湖二路 1520 數位電驛故障 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_RYFA | 北港四湖二路(1520)數位電驛故障 | OTHER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | RCA |  | B1 | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 1530 | RCA | 湖風四湖線 79Ry 動作 |  |  | B1/W01_A1 | [8 empty] | 四湖DS.1530_RCA | 湖風四湖線(1530)79RY復閉動作 | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | DTTA |  | B1 | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | 1530 | DTTA | 湖風四湖線 遠方搖跳 |  |  | B1/W01_A1 | [8 empty] | 四湖DS.1530_DTTA | 湖風四湖線(1530) 遠方遙跳 | OTHER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | 待新增!!__BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | 火災警報(1) | ON/OFF | 火災警報(1)受信總機 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Fire3 | 無人化防火 |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | Locate Empty | ON/OFF | 無人化防火(3) |  |  | B3/D22_A1 | [16 empty] | 450 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | 保全系統 | ON/OFF | 保全系統 無人化防盜(1) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | Locate Empty | ON/OFF | 無人化防盜(2) |  |  | B3/D22_A1 | [16 empty] | 452 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | Locate Empty | ON/OFF | 無人化防盜(3) |  |  | B3/D22_A1 | [16 empty] | 453 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Door1 | 大門門禁 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | DOOR | ON/OFF | DOOR 大門 無人化門禁(1) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室門禁 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | 控制室 | ON/OFF | 控制室 無人化門禁(2) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | Locate Empty | ON/OFF | 無人化門禁(3) |  |  | B3/D22_A1 | [16 empty] | 456 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0576 |  |  | 1-34-00 |  |  | STUV | ON/OFF | STUV 所內欠壓 |  |  | ELEM/D22_A1 | [8 empty] | 四湖DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | 161KV | ON/OFF | 161KV CB 重故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0578 |  |  | 1-34-02 |  |  | 161KV | ON/OFF | 161KV CB 輕故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | 161KV | ON/OFF | 161KV VUA1 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | 161KV | ON/OFF | 161KV VUA2 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | DCE | ON/OFF | DCE DC 接地 |  |  | ELEM/D22_A1 | [8 empty] | 四湖DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 1-34-06 |  |  | CHG1 | ON/OFF | CHG1 變電充電機故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | ACBA | ON/OFF | ACBA ACB 警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | DCA | ON/OFF | DCA DC 警報 |  |  | ELEM/D22_A1 | [8 empty] | 四湖DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | SC | ON/OFF | 60A |  |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_SC_60A | 11KV SC 60A | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0586 |  |  | 1-34-10 |  |  | COMT | ON/OFF | COMT 空壓機超時 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0587 |  |  | 1-34-11 |  |  | AIRA | ON/OFF | AIRA 空調機警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0588 |  |  | 1-34-12 |  |  | OWA | A/N | 主變蓄油池警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | 地下室 | A/N | 地下室水位警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D22_A1 | [8 empty] | 四湖DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | PDA |  |  | Status | 部分放電 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | Locate Empty | PDA | #1、2DTR局部放電警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.TR_PDA | #1,#2DTR局部放電警報 | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0593 |  |  | 1-35-01 |  |  | #1DTR | ON/OFF | #1DTR 96D |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0594 |  |  | 1-35-02 |  |  | #1DTR | ON/OFF | #1DTR 96P |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | #1DTR | ON/OFF | #1DTR 63Q |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | #1DTR | ON/OFF | #1DTR 96B1 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | #1DTR | ON/OFF | #1DTR 96B2 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0598 |  |  | 1-35-06 |  |  | #2DTR | ON/OFF | #2DTR 96D |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | #2DTR | ON/OFF | #2DTR 96P |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | #2DTR | ON/OFF | #2DTR 63Q |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0601 |  |  | 1-35-09 |  |  | #2DTR | ON/OFF | #2DTR 96B1 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0602 |  |  | 1-35-10 |  |  | #2DTR | ON/OFF | #2DTR 96B2 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0608 | 609 | 0090 | 1-36-00 | 1-36-01 | 1-5A | 1501 | ON | 161KV TIE 1501 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0610 | 611 | 0091 | 1-36-02 | 1-36-03 | 1-5B | 1502 | ON | 161KV TIE 1502 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | DS1 | 1511 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0612 | 613 | 0092 | 1-36-04 | 1-36-05 | 1-5C | 1511 | ON | 北港四湖一路 1511 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1511_DS | 1511(北港四湖一路) DS | LINE161 | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | DS2 | 1512 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0614 | 615 | 0093 | 1-36-06 | 1-36-07 | 1-5D | 1512 | ON | 北港四湖一路 1512 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1512_DS | 1512(北港四湖一路) DS | LINE161 | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | DS3 | 1513 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0616 | 617 | 0094 | 1-36-08 | 1-36-09 | 1-5E | 1513 | ON | 北港四湖一路 1513 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1513_DS | 1513(北港四湖一路) DS | LINE161 | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0618 | 619 | 0095 | 1-36-10 | 1-36-11 | 1-5F | 1513E | ON | 北港四湖一路 1513E ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1513E_ES | 1513E(北港四湖一路) ES | LINE161 | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | DS1 | 1521 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0620 | 621 | 0096 | 1-36-12 | 1-36-13 | 1-60 | 1521 | ON | 北港四湖二路 1521 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1521_DS | 1521(北港四湖二路) DS | LINE161 | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | DS2 | 1522 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0622 | 623 | 0097 | 1-36-14 | 1-36-15 | 1-61 | 1522 | ON | 北港四湖二路 1522 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1522_DS | 1522(北港四湖二路) DS | LINE161 | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | DS3 | 1523 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0624 | 625 | 0098 | 1-37-00 | 1-37-01 | 1-62 | 1523 | ON | 北港四湖二路 1523 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1523_DS | 1523(北港四湖二路) DS | LINE161 | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0626 | 627 | 0099 | 1-37-02 | 1-37-03 | 1-63 | 1523E | ON | 北港四湖二路 1523E ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1523E_ES | 1523E(北港四湖二路) ES | LINE161 | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | CB |  | B1 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | L/W01D22/T1 | T/1DTR |  |  | 0096 |  |  | 1-0C-00 |  |  | 1530 | ON/OFF | 湖風G/S湖風四湖線 CB |  | aaaa | B1/W01_A1 | [8 empty] | 湖風GS.1530_CB | 1530(湖風四湖線) CB | LINE161 | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | 87A |  | B1 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 1530 | 87A | 湖風G/S湖風四湖線 87A |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1530_87A | 湖風四湖線(1530) 87RY | LINE161 | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | PHA |  | B1 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | 1530 | PHA | 湖風G/S湖風四湖線 PHA |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1530_PHA | 湖風四湖線(1530) 相間RY | LINE161 | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | GDA |  | B1 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 1530 | GDA | 湖風G/S湖風四湖線 GDA |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1530_GDA | 湖風四湖線(1530) 接地RY | LINE161 | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 | 0120 | 1-39-12 | 1-39-13 | 1-78 | #1DTR | ON | #1DTR 1751 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0670 | 671 | 0121 | 1-39-14 | 1-39-15 | 1-79 | #1DTR | ON | #1DTR 1752 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 673 | 0122 | 1-3A-00 | 1-3A-01 | 1-7A | #2DTR | ON | #2DTR 1761 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0674 | 675 | 0123 | 1-3A-02 | 1-3A-03 | 2-7B | #2DTR | ON | #2DTR 1762 ABS |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | DS1 | 1531 | B1,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 |  |  | 1-3A-08 | 1-3A-09 |  | 1531 | ON/OFF | 湖風G/S湖風四湖線 1531 ABS |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1531_DS | 1531(湖風四湖線) DS | LINE161 |  | CDC_Mon1_DPC |  |  |  | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | E1 | 1531E | B1,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0681 |  |  | 1-3A-09 |  |  | 1531E | ON/OFF | 湖風G/S湖風四湖線 1531E ABS |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1531E_ES | 1531E(湖風四湖線) ES | LINE161 |  | CDC_Mon1_DPC |  |  |  | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | LE0 |  | B1 | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0682 |  |  | 1-3A-10 |  |  | 1530LE | ON/OFF | 湖風G/S湖風四湖線 1530LE ABS |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1530LE_ES | 1530LE(湖風四湖線) ES | LINE161 | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | TE0 |  | B1,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0683 |  |  | 1-3A-11 |  |  | 1530TE | ON/OFF | 湖風G/S湖風四湖線 1530TE ABS |  |  | B1/W01_A1 | [8 empty] | 湖風GS.1530TE_ES | 1530TE(湖風四湖線) ES | LINE161 | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0688 |  | 0063 | 1-3B-00 |  | 1-3F | 1510 | USE/LOCK | 北港四湖一路 1510 87RY UL2 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1510_87UL2 | 北港四湖一路(1510)#2 87RY U/L | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0689 |  | 0062 | 1-3B-01 |  | 1-3E | 1520 | USE/LOCK | 北港四湖二路 1520 87RY UL2 |  |  | B2/D22_A1 | [8 empty] | 四湖DS.1520_87UL2 | 北港四湖二路(1520)#2 87RY U/L | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | B1ASC | #1DTR(1A)(1ASC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1ASC(B) |  |  | 0768 | 769 | 0202 | 2-30-00 | 2-30-01 | 2-4A | #1ASC | ON | #1ASC LBS |  |  | B3/D22_A1 | [8 empty] | 四湖DS.210_LBS | 210(11KV #1SC) LBS | SC | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 1BSC | #1DTR(1B)(1BSC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/1BSC(B) |  |  | 0770 | 771 | 0203 | 2-30-02 | 2-30-03 | 2-4B | #1BSC | ON | #1BSC LBS |  |  | B3/D22_A1 | [8 empty] | 四湖DS.220_LBS | 220(11KV #2SC) LBS | SC | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | B2ASC | #2DTR(2A)(2ASC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/2ASC(B) |  |  | 0772 | 773 | 0204 | 2-30-04 | 2-30-05 | 2-4C | #2ASC | ON | #2ASC LBS |  |  | B3/D22_A1 | [8 empty] | 四湖DS.230_LBS | 230(11KV #3SC) LBS | SC | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 2BSC | #2DTR(2B)(2BSC) |  | LBS |  | Element | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/2BSC(B) |  |  | 0774 | 775 | 0205 | 2-30-06 | 2-30-07 | 2-4D | #2BSC | ON | #2BSC LBS |  |  | B3/D22_A1 | [8 empty] | 四湖DS.240_LBS | 240(11KV #4SC) LBS | SC | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0896 |  | 0128 | 2-38-00 |  | 2-00 | #1ASC | USE/LOCK | #1A 210 SC Q-CTL A/M |  |  | B3/D22_A1 | [8 empty] | 四湖DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | 1A5A_M | SC_A_M #2 | Element | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0897 |  | 0129 | 2-38-01 |  | 2-01 | #1ASC | USE/LOCK | #1A 210 SC Q-CTL A/M-1 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.210_LBS_A/M | 11KV #1SC LBS 乏控器 A/M | SC | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0898 |  | 0130 | 2-38-02 |  | 2-02 | F1 | USE/LOCK | F1 XQ21 飛一線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_79UL | 11KV飛一線(XQ21) 79RY U/L | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0899 |  | 0131 | 2-38-03 |  | 2-03 | F1 | USE/LOCK | F1 XQ21 飛一線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ21_LCO_TAP | 11KV飛一線(XQ21) LCO TAP | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0900 |  | 0132 | 2-38-04 |  | 2-04 | F2 | USE/LOCK | F2 XQ22 飛二線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_79UL | 11KV飛二線(XQ22) 79RY U/L | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0901 |  | 0133 | 2-38-05 |  | 2-05 | F2 | USE/LOCK | F2 XQ22 飛二線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ22_LCO_TAP | 11KV飛二線(XQ22) LCO TAP | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0902 |  | 0134 | 2-38-06 |  | 2-06 | F3 | USE/LOCK | F3 XQ23 飛三線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_79UL | 11KV飛三線(XQ23) 79RY U/L | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0903 |  | 0135 | 2-38-07 |  | 2-07 | F3 | USE/LOCK | F3 XQ23 飛三線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ23_LCO_TAP | 11KV飛三線(XQ23) LCO TAP | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0904 |  | 0136 | 2-38-08 |  | 2-08 | F4 | USE/LOCK | F4 XQ24 飛四線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_79UL | 11KV飛四線(XQ24) 79RY U/L | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0905 |  | 0137 | 2-38-09 |  | 2-09 | F4 | USE/LOCK | F4 XQ24 飛四線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ24_LCO_TAP | 11KV飛四線(XQ24) LCO TAP | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0906 |  | 0138 | 2-38-10 |  | 2-0A | F5 | USE/LOCK | F5 XQ25 飛五線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_79UL | 11KV飛五線(XQ25) 79RY U/L | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0907 |  | 0139 | 2-38-11 |  | 2-0B | F5 | USE/LOCK | F5 XQ25 飛五線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ25_LCO_TAP | 11KV飛五線(XQ25) LCO TAP | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0908 |  | 0140 | 2-38-12 |  | 2-0C | #1BSC | USE/LOCK | #1B 220 SC Q-CTL A/M |  |  | B3/D22_A1 | [8 empty] | 四湖DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(1B)(220) |  | 1A5A_M | SC_A_M #2 | Element | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0909 |  | 0141 | 2-38-13 |  | 2-0D | #1BSC | USE/LOCK | #1B 220 SC Q-CTL A/M-1 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0910 |  | 0142 | 2-38-14 |  | 2-0E | F6 | USE/LOCK | F6 XQ26 飛六線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_79UL | 11KV飛六線(XQ26) 79RY U/L | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0911 |  | 0143 | 2-38-15 |  | 2-0F | F6 | USE/LOCK | F6 XQ26 飛六線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ26_LCO_TAP | 11KV飛六線(XQ26) LCO TAP | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0912 |  | 0144 | 2-39-00 |  | 2-10 | F7 | USE/LOCK | F7 XQ27 飛七線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_79UL | 11KV飛七線(XQ27) 79RY U/L | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0913 |  | 0145 | 2-39-01 |  | 2-11 | F7 | USE/LOCK | F7 XQ27 飛七線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ27_LCO_TAP | 11KV飛七線(XQ27) LCO TAP | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0914 |  | 0146 | 2-39-02 |  | 2-12 | F8 | USE/LOCK | F8 XQ28 飛八線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_79UL | 11KV飛八線(XQ28) 79RY U/L | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0915 |  | 0147 | 2-39-03 |  | 2-13 | F8 | USE/LOCK | F8 XQ28 飛八線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ28_LCO_TAP | 11KV飛八線(XQ28) LCO TAP | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0916 |  | 0148 | 2-39-04 |  | 2-14 | F9 | USE/LOCK | F9 XQ29 飛九線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_79UL | 11KV飛九線(XQ29) 79RY U/L | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0917 |  | 0149 | 2-39-05 |  | 2-15 | F9 | USE/LOCK | F9 XQ29 飛九線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ29_LCO_TAP | 11KV飛九線(XQ29) LCO TAP | FEEDER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0918 |  | 0150 | 2-39-06 |  | 2-16 | F10 | USE/LOCK | F10 XQ30 飛十線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_79UL | 11KV飛十線(XQ30) 79RY U/L | FEEDER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0919 |  | 0151 | 2-39-07 |  | 2-17 | F10 | USE/LOCK | F10 XQ30 飛十線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ30_LCO_TAP | 11KV飛十線(XQ30) LCO TAP | FEEDER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0920 |  | 0152 | 2-39-08 |  | 2-18 | F11 | USE/LOCK | F11 XQ31 飛十一線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_79UL | 11KV飛十一線(XQ31) 79RY U/L | FEEDER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0921 |  | 0153 | 2-39-09 |  | 2-19 | F11 | USE/LOCK | F11 XQ31 飛十一線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ31_LCO_TAP | 11KV飛十一線(XQ31) LCO TAP | FEEDER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0922 |  | 0154 | 2-39-10 |  | 2-1A | F12 | USE/LOCK | F12 XQ32 飛十二線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_79UL | 11KV飛十二線(XQ32) 79RY U/L | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0923 |  | 0155 | 2-39-11 |  | 2-1B | F12 | USE/LOCK | F12 XQ32 飛十二線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ32_LCO_TAP | 11KV飛十二線(XQ32) LCO TAP | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0924 |  | 0156 | 2-39-12 |  | 2-1C | F13 | USE/LOCK | F13 XQ33 飛十三線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_79UL | 11KV飛十三線(XQ33) 79RY U/L | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0925 |  | 0157 | 2-39-13 |  | 2-1D | F13 | USE/LOCK | F13 XQ33 飛十三線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ33_LCO_TAP | 11KV飛十三線(XQ33) LCO TAP | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0926 |  | 0158 | 2-39-14 |  | 2-1E | #2ASC | USE/LOCK | #2A 230 SC Q-CTL A/M |  |  | B3/D22_A1 | [8 empty] | 四湖DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | 1A5A_M | SC_A_M #2 | Element | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0927 |  | 0159 | 2-39-15 |  | 2-1F | #2ASC | USE/LOCK | #2A 230 SC Q-CTL A/M-1 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.230_LBS_A/M | 11KV #3SC LBS 乏控器 A/M | SC | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  | 0160 | 2-3A-00 |  | 2-20 | F14 | USE/LOCK | F14 XQ34 飛十四線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_79UL | 11KV飛十四線(XQ34) 79RY U/L | FEEDER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0929 |  | 0161 | 2-3A-01 |  | 2-21 | F14 | USE/LOCK | F14 XQ34 飛十四線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ34_LCO_TAP | 11KV飛十四線(XQ34) LCO TAP | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  | 0162 | 2-3A-02 |  | 2-22 | F15 | USE/LOCK | F15 XQ35 飛十五線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_79UL | 11KV飛十五線(XQ35) 79RY U/L | FEEDER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0931 |  | 0163 | 2-3A-03 |  | 2-23 | F15 | USE/LOCK | F15 XQ35 飛十五線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ35_LCO_TAP | 11KV飛十五線(XQ35) LCO TAP | FEEDER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0932 |  | 0164 | 2-3A-04 |  | 2-24 | F16 | USE/LOCK | F16 XQ36 飛十六線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_79UL | 11KV飛十六線(XQ36) 79RY U/L | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0933 |  | 0165 | 2-3A-05 |  | 2-25 | F16 | USE/LOCK | F16 XQ36 飛十六線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ36_LCO_TAP | 11KV飛十六線(XQ36) LCO TAP | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0934 |  | 0166 | 2-3A-06 |  | 2-26 | F17 | USE/LOCK | F17 XQ37 飛十七線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_79UL | 11KV飛十七線(XQ37) 79RY U/L | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0935 |  | 0167 | 2-3A-07 |  | 2-27 | F17 | USE/LOCK | F17 XQ37 飛十七線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ37_LCO_TAP | 11KV飛十七線(XQ37) LCO TAP | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0936 |  | 0168 | 2-3A-08 |  | 2-28 | #2BSC | USE/LOCK | #2B 240 SC Q-CTL A/M |  |  | B3/D22_A1 | [8 empty] | 四湖DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | 1A5A_M | SC_A_M #2 | Element | Status | A_M動作1 | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0937 |  | 0169 | 2-3A-09 |  | 2-29 | #2BSC | USE/LOCK | #2B 240 SC Q-CTL A/M-1 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.240_LBS_A/M | 11KV #4SC LBS 乏控器 A/M | SC | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0938 |  | 0170 | 2-3A-10 |  | 2-2A | F18 | USE/LOCK | F18 XQ38 飛十八線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_79UL | 11KV飛十八線(XQ38) 79RY U/L | FEEDER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0939 |  | 0171 | 2-3A-11 |  | 2-2B | F18 | USE/LOCK | F18 XQ38 飛十八線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ38_LCO_TAP | 11KV飛十八線(XQ38) LCO TAP | FEEDER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0940 |  | 0172 | 2-3A-12 |  | 2-2C | F19 | USE/LOCK | F19 XQ39 飛十九線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_79UL | 11KV飛十九線(XQ39) 79RY U/L | FEEDER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0941 |  | 0173 | 2-3A-13 |  | 2-2D | F19 | USE/LOCK | F19 XQ39 飛十九線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ39_LCO_TAP | 11KV飛十九線(XQ39) LCO TAP | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0942 |  | 0174 | 2-3A-14 |  | 2-2E | F20 | USE/LOCK | F20 XQ40 飛二十線 79RY U/L |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_79UL | 11KV飛二十線(XQ40) 79RY U/L | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0943 |  | 0175 | 2-3A-15 |  | 2-2F | F20 | USE/LOCK | F20 XQ40 飛二十線 LCO 分流器 |  |  | B2/D22_D1 | [8 empty] | 四湖DS.XQ40_LCO_TAP | 11KV飛二十線(XQ40) LCO TAP | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0968 |  | 0200 | 2-3C-08 |  | 2-48 | Locate Empty | ON/OFF | 開關場照明(A) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0969 |  | 0201 | 2-3C-09 |  | 2-49 | Locate Empty | ON/OFF | 開關場照明(B) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0970 |  |  | 2-3C-10 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0971 |  |  | 2-3C-11 |  |  | PSF | ON/OFF | PSF 其他輕故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.其他輕故障 | 變電所內其他輕故障 | OTHER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0972 |  |  | 2-3C-12 |  |  | PSA | ON/OFF | PSA 其他重故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0973 |  |  | 2-3C-13 |  |  | 22KV/11KV | ON/OFF | 22KV/11KV CB 重故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_CBA | 11KV斷路器重故障 | OTHER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0974 |  |  | 2-3C-14 |  |  | 22KV/11KV | ON/OFF | 22KV/11KV CB 輕故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.11KV_CBF | 11KV斷路器輕故障 | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0975 |  |  | 2-3C-15 |  |  | 22KV/11KV | ON/OFF | 22KV/11KV LOA 復閉失敗 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0976 |  |  | 2-3D-00 |  |  | CHG2 | ON/OFF | 通訊充電機故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0977 |  |  | 2-3D-01 |  |  | 通訊設備 | ON/OFF | 通訊設備 AC故障 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0980 |  |  | 2-3D-04 |  |  | 通訊設備 | ON/OFF | 通信室溫控警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0982 |  |  | 2-3D-06 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D22_A1 | [8 empty] | 四湖DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0983 |  | 0212 | 2-3D-07 |  | 2-54 | #1DTR | USE/LOCK | #1DTR. #1 87RY U/L |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0984 |  | 0213 | 2-3D-08 |  | 2-55 | #1DTR | USE/LOCK | #1DTR. #2 87RY U/L |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0985 |  | 0214 | 2-3D-09 |  | 2-56 | #1DTR | USE/LOCK | #1DTR. 51Z U/L |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0986 |  |  | 2-3D-10 |  |  | #1DTR | USE/LOCK | #1DTR. 數位電驛故障 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0987 |  | 0215 | 2-3D-11 |  | 2-57 | #2DTR | USE/LOCK | #2DTR. #1 87RY U/L |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0988 |  | 0216 | 2-3D-12 |  | 2-58 | #2DTR | USE/LOCK | #2DTR. #2 87RY U/L |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0989 |  | 0217 | 2-3D-13 |  | 2-59 | #2DTR | USE/LOCK | #2DTR. 51Z U/L |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D22 | 四湖DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0990 |  |  | 2-3D-14 |  |  | #2DTR | USE/LOCK | #2DTR. 數位電驛故障 |  |  | B1/D22_A1 | [8 empty] | 四湖DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0991 |  |  | 2-3D-15 |  |  | Power Meter | A/N | Power Meter 故障警報 PMA |  |  | ELEM/D22_A1 | [8 empty] | 四湖DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 310 | #1DTR(310) |  | 2_PHA |  | INSERT | Status | 第2套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | D1A | PHA | D1A 310 PHA(RY盤) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 583 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 320 | #1DTR(320) |  | 2_PHA |  | INSERT | Status | 第2套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | D1B | PHA | D1B 320 PHA(RY盤) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 584 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 330A1 | #2DTR(A)(330A1) |  | 2_PHA |  | INSERT | Status | 第2套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | D2A1 | PHA | D2A1 330A1 PHA(RY盤) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.330A1_51A | #2DTR二次側(330A1) 51RY | MTR | [5 empty] | 585 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 330A2 | #2DTR(A)(330A2) |  | 2_PHA |  | INSERT | Status | 第2套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | D2A2 | PHA | D2A2 330A2 PHA(RY盤) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.330A2_51A | #2DTR二次側(330A2) 51RY | MTR | [5 empty] | 586 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 340B1 | #2DTR(B)(340B1) |  | 2_PHA |  | INSERT | Status | 第2套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | D2B1 | PHA | D2B1 340B1 PHA(RY盤) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.340B1_51A | #2DTR二次側(340B1) 51RY | MTR | [5 empty] | 587 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 340B2 | #2DTR(B)(340B2) |  | 2_PHA |  | INSERT | Status | 第2套PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | D2B2 | PHA | D2B2 340B2 PHA(RY盤) |  |  | B3/D22_A1 | [8 empty] | 四湖DS.340B2_51A | #2DTR二次側(340B2) 51RY | MTR | [5 empty] | 588 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D22 | 四湖DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D22_A1 | [12 empty] | 四湖DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D22/161/1BUS/V; OPRD2: D22/161/2BUS/V
D22 | 四湖DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D22_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D22/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D22 | 四湖DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D22_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_3 | OPRD1: D22/161/1510/MW; OPRD2: D22/161/1520/MW; OPRD3: D22/161/1530/MW
W01 | 湖風GS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/W01_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_1 | OPRD1: W01/161/1530/MW
W01 | 湖風GS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/W01_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: W01/0/CalcPoint/OPRN2_MW
D22 | 四湖DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D22_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D22/0/CalcPoint/OPRN2_MW
W01 | 湖風GS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/W01_A1 | [17 empty] | none
D22 | 四湖DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D22_A1 | [17 empty] | none
W01 | 湖風GS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/W01_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: NULL; OPRD2: W01/0/CalcPoint/OPRN2; OPRD3: W01/0/CalcPoint/PRFL_UL
D22 | 四湖DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D22_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D22/0/CalcPoint/OPRN1; OPRD2: D22/0/CalcPoint/OPRN2; OPRD3: D22/0/CalcPoint/PRFL_UL
D22 | 四湖DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D22_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D22/11/310/I_R; OPRD2: D22/11/320/I_R
D22 | 四湖DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D22_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D22/11/310/I_S; OPRD2: D22/11/320/I_S
D22 | 四湖DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D22_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D22/11/310/I_T; OPRD2: D22/11/320/I_T
D22 | 四湖DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D22_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D22/11/330A1/I_R; OPRD2: D22/11/330A2/I_R
D22 | 四湖DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D22_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D22/11/330A1/I_S; OPRD2: D22/11/330A2/I_S
D22 | 四湖DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D22_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D22/11/330A1/I_T; OPRD2: D22/11/330A2/I_T
D22 | 四湖DS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D22_A1 | [12 empty] | 四湖DS.1510_AMP | 北港四湖一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D22/161/1510/MW; OPRD2: D22/161/1510/MVAR; OPRD3: D22/0/CalcPoint/Vbs4
D22 | 四湖DS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D22_A1 | [12 empty] | 四湖DS.1520_AMP | 北港四湖二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D22/161/1520/MW; OPRD2: D22/161/1520/MVAR; OPRD3: D22/0/CalcPoint/Vbs4
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D22_A1 | [12 empty] | 四湖DS.1530_AMP | 湖風四湖線 AMP | LINE161 | AMP_CAL | C20R0964 | amp_cal | OPRD1: D22/161/1530/MW; OPRD2: D22/161/1530/MVAR; OPRD3: D22/0/CalcPoint/Vbs4
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風～四湖線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/W01_A1 | [12 empty] | 湖風GS.1530_AMP | 湖風四湖線 AMP | LINE161 | AMP_CAL | C20R1600 | amp_cal | OPRD1: W01/161/1530/MW; OPRD2: W01/161/1530/MVAR; OPRD3: NULL
D22 | 四湖DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D22_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D22/11/1ABUS/V
D22 | 四湖DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D22_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D22/11/1BBUS/V
D22 | 四湖DS | 11 | 11kV | 2A1BUS | #2A1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D22_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D22/11/2A1BUS/V
D22 | 四湖DS | 11 | 11kV | 2A2BUS | #2A2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D22_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D22/11/2A2BUS/V
D22 | 四湖DS | 11 | 11kV | 2B1BUS | #2B1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D22_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D22/11/2B1BUS/V
D22 | 四湖DS | 11 | 11kV | 2B2BUS | #2B2BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D22_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D22/11/2B2BUS/V
D22 | 四湖DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D22_A1 | [12 empty] | 四湖DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D22//1DTR(A)/SupLocal; OPRD2: D22//1DTR(A)/Tap Chan
D22 | 四湖DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D22_A1 | [12 empty] | 四湖DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D22//1DTR(B)/SupLocal; OPRD2: D22//1DTR(B)/Tap Chan
D22 | 四湖DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D22_A1 | [12 empty] | 四湖DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D22//2DTR(A)/SupLocal; OPRD2: D22//2DTR(A)/Tap Chan
D22 | 四湖DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D22_A1 | [12 empty] | 四湖DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D22//2DTR(B)/SupLocal; OPRD2: D22//2DTR(B)/Tap Chan
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1ABUS/V; OPRD2: D22/11/XQ21/I_R; OPRD3: D22/11/XQ21/I_S; OPRD4: D22/11/XQ21/I_T
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1ABUS/V; OPRD2: D22/11/XQ22/I_R; OPRD3: D22/11/XQ22/I_S; OPRD4: D22/11/XQ22/I_T
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1ABUS/V; OPRD2: D22/11/XQ23/I_R; OPRD3: D22/11/XQ23/I_S; OPRD4: D22/11/XQ23/I_T
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1ABUS/V; OPRD2: D22/11/XQ24/I_R; OPRD3: D22/11/XQ24/I_S; OPRD4: D22/11/XQ24/I_T
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1ABUS/V; OPRD2: D22/11/XQ25/I_R; OPRD3: D22/11/XQ25/I_S; OPRD4: D22/11/XQ25/I_T
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1BBUS/V; OPRD2: D22/11/XQ26/I_R; OPRD3: D22/11/XQ26/I_S; OPRD4: D22/11/XQ26/I_T
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1BBUS/V; OPRD2: D22/11/XQ27/I_R; OPRD3: D22/11/XQ27/I_S; OPRD4: D22/11/XQ27/I_T
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1BBUS/V; OPRD2: D22/11/XQ28/I_R; OPRD3: D22/11/XQ28/I_S; OPRD4: D22/11/XQ28/I_T
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1BBUS/V; OPRD2: D22/11/XQ29/I_R; OPRD3: D22/11/XQ29/I_S; OPRD4: D22/11/XQ29/I_T
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/1BBUS/V; OPRD2: D22/11/XQ30/I_R; OPRD3: D22/11/XQ30/I_S; OPRD4: D22/11/XQ30/I_T
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2A1BUS/V; OPRD2: D22/11/XQ31/I_R; OPRD3: D22/11/XQ31/I_S; OPRD4: D22/11/XQ31/I_T
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2A1BUS/V; OPRD2: D22/11/XQ32/I_R; OPRD3: D22/11/XQ32/I_S; OPRD4: D22/11/XQ32/I_T
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2A1BUS/V; OPRD2: D22/11/XQ33/I_R; OPRD3: D22/11/XQ33/I_S; OPRD4: D22/11/XQ33/I_T
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2A2BUS/V; OPRD2: D22/11/XQ34/I_R; OPRD3: D22/11/XQ34/I_S; OPRD4: D22/11/XQ34/I_T
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2A2BUS/V; OPRD2: D22/11/XQ35/I_R; OPRD3: D22/11/XQ35/I_S; OPRD4: D22/11/XQ35/I_T
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2B1BUS/V; OPRD2: D22/11/XQ36/I_R; OPRD3: D22/11/XQ36/I_S; OPRD4: D22/11/XQ36/I_T
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2B1BUS/V; OPRD2: D22/11/XQ37/I_R; OPRD3: D22/11/XQ37/I_S; OPRD4: D22/11/XQ37/I_T
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2B2BUS/V; OPRD2: D22/11/XQ38/I_R; OPRD3: D22/11/XQ38/I_S; OPRD4: D22/11/XQ38/I_T
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2B2BUS/V; OPRD2: D22/11/XQ39/I_R; OPRD3: D22/11/XQ39/I_S; OPRD4: D22/11/XQ39/I_T
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D22/11/2B2BUS/V; OPRD2: D22/11/XQ40/I_R; OPRD3: D22/11/XQ40/I_S; OPRD4: D22/11/XQ40/I_T
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ21/kVA; OPRD2: D22/11/XQ21/KVAR
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ22/kVA; OPRD2: D22/11/XQ22/KVAR
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ23/kVA; OPRD2: D22/11/XQ23/KVAR
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ24/kVA; OPRD2: D22/11/XQ24/KVAR
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ25/kVA; OPRD2: D22/11/XQ25/KVAR
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ26/kVA; OPRD2: D22/11/XQ26/KVAR
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ27/kVA; OPRD2: D22/11/XQ27/KVAR
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ28/kVA; OPRD2: D22/11/XQ28/KVAR
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ29/kVA; OPRD2: D22/11/XQ29/KVAR
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ30/kVA; OPRD2: D22/11/XQ30/KVAR
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ31/kVA; OPRD2: D22/11/XQ31/KVAR
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ32/kVA; OPRD2: D22/11/XQ32/KVAR
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ33/kVA; OPRD2: D22/11/XQ33/KVAR
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ34/kVA; OPRD2: D22/11/XQ34/KVAR
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ35/kVA; OPRD2: D22/11/XQ35/KVAR
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ36/kVA; OPRD2: D22/11/XQ36/KVAR
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ37/kVA; OPRD2: D22/11/XQ37/KVAR
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ38/kVA; OPRD2: D22/11/XQ38/KVAR
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ39/kVA; OPRD2: D22/11/XQ39/KVAR
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D22_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D22/11/XQ40/kVA; OPRD2: D22/11/XQ40/KVAR
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D22_A1 | [12 empty] | 四湖DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D22/11/210/CB; OPRD2: 6.9; OPRD3: 0
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D22_A1 | [12 empty] | 四湖DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D22/11/220/CB; OPRD2: 6.9; OPRD3: 0
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D22_A1 | [12 empty] | 四湖DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D22/11/230/CB; OPRD2: 6.9; OPRD3: 0
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D22_A1 | [12 empty] | 四湖DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_LBS_11 | LG_MVAR | sc_mvar | OPRD1: D22/11/240/CB; OPRD2: 6.9; OPRD3: 0
D22 | 四湖DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D22_A1 | [12 empty] | 四湖DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_28 | OPRD1: D22//1DTR/63Q; OPRD2: D22//1DTR/51ZA; OPRD3: D22//1DTR/TRA; OPRD4: D22//1DTR/96D; OPRD5: D22//1DTR/96B1; OPRD6: D22//1DTR/96B2; OPRD7: D22//1DTR/96PA; OPRD8: D22//1DTR/87A; OPRD9: D22//2DTR/63Q; OPRD10: D22//2DTR/96D; OPRD11: D22//2DTR/TRA; OPRD12: D22//2DTR/51ZA; OPRD13: D22//2DTR/96B2; OPRD14: D22//2DTR/96B1; OPRD15: D22//2DTR/96PA; OPRD16: D22//2DTR/87A; OPRD17: D22/11/310/GDA; OPRD18: D22/11/320/GDA; OPRD19: D22/11/330A1/GDA; OPRD20: D22/11/330A2/GDA; OPRD21: D22/11/340B1/GDA; OPRD22: D22/11/340B2/GDA; OPRD23: D22/161/1750/GDA; OPRD24: D22/161/1750/PHA; OPRD25: D22/161/1760/PHA; OPRD26: D22/161/1760/GDA; OPRD27: D22/161/1BUS/87A; OPRD28: D22/161/2BUS/87A
D22 | 四湖DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D22_A1 | [12 empty] | 四湖DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D22//1DTR/TRF; OPRD2: D22//2DTR/TRF
D22 | 四湖DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/161/1750/CB
D22 | 四湖DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/11/310/CB
D22 | 四湖DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/11/320/CB
D22 | 四湖DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/161/1760/CB
D22 | 四湖DS | 11 | 11kV | 330A1_D1 | #2DTR(A)(330A1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/11/330A1/CB
D22 | 四湖DS | 11 | 11kV | 330A2_D1 | #2DTR(A)(330A2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/11/330A2/CB
D22 | 四湖DS | 11 | 11kV | 340B1_D1 | #2DTR(B)(340B1) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/11/340B1/CB
D22 | 四湖DS | 11 | 11kV | 340B2_D1 | #2DTR(B)(340B2) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/11/340B2/CB
D22 | 四湖DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/0/RTU/RTU_R_L
D22 | 四湖DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/0/StaDev/STUV
D22 | 四湖DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/0/StaDev/DCE
D22 | 四湖DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/0/StaDev/DCA
D22 | 四湖DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D22_D1 | [17 empty] | lamp2CC | OPRD1: D22/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D22 | 四湖DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D22/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 四湖DS.1510_AMP | 北港四湖一路 AMP | LINE161 | D22/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 四湖DS.1520_AMP | 北港四湖二路 AMP | LINE161 | D22/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛一線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛一線KVA | 11KV飛一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛一線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛一線KW | 11KV飛一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛七線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛七線KVA | 11KV飛七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛七線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛七線KW | 11KV飛七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛九線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛九線KVA | 11KV飛九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛九線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛九線KW | 11KV飛九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛二十線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛二十線KVA | 11KV飛二十線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛二十線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛二十線KW | 11KV飛二十線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛二線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛二線KVA | 11KV飛二線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛二線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛二線KW | 11KV飛二線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛八線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛八線KVA | 11KV飛八線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛八線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛八線KW | 11KV飛八線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十一線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十一線KVA | 11KV飛十一線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十一線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十一線KW | 11KV飛十一線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十七線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十七線KVA | 11KV飛十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十七線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十七線KW | 11KV飛十七線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十九線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十九線KVA | 11KV飛十九線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十九線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十九線KW | 11KV飛十九線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十二線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十二線KVA | 11KV飛十二線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十二線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十二線KW | 11KV飛十二線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十八線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十八線KVA | 11KV飛十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十八線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十八線KW | 11KV飛十八線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十三線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十三線KVA | 11KV飛十三線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十三線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十三線KW | 11KV飛十三線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十五線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十五線KVA | 11KV飛十五線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十五線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十五線KW | 11KV飛十五線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十六線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十六線KVA | 11KV飛十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十六線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十六線KW | 11KV飛十六線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十四線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十四線KVA | 11KV飛十四線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十四線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十四線KW | 11KV飛十四線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十線KVA | 11KV飛十線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛十線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛十線KW | 11KV飛十線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛三線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛三線KVA | 11KV飛三線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛三線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛三線KW | 11KV飛三線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛五線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛五線KVA | 11KV飛五線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛五線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛五線KW | 11KV飛五線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛六線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛六線KVA | 11KV飛六線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛六線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛六線KW | 11KV飛六線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛四線KVA | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛四線KVA | 11KV飛四線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  |  |  |  | 飛四線KW | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.飛四線KW | 11KV飛四線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 四湖DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D22/11/210/MVAR |  | SC_LBS_11 |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 四湖DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D22/11/220/MVAR |  | SC_LBS_11 |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 四湖DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D22/11/230/MVAR |  | SC_LBS_11 |  |  | 47 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 四湖DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D22/11/240/MVAR |  | SC_LBS_11 |  |  | 48 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | TRTOT | 四湖主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 四湖DS.TRTOT_MW | 四湖主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | TRTOT | 四湖主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 四湖DS.TRTOT_MVAR | 四湖主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 55 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 58 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 66 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 70 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D22 | 四湖DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [25 empty] | ADCS_N | [8 empty] | 四湖DS.11KV#2ABUS_KV | 11KV #2ABUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 71 | CalcAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [25 empty] | ADCS_N | [8 empty] | 四湖DS.11KV#2BBUS_KV | 11KV #2BBUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 72 | CalcAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 四湖DS.1530_AMP | 湖風四湖線 AMP | LINE161 | D22/161/1530/I |  | AMP_CAL |  |  | 73 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D22 | 四湖DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 200_CB | 200(200_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.200_CB_1 | 200 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 300_CB | 300(300_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.300_CB_1 | 300 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 400_CB | 400(400_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.400_CB_1 | 400 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.1750_CB_1 | 1750(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.310_CB_1 | 310(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.320_CB_1 | 320(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.210_CB_1 | 210(11KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.220_CB_1 | 220(11KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.230_CB_1 | 230(11KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.240_CB_1 | 240(11KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | _CBA | 斷路器重故障(_CBA) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.11KV_CBA_1 | 11KV斷路器重故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 86 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | _CBF | 斷路器輕故障(_CBF) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.11KV_CBF_1 | 11KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 87 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | RTU_S_L | RTU |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.RTU_S/L_1 | RTU SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 88 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D22 | 四湖DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 四湖DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D22/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 89 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 四湖DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D22/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 90 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510_AMP | 北港四湖一路 | [27 empty] | ADCS_N | [8 empty] | 四湖DS.1510_AMP_A | 北港四湖一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520_AMP | 北港四湖二路 | [27 empty] | ADCS_N | [8 empty] | 四湖DS.1520_AMP_A | 北港四湖二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D22//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D22//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D22//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D22//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1DTR_MVA | #1DTR |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.#1DTR_MVA_1 | #1DTR MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1DTR_MVA | #1DTR(B) | [27 empty] | DDCS1_2 | [8 empty] | 四湖DS.#1DTR_MVA_2 | #1DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 101 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2DTR_MVA | #2DTR |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.#2DTR_MVA_1 | #2DTR MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_2 | [8 empty] | 四湖DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 104 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 330A1_CB | #2DTR(330A1_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.330A1_CB_1 | 330A1(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 105 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 330A2_CB | #2DTR(330A2_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.330A2_CB_1 | 330A2(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 106 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 340B1_CB | #2DTR(340B1_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.340B1_CB_1 | 340B1(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 107 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 340B2_CB | #2DTR(340B2_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 四湖DS.340B2_CB_1 | 340B2(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 108 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 四湖DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 109 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530_AMP | 湖風四湖線 | [27 empty] | ADCS_N | [8 empty] | 四湖DS.1530_AMP_A | 湖風四湖線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 四湖DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 四湖DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2A1BUS | #2A1BUS |  | 11KV#2A1BUSC | [25 empty] | CDCS | [8 empty] | 四湖DS.11KV#2A1BUSC | #2A1BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2A2BUS | #2A2BUS |  | 11KV#2A2BUSC | [25 empty] | CDCS | [8 empty] | 四湖DS.11KV#2A2BUSC | #2A2BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2B1BUS | #2B1BUS |  | 11KV#2B1BUSC | [25 empty] | CDCS | [8 empty] | 四湖DS.11KV#2B1BUSC | #2B1BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 2B2BUS | #2B2BUS |  | 11KV#2B2BUSC | [25 empty] | CDCS | [8 empty] | 四湖DS.11KV#2B2BUSC | #2B2BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 四湖DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 四湖DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D22 | 四湖DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 四湖DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 四湖DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 120 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D22/0/RTU/ADCH1 |  |  |  | CDC | 121 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D22/0/RTU/ADCH2 |  |  |  | CDC | 122 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D22/0/RTU/ADCH3 |  |  |  | CDC | 123 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D22/0/RTU/ADCH4 |  |  |  | CDC | 124 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D22/0/RTU/ADCL1 |  |  |  | CDC | 125 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D22/0/RTU/ADCL2 |  |  |  | CDC | 126 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D22/0/RTU/ADCL3 |  |  |  | CDC | 127 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D22/0/RTU/ADCL4 |  |  |  | CDC | 128 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D22/161/1BUS/V |  |  |  | CDC | 129 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D22 | 四湖DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D22/161/2BUS/V |  |  |  | CDC | 130 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D22 | 四湖DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-A2 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D22/11/1ABUS/V |  |  |  | CDC | 131 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-C6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D22/11/1BBUS/V |  |  |  | CDC | 132 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 2A1BUS | #2A1BUS |  | V | [17 empty] | 1-FC | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV#2A1BUS_KV | 11KV #2A1BUS KV | BUS | D22/11/2A1BUS/V |  |  |  | CDC | 133 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 2A2BUS | #2A2BUS |  | V | [17 empty] | 1-FD | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV#2A2BUS_KV | 11KV #2A2BUS KV | BUS | D22/11/2A2BUS/V |  |  |  | CDC | 134 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 2B1BUS | #2B1BUS |  | V | [17 empty] | 2-A1 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV#2B1BUS_KV | 11KV #2B1BUS KV | BUS | D22/11/2B1BUS/V |  |  |  | CDC | 135 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 2B2BUS | #2B2BUS |  | V | [17 empty] | 2-A2 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV#2B2BUS_KV | 11KV #2B2BUS KV | BUS | D22/11/2B2BUS/V |  |  |  | CDC | 136 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1510_MW | 北港四湖一路 MW | LINE161 | D22/161/1510/MW |  |  |  | CDC | 137 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1510_MVAR | 北港四湖一路 MVAR | LINE161 | D22/161/1510/MVAR |  |  |  | CDC | 138 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1520_MW | 北港四湖二路 MW | LINE161 | D22/161/1520/MW |  |  |  | CDC | 139 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1520_MVAR | 北港四湖二路 MVAR | LINE161 | D22/161/1520/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛一線 | 飛一線 |  | 飛一線KVAR | [17 empty] | 1-A8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛一線KVAR | 11KV飛一線 KVAR | FEEDER | D22/11/XQ21/KVAR |  |  |  | CDC | 141 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛一線 | 飛一線 |  | 飛一線A1 | [17 empty] | 1-A9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛一線A1 | 11KV飛一線 R相AMP | FEEDER | D22/11/XQ21/I_R |  |  |  | CDC | 142 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛一線 | 飛一線 |  | 飛一線A2 | [17 empty] | 1-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛一線A2 | 11KV飛一線 S相AMP | FEEDER | D22/11/XQ21/I_S |  |  |  | CDC | 143 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛一線 | 飛一線 |  | 飛一線A3 | [17 empty] | 1-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛一線A3 | 11KV飛一線 T相AMP | FEEDER | D22/11/XQ21/I_T |  |  |  | CDC | 144 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛一線 | 飛一線 |  | 飛一線A0 | [17 empty] | 1-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛一線A0 | 11KV飛一線 N相AMP | FEEDER | D22/11/XQ21/I_N |  |  |  | CDC | 145 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛七線 | 飛七線 |  | 飛七線KVAR | [17 empty] | 1-D1 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛七線KVAR | 11KV飛七線 KVAR | FEEDER | D22/11/XQ27/KVAR |  |  |  | CDC | 146 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛七線 | 飛七線 |  | 飛七線A1 | [17 empty] | 1-D2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛七線A1 | 11KV飛七線 R相AMP | FEEDER | D22/11/XQ27/I_R |  |  |  | CDC | 147 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛七線 | 飛七線 |  | 飛七線A2 | [17 empty] | 1-D3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛七線A2 | 11KV飛七線 S相AMP | FEEDER | D22/11/XQ27/I_S |  |  |  | CDC | 148 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛七線 | 飛七線 |  | 飛七線A3 | [17 empty] | 1-D4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛七線A3 | 11KV飛七線 T相AMP | FEEDER | D22/11/XQ27/I_T |  |  |  | CDC | 149 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛七線 | 飛七線 |  | 飛七線A0 | [17 empty] | 1-D5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛七線A0 | 11KV飛七線 N相AMP | FEEDER | D22/11/XQ27/I_N |  |  |  | CDC | 150 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛九線 | 飛九線 |  | 飛九線KVAR | [17 empty] | 1-DB | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛九線KVAR | 11KV飛九線 KVAR | FEEDER | D22/11/XQ29/KVAR |  |  |  | CDC | 151 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛九線 | 飛九線 |  | 飛九線A1 | [17 empty] | 1-DC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛九線A1 | 11KV飛九線 R相AMP | FEEDER | D22/11/XQ29/I_R |  |  |  | CDC | 152 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛九線 | 飛九線 |  | 飛九線A2 | [17 empty] | 1-DD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛九線A2 | 11KV飛九線 S相AMP | FEEDER | D22/11/XQ29/I_S |  |  |  | CDC | 153 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛九線 | 飛九線 |  | 飛九線A3 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛九線A3 | 11KV飛九線 T相AMP | FEEDER | D22/11/XQ29/I_T |  |  |  | CDC | 154 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛九線 | 飛九線 |  | 飛九線A0 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛九線A0 | 11KV飛九線 N相AMP | FEEDER | D22/11/XQ29/I_N |  |  |  | CDC | 155 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二十線 | 飛二十線 |  | 飛二十線KVAR | [17 empty] | 2-B2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二十線KVAR | 11KV飛二十線 KVAR | FEEDER | D22/11/XQ40/KW |  |  |  | CDC | 156 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二十線 | 飛二十線 |  | 飛二十線A1 | [17 empty] | 2-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二十線A1 | 11KV飛二十線 R相AMP | FEEDER | D22/11/XQ40/KVAR |  |  |  | CDC | 157 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二十線 | 飛二十線 |  | 飛二十線A2 | [17 empty] | 2-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二十線A2 | 11KV飛二十線 S相AMP | FEEDER | D22/11/XQ40/I_R |  |  |  | CDC | 158 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二十線 | 飛二十線 |  | 飛二十線A3 | [17 empty] | 2-B5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二十線A3 | 11KV飛二十線 T相AMP | FEEDER | D22/11/XQ40/I_S |  |  |  | CDC | 159 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二十線 | 飛二十線 |  | 飛二十線A0 | [17 empty] | 2-B6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二十線A0 | 11KV飛二十線 N相AMP | FEEDER | D22/11/XQ40/I_T |  |  |  | CDC | 160 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二線 | 飛二線 |  | 飛二線KVAR | [17 empty] | 1-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二線KVAR | 11KV飛二線 KVAR | FEEDER | D22/11/XQ22/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二線 | 飛二線 |  | 飛二線A1 | [17 empty] | 1-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二線A1 | 11KV飛二線 R相AMP | FEEDER | D22/11/XQ22/I_R |  |  |  | CDC | 162 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二線 | 飛二線 |  | 飛二線A2 | [17 empty] | 1-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二線A2 | 11KV飛二線 S相AMP | FEEDER | D22/11/XQ22/I_S |  |  |  | CDC | 163 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二線 | 飛二線 |  | 飛二線A3 | [17 empty] | 1-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二線A3 | 11KV飛二線 T相AMP | FEEDER | D22/11/XQ22/I_T |  |  |  | CDC | 164 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛二線 | 飛二線 |  | 飛二線A0 | [17 empty] | 1-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛二線A0 | 11KV飛二線 N相AMP | FEEDER | D22/11/XQ22/I_N |  |  |  | CDC | 165 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛八線 | 飛八線 |  | 飛八線KVAR | [17 empty] | 1-D6 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛八線KVAR | 11KV飛八線 KVAR | FEEDER | D22/11/XQ28/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛八線 | 飛八線 |  | 飛八線A1 | [17 empty] | 1-D7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛八線A1 | 11KV飛八線 R相AMP | FEEDER | D22/11/XQ28/I_R |  |  |  | CDC | 167 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛八線 | 飛八線 |  | 飛八線A2 | [17 empty] | 1-D8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛八線A2 | 11KV飛八線 S相AMP | FEEDER | D22/11/XQ28/I_S |  |  |  | CDC | 168 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛八線 | 飛八線 |  | 飛八線A3 | [17 empty] | 1-D9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛八線A3 | 11KV飛八線 T相AMP | FEEDER | D22/11/XQ28/I_T |  |  |  | CDC | 169 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛八線 | 飛八線 |  | 飛八線A0 | [17 empty] | 1-DA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛八線A0 | 11KV飛八線 N相AMP | FEEDER | D22/11/XQ28/I_N |  |  |  | CDC | 170 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十一線 | 飛十一線 |  | 飛十一線KVAR | [17 empty] | 1-E8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十一線KVAR | 11KV飛十一線 KVAR | FEEDER | D22/11/XQ31/KVAR |  |  |  | CDC | 171 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十一線 | 飛十一線 |  | 飛十一線A1 | [17 empty] | 1-E9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十一線A1 | 11KV飛十一線 R相AMP | FEEDER | D22/11/XQ31/I_R |  |  |  | CDC | 172 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十一線 | 飛十一線 |  | 飛十一線A2 | [17 empty] | 1-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十一線A2 | 11KV飛十一線 S相AMP | FEEDER | D22/11/XQ31/I_S |  |  |  | CDC | 173 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十一線 | 飛十一線 |  | 飛十一線A3 | [17 empty] | 1-EB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十一線A3 | 11KV飛十一線 T相AMP | FEEDER | D22/11/XQ31/I_T |  |  |  | CDC | 174 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十一線 | 飛十一線 |  | 飛十一線A0 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十一線A0 | 11KV飛十一線 N相AMP | FEEDER | D22/11/XQ31/I_N |  |  |  | CDC | 175 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十七線 | 飛十七線 |  | 飛十七線KVAR | [17 empty] | 2-97 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十七線KVAR | 11KV飛十七線 KVAR | FEEDER | D22/11/XQ37/KVAR |  |  |  | CDC | 176 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十七線 | 飛十七線 |  | 飛十七線A1 | [17 empty] | 2-98 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十七線A1 | 11KV飛十七線 R相AMP | FEEDER | D22/11/XQ37/I_R |  |  |  | CDC | 177 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十七線 | 飛十七線 |  | 飛十七線A2 | [17 empty] | 2-99 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十七線A2 | 11KV飛十七線 S相AMP | FEEDER | D22/11/XQ37/I_S |  |  |  | CDC | 178 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十七線 | 飛十七線 |  | 飛十七線A3 | [17 empty] | 2-9A | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十七線A3 | 11KV飛十七線 T相AMP | FEEDER | D22/11/XQ37/I_T |  |  |  | CDC | 179 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十七線 | 飛十七線 |  | 飛十七線A0 | [17 empty] | 2-9B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十七線A0 | 11KV飛十七線 N相AMP | FEEDER | D22/11/XQ37/I_N |  |  |  | CDC | 180 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十九線 | 飛十九線 |  | 飛十九線KVAR | [17 empty] | 2-AD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十九線KVAR | 11KV飛十九線 KVAR | FEEDER | D22/11/XQ39/KW |  |  |  | CDC | 181 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十九線 | 飛十九線 |  | 飛十九線A1 | [17 empty] | 2-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十九線A1 | 11KV飛十九線 R相AMP | FEEDER | D22/11/XQ39/KVAR |  |  |  | CDC | 182 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十九線 | 飛十九線 |  | 飛十九線A2 | [17 empty] | 2-AF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十九線A2 | 11KV飛十九線 S相AMP | FEEDER | D22/11/XQ39/I_R |  |  |  | CDC | 183 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十九線 | 飛十九線 |  | 飛十九線A3 | [17 empty] | 2-B0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十九線A3 | 11KV飛十九線 T相AMP | FEEDER | D22/11/XQ39/I_S |  |  |  | CDC | 184 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十九線 | 飛十九線 |  | 飛十九線A0 | [17 empty] | 2-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十九線A0 | 11KV飛十九線 N相AMP | FEEDER | D22/11/XQ39/I_T |  |  |  | CDC | 185 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十二線 | 飛十二線 |  | 飛十二線KVAR | [17 empty] | 1-ED | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十二線KVAR | 11KV飛十二線 KVAR | FEEDER | D22/11/XQ32/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十二線 | 飛十二線 |  | 飛十二線A1 | [17 empty] | 1-EE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十二線A1 | 11KV飛十二線 R相AMP | FEEDER | D22/11/XQ32/I_R |  |  |  | CDC | 187 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十二線 | 飛十二線 |  | 飛十二線A2 | [17 empty] | 1-EF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十二線A2 | 11KV飛十二線 S相AMP | FEEDER | D22/11/XQ32/I_S |  |  |  | CDC | 188 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十二線 | 飛十二線 |  | 飛十二線A3 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十二線A3 | 11KV飛十二線 T相AMP | FEEDER | D22/11/XQ32/I_T |  |  |  | CDC | 189 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十二線 | 飛十二線 |  | 飛十二線A0 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十二線A0 | 11KV飛十二線 N相AMP | FEEDER | D22/11/XQ32/I_N |  |  |  | CDC | 190 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十八線 | 飛十八線 |  | 飛十八線KVAR | [17 empty] | 2-A8 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十八線KVAR | 11KV飛十八線 KVAR | FEEDER | D22/11/XQ38/KW |  |  |  | CDC | 191 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十八線 | 飛十八線 |  | 飛十八線A1 | [17 empty] | 2-A9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十八線A1 | 11KV飛十八線 R相AMP | FEEDER | D22/11/XQ38/KVAR |  |  |  | CDC | 192 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十八線 | 飛十八線 |  | 飛十八線A2 | [17 empty] | 2-AA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十八線A2 | 11KV飛十八線 S相AMP | FEEDER | D22/11/XQ38/I_R |  |  |  | CDC | 193 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十八線 | 飛十八線 |  | 飛十八線A3 | [17 empty] | 2-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十八線A3 | 11KV飛十八線 T相AMP | FEEDER | D22/11/XQ38/I_S |  |  |  | CDC | 194 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十八線 | 飛十八線 |  | 飛十八線A0 | [17 empty] | 2-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十八線A0 | 11KV飛十八線 N相AMP | FEEDER | D22/11/XQ38/I_T |  |  |  | CDC | 195 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十三線 | 飛十三線 |  | 飛十三線KVAR | [17 empty] | 1-F2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十三線KVAR | 11KV飛十三線 KVAR | FEEDER | D22/11/XQ33/KVAR |  |  |  | CDC | 196 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十三線 | 飛十三線 |  | 飛十三線A1 | [17 empty] | 1-F3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十三線A1 | 11KV飛十三線 R相AMP | FEEDER | D22/11/XQ33/I_R |  |  |  | CDC | 197 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十三線 | 飛十三線 |  | 飛十三線A2 | [17 empty] | 1-F4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十三線A2 | 11KV飛十三線 S相AMP | FEEDER | D22/11/XQ33/I_S |  |  |  | CDC | 198 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十三線 | 飛十三線 |  | 飛十三線A3 | [17 empty] | 1-F5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十三線A3 | 11KV飛十三線 T相AMP | FEEDER | D22/11/XQ33/I_T |  |  |  | CDC | 199 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十三線 | 飛十三線 |  | 飛十三線A0 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十三線A0 | 11KV飛十三線 N相AMP | FEEDER | D22/11/XQ33/I_N |  |  |  | CDC | 200 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十五線 | 飛十五線 |  | 飛十五線KVAR | [17 empty] | 2-8A | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十五線KVAR | 11KV飛十五線 KVAR | FEEDER | D22/11/XQ35/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十五線 | 飛十五線 |  | 飛十五線A1 | [17 empty] | 2-8B | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十五線A1 | 11KV飛十五線 R相AMP | FEEDER | D22/11/XQ35/I_R |  |  |  | CDC | 202 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十五線 | 飛十五線 |  | 飛十五線A2 | [17 empty] | 2-8C | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十五線A2 | 11KV飛十五線 S相AMP | FEEDER | D22/11/XQ35/I_S |  |  |  | CDC | 203 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十五線 | 飛十五線 |  | 飛十五線A3 | [17 empty] | 2-8D | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十五線A3 | 11KV飛十五線 T相AMP | FEEDER | D22/11/XQ35/I_T |  |  |  | CDC | 204 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十五線 | 飛十五線 |  | 飛十五線A0 | [17 empty] | 2-8E | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十五線A0 | 11KV飛十五線 N相AMP | FEEDER | D22/11/XQ35/I_N |  |  |  | CDC | 205 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十六線 | 飛十六線 |  | 飛十六線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十六線KVAR | 11KV飛十六線 KVAR | FEEDER | D22/11/XQ36/KVAR |  |  |  | CDC | 206 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十六線 | 飛十六線 |  | 飛十六線A1 | [17 empty] | 2-93 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十六線A1 | 11KV飛十六線 R相AMP | FEEDER | D22/11/XQ36/I_R |  |  |  | CDC | 207 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十六線 | 飛十六線 |  | 飛十六線A2 | [17 empty] | 2-94 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十六線A2 | 11KV飛十六線 S相AMP | FEEDER | D22/11/XQ36/I_S |  |  |  | CDC | 208 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十六線 | 飛十六線 |  | 飛十六線A3 | [17 empty] | 2-95 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十六線A3 | 11KV飛十六線 T相AMP | FEEDER | D22/11/XQ36/I_T |  |  |  | CDC | 209 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十六線 | 飛十六線 |  | 飛十六線A0 | [17 empty] | 2-96 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十六線A0 | 11KV飛十六線 N相AMP | FEEDER | D22/11/XQ36/I_N |  |  |  | CDC | 210 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十四線 | 飛十四線 |  | 飛十四線KVAR | [17 empty] | 2-85 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十四線KVAR | 11KV飛十四線 KVAR | FEEDER | D22/11/XQ34/KVAR |  |  |  | CDC | 211 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十四線 | 飛十四線 |  | 飛十四線A1 | [17 empty] | 2-86 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十四線A1 | 11KV飛十四線 R相AMP | FEEDER | D22/11/XQ34/I_R |  |  |  | CDC | 212 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十四線 | 飛十四線 |  | 飛十四線A2 | [17 empty] | 2-87 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十四線A2 | 11KV飛十四線 S相AMP | FEEDER | D22/11/XQ34/I_S |  |  |  | CDC | 213 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十四線 | 飛十四線 |  | 飛十四線A3 | [17 empty] | 2-88 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十四線A3 | 11KV飛十四線 T相AMP | FEEDER | D22/11/XQ34/I_T |  |  |  | CDC | 214 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十四線 | 飛十四線 |  | 飛十四線A0 | [17 empty] | 2-89 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十四線A0 | 11KV飛十四線 N相AMP | FEEDER | D22/11/XQ34/I_N |  |  |  | CDC | 215 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十線 | 飛十線 |  | 飛十線KVAR | [17 empty] | 1-E0 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十線KVAR | 11KV飛十線 KVAR | FEEDER | D22/11/XQ30/KVAR |  |  |  | CDC | 216 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十線 | 飛十線 |  | 飛十線A1 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十線A1 | 11KV飛十線 R相AMP | FEEDER | D22/11/XQ30/I_R |  |  |  | CDC | 217 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十線 | 飛十線 |  | 飛十線A2 | [17 empty] | 1-E2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十線A2 | 11KV飛十線 S相AMP | FEEDER | D22/11/XQ30/I_S |  |  |  | CDC | 218 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十線 | 飛十線 |  | 飛十線A3 | [17 empty] | 1-E3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十線A3 | 11KV飛十線 T相AMP | FEEDER | D22/11/XQ30/I_T |  |  |  | CDC | 219 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛十線 | 飛十線 |  | 飛十線A0 | [17 empty] | 1-E4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛十線A0 | 11KV飛十線 N相AMP | FEEDER | D22/11/XQ30/I_N |  |  |  | CDC | 220 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛三線 | 飛三線 |  | 飛三線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛三線KVAR | 11KV飛三線 KVAR | FEEDER | D22/11/XQ23/KVAR |  |  |  | CDC | 221 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛三線 | 飛三線 |  | 飛三線A1 | [17 empty] | 1-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛三線A1 | 11KV飛三線 R相AMP | FEEDER | D22/11/XQ23/I_R |  |  |  | CDC | 222 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛三線 | 飛三線 |  | 飛三線A2 | [17 empty] | 1-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛三線A2 | 11KV飛三線 S相AMP | FEEDER | D22/11/XQ23/I_S |  |  |  | CDC | 223 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛三線 | 飛三線 |  | 飛三線A3 | [17 empty] | 1-B5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛三線A3 | 11KV飛三線 T相AMP | FEEDER | D22/11/XQ23/I_T |  |  |  | CDC | 224 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛三線 | 飛三線 |  | 飛三線A0 | [17 empty] | 1-B6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛三線A0 | 11KV飛三線 N相AMP | FEEDER | D22/11/XQ23/I_N |  |  |  | CDC | 225 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛五線 | 飛五線 |  | 飛五線KVAR | [17 empty] | 1-BC | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛五線KVAR | 11KV飛五線 KVAR | FEEDER | D22/11/XQ25/KVAR |  |  |  | CDC | 226 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛五線 | 飛五線 |  | 飛五線A1 | [17 empty] | 1-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛五線A1 | 11KV飛五線 R相AMP | FEEDER | D22/11/XQ25/I_R |  |  |  | CDC | 227 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛五線 | 飛五線 |  | 飛五線A2 | [17 empty] | 1-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛五線A2 | 11KV飛五線 S相AMP | FEEDER | D22/11/XQ25/I_S |  |  |  | CDC | 228 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛五線 | 飛五線 |  | 飛五線A3 | [17 empty] | 1-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛五線A3 | 11KV飛五線 T相AMP | FEEDER | D22/11/XQ25/I_T |  |  |  | CDC | 229 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛五線 | 飛五線 |  | 飛五線A0 | [17 empty] | 1-C2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛五線A0 | 11KV飛五線 N相AMP | FEEDER | D22/11/XQ25/I_N |  |  |  | CDC | 230 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛六線 | 飛六線 |  | 飛六線KVAR | [17 empty] | 1-CC | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛六線KVAR | 11KV飛六線 KVAR | FEEDER | D22/11/XQ26/KVAR |  |  |  | CDC | 231 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛六線 | 飛六線 |  | 飛六線A1 | [17 empty] | 1-CD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛六線A1 | 11KV飛六線 R相AMP | FEEDER | D22/11/XQ26/I_R |  |  |  | CDC | 232 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛六線 | 飛六線 |  | 飛六線A2 | [17 empty] | 1-CE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛六線A2 | 11KV飛六線 S相AMP | FEEDER | D22/11/XQ26/I_S |  |  |  | CDC | 233 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛六線 | 飛六線 |  | 飛六線A3 | [17 empty] | 1-CF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛六線A3 | 11KV飛六線 T相AMP | FEEDER | D22/11/XQ26/I_T |  |  |  | CDC | 234 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛六線 | 飛六線 |  | 飛六線A0 | [17 empty] | 1-D0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛六線A0 | 11KV飛六線 N相AMP | FEEDER | D22/11/XQ26/I_N |  |  |  | CDC | 235 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛四線 | 飛四線 |  | 飛四線KVAR | [17 empty] | 1-B7 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛四線KVAR | 11KV飛四線 KVAR | FEEDER | D22/11/XQ24/KVAR |  |  |  | CDC | 236 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛四線 | 飛四線 |  | 飛四線A1 | [17 empty] | 1-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛四線A1 | 11KV飛四線 R相AMP | FEEDER | D22/11/XQ24/I_R |  |  |  | CDC | 237 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛四線 | 飛四線 |  | 飛四線A2 | [17 empty] | 1-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛四線A2 | 11KV飛四線 S相AMP | FEEDER | D22/11/XQ24/I_S |  |  |  | CDC | 238 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛四線 | 飛四線 |  | 飛四線A3 | [17 empty] | 1-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛四線A3 | 11KV飛四線 T相AMP | FEEDER | D22/11/XQ24/I_T |  |  |  | CDC | 239 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 飛四線 | 飛四線 |  | 飛四線A0 | [17 empty] | 1-BB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.飛四線A0 | 11KV飛四線 N相AMP | FEEDER | D22/11/XQ24/I_N |  |  |  | CDC | 240 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-92 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1500TIE_AMP | 1500TIE AMP | TIE | D22/161/1500/I_R |  |  |  | CDC | 241 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-C3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D22/11/100/I_R |  |  |  | CDC | 242 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D22/11/100/I_S |  |  |  | CDC | 243 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D22/11/100/I_T |  |  |  | CDC | 244 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D22/11/200/I_R |  |  |  | CDC | 245 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D22/11/200/I_S |  |  |  | CDC | 246 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-E7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D22/11/200/I_T |  |  |  | CDC | 247 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _300 | 300 |  | I_R | [17 empty] | 2-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_300_A1 | 11KV 300 R相AMP | TIE | D22/11/300/I_R |  |  |  | CDC | 248 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _300 | 300 |  | I_S | [17 empty] | 2-90 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_300_A2 | 11KV 300 S相AMP | TIE | D22/11/300/I_S |  |  |  | CDC | 249 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _300 | 300 |  | I_T | [17 empty] | 2-91 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_300_A3 | 11KV 300 T相AMP | TIE | D22/11/300/I_T |  |  |  | CDC | 250 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _400 | 400 |  | I_R | [17 empty] | 2-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | D22/11/400/I_R |  |  |  | CDC | 251 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _400 | 400 |  | I_S | [17 empty] | 2-B8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | D22/11/400/I_S |  |  |  | CDC | 252 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | _400 | 400 |  | I_T | [17 empty] | 2-B9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | D22/11/400/I_T |  |  |  | CDC | 253 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  |  |  |  | DCV_N | [17 empty] | 2-FB | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D22/0/StaDev/DCV_N |  |  |  | CDC | 254 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D22 | 四湖DS | 0 |  |  |  |  | DCV_P | [17 empty] | 2-FA | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D22/0/StaDev/DCV_P |  |  |  | CDC | 255 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A3 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D22/11/310/KW |  |  |  | CDC | 256 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-A4 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D22/11/310/KVAR |  |  |  | CDC | 257 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-A5 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D22/11/310/I_R |  |  |  | CDC | 258 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-A6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D22/11/310/I_S |  |  |  | CDC | 259 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-A7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D22/11/310/I_T |  |  |  | CDC | 260 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-93 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR_OIL | #1DTR 油溫 | MTR | D22//1DTR/OilTemp |  |  |  | CDC | 261 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-94 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D22//1DTR(A)/CoilTemp |  |  |  | CDC | 262 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-96 |  | 1-4F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D22//1DTR(A)/TapPosMv |  |  |  | CDC | 263 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-C7 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D22/11/320/KW |  |  |  | CDC | 264 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-C8 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D22/11/320/KVAR |  |  |  | CDC | 265 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-C9 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D22/11/320/I_R |  |  |  | CDC | 266 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-CA | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D22/11/320/I_S |  |  |  | CDC | 267 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-CB | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D22/11/320/I_T |  |  |  | CDC | 268 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-95 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D22//1DTR(B)/CoilTemp |  |  |  | CDC | 269 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-97 |  | 1-51 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D22//1DTR(B)/TapPosMv |  |  |  | CDC | 270 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-FE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D22/11/330A2/KW |  |  |  | CDC | 271 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-FF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D22/11/330A2/KVAR |  |  |  | CDC | 272 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D22/11/330A2/I_R |  |  |  | CDC | 273 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D22/11/330A2/I_S |  |  |  | CDC | 274 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D22/11/330A2/I_T |  |  |  | CDC | 275 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-98 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR_OIL | #2DTR 油溫 | MTR | D22//2DTR/OilTemp |  |  |  | CDC | 276 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D22//2DTR(A)/CoilTemp |  |  |  | CDC | 277 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9B |  | 1-53 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D22//2DTR(A)/TapPosMv |  |  |  | CDC | 278 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-A3 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D22/11/340B2/KW |  |  |  | CDC | 279 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-A4 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D22/11/340B2/KVAR |  |  |  | CDC | 280 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-A5 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D22/11/340B2/I_R |  |  |  | CDC | 281 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-A6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D22/11/340B2/I_S |  |  |  | CDC | 282 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-A7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D22/11/340B2/I_T |  |  |  | CDC | 283 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-9A | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D22//2DTR(B)/CoilTemp |  |  |  | CDC | 284 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9C |  | 1-55 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D22//2DTR(B)/TapPosMv |  |  |  | CDC | 285 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1530_MW | 湖風四湖線 MW | LINE161 | D22/161/1530/MW |  |  |  | CDC | 286 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 四湖DS.1530_MVAR | 湖風四湖線 MVAR | LINE161 | D22/161/1530/MVAR |  |  |  | CDC | 287 | GENERICAIPoint | DS039_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | MW | [17 empty] | 2-FC | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 湖風GS.1530_MW | 湖風四湖線 MW | LINE161 | W01/161/1530/MW |  |  |  | CDC | 288 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | MVAR | [17 empty] | 2-FD | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 湖風GS.1530_MVAR | 湖風四湖線 MVAR | LINE161 | W01/161/1530/MVAR |  |  |  | CDC | 289 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1530LPD | 湖風四湖線(1530) |  | V | [17 empty] | 2-FE | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 湖風GS.1530LPD_KV | 湖風四湖線(1530) LPD KV | LINE161 | D22/161/1530/V |  |  |  | CDC | 290 | GENERICAIPoint | DS039_L2 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D22 | 四湖DS | 11 | 11kV | 博斯線 | 博斯線 |  | 博斯線KVAR | [17 empty] | 3-87 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線KVAR | 11KV博斯線 KVAR | FEEDER |  |  |  |  | CDC | 291 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 6.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 博斯線 | 博斯線 |  | 博斯線A1 | [17 empty] | 3-80 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線A1 | 11KV博斯線 R相AMP | FEEDER |  |  |  |  | CDC | 292 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 博斯線 | 博斯線 |  | 博斯線A2 | [17 empty] | 3-81 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線A2 | 11KV博斯線 S相AMP | FEEDER |  |  |  |  | CDC | 293 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 博斯線 | 博斯線 |  | 博斯線A3 | [17 empty] | 3-82 | [5 empty] | A_-300_300(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線A3 | 11KV博斯線 T相AMP | FEEDER |  |  |  |  | CDC | 294 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 博斯線_KV | 博斯線 |  | R | [17 empty] | 3-83 | [5 empty] | kV_-15_15(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線_KV_R | 11KV博斯線 R | OTHER |  |  |  |  | CDC | 295 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 1.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 博斯線_KV | 博斯線 |  | S | [17 empty] | 3-84 | [5 empty] | kV_-15_15(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線_KV_S | 11KV博斯線 S | OTHER |  |  |  |  | CDC | 296 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 1.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 博斯線_KV | 博斯線 |  | T | [17 empty] | 3-85 | [5 empty] | kV_-15_15(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線_KV_T | 11KV博斯線 T | OTHER |  |  |  |  | CDC | 297 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 1.000000 | 1.500000
D22 | 四湖DS | 0 |  | 博斯線 | 博斯線 |  | KW | [17 empty] | 3-86 | [5 empty] | kW_-9000_9000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.博斯線_KW | 11KV博斯線 | OTHER |  |  |  |  | CDC | 298 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 6.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 速力線 | 速力線 |  | 速力線KVAR | [17 empty] | 3-8F | [5 empty] | KVAR_-12000_12000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線KVAR | 11KV速力線 KVAR | FEEDER |  |  |  |  | CDC | 299 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 6.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 速力線 | 速力線 |  | 速力線A1 | [17 empty] | 3-88 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線A1 | 11KV速力線 R相AMP | FEEDER |  |  |  |  | CDC | 300 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 速力線 | 速力線 |  | 速力線A2 | [17 empty] | 3-89 | [5 empty] | A_-400_400(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線A2 | 11KV速力線 S相AMP | FEEDER |  |  |  |  | CDC | 301 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 速力線 | 速力線 |  | 速力線A3 | [17 empty] | 3-8A | [5 empty] | A_-400_400(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線A3 | 11KV速力線 T相AMP | FEEDER |  |  |  |  | CDC | 302 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D22 | 四湖DS | 11 | 11kV | 速力線_KV | 速力線 |  | R | [17 empty] | 3-8B | [5 empty] | kV_-15_15(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線_KV_R | 11KV速力線 R | OTHER |  |  |  |  | CDC | 303 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 1.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 速力線_KV | 速力線 |  | S | [17 empty] | 3-8C | [5 empty] | kV_-15_15(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線_KV_S | 11KV速力線 S | OTHER |  |  |  |  | CDC | 304 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 1.000000 | 1.500000
D22 | 四湖DS | 11 | 11kV | 速力線_KV | 速力線 |  | T | [17 empty] | 3-8D | [5 empty] | kV_-15_15(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線_KV_T | 11KV速力線 T | OTHER |  |  |  |  | CDC | 305 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 1.000000 | 1.500000
D22 | 四湖DS | 0 |  | 速力線 | 速力線 |  | KW | [17 empty] | 3-8E | [5 empty] | kW_-12000_12000(-2000_2000) |  | DDCS1_2 | [8 empty] | 四湖DS.速力線_KW | 11KV速力線 | OTHER |  |  |  |  | CDC | 306 | GENERICAIPoint | DS039_L3 | CDC2_AI |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 6.000000 | 0.010000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1510_PHA | 北港四湖一路(1510) 相間RY | LINE161 | D22/161/1510/PHA |  |  |  | CDC | 307 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1510_GDA | 北港四湖一路(1510) 接地RY | LINE161 | D22/161/1510/GDA |  |  |  | CDC | 308 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.1510_CB | 1510(北港四湖一路) CB | LINE161 | D22/161/1510/CB |  |  |  | CDC | 309 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | 79UL | [17 empty] | 1-30-03 |  | 1-41 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1510_79UL | 北港四湖一路(1510) 79RY U/L | LINE161 | D22/161/1510/79UL |  |  |  | CDC | 310 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | DS1 | 1511 | [16 empty] | 1-36-04 | 1-36-05 | 1-5C | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1511_DS | 1511(北港四湖一路) DS | LINE161 | D22/161/1510/DS1 |  |  |  | CDC | 311 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | DS2 | 1512 | [16 empty] | 1-36-06 | 1-36-07 | 1-5D | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1512_DS | 1512(北港四湖一路) DS | LINE161 | D22/161/1510/DS2 |  |  |  | CDC | 312 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | DS3 | 1513 | [16 empty] | 1-36-08 | 1-36-09 | 1-5E | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1513_DS | 1513(北港四湖一路) DS | LINE161 | D22/161/1510/DS3 |  |  |  | CDC | 313 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | E3 | 1513E | [16 empty] | 1-36-10 | 1-36-11 | 1-5F | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1513E_ES | 1513E(北港四湖一路) ES | LINE161 | D22/161/1510/ES3 |  |  |  | CDC | 314 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1520_PHA | 北港四湖二路(1520) 相間RY | LINE161 | D22/161/1520/PHA |  |  |  | CDC | 315 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1520_GDA | 北港四湖二路(1520) 接地RY | LINE161 | D22/161/1520/GDA |  |  |  | CDC | 316 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.1520_CB | 1520(北港四湖二路) CB | LINE161 | D22/161/1520/CB |  |  |  | CDC | 317 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | 79UL | [17 empty] | 1-30-05 |  | 1-43 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1520_79UL | 北港四湖二路(1520) 79RY U/L | LINE161 | D22/161/1520/79UL |  |  |  | CDC | 318 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | DS1 | 1521 | [16 empty] | 1-36-12 | 1-36-13 | 1-60 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1521_DS | 1521(北港四湖二路) DS | LINE161 | D22/161/1520/DS1 |  |  |  | CDC | 319 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | DS2 | 1522 | [16 empty] | 1-36-14 | 1-36-15 | 1-61 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1522_DS | 1522(北港四湖二路) DS | LINE161 | D22/161/1520/DS2 |  |  |  | CDC | 320 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | DS3 | 1523 | [16 empty] | 1-37-00 | 1-37-01 | 1-62 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1523_DS | 1523(北港四湖二路) DS | LINE161 | D22/161/1520/DS3 |  |  |  | CDC | 321 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | E3 | 1523E | [16 empty] | 1-37-02 | 1-37-03 | 1-63 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1523E_ES | 1523E(北港四湖二路) ES | LINE161 | D22/161/1520/ES3 |  |  |  | CDC | 322 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | PHA | [17 empty] | 1-10-04 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_PHA | 11KV飛一線(XQ21) 相間RY | FEEDER | D22/11/XQ21/PHA |  |  |  | CDC | 323 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) |  | GDA | [17 empty] | 1-10-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_GDA | 11KV飛一線(XQ21) 接地RY | FEEDER | D22/11/XQ21/GDA |  |  |  | CDC | 324 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ21 | 飛一線(XQ21) 79RY |  | 79UL | [17 empty] | 2-38-02 |  | 2-02 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_79UL | 11KV飛一線(XQ21) 79RY U/L | FEEDER | D22/11/XQ21/79UL |  |  |  | CDC | 325 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ21_LCO | 飛一線(XQ21) LCO |  | TapPosMv | [17 empty] | 2-38-03 |  | 2-03 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_LCO_TAP | 11KV飛一線(XQ21) LCO TAP | FEEDER | D22/11/XQ21/ADJ |  |  |  | CDC | 326 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ21 | XQ21(11KV飛一線) |  | CB | [17 empty] | 1-10-03 |  | 1-0E | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_CB | XQ21(11KV飛一線) CB | FEEDER | D22/11/XQ21/CB |  |  |  | CDC | 327 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_PHA | 11KV飛二線(XQ22) 相間RY | FEEDER | D22/11/XQ22/PHA |  |  |  | CDC | 328 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_GDA | 11KV飛二線(XQ22) 接地RY | FEEDER | D22/11/XQ22/GDA |  |  |  | CDC | 329 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ22 | 飛二線(XQ22) 79RY |  | 79UL | [17 empty] | 2-38-04 |  | 2-04 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_79UL | 11KV飛二線(XQ22) 79RY U/L | FEEDER | D22/11/XQ22/79UL |  |  |  | CDC | 330 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ22_LCO | 飛二線(XQ22) LCO |  | TapPosMv | [17 empty] | 2-38-05 |  | 2-05 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_LCO_TAP | 11KV飛二線(XQ22) LCO TAP | FEEDER | D22/11/XQ22/ADJ |  |  |  | CDC | 331 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ22 | XQ22(11KV飛二線) |  | CB | [17 empty] | 1-10-06 |  | 1-0F | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_CB | XQ22(11KV飛二線) CB | FEEDER | D22/11/XQ22/CB |  |  |  | CDC | 332 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_PHA | 11KV飛三線(XQ23) 相間RY | FEEDER | D22/11/XQ23/PHA |  |  |  | CDC | 333 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_GDA | 11KV飛三線(XQ23) 接地RY | FEEDER | D22/11/XQ23/GDA |  |  |  | CDC | 334 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ23 | 飛三線(XQ23) 79RY |  | 79UL | [17 empty] | 2-38-06 |  | 2-06 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_79UL | 11KV飛三線(XQ23) 79RY U/L | FEEDER | D22/11/XQ23/79UL |  |  |  | CDC | 335 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ23_LCO | 飛三線(XQ23) LCO |  | TapPosMv | [17 empty] | 2-38-07 |  | 2-07 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_LCO_TAP | 11KV飛三線(XQ23) LCO TAP | FEEDER | D22/11/XQ23/ADJ |  |  |  | CDC | 336 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ23 | XQ23(11KV飛三線) |  | CB | [17 empty] | 1-11-01 |  | 1-10 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_CB | XQ23(11KV飛三線) CB | FEEDER | D22/11/XQ23/CB |  |  |  | CDC | 337 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_PHA | 11KV飛四線(XQ24) 相間RY | FEEDER | D22/11/XQ24/PHA |  |  |  | CDC | 338 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_GDA | 11KV飛四線(XQ24) 接地RY | FEEDER | D22/11/XQ24/GDA |  |  |  | CDC | 339 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ24 | 飛四線(XQ24) 79RY |  | 79UL | [17 empty] | 2-38-08 |  | 2-08 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_79UL | 11KV飛四線(XQ24) 79RY U/L | FEEDER | D22/11/XQ24/79UL |  |  |  | CDC | 340 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ24_LCO | 飛四線(XQ24) LCO |  | TapPosMv | [17 empty] | 2-38-09 |  | 2-09 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_LCO_TAP | 11KV飛四線(XQ24) LCO TAP | FEEDER | D22/11/XQ24/ADJ |  |  |  | CDC | 341 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ24 | XQ24(11KV飛四線) |  | CB | [17 empty] | 1-11-04 |  | 1-11 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_CB | XQ24(11KV飛四線) CB | FEEDER | D22/11/XQ24/CB |  |  |  | CDC | 342 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | PHA | [17 empty] | 1-12-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_PHA | 11KV飛五線(XQ25) 相間RY | FEEDER | D22/11/XQ25/PHA |  |  |  | CDC | 343 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) |  | GDA | [17 empty] | 1-12-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_GDA | 11KV飛五線(XQ25) 接地RY | FEEDER | D22/11/XQ25/GDA |  |  |  | CDC | 344 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ25 | 飛五線(XQ25) 79RY |  | 79UL | [17 empty] | 2-38-10 |  | 2-0A | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_79UL | 11KV飛五線(XQ25) 79RY U/L | FEEDER | D22/11/XQ25/79UL |  |  |  | CDC | 345 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ25_LCO | 飛五線(XQ25) LCO |  | TapPosMv | [17 empty] | 2-38-11 |  | 2-0B | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_LCO_TAP | 11KV飛五線(XQ25) LCO TAP | FEEDER | D22/11/XQ25/ADJ |  |  |  | CDC | 346 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ25 | XQ25(11KV飛五線) |  | CB | [17 empty] | 1-11-07 |  | 1-12 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_CB | XQ25(11KV飛五線) CB | FEEDER | D22/11/XQ25/CB |  |  |  | CDC | 347 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_PHA | 11KV飛六線(XQ26) 相間RY | FEEDER | D22/11/XQ26/PHA |  |  |  | CDC | 348 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_GDA | 11KV飛六線(XQ26) 接地RY | FEEDER | D22/11/XQ26/GDA |  |  |  | CDC | 349 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ26 | 飛六線(XQ26) 79RY |  | 79UL | [17 empty] | 2-38-14 |  | 2-0E | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_79UL | 11KV飛六線(XQ26) 79RY U/L | FEEDER | D22/11/XQ26/79UL |  |  |  | CDC | 350 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ26_LCO | 飛六線(XQ26) LCO |  | TapPosMv | [17 empty] | 2-38-15 |  | 2-0F | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_LCO_TAP | 11KV飛六線(XQ26) LCO TAP | FEEDER | D22/11/XQ26/ADJ |  |  |  | CDC | 351 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ26 | XQ26(11KV飛六線) |  | CB | [17 empty] | 1-13-03 |  | 1-17 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_CB | XQ26(11KV飛六線) CB | FEEDER | D22/11/XQ26/CB |  |  |  | CDC | 352 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | PHA | [17 empty] | 1-13-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_PHA | 11KV飛七線(XQ27) 相間RY | FEEDER | D22/11/XQ27/PHA |  |  |  | CDC | 353 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) |  | GDA | [17 empty] | 1-14-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_GDA | 11KV飛七線(XQ27) 接地RY | FEEDER | D22/11/XQ27/GDA |  |  |  | CDC | 354 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ27 | 飛七線(XQ27) 79RY |  | 79UL | [17 empty] | 2-39-00 |  | 2-10 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_79UL | 11KV飛七線(XQ27) 79RY U/L | FEEDER | D22/11/XQ27/79UL |  |  |  | CDC | 355 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ27_LCO | 飛七線(XQ27) LCO |  | TapPosMv | [17 empty] | 2-39-01 |  | 2-11 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_LCO_TAP | 11KV飛七線(XQ27) LCO TAP | FEEDER | D22/11/XQ27/ADJ |  |  |  | CDC | 356 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ27 | XQ27(11KV飛七線) |  | CB | [17 empty] | 1-13-06 |  | 1-18 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_CB | XQ27(11KV飛七線) CB | FEEDER | D22/11/XQ27/CB |  |  |  | CDC | 357 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | PHA | [17 empty] | 1-14-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_PHA | 11KV飛八線(XQ28) 相間RY | FEEDER | D22/11/XQ28/PHA |  |  |  | CDC | 358 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) |  | GDA | [17 empty] | 1-14-03 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_GDA | 11KV飛八線(XQ28) 接地RY | FEEDER | D22/11/XQ28/GDA |  |  |  | CDC | 359 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ28 | 飛八線(XQ28) 79RY |  | 79UL | [17 empty] | 2-39-02 |  | 2-12 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_79UL | 11KV飛八線(XQ28) 79RY U/L | FEEDER | D22/11/XQ28/79UL |  |  |  | CDC | 360 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ28_LCO | 飛八線(XQ28) LCO |  | TapPosMv | [17 empty] | 2-39-03 |  | 2-13 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_LCO_TAP | 11KV飛八線(XQ28) LCO TAP | FEEDER | D22/11/XQ28/ADJ |  |  |  | CDC | 361 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ28 | XQ28(11KV飛八線) |  | CB | [17 empty] | 1-14-01 |  | 1-19 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_CB | XQ28(11KV飛八線) CB | FEEDER | D22/11/XQ28/CB |  |  |  | CDC | 362 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | PHA | [17 empty] | 1-14-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_PHA | 11KV飛九線(XQ29) 相間RY | FEEDER | D22/11/XQ29/PHA |  |  |  | CDC | 363 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) |  | GDA | [17 empty] | 1-14-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_GDA | 11KV飛九線(XQ29) 接地RY | FEEDER | D22/11/XQ29/GDA |  |  |  | CDC | 364 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ29 | 飛九線(XQ29) 79RY |  | 79UL | [17 empty] | 2-39-04 |  | 2-14 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_79UL | 11KV飛九線(XQ29) 79RY U/L | FEEDER | D22/11/XQ29/79UL |  |  |  | CDC | 365 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ29_LCO | 飛九線(XQ29) LCO |  | TapPosMv | [17 empty] | 2-39-05 |  | 2-15 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_LCO_TAP | 11KV飛九線(XQ29) LCO TAP | FEEDER | D22/11/XQ29/ADJ |  |  |  | CDC | 366 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ29 | XQ29(11KV飛九線) |  | CB | [17 empty] | 1-14-04 |  | 1-1A | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_CB | XQ29(11KV飛九線) CB | FEEDER | D22/11/XQ29/CB |  |  |  | CDC | 367 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | PHA | [17 empty] | 1-15-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_PHA | 11KV飛十線(XQ30) 相間RY | FEEDER | D22/11/XQ30/PHA |  |  |  | CDC | 368 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) |  | GDA | [17 empty] | 1-15-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_GDA | 11KV飛十線(XQ30) 接地RY | FEEDER | D22/11/XQ30/GDA |  |  |  | CDC | 369 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ30 | 飛十線(XQ30) 79RY |  | 79UL | [17 empty] | 2-39-06 |  | 2-16 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_79UL | 11KV飛十線(XQ30) 79RY U/L | FEEDER | D22/11/XQ30/79UL |  |  |  | CDC | 370 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ30_LCO | 飛十線(XQ30) LCO |  | TapPosMv | [17 empty] | 2-39-07 |  | 2-17 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_LCO_TAP | 11KV飛十線(XQ30) LCO TAP | FEEDER | D22/11/XQ30/ADJ |  |  |  | CDC | 371 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ30 | XQ30(11KV飛十線) |  | CB | [17 empty] | 1-14-07 |  | 1-1B | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_CB | XQ30(11KV飛十線) CB | FEEDER | D22/11/XQ30/CB |  |  |  | CDC | 372 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_PHA | 11KV飛十一線(XQ31) 相間RY | FEEDER | D22/11/XQ31/PHA |  |  |  | CDC | 373 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_GDA | 11KV飛十一線(XQ31) 接地RY | FEEDER | D22/11/XQ31/GDA |  |  |  | CDC | 374 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ31 | 飛十一線(XQ31) 79RY |  | 79UL | [17 empty] | 2-39-08 |  | 2-18 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_79UL | 11KV飛十一線(XQ31) 79RY U/L | FEEDER | D22/11/XQ31/79UL |  |  |  | CDC | 375 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ31_LCO | 飛十一線(XQ31) LCO |  | TapPosMv | [17 empty] | 2-39-09 |  | 2-19 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_LCO_TAP | 11KV飛十一線(XQ31) LCO TAP | FEEDER | D22/11/XQ31/ADJ |  |  |  | CDC | 376 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ31 | XQ31(11KV飛十一線) |  | CB | [17 empty] | 1-15-05 |  | 1-1D | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_CB | XQ31(11KV飛十一線) CB | FEEDER | D22/11/XQ31/CB |  |  |  | CDC | 377 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | PHA | [17 empty] | 1-16-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_PHA | 11KV飛十二線(XQ32) 相間RY | FEEDER | D22/11/XQ32/PHA |  |  |  | CDC | 378 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) |  | GDA | [17 empty] | 1-16-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_GDA | 11KV飛十二線(XQ32) 接地RY | FEEDER | D22/11/XQ32/GDA |  |  |  | CDC | 379 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ32 | 飛十二線(XQ32) 79RY |  | 79UL | [17 empty] | 2-39-10 |  | 2-1A | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_79UL | 11KV飛十二線(XQ32) 79RY U/L | FEEDER | D22/11/XQ32/79UL |  |  |  | CDC | 380 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ32_LCO | 飛十二線(XQ32) LCO |  | TapPosMv | [17 empty] | 2-39-11 |  | 2-1B | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_LCO_TAP | 11KV飛十二線(XQ32) LCO TAP | FEEDER | D22/11/XQ32/ADJ |  |  |  | CDC | 381 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ32 | XQ32(11KV飛十二線) |  | CB | [17 empty] | 1-16-00 |  | 1-1E | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_CB | XQ32(11KV飛十二線) CB | FEEDER | D22/11/XQ32/CB |  |  |  | CDC | 382 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | PHA | [17 empty] | 1-16-04 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_PHA | 11KV飛十三線(XQ33) 相間RY | FEEDER | D22/11/XQ33/PHA |  |  |  | CDC | 383 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) |  | GDA | [17 empty] | 1-16-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_GDA | 11KV飛十三線(XQ33) 接地RY | FEEDER | D22/11/XQ33/GDA |  |  |  | CDC | 384 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ33 | 飛十三線(XQ33) 79RY |  | 79UL | [17 empty] | 2-39-12 |  | 2-1C | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_79UL | 11KV飛十三線(XQ33) 79RY U/L | FEEDER | D22/11/XQ33/79UL |  |  |  | CDC | 385 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ33_LCO | 飛十三線(XQ33) LCO |  | TapPosMv | [17 empty] | 2-39-13 |  | 2-1D | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_LCO_TAP | 11KV飛十三線(XQ33) LCO TAP | FEEDER | D22/11/XQ33/ADJ |  |  |  | CDC | 386 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ33 | XQ33(11KV飛十三線) |  | CB | [17 empty] | 1-16-03 |  | 1-1F | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_CB | XQ33(11KV飛十三線) CB | FEEDER | D22/11/XQ33/CB |  |  |  | CDC | 387 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | PHA | [17 empty] | 1-17-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_PHA | 11KV飛十四線(XQ34) 相間RY | FEEDER | D22/11/XQ34/PHA |  |  |  | CDC | 388 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) |  | GDA | [17 empty] | 1-17-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_GDA | 11KV飛十四線(XQ34) 接地RY | FEEDER | D22/11/XQ34/GDA |  |  |  | CDC | 389 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ34 | 飛十四線(XQ34) 79RY |  | 79UL | [17 empty] | 2-3A-00 |  | 2-20 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_79UL | 11KV飛十四線(XQ34) 79RY U/L | FEEDER | D22/11/XQ34/79UL |  |  |  | CDC | 390 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ34_LCO | 飛十四線(XQ34) LCO |  | TapPosMv | [17 empty] | 2-3A-01 |  | 2-21 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_LCO_TAP | 11KV飛十四線(XQ34) LCO TAP | FEEDER | D22/11/XQ34/ADJ |  |  |  | CDC | 391 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ34 | XQ34(11KV飛十四線) |  | CB | [17 empty] | 1-17-04 |  | 1-24 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_CB | XQ34(11KV飛十四線) CB | FEEDER | D22/11/XQ34/CB |  |  |  | CDC | 392 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | PHA | [17 empty] | 1-18-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_PHA | 11KV飛十五線(XQ35) 相間RY | FEEDER | D22/11/XQ35/PHA |  |  |  | CDC | 393 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) |  | GDA | [17 empty] | 1-18-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_GDA | 11KV飛十五線(XQ35) 接地RY | FEEDER | D22/11/XQ35/GDA |  |  |  | CDC | 394 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ35 | 飛十五線(XQ35) 79RY |  | 79UL | [17 empty] | 2-3A-02 |  | 2-22 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_79UL | 11KV飛十五線(XQ35) 79RY U/L | FEEDER | D22/11/XQ35/79UL |  |  |  | CDC | 395 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ35_LCO | 飛十五線(XQ35) LCO |  | TapPosMv | [17 empty] | 2-3A-03 |  | 2-23 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_LCO_TAP | 11KV飛十五線(XQ35) LCO TAP | FEEDER | D22/11/XQ35/ADJ |  |  |  | CDC | 396 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ35 | XQ35(11KV飛十五線) |  | CB | [17 empty] | 1-17-07 |  | 1-25 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_CB | XQ35(11KV飛十五線) CB | FEEDER | D22/11/XQ35/CB |  |  |  | CDC | 397 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_PHA | 11KV飛十六線(XQ36) 相間RY | FEEDER | D22/11/XQ36/PHA |  |  |  | CDC | 398 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_GDA | 11KV飛十六線(XQ36) 接地RY | FEEDER | D22/11/XQ36/GDA |  |  |  | CDC | 399 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ36 | 飛十六線(XQ36) 79RY |  | 79UL | [17 empty] | 2-3A-04 |  | 2-24 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_79UL | 11KV飛十六線(XQ36) 79RY U/L | FEEDER | D22/11/XQ36/79UL |  |  |  | CDC | 400 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ36_LCO | 飛十六線(XQ36) LCO |  | TapPosMv | [17 empty] | 2-3A-05 |  | 2-25 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_LCO_TAP | 11KV飛十六線(XQ36) LCO TAP | FEEDER | D22/11/XQ36/ADJ |  |  |  | CDC | 401 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ36 | XQ36(11KV飛十六線) |  | CB | [17 empty] | 1-18-05 |  | 1-27 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_CB | XQ36(11KV飛十六線) CB | FEEDER | D22/11/XQ36/CB |  |  |  | CDC | 402 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | PHA | [17 empty] | 1-19-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_PHA | 11KV飛十七線(XQ37) 相間RY | FEEDER | D22/11/XQ37/PHA |  |  |  | CDC | 403 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) |  | GDA | [17 empty] | 1-19-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_GDA | 11KV飛十七線(XQ37) 接地RY | FEEDER | D22/11/XQ37/GDA |  |  |  | CDC | 404 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ37 | 飛十七線(XQ37) 79RY |  | 79UL | [17 empty] | 2-3A-06 |  | 2-26 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_79UL | 11KV飛十七線(XQ37) 79RY U/L | FEEDER | D22/11/XQ37/79UL |  |  |  | CDC | 405 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ37_LCO | 飛十七線(XQ37) LCO |  | TapPosMv | [17 empty] | 2-3A-07 |  | 2-27 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_LCO_TAP | 11KV飛十七線(XQ37) LCO TAP | FEEDER | D22/11/XQ37/ADJ |  |  |  | CDC | 406 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ37 | XQ37(11KV飛十七線) |  | CB | [17 empty] | 1-19-00 |  | 1-28 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_CB | XQ37(11KV飛十七線) CB | FEEDER | D22/11/XQ37/CB |  |  |  | CDC | 407 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | PHA | [17 empty] | 1-19-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_PHA | 11KV飛十八線(XQ38) 相間RY | FEEDER | D22/11/XQ38/PHA |  |  |  | CDC | 408 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) |  | GDA | [17 empty] | 1-1A-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_GDA | 11KV飛十八線(XQ38) 接地RY | FEEDER | D22/11/XQ38/GDA |  |  |  | CDC | 409 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ38 | 飛十八線(XQ38) 79RY |  | 79UL | [17 empty] | 2-3A-10 |  | 2-2A | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_79UL | 11KV飛十八線(XQ38) 79RY U/L | FEEDER | D22/11/XQ38/79UL |  |  |  | CDC | 410 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ38_LCO | 飛十八線(XQ38) LCO |  | TapPosMv | [17 empty] | 2-3A-11 |  | 2-2B | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_LCO_TAP | 11KV飛十八線(XQ38) LCO TAP | FEEDER | D22/11/XQ38/ADJ |  |  |  | CDC | 411 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ38 | XQ38(11KV飛十八線) |  | CB | [17 empty] | 1-19-06 |  | 1-2C | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_CB | XQ38(11KV飛十八線) CB | FEEDER | D22/11/XQ38/CB |  |  |  | CDC | 412 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | PHA | [17 empty] | 1-1A-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_PHA | 11KV飛十九線(XQ39) 相間RY | FEEDER | D22/11/XQ39/PHA |  |  |  | CDC | 413 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) |  | GDA | [17 empty] | 1-1A-03 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_GDA | 11KV飛十九線(XQ39) 接地RY | FEEDER | D22/11/XQ39/GDA |  |  |  | CDC | 414 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ39 | 飛十九線(XQ39) 79RY |  | 79UL | [17 empty] | 2-3A-12 |  | 2-2C | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_79UL | 11KV飛十九線(XQ39) 79RY U/L | FEEDER | D22/11/XQ39/79UL |  |  |  | CDC | 415 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ39_LCO | 飛十九線(XQ39) LCO |  | TapPosMv | [17 empty] | 2-3A-13 |  | 2-2D | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_LCO_TAP | 11KV飛十九線(XQ39) LCO TAP | FEEDER | D22/11/XQ39/ADJ |  |  |  | CDC | 416 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ39 | XQ39(11KV飛十九線) |  | CB | [17 empty] | 1-1A-01 |  | 1-2D | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_CB | XQ39(11KV飛十九線) CB | FEEDER | D22/11/XQ39/CB |  |  |  | CDC | 417 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | PHA | [17 empty] | 1-1A-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_PHA | 11KV飛二十線(XQ40) 相間RY | FEEDER | D22/11/XQ40/PHA |  |  |  | CDC | 418 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) |  | GDA | [17 empty] | 1-1A-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_GDA | 11KV飛二十線(XQ40) 接地RY | FEEDER | D22/11/XQ40/GDA |  |  |  | CDC | 419 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | XQ40 | 飛二十線(XQ40) 79RY |  | 79UL | [17 empty] | 2-3A-14 |  | 2-2E | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_79UL | 11KV飛二十線(XQ40) 79RY U/L | FEEDER | D22/11/XQ40/79UL |  |  |  | CDC | 420 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV | XQ40_LCO | 飛二十線(XQ40) LCO |  | TapPosMv | [17 empty] | 2-3A-15 |  | 2-2F | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_LCO_TAP | 11KV飛二十線(XQ40) LCO TAP | FEEDER | D22/11/XQ40/ADJ |  |  |  | CDC | 421 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D22 | 四湖DS | 11 | 11kV | XQ40 | XQ40(11KV飛二十線) |  | CB | [17 empty] | 1-1A-04 |  | 1-2E | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_CB | XQ40(11KV飛二十線) CB | FEEDER | D22/11/XQ40/CB |  |  |  | CDC | 422 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-12-02 |  | 1-13 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.100_CB | 100(TIE) CB | TIE | D22/11/100/CB |  |  |  | CDC | 423 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-12-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.100_51A | 11KV TIE(100) 51RY | TIE | D22/11/100/PHA |  |  |  | CDC | 424 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-12-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D22/11/100/GDA |  |  |  | CDC | 425 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-04-04 |  | 1-08 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.1500_CB | 1500(TIE) CB | TIE | D22/161/1500/CB |  |  |  | CDC | 426 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-04-05 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D22/161/1500/50A |  |  |  | CDC | 427 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-36-00 | 1-36-01 | 1-5A | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1501_DS | 1501(TIE) DS | TIE | D22/161/1500/DS1 |  |  |  | CDC | 428 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-36-02 | 1-36-03 | 1-5B | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1502_DS | 1502(TIE) DS | TIE | D22/161/1500/DS2 |  |  |  | CDC | 429 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-15-02 |  | 1-1C | [5 empty] | ADCS_N | [8 empty] | 四湖DS.200_CB | 200(TIE) CB | TIE | D22/11/200/CB |  |  |  | CDC | 430 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-15-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.200_51A | 11KV TIE(200) 51RY | TIE | D22/11/200/PHA |  |  |  | CDC | 431 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-15-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D22/11/200/GDA |  |  |  | CDC | 432 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 1-18-02 |  | 1-26 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.300_CB | 300(TIE) CB | TIE | D22/11/300/CB |  |  |  | CDC | 433 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 1-18-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.300_51A | 11KV TIE(300) 51RY | TIE | D22/11/300/PHA |  |  |  | CDC | 434 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 1-18-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.300_51NA | 11KV TIE(300) 51N RY | TIE | D22/11/300/GDA |  |  |  | CDC | 435 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 1-1A-07 |  | 1-2F | [5 empty] | ADCS_N | [8 empty] | 四湖DS.400_CB | 400(TIE) CB | TIE | D22/11/400/CB |  |  |  | CDC | 436 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 1-1B-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.400_51A | 11KV TIE(400) 51RY | TIE | D22/11/400/PHA |  |  |  | CDC | 437 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 1-1B-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.400_51NA | 11KV TIE(400) 51N RY | TIE | D22/11/400/GDA |  |  |  | CDC | 438 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-12-05 |  | 1-14 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.390_CB | 390(#1SSTR) CB | OTHER | D22/11/390/CB |  |  |  | CDC | 439 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-12-06 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D22/11/390/PHA |  |  |  | CDC | 440 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-12-07 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D22/11/390/GDA |  |  |  | CDC | 441 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-17-01 |  | 1-23 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.490_CB | 490(#2SSTR) CB | OTHER | D22/11/490/CB |  |  |  | CDC | 442 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-17-02 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D22/11/490/PHA |  |  |  | CDC | 443 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-17-03 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D22/11/490/GDA |  |  |  | CDC | 444 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-05-02 |  | 1-09 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.1750_CB | 1750(#1DTR) CB | MTR | D22/161/1750/CB |  |  |  | CDC | 445 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-06-02 |  | 1-0C | [5 empty] | ADCS_N | [8 empty] | 四湖DS.310_CB | 310(#1DTR) CB | MTR | D22/11/310/CB |  |  |  | CDC | 446 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-06-05 |  | 1-15 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.320_CB | 320(#1DTR) CB | MTR | D22/11/320/CB |  |  |  | CDC | 447 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.310_51A | #1DTR二次側(310) 51RY | MTR | D22/11/310/2_PHA |  |  |  | CDC | 448 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-06-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.320_51A | #1DTR二次側(320) 51RY | MTR | D22/11/320/2_PHA |  |  |  | CDC | 449 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-39-12 | 1-39-13 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1751_DS | 1751(#1DTR) DS | MTR | D22/161/1750/DS1 |  |  |  | CDC | 450 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-39-14 | 1-39-15 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1752_DS | 1752(#1DTR) DS | MTR | D22/161/1750/DS2 |  |  |  | CDC | 451 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-07-00 |  | 1-0A | [5 empty] | 161KV_N | [8 empty] | 四湖DS.1760_CB | 1760(#2DTR) CB | MTR | D22/161/1760/CB |  |  |  | CDC | 452 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-7A | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1761_DS | 1761(#2DTR) DS | MTR | D22/161/1760/DS1 |  |  |  | CDC | 453 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-7B | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1762_DS | 1762(#2DTR) DS | MTR | D22/161/1760/DS2 |  |  |  | CDC | 454 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-10-00 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 四湖DS.210_CB | 210(11KV #1SC) CB | SC | D22/11/210/CB |  |  |  | CDC | 455 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-38-00 |  | 2-00 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | D22/11/210/SC_A_M |  |  |  | CDC | 456 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-10-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.210_SCA | 11KV #1SC 51,51N RY | SC | D22/11/210/SCA |  |  |  | CDC | 457 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-10-02 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D22/11/210/UVA |  |  |  | CDC | 458 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 210 | #1SC(210) |  | LBS | [17 empty] | 2-30-00 | 2-30-01 | 2-4A | [5 empty] | ADCS_N | [8 empty] | 四湖DS.210_LBS | 210(11KV #1SC) LBS | SC | D22/11/1ASC/LBS |  |  |  | CDC | 459 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 210_LBS | #1SC |  | SC_A_M | [17 empty] | 2-38-01 |  | 2-01 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.210_LBS_A/M | 11KV #1SC LBS 乏控器 A/M | SC | D22/11/210/1A5A_M |  |  |  | CDC | 460 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-13-00 |  | 1-16 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.220_CB | 220(11KV #2SC) CB | SC | D22/11/220/CB |  |  |  | CDC | 461 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-38-12 |  | 2-0C | [5 empty] | ADCS_N | [8 empty] | 四湖DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D22/11/220/SC_A_M |  |  |  | CDC | 462 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-13-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.220_SCA | 11KV #2SC 51,51N RY | SC | D22/11/220/SCA |  |  |  | CDC | 463 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-13-02 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D22/11/220/UVA |  |  |  | CDC | 464 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 2-30-02 | 2-30-03 | 2-4B | [5 empty] | ADCS_N | [8 empty] | 四湖DS.220_LBS | 220(11KV #2SC) LBS | SC | D22/11/1BSC/LBS |  |  |  | CDC | 465 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 220_LBS | #2SC |  | SC_A_M | [17 empty] | 2-38-13 |  | 2-0D | [5 empty] | ADCS_N | [8 empty] | 四湖DS.220_LBS_A/M | 11KV #2SC LBS 乏控器 A/M | SC | D22/11/220/1A5A_M |  |  |  | CDC | 466 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-16-06 |  | 1-20 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.230_CB | 230(11KV #3SC) CB | SC | D22/11/230/CB |  |  |  | CDC | 467 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-39-14 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 四湖DS.230_A/M | 11KV #3SC 乏控器 A/M | SC | D22/11/230/SC_A_M |  |  |  | CDC | 468 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-16-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.230_SCA | 11KV #3SC 51,51N RY | SC | D22/11/230/SCA |  |  |  | CDC | 469 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-17-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D22/11/230/UVA |  |  |  | CDC | 470 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 230 | #3SC(230) |  | LBS | [17 empty] | 2-30-04 | 2-30-05 | 2-4C | [5 empty] | ADCS_N | [8 empty] | 四湖DS.230_LBS | 230(11KV #3SC) LBS | SC | D22/11/2ASC/LBS |  |  |  | CDC | 471 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 230_LBS | #3SC |  | SC_A_M | [17 empty] | 2-39-15 |  | 2-1F | [5 empty] | ADCS_N | [8 empty] | 四湖DS.230_LBS_A/M | 11KV #3SC LBS 乏控器 A/M | SC | D22/11/230/1A5A_M |  |  |  | CDC | 472 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-19-03 |  | 1-2B | [5 empty] | ADCS_N | [8 empty] | 四湖DS.240_CB | 240(11KV #4SC) CB | SC | D22/11/240/CB |  |  |  | CDC | 473 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-3A-08 |  | 2-28 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.240_A/M | 11KV #4SC 乏控器 A/M | SC | D22/11/240/SC_A_M |  |  |  | CDC | 474 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-19-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.240_SCA | 11KV #4SC 51,51N RY | SC | D22/11/240/SCA |  |  |  | CDC | 475 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-19-05 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D22/11/240/UVA |  |  |  | CDC | 476 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 2-30-06 | 2-30-07 | 2-4D | [5 empty] | ADCS_N | [8 empty] | 四湖DS.240_LBS | 240(11KV #4SC) LBS | SC | D22/11/2BSC/LBS |  |  |  | CDC | 477 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 240_LBS | #4SC |  | SC_A_M | [17 empty] | 2-3A-09 |  | 2-29 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.240_LBS_A/M | 11KV #4SC LBS 乏控器 A/M | SC | D22/11/240/1A5A_M |  |  |  | CDC | 478 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D22 | 四湖DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-34-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D22/161/1BUS/BUS_VUA |  |  |  | CDC | 479 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-04-06 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D22/161/1BUS/87A |  |  |  | CDC | 480 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-05 |  | 1-4C | [5 empty] | ADCS_N | [8 empty] | 四湖DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D22/161/1BUS/87UL |  |  |  | CDC | 481 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-34-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D22/161/2BUS/BUS_VUA |  |  |  | CDC | 482 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-04-07 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D22/161/2BUS/87A |  |  |  | CDC | 483 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-06 |  | 1-4D | [5 empty] | ADCS_N | [8 empty] | 四湖DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D22/161/2BUS/87UL |  |  |  | CDC | 484 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 11 | 11kV |  |  |  | CBA | [17 empty] | 2-3C-13 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.11KV_CBA | 11KV斷路器重故障 | OTHER | D22/0/ComPoint/CBA |  |  |  | CDC | 485 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV |  |  |  | CBF | [17 empty] | 2-3C-14 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.11KV_CBF | 11KV斷路器輕故障 | OTHER | D22/0/ComPoint/CBF |  |  |  | CDC | 486 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 11 | 11kV | _SC | SC |  | 60A | [17 empty] | 1-34-09 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.11KV_SC_60A | 11KV SC 60A | OTHER | D22/0/ComPoint/60A |  |  |  | CDC | 487 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-34-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D22/161/ComPoint/CBA |  |  |  | CDC | 488 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-34-02 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D22/161/ComPoint/CBF |  |  |  | CDC | 489 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-05-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D22/161/ComPoint/OSCA |  |  |  | CDC | 490 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-05-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D22/161/ComPoint/RCA |  |  |  | CDC | 491 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-34-10 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D22/0/ComPoint/COMT |  |  |  | CDC | 492 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D22/0/RTU/RTU_R_L |  |  |  | CDC | 493 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D22 | 四湖DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.TEST_CB | TEST CB | OTHER | D22/0/RTU/Test_CB |  |  |  | CDC | 494 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D22/0/StaDev/Fire1 |  |  |  | CDC | 495 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | SUBA | [17 empty] | 2-3C-12 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.其他重故障 | 變電所內其他重故障 | OTHER | D22/0/StaDev/PSA |  |  |  | CDC | 496 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | SUBF | [17 empty] | 2-3C-11 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.其他輕故障 | 變電所內其他輕故障 | OTHER | D22/0/StaDev/PSF |  |  |  | CDC | 497 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-33-14 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D22/0/StaDev/ACB1 |  |  |  | CDC | 498 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D22 | 四湖DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-33-15 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D22/0/StaDev/ACB2 |  |  |  | CDC | 499 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D22 | 四湖DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-34-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.所內電源ACBA | 所內電源故障警報 | OTHER | D22/0/StaDev/ACBA |  |  |  | CDC | 500 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | STUV | [17 empty] | 1-34-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D22/0/StaDev/STUV |  |  |  | CDC | 501 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D22/0/StaDev/CHG1 |  |  |  | CDC | 502 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | DCA | [17 empty] | 1-34-08 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.直流電源DCA | 直流電源故障警報 | OTHER | D22/0/StaDev/DCA |  |  |  | CDC | 503 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | DCE | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D22/0/StaDev/DCE |  |  |  | CDC | 504 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-34-12 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D22/0/StaDev/OilLeak1 |  |  |  | CDC | 505 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-3D-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D22/0/StaDev/CHG2 |  |  |  | CDC | 506 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | CommACF | [17 empty] | 2-3D-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D22/0/StaDev/CommACF |  |  |  | CDC | 507 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-33-08 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D22/0/StaDev/Burglar1 |  |  |  | CDC | 508 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-33-11 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | D22/0/StaDev/Door1 |  |  |  | CDC | 509 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-33-12 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | D22/0/StaDev/Door2 |  |  |  | CDC | 510 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-3C-08 |  | 2-48 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.開關場照明(A) | 開關場照明(A) | OTHER | D22/0/StaDev/Lights1 |  |  |  | CDC | 511 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D22 | 四湖DS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-3C-09 |  | 2-49 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.開關場照明(B) | 開關場照明(B) | OTHER | D22/0/StaDev/Lights2 |  |  |  | CDC | 512 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D22 | 四湖DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-06-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.310_GDA | 310開關箱IED RY GDA | OTHER | D22/11/310/GDA |  |  |  | CDC | 513 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-06-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.310_PHA2 | 310開關箱IED RY PHA | OTHER | D22/11/310/1_PHA |  |  |  | CDC | 514 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.320_GDA | 320開關箱IED RY GDA | OTHER | D22/11/320/GDA |  |  |  | CDC | 515 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-06-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.320_PHA2 | 320開關箱IED RY PHA | OTHER | D22/11/320/1_PHA |  |  |  | CDC | 516 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-34-11 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.空調機故障 | 空調機故障或電源跳脫 | OTHER | D22/0/StaDev/AIRCON |  |  |  | CDC | 517 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D22 | 四湖DS | 0 |  | FEEDER | FEEDER |  | RCA | [17 empty] | 2-3C-15 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.FEEDER_RCA | 饋線復閉電驛動作 | OTHER | D22/0/ComPoint/LOA |  |  |  | CDC | 518 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-34-13 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.水位警報(1) | 地下室水位警報(1) | OTHER | D22/0/StaDev/Water1 |  |  |  | CDC | 519 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-05-06 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1DTR_51A | #1DTR 51RY | MTR | D22/161/1750/PHA |  |  |  | CDC | 520 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-05-07 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1DTR_51NA | #1DTR 51N RY | MTR | D22/161/1750/GDA |  |  |  | CDC | 521 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-05-05 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D22//1DTR/51ZA |  |  |  | CDC | 522 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1DTR_87A | #1DTR 87RY | MTR | D22//1DTR/87A |  |  |  | CDC | 523 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-05-04 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D22//1DTR/96PA |  |  |  | CDC | 524 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-35-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_96D | #1DTR 96D RY | MTR | D22//1DTR/96D |  |  |  | CDC | 525 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-35-02 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_96P | #1DTR 96P RY | MTR | D22//1DTR/96P |  |  |  | CDC | 526 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D22//1DTR/63Q |  |  |  | CDC | 527 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D22//1DTR/96B1 |  |  |  | CDC | 528 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D22//1DTR/96B2 |  |  |  | CDC | 529 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-31-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_TRA | #1DTR 重故障 | MTR | D22//1DTR/TRA |  |  |  | CDC | 530 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-31-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D22//1DTR/TRF |  |  |  | CDC | 531 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-31-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D22//1DTR(A)/SupLocal |  |  |  | CDC | 532 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-31-02 |  | 1-4E | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D22//1DTR(A)/Tap Chan |  |  |  | CDC | 533 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-31-05 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D22//1DTR(B)/SupLocal |  |  |  | CDC | 534 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-31-06 |  | 1-50 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D22//1DTR(B)/Tap Chan |  |  |  | CDC | 535 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2DTR_51NA | #2DTR 51N RY | MTR | D22/161/1760/GDA |  |  |  | CDC | 536 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D22//2DTR/51ZA |  |  |  | CDC | 537 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-01 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2DTR_87A | #2DTR 87RY | MTR | D22//2DTR/87A |  |  |  | CDC | 538 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-07-02 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D22//2DTR/96PA |  |  |  | CDC | 539 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_96D | #2DTR 96D RY | MTR | D22//2DTR/96D |  |  |  | CDC | 540 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_96P | #2DTR 96P RY | MTR | D22//2DTR/96P |  |  |  | CDC | 541 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D22//2DTR/63Q |  |  |  | CDC | 542 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D22//2DTR/96B1 |  |  |  | CDC | 543 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D22//2DTR/96B2 |  |  |  | CDC | 544 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-31-10 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_TRA | #2DTR 重故障 | MTR | D22//2DTR/TRA |  |  |  | CDC | 545 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-31-11 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D22//2DTR/TRF |  |  |  | CDC | 546 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-31-08 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D22//2DTR(A)/SupLocal |  |  |  | CDC | 547 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-31-09 |  | 1-52 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D22//2DTR(A)/Tap Chan |  |  |  | CDC | 548 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-31-12 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D22//2DTR(B)/SupLocal |  |  |  | CDC | 549 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D22 | 四湖DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-31-13 |  | 1-54 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D22//2DTR(B)/Tap Chan |  |  |  | CDC | 550 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.#2DTR_51A | #2DTR 51RY | MTR | D22/161/1760/PHA |  |  |  | CDC | 551 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-34-14 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D22/161/1500/50SA |  |  |  | CDC | 552 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 330A1 | #2DTR |  | CB | [17 empty] | 1-08-02 |  | 1-21 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.330A1_CB | 330A1(#2DTR) CB | MTR | D22/11/330A1/CB |  |  |  | CDC | 553 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 330A2 | #2DTR |  | CB | [17 empty] | 1-08-05 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.330A2_CB | 330A2(#2DTR) CB | MTR | D22/11/330A2/CB |  |  |  | CDC | 554 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 340B1 | #2DTR |  | CB | [17 empty] | 1-09-00 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.340B1_CB | 340B1(#2DTR) CB | MTR | D22/11/340B1/CB |  |  |  | CDC | 555 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 340B2 | #2DTR |  | CB | [17 empty] | 1-09-03 |  | 1-2A | [5 empty] | ADCS_N | [8 empty] | 四湖DS.340B2_CB | 340B2(#2DTR) CB | MTR | D22/11/340B2/CB |  |  |  | CDC | 556 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 330A1 | #2DTR二次側(330A1) |  | 51A | [17 empty] | 1-07-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.330A1_51A | #2DTR二次側(330A1) 51RY | MTR | D22/11/330A1/2_PHA |  |  |  | CDC | 557 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 330A2 | #2DTR二次側(330A2) |  | 51A | [17 empty] | 1-07-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.330A2_51A | #2DTR二次側(330A2) 51RY | MTR | D22/11/330A2/2_PHA |  |  |  | CDC | 558 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 340B1 | #2DTR二次側(340B1) |  | 51A | [17 empty] | 1-08-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.340B1_51A | #2DTR二次側(340B1) 51RY | MTR | D22/11/340B1/2_PHA |  |  |  | CDC | 559 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 340B2 | #2DTR二次側(340B2) |  | 51A | [17 empty] | 1-08-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.340B2_51A | #2DTR二次側(340B2) 51RY | MTR | D22/11/340B2/2_PHA |  |  |  | CDC | 560 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 330A1 | 330A1開關箱IED |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.330A1_GDA | 330A1開關箱IED RY GDA | OTHER | D22/11/330A1/GDA |  |  |  | CDC | 561 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 330A1 | 330A1開關箱IED |  | PHA2 | [17 empty] | 1-08-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.330A1_PHA2 | 330A1開關箱IED RY PHA | OTHER | D22/11/330A1/1_PHA |  |  |  | CDC | 562 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 330A2 | 330A2開關箱IED |  | GDA | [17 empty] | 1-08-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.330A2_GDA | 330A2開關箱IED RY GDA | OTHER | D22/11/330A2/GDA |  |  |  | CDC | 563 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 330A2 | 330A2開關箱IED |  | PHA2 | [17 empty] | 1-08-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.330A2_PHA2 | 330A2開關箱IED RY PHA | OTHER | D22/11/330A2/1_PHA |  |  |  | CDC | 564 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 340B1 | 340B1開關箱IED |  | GDA | [17 empty] | 1-09-02 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.340B1_GDA | 340B1開關箱IED RY GDA | OTHER | D22/11/340B1/GDA |  |  |  | CDC | 565 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 340B1 | 340B1開關箱IED |  | PHA2 | [17 empty] | 1-09-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.340B1_PHA2 | 340B1開關箱IED RY PHA | OTHER | D22/11/340B1/1_PHA |  |  |  | CDC | 566 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 340B2 | 340B2開關箱IED |  | GDA | [17 empty] | 1-09-05 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.340B2_GDA | 340B2開關箱IED RY GDA | OTHER | D22/11/340B2/GDA |  |  |  | CDC | 567 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 340B2 | 340B2開關箱IED |  | PHA2 | [17 empty] | 1-09-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.340B2_PHA2 | 340B2開關箱IED RY PHA | OTHER | D22/11/340B2/1_PHA |  |  |  | CDC | 568 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-3D-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D22/0/StaDev/R_Temp |  |  |  | CDC | 569 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-34-15 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D22/161/ComPoint/OSCF |  |  |  | CDC | 570 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 81RY | 81RY |  | A/S(1) | [17 empty] | 1-1F-06 |  | 2-50 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.81RY_A/S(1) | 飛一線(XQ21)低頻電驛動作/復歸 | OTHER | D22/11/XQ21/81AS |  |  |  | CDC | 571 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D22 | 四湖DS | 0 |  | 81RY | 81RY |  | A/S(2) | [17 empty] | 1-1F-07 |  | 2-51 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.81RY_A/S(2) | 飛二線(XQ22)低頻電驛動作/復歸 | OTHER | D22/11/XQ22/81AS |  |  |  | CDC | 572 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D22 | 四湖DS | 0 |  | 81RY | 81RY |  | A/S(3) | [17 empty] | 2-00-00 |  | 2-52 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.81RY_A/S(3) | 飛三線(XQ23)低頻電驛動作/復歸 | OTHER | D22/11/XQ23/81AS |  |  |  | CDC | 573 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D22 | 四湖DS | 0 |  | 81RY | 81RY |  | A/S(4) | [17 empty] | 2-00-01 |  | 2-53 | [5 empty] | DDCS1_2 | [8 empty] | 四湖DS.81RY_A/S(4) | 飛六線(XQ26)低頻電驛動作/復歸 | OTHER | D22/11/XQ26/81AS |  |  |  | CDC | 574 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D22 | 四湖DS | 0 |  | 81RY | 81RY |  | A/S(5) | [17 empty] | 2-00-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.81RY_A/S(5) | XQ37低頻電驛動作/復歸 | OTHER | D22/11/XQ37/81AS |  |  |  | CDC | 575 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1530_PHA | 湖風四湖線(1530) 相間RY | LINE161 | D22/161/1530/PHA |  |  |  | CDC | 576 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1530_GDA | 湖風四湖線(1530) 接地RY | LINE161 | D22/161/1530/GDA |  |  |  | CDC | 577 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 四湖DS.1530_87A | 湖風四湖線(1530) 87RY | LINE161 | D22/161/1530/87A |  |  |  | CDC | 578 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | 87UL | [17 empty] | 1-30-06 |  | 1-44 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1530_87UL | 湖風四湖線(1530) 87RY U/L | LINE161 | D22/161/1530/87UL |  |  |  | CDC | 579 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 四湖DS.1530_CB | 1530(湖風四湖線) CB | LINE161 | D22/161/1530/CB |  |  |  | CDC | 580 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | 79UL | [17 empty] | 1-30-07 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1530_79UL | 湖風四湖線(1530) 79RY U/L | LINE161 | D22/161/1530/79UL |  |  |  | CDC | 581 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | DS1 | 1531 | [16 empty] | 1-37-04 | 1-37-05 | 1-64 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1531_DS | 1531(湖風四湖線) DS | LINE161 | D22/161/1530/DS1 |  |  |  | CDC | 582 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | DS2 | 1532 | [16 empty] | 1-37-06 | 1-37-07 | 1-65 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1532_DS | 1532(湖風四湖線) DS | LINE161 | D22/161/1530/DS2 |  |  |  | CDC | 583 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | DS3 | 1533 | [16 empty] | 1-37-08 | 1-37-09 | 1-66 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1533_DS | 1533(湖風四湖線) DS | LINE161 | D22/161/1530/DS3 |  |  |  | CDC | 584 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | E3 | 1533E | [16 empty] | 1-37-10 | 1-37-11 | 1-67 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1533E_ES | 1533E(湖風四湖線) ES | LINE161 | D22/161/1530/ES3 |  |  |  | CDC | 585 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D22 | 四湖DS | 0 |  | 1530 | 湖風四湖線(1530) |  | 87CFA | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1530_87CFA | 湖風四湖線(1530)87RY通訊故障 | OTHER | D22/161/1530/87CFA |  |  |  | CDC | 586 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1530 | 湖風四湖線(1530) |  | DTTA | [17 empty] | 1-0B-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1530_DTTA | 湖風四湖線(1530) 遠方遙跳 | OTHER | W01/161/1530/DTTA |  |  |  | CDC | 587 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1530 | 湖風四湖線(1530) |  | RCA | [17 empty] | 1-0B-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1530_RCA | 湖風四湖線(1530)79RY復閉動作 | OTHER | W01/161/1530/RCA |  |  |  | CDC | 588 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1530 | 湖風四湖線(1530) |  | RYFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1530_RYFA | 湖風四湖線(1530)數位電驛故障 | OTHER | D22/161/1530/RYFA |  |  |  | CDC | 589 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | LE0 | 1530LE | [16 empty] | 1-3A-10 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1530LE_ES | 1530LE(湖風四湖線) ES | LINE161 | W01/161/1530/LE0 |  |  |  | CDC | 590 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | TE0 | 1530TE | [16 empty] | 1-3A-11 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1530TE_ES | 1530TE(湖風四湖線) ES | LINE161 | W01/161/1530/TE0 |  |  |  | CDC | 591 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | 87A | [17 empty] | 1-0C-01 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1530_87A | 湖風四湖線(1530) 87RY | LINE161 | W01/161/1530/87A |  |  |  | CDC | 592 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | CB | [17 empty] | 1-0C-00 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1530_CB | 1530(湖風四湖線) CB | LINE161 | W01/161/1530/CB |  |  |  | CDC | 593 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | GDA | [17 empty] | 1-0C-03 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1530_GDA | 湖風四湖線(1530) 接地RY | LINE161 | W01/161/1530/GDA |  |  |  | CDC | 594 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | PHA | [17 empty] | 1-0C-02 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1530_PHA | 湖風四湖線(1530) 相間RY | LINE161 | W01/161/1530/PHA |  |  |  | CDC | 595 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | D_KEY | [33 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | E1 | 1531E | [16 empty] | 1-3A-09 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1531E_ES | 1531E(湖風四湖線) ES | LINE161 | W01/161/1530/E1 |  |  |  | CDC | 596 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | DS1 | 1531 | [16 empty] | 1-3A-08 | [7 empty] | ADCS_N | [8 empty] | 湖風GS.1531_DS | 1531(湖風四湖線) DS | LINE161 | W01/161/1530/DS1 |  |  |  | CDC | 597 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 81RY | XQ(30 36 38-40) |  | A/S(6) | [17 empty] | 2-00-03 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.81RY_A/S(6) | XQ(30 36 38-40)低頻RY動作/復歸 | OTHER | D22/11/ComPoint/81AS1 |  |  |  | CDC | 598 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D22 | 四湖DS | 0 |  |  |  |  | GEN | [17 empty] | 2-3C-10 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.GEN | 緊急發電機運轉 | OTHER | D22/0/StaDev/1A5Other |  |  |  | CDC | 599 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D22 | 四湖DS | 0 |  | 1510 | 北港四湖一路(1510) |  | 87A1 | [17 empty] | 1-00-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1510_87A1 | 北港四湖一路(1510)第一套87RY | OTHER | D22/161/1510/87A1 |  |  |  | CDC | 600 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1510 | 北港四湖一路(1510) |  | 87A2 | [17 empty] | 1-00-02 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1510_87A2 | 北港四湖一路(1510)第二套87RY | OTHER | D22/161/1510/87A2 |  |  |  | CDC | 601 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1510 | 北港四湖一路(1510) |  | 87CFA | [17 empty] | 1-32-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1510_87CFA | 北港四湖一路(1510)87RY通訊故障 | OTHER | D22/161/1510/87CFA |  |  |  | CDC | 602 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1510 | 北港四湖一路(1510) |  | 1_87UL1 | [17 empty] | 1-30-02 |  | 1-40 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1510_87UL1 | 北港四湖一路(1510)#1 87RY U/L | OTHER | D22/161/1510/1_87UL1 |  |  |  | CDC | 603 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1510 | 北港四湖一路(1510) |  | 1_87UL2 | [17 empty] | 1-3B-00 |  | 1-3F | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1510_87UL2 | 北港四湖一路(1510)#2 87RY U/L | OTHER | D22/161/1510/1_87UL2 |  |  |  | CDC | 604 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1510 | 北港四湖一路(1510) |  | RYFA | [17 empty] | 1-32-08 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1510_RYFA | 北港四湖一路(1510)數位電驛故障 | OTHER | D22/161/1510/RYFA |  |  |  | CDC | 605 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1520 | 北港四湖二路(1520) |  | 87A1 | [17 empty] | 1-00-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1520_87A1 | 北港四湖二路(1520)第一套87RY | OTHER | D22/161/1520/87A1 |  |  |  | CDC | 606 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1520 | 北港四湖二路(1520) |  | 87A2 | [17 empty] | 1-00-07 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1520_87A2 | 北港四湖二路(1520)第二套87RY | OTHER | D22/161/1520/87A2 |  |  |  | CDC | 607 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1520 | 北港四湖二路(1520) |  | 87CFA | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1520_87CFA | 北港四湖二路(1520)87RY通訊故障 | OTHER | D22/161/1520/87CFA |  |  |  | CDC | 608 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1520 | 北港四湖二路(1520) |  | 1_87UL1 | [17 empty] | 1-30-04 |  | 1-42 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1520_87UL1 | 北港四湖二路(1520)#1 87RY U/L | OTHER | D22/161/1520/1_87UL1 |  |  |  | CDC | 609 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1520 | 北港四湖二路(1520) |  | 1_87UL2 | [17 empty] | 1-3B-01 |  | 1-3E | [5 empty] | ADCS_N | [8 empty] | 四湖DS.1520_87UL2 | 北港四湖二路(1520)#2 87RY U/L | OTHER | D22/161/1520/1_87UL2 |  |  |  | CDC | 610 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1520 | 北港四湖二路(1520) |  | RYFA | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.1520_RYFA | 北港四湖二路(1520)數位電驛故障 | OTHER | D22/161/1520/RYFA |  |  |  | CDC | 611 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | TR | TR |  | PDA | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.TR_PDA | #1,#2DTR局部放電警報 | OTHER | D22/0/StaDev/PDA |  |  |  | CDC | 612 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-33-04 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D22/161/ComPoint/12B_CTFA |  |  |  | CDC | 613 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-33-03 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D22/161/ComPoint/BUS_RYFA |  |  |  | CDC | 614 | GENERICDIPoint | DS039_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-3D-09 |  | 2-56 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | D22//1DTR/51Z_UL |  |  |  | CDC | 615 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0D-00 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_86A | #1DTR 86A | OTHER | D22//1DTR/DTR_86A |  |  |  | CDC | 616 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [17 empty] | 2-3D-07 |  | 2-54 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | D22//1DTR/1_87UL1 |  |  |  | CDC | 617 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [17 empty] | 2-3D-08 |  | 2-55 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | D22//1DTR/1_87UL2 |  |  |  | CDC | 618 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 1DTR | #1DTR |  | RYFA | [17 empty] | 2-3D-10 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | D22//1DTR/RYFA |  |  |  | CDC | 619 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-3D-13 |  | 2-59 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | D22//2DTR/51Z_UL |  |  |  | CDC | 620 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0D-01 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_86A | #2DTR 86A | OTHER | D22//2DTR/DTR_86A |  |  |  | CDC | 621 | GENERICDIPoint | DS039_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 2-3D-11 |  | 2-57 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | D22//2DTR/1_87UL1 |  |  |  | CDC | 622 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 2-3D-12 |  | 2-58 | [5 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | D22//2DTR/1_87UL2 |  |  |  | CDC | 623 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D22 | 四湖DS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 2-3D-14 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | D22//2DTR/RYFA |  |  |  | CDC | 624 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  |  |  |  | PMA | [17 empty] | 2-3D-15 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.PMA | 電力量測表計故障 | OTHER | D22/0/StaDev/PMA |  |  |  | CDC | 625 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 2-3D-06 | [7 empty] | ADCS_N | [8 empty] | 四湖DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D22/0/ComPoint/OLTC_A |  |  |  | CDC | 626 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | 59V0 | [17 empty] | 2-01-02 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_59V0 | 博斯太陽光電 59V0 | OTHER |  |  |  |  | CDC | 627 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | 81A | [17 empty] | 2-01-05 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_81A | 博斯太陽光電 81A | OTHER |  |  |  |  | CDC | 628 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | CB | [17 empty] | 2-01-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_CB | 博斯太陽光電 CB | OTHER |  |  |  |  | CDC | 629 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | BOSI | BOSI |  | CFA | [17 empty] | 2-31-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_CFA | 博斯太陽光電通訊故障 | OTHER |  |  |  |  | CDC | 630 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | DS1 | BOSI | [16 empty] | 2-31-00 | 2-31-01 | [6 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_DS | 博斯太陽光電 DS | OTHER |  |  |  |  | CDC | 631 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | GDA | [17 empty] | 2-01-04 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_GDA | 博斯太陽光電 GDA | OTHER |  |  |  |  | CDC | 632 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | UVA | [17 empty] | 2-01-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_OUVA | 博斯太陽光電 OUVA | OTHER |  |  |  |  | CDC | 633 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | PHA | [17 empty] | 2-01-03 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_PHA | 博斯太陽光電 PHA | OTHER |  |  |  |  | CDC | 634 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | BOSI | 博斯太陽光電 |  | PTDS | [17 empty] | 2-31-02 | 2-31-03 | [6 empty] | DDCS1_2 | [8 empty] | 四湖DS.BOSI_PTDS | 博斯太陽光電 PTDS | OTHER |  |  |  |  | CDC | 635 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 0 |  | SULI | 速力太陽光電 |  | CB1 | [17 empty] | 2-02-00 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_CB1 | 速力太陽光電 CB1 | OTHER |  |  |  |  | CDC | 636 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | SULI | 速力太陽光電 |  | CB2 | [17 empty] | 2-02-06 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_CB2 | 速力太陽光電 CB2 | OTHER |  |  |  |  | CDC | 637 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | SULI | SULI |  | CFA | [17 empty] | 2-31-15 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_CFA | 速力太陽光電通訊故障 | OTHER |  |  |  |  | CDC | 638 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | SULI | 速力太陽光電 |  | LBS | [17 empty] | 2-31-08 | 2-31-09 | [6 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_LBS | 速力太陽光電 LBS | OTHER |  |  |  |  | CDC | 639 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 0 |  | SULI | 速力太陽光電 |  | UVA | [17 empty] | 2-02-01 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_OUVA | 速力太陽光電 OUVA 81A | OTHER |  |  |  |  | CDC | 640 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | SULI_PHA | 速力太陽光電 |  | GDA1 | [17 empty] | 2-02-03 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_PHA_GDA1 | 速力太陽光電 PHA GDA1 | OTHER |  |  |  |  | CDC | 641 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | SULI_PHA | 速力太陽光電 |  | GDA2 | [17 empty] | 2-02-07 | [7 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_PHA_GDA2 | 速力太陽光電 PHA GDA2 | OTHER |  |  |  |  | CDC | 642 | GENERICDIPoint | DS039_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D22 | 四湖DS | 0 |  | SULI | 速力太陽光電 |  | PTDS | [17 empty] | 2-31-10 | 2-31-11 | [6 empty] | DDCS1_2 | [8 empty] | 四湖DS.SULI_PTDS | 速力太陽光電 PTDS | OTHER |  |  |  |  | CDC | 643 | GENERICDIPoint | DS039_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D22 | 四湖DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 四湖DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 644 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 四湖DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 645 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 四湖DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 646 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 四湖DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 647 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 133 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_133 | 四湖DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 648 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 134 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_134 | 四湖DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 649 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 135 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_135 | 四湖DS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 650 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 136 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_136 | 四湖DS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 651 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 137 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_137 | 四湖DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 652 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 138 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_138 | 四湖DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 653 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 139 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_139 | 四湖DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 654 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 0 |  | TRD | 四湖DS |  | 140 | [25 empty] | TRAIN_AD | [8 empty] | 四湖DS.TRD_140 | 四湖DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 655 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1510LE | 1510LE (非取樣點) | LINE161 | D22/161/1510/LE0 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1510BE | 1510BE (非取樣點) | LINE161 | D22/161/1510/BE0 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1520LE | 1520LE (非取樣點) | LINE161 | D22/161/1520/LE0 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1520BE | 1520BE (非取樣點) | LINE161 | D22/161/1520/BE0 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ21 | XQ21_DS |  | DS1 | XQ21_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_DS | XQ21_DS (非取樣點) | FEEDER | D22/11/XQ21/DS |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ21 | XQ21_ES |  | LE0 | XQ21_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ21_ES | XQ21_ES (非取樣點) | FEEDER | D22/11/XQ21/ES |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ22 | XQ22_DS |  | DS1 | XQ22_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_DS | XQ22_DS (非取樣點) | FEEDER | D22/11/XQ22/DS |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ22 | XQ22_ES |  | LE0 | XQ22_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ22_ES | XQ22_ES (非取樣點) | FEEDER | D22/11/XQ22/ES |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ23 | XQ23_DS |  | DS1 | XQ23_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_DS | XQ23_DS (非取樣點) | FEEDER | D22/11/XQ23/DS |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ23 | XQ23_ES |  | LE0 | XQ23_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ23_ES | XQ23_ES (非取樣點) | FEEDER | D22/11/XQ23/ES |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ24 | XQ24_DS |  | DS1 | XQ24_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_DS | XQ24_DS (非取樣點) | FEEDER | D22/11/XQ24/DS |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ24 | XQ24_ES |  | LE0 | XQ24_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ24_ES | XQ24_ES (非取樣點) | FEEDER | D22/11/XQ24/ES |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ25 | XQ25_DS |  | DS1 | XQ25_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_DS | XQ25_DS (非取樣點) | FEEDER | D22/11/XQ25/DS |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ25 | XQ25_ES |  | LE0 | XQ25_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ25_ES | XQ25_ES (非取樣點) | FEEDER | D22/11/XQ25/ES |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ26 | XQ26_DS |  | DS1 | XQ26_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_DS | XQ26_DS (非取樣點) | FEEDER | D22/11/XQ26/DS |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ26 | XQ26_ES |  | LE0 | XQ26_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ26_ES | XQ26_ES (非取樣點) | FEEDER | D22/11/XQ26/ES |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ27 | XQ27_DS |  | DS1 | XQ27_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_DS | XQ27_DS (非取樣點) | FEEDER | D22/11/XQ27/DS |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ27 | XQ27_ES |  | LE0 | XQ27_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ27_ES | XQ27_ES (非取樣點) | FEEDER | D22/11/XQ27/ES |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ28 | XQ28_DS |  | DS1 | XQ28_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_DS | XQ28_DS (非取樣點) | FEEDER | D22/11/XQ28/DS |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ28 | XQ28_ES |  | LE0 | XQ28_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ28_ES | XQ28_ES (非取樣點) | FEEDER | D22/11/XQ28/ES |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ29 | XQ29_DS |  | DS1 | XQ29_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_DS | XQ29_DS (非取樣點) | FEEDER | D22/11/XQ29/DS |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ29 | XQ29_ES |  | LE0 | XQ29_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ29_ES | XQ29_ES (非取樣點) | FEEDER | D22/11/XQ29/ES |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ30 | XQ30_DS |  | DS1 | XQ30_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_DS | XQ30_DS (非取樣點) | FEEDER | D22/11/XQ30/DS |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ30 | XQ30_ES |  | LE0 | XQ30_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ30_ES | XQ30_ES (非取樣點) | FEEDER | D22/11/XQ30/ES |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ31 | XQ31_DS |  | DS1 | XQ31_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_DS | XQ31_DS (非取樣點) | FEEDER | D22/11/XQ31/DS |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ31 | XQ31_ES |  | LE0 | XQ31_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ31_ES | XQ31_ES (非取樣點) | FEEDER | D22/11/XQ31/ES |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ32 | XQ32_DS |  | DS1 | XQ32_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_DS | XQ32_DS (非取樣點) | FEEDER | D22/11/XQ32/DS |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ32 | XQ32_ES |  | LE0 | XQ32_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ32_ES | XQ32_ES (非取樣點) | FEEDER | D22/11/XQ32/ES |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ33 | XQ33_DS |  | DS1 | XQ33_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_DS | XQ33_DS (非取樣點) | FEEDER | D22/11/XQ33/DS |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ33 | XQ33_ES |  | LE0 | XQ33_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ33_ES | XQ33_ES (非取樣點) | FEEDER | D22/11/XQ33/ES |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ34 | XQ34_DS |  | DS1 | XQ34_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_DS | XQ34_DS (非取樣點) | FEEDER | D22/11/XQ34/DS |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ34 | XQ34_ES |  | LE0 | XQ34_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ34_ES | XQ34_ES (非取樣點) | FEEDER | D22/11/XQ34/ES |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ35 | XQ35_DS |  | DS1 | XQ35_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_DS | XQ35_DS (非取樣點) | FEEDER | D22/11/XQ35/DS |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ35 | XQ35_ES |  | LE0 | XQ35_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ35_ES | XQ35_ES (非取樣點) | FEEDER | D22/11/XQ35/ES |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ36 | XQ36_DS |  | DS1 | XQ36_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_DS | XQ36_DS (非取樣點) | FEEDER | D22/11/XQ36/DS |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ36 | XQ36_ES |  | LE0 | XQ36_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ36_ES | XQ36_ES (非取樣點) | FEEDER | D22/11/XQ36/ES |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ37 | XQ37_DS |  | DS1 | XQ37_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_DS | XQ37_DS (非取樣點) | FEEDER | D22/11/XQ37/DS |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ37 | XQ37_ES |  | LE0 | XQ37_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ37_ES | XQ37_ES (非取樣點) | FEEDER | D22/11/XQ37/ES |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ38 | XQ38_DS |  | DS1 | XQ38_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_DS | XQ38_DS (非取樣點) | FEEDER | D22/11/XQ38/DS |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ38 | XQ38_ES |  | LE0 | XQ38_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ38_ES | XQ38_ES (非取樣點) | FEEDER | D22/11/XQ38/ES |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ39 | XQ39_DS |  | DS1 | XQ39_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_DS | XQ39_DS (非取樣點) | FEEDER | D22/11/XQ39/DS |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ39 | XQ39_ES |  | LE0 | XQ39_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ39_ES | XQ39_ES (非取樣點) | FEEDER | D22/11/XQ39/ES |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | XQ40 | XQ40_DS |  | DS1 | XQ40_DS | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_DS | XQ40_DS (非取樣點) | FEEDER | D22/11/XQ40/DS |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | XQ40 | XQ40_ES |  | LE0 | XQ40_ES | [24 empty] | DDCS1_2 | [8 empty] | 四湖DS.XQ40_ES | XQ40_ES (非取樣點) | FEEDER | D22/11/XQ40/ES |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.101 | 101 (非取樣點) | TIE | D22/11/100/D1 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.102 | 102 (非取樣點) | TIE | D22/11/100/D2 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1501E | 1501E (非取樣點) | TIE | D22/161/1500/E1 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1502E | 1502E (非取樣點) | TIE | D22/161/1500/E2 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.201 | 201 (非取樣點) | TIE | D22/11/200/D1 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.202 | 202 (非取樣點) | TIE | D22/11/200/D2 |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.301 | 301 (非取樣點) | TIE | D22/11/300/D1 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.401 | 401 (非取樣點) | TIE | D22/11/400/D1 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.391 | 391 (非取樣點) | OTHER | D22/11/390/D1 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.391E | 391E (非取樣點) | OTHER | D22/11/390/E1 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.491 | 491 (非取樣點) | OTHER | D22/11/490/D1 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.491E | 491E (非取樣點) | OTHER | D22/11/490/E1 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1750TE | 1750TE (非取樣點) | MTR | D22/161/1750/TE0 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1750BE | 1750BE (非取樣點) | MTR | D22/161/1750/BE0 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.311 | 311 (非取樣點) | MTR | D22/11/310/D1 |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.311E | 311E (非取樣點) | MTR | D22/11/310/E1 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.321 | 321 (非取樣點) | MTR | D22/11/320/D1 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.321E | 321E (非取樣點) | MTR | D22/11/320/E1 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1760TE | 1760TE (非取樣點) | MTR | D22/161/1760/TE0 |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1760BE | 1760BE (非取樣點) | MTR | D22/161/1760/BE0 |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.211E | 211E (非取樣點) | SC | D22/11/210/E1 |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 210 | #1SC(210) |  | SC10 | 210SC1 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.210SC1_ES | 210SC1_ES (非取樣點) | SC | [5 empty] | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.211 | 211 (非取樣點) | SC | D22/11/210/D1 |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 210 | #1SC(210) |  | SC20 | 210SC2 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.210SC2_ES | 210SC2_ES (非取樣點) | SC | [5 empty] | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.221E | 221E (非取樣點) | SC | D22/11/220/E1 |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 220 | #2SC(220) |  | SC10 | 220SC1 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.220SC1_ES | 220SC1_ES (非取樣點) | SC | [5 empty] | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.221 | 221 (非取樣點) | SC | D22/11/220/D1 |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 220 | #2SC(220) |  | SC20 | 220SC2 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.220SC2_ES | 220SC2_ES (非取樣點) | SC | [5 empty] | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.231E | 231E (非取樣點) | SC | D22/11/230/E1 |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 230 | #3SC(230) |  | SC10 | 230SC1 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.230SC1_ES | 230SC1_ES (非取樣點) | SC | [5 empty] | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.231 | 231 (非取樣點) | SC | D22/11/230/D1 |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 230 | #3SC(230) |  | SC20 | 230SC2 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.230SC2_ES | 230SC2_ES (非取樣點) | SC | [5 empty] | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.241E | 241E (非取樣點) | SC | D22/11/240/E1 |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 240 | #4SC(240) |  | SC10 | 240SC1 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.240SC1_ES | 240SC1_ES (非取樣點) | SC | [5 empty] | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.241 | 241 (非取樣點) | SC | D22/11/240/D1 |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 240 | #4SC(240) |  | SC20 | 240SC2 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.240SC2_ES | 240SC2_ES (非取樣點) | SC | [5 empty] | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.15B1E | 15B1E (非取樣點) | BUS | D22/161/161B1E/BE1 |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.15B2E | 15B2E (非取樣點) | BUS | D22/161/161B2E/BE2 |  |  |  |  | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 738 | NotelDIPoint | [38 empty] | START/STOP | STOP
D22 | 四湖DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.101E | 101E(非取樣點) | OTHER | D22/11/100/E1 |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.102E | 102E(非取樣點) | OTHER | D22/11/100/E2 |  |  |  |  | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.201E | 201E(非取樣點) | OTHER | D22/11/200/E1 |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.202E | 202E(非取樣點) | OTHER | D22/11/200/E2 |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.301E | 301E(非取樣點) | OTHER | D22/11/300/E1 |  |  |  |  | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  |  |  |  | 401E | 401E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.401E | 401E(非取樣點) | OTHER | D22/11/400/E1 |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 330 | 330 |  | A11 | 331A1 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.331A1 | 331A1 (非取樣點) | MTR | [5 empty] | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 330 | 330 |  | A1E1 | 331A1E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.331A1E | 331A1E (非取樣點) | MTR | [5 empty] | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 330 | 330 |  | A21 | 331A2 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.331A2 | 331A2 (非取樣點) | MTR | [5 empty] | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 330 | 330 |  | A2E1 | 331A2E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.331A2E | 331A2E (非取樣點) | MTR | [5 empty] | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 340 | 340 |  | B11 | 341B1 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.341B1 | 341B1 (非取樣點) | MTR | [5 empty] | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 340 | 340 |  | BE1 | 341B1E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.341B1E | 341B1E (非取樣點) | MTR | [5 empty] | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 340 | 340 |  | B21 | 341B2 | [24 empty] | ADCS_N | [8 empty] | 四湖DS.341B2 | 341B2 (非取樣點) | MTR | [5 empty] | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D22 | 四湖DS | 0 |  | 340 | 340 |  | BE2 | 341B2E | [24 empty] | ADCS_N | [8 empty] | 四湖DS.341B2E | 341B2E (非取樣點) | MTR | [5 empty] | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1530LE | 1530LE (非取樣點) | LINE161 | D22/161/1530/LE0 |  |  |  |  | 753 | NotelDIPoint |  |  |  |  | D_KEY | [33 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1530BE | 1530BE (非取樣點) | LINE161 | D22/161/1530/BE0 |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 2A1BUS | 2A1BUS |  | PTE | 2A1BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.2A1BUS_PTE | #2A1BUS_PTE(非取樣點) | OTHER | [5 empty] | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 2A2BUS | 2A2BUS |  | PTE | 2A2BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.2A2BUS_PTE | #2A2BUS_PTE(非取樣點) | OTHER | [5 empty] | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 2B1BUS | 2B1BUS |  | PTE | 2B1BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.2B1BUS_PTE | #2B1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D22 | 四湖DS | 0 |  | 2B2BUS | 2B2BUS |  | PTE | 2B2BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 四湖DS.2B2BUS_PTE | #2B2BUS_PTE(非取樣點) | OTHER | [5 empty] | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
W01 | 湖風GS | 161 | 161kV | 1530 | 湖風四湖線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 湖風GS.1530_AMP | 湖風四湖線 AMP | LINE161 | W01/161/1530/I |  | AMP_CAL |  |  | 761 | CalcAIPoint | [21 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo