## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D23 | 斗六DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  |  | MCC-1 | TEST | TEST CB (開啟/ 閉合) |  |  | ELEM/ALL | [8 empty] | 斗六DS.TEST_CB | TEST CB | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 2 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0001 | 1-30-03 |  |  | M1 | 343AS1 | #3 DTR WIND ULTC(自動/手動) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_A/M | #3DTR OLTC A/M | MTR |  | CDC_Cmd_EMPTY |  |  |  | 3 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0000 |  | 0002 | 1-80 |  |  | M1 | ------ | #3 DTR ULTC TAP 指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_TAP | #3DTR OLTC TAP | MTR |  | CDC_Cmd_EMPTY |  |  |  | 4 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0005 | 1-30-14 |  |  | M2 | 443AS1 | #4 DTR WIND ULTC(自動/手動) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_A/M | #4DTR OLTC A/M | MTR |  | CDC_Cmd_EMPTY |  |  |  | 5 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0005 |  | 0006 | 1-85 |  |  | M2 | ------ | #4 DTR ULTC TAP 指示量 t=-8~+8 | TAP_-8.5_8.5(0_2000) |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_TAP | #4DTR OLTC TAP | MTR |  | CDC_Cmd_EMPTY |  |  |  | 6 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0553 |  | 0017 | 1-32-09 |  |  | R1 | L187S | 1610 雲林斗六一路主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_87UL | 雲林斗六一路(1610) 87RY U/L | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 7 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0019 | 1-32-11 |  |  | R1 | L179S | 1610 雲林斗六一路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_79UL | 雲林斗六一路(1610) 79RY U/L | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 8 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0020 | 1-32-10 |  |  | R2 | L287S | 1620 雲林斗六二路主保護電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_87UL | 雲林斗六二路(1620) 87RY U/L | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 9 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0022 | 1-32-12 |  |  | R2 | L279S | 1620 雲林斗六二路復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_79UL | 雲林斗六二路(1620) 79RY U/L | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 10 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0593 |  | 0023 | 1-35-01 |  |  | R5 | 87B1S | 161KV #1 BUS 87電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 11 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0594 |  | 0024 | 1-35-02 |  |  | R5 | 87B2S | 161KV #2 BUS 87電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 12 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0122 |  | 0053 | 1-0F-02 |  |  | GB1 | 52AS | 1500 CB (ON/OFF) |  | aaaz | B2/D23_A1 | [8 empty] | 斗六DS.1500_CB | 1500(TIE) CB | TIE |  | CDC_Cmd_EMPTY |  |  |  | 13 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 | 0054 | 2-30-00 | 2-30-01 |  | GB1 | DS (ON) | 1501 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1501_DS | 1501(TIE) DS | TIE |  | CDC_Cmd_EMPTY |  |  |  | 14 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 | 0055 | 2-30-02 | 2-30-03 |  | GB1 | DS (ON) | 1502 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1502_DS | 1502(TIE) DS | TIE |  | CDC_Cmd_EMPTY |  |  |  | 15 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P03D231/T2 |  | 0118 |  | 0056 | 1-0E-06 |  |  | GL1 | 52AS | 1610 CB (ON/OFF) |  | aaca | B2/D23_A1 | [8 empty] | 斗六DS.1610_CB | 1610(雲林斗六一路) CB | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 16 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | DS1 | 1611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0772 | 773 | 0057 | 2-30-04 | 2-30-05 |  | GL1 | DS (ON) | 1611 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1611_DS | 1611(雲林斗六一路) DS | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 17 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | DS2 | 1612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0774 | 775 | 0058 | 2-30-06 | 2-30-07 |  | GL1 | DS (ON) | 1612 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1612_DS | 1612(雲林斗六一路) DS | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 18 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | DS3 | 1613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0776 | 777 | 0059 | 2-30-08 | 2-30-09 |  | GL1 | DS (ON) | 1613 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1613_DS | 1613(雲林斗六一路) DS | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 19 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | ES3 | 1613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0778 | 779 | 0060 | 2-30-10 | 2-30-11 |  | GL1 | ES (ON) | 1613E ES ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1613E_ES | 1613E(雲林斗六一路) ES | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 20 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P03D232/T2 |  | 0119 |  | 0061 | 1-0E-07 |  |  | GL2 | 52AS | 1620CB (ON/OFF) |  | aada | B2/D23_A1 | [8 empty] | 斗六DS.1620_CB | 1620(雲林斗六二路) CB | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 21 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | DS1 | 1621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0780 | 781 | 0062 | 2-30-12 | 2-30-13 |  | GL2 | DS (ON) | 1621 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1621_DS | 1621(雲林斗六二路) DS | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 22 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | DS2 | 1622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0782 | 783 | 0063 | 2-30-14 | 2-30-15 |  | GL2 | DS (ON) | 1622 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1622_DS | 1622(雲林斗六二路) DS | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 23 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | DS3 | 1623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 | 0064 | 2-31-00 | 2-31-01 |  | GL2 | DS (ON) | 1623 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1623_DS | 1623(雲林斗六二路) DS | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 24 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | ES3 | 1623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0786 | 787 | 0065 | 2-31-02 | 2-31-03 |  | GL2 | ES (ON) | 1623E ES ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1623E_ES | 1623E(雲林斗六二路) ES | LINE161 |  | CDC_Cmd_EMPTY |  |  |  | 25 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0120 |  | 0116 | 1-0F-00 |  |  | GT1 | 52AS | 1770 CB (ON/OFF) |  | aabb | ELEM/D23_A1 | [8 empty] | 斗六DS.1770_CB | 1770(#3DTR) CB | MTR |  | CDC_Cmd_EMPTY |  |  |  | 26 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0868 | 869 | 0117 | 2-36-04 | 2-36-05 |  | GT1 | DS (ON) | 1771 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 27 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0870 | 871 | 0118 | 2-36-06 | 2-36-07 |  | GT1 | DS (ON) | 1772 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 28 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0121 |  | 0119 | 1-0F-01 |  |  | GT2 | 52AS | 1780 CB (ON/OFF) |  | aaeb | ELEM/D23_A1 | [8 empty] | 斗六DS.1780_CB | 1780(#4DTR) CB | MTR |  | CDC_Cmd_EMPTY |  |  |  | 29 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | INSERT | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0872 | 873 | 0120 | 2-36-08 | 2-36-09 |  | GT2 | DS (ON) | 1781 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1781_DS | 1781(#4DTR) DS | MTR | [5 empty] | 30 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | INSERT | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0874 | 875 | 0121 | 2-36-10 | 2-36-11 |  | GT2 | DS (ON) | 1782 DS ON |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1782_DS | 1782(#4DTR) DS | MTR | [5 empty] | 31 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3ABus | B/3BBus |  |  | 0258 |  | 0128 | 2-00-02 |  |  | 300 | 52AS | 300 CB (ON/OFF) |  | aaab | B3/D23_A1 | [8 empty] | 斗六DS.300_CB | 300(TIE) CB | TIE |  | CDC_Cmd_EMPTY |  |  |  | 32 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XN61/T1 |  |  | 0262 |  | 0129 | 2-00-06 |  |  | XN61 | 52AS | XN61 CB (ON/OFF) |  | aabb | B2/D23_D1 | [8 empty] | 斗六DS.XN61_CB | XN61(23KV斗61線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 33 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0660 |  | 0130 | 1-39-04 |  |  | XN61 | 79S | XN61 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN61_79UL | 23KV斗61線(XN61) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 34 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0661 |  | 0131 | 1-39-05 |  |  | XN61 | TAPS | XN61 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN61_LCO_TAP | 23KV斗61線(XN61) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 35 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XN62/T1 |  |  | 0266 |  | 0132 | 2-01-02 |  |  | XN62 | 52AS | XN62 CB (ON/OFF) |  | aacb | B2/D23_D1 | [8 empty] | 斗六DS.XN62_CB | XN62(23KV斗62線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 36 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0662 |  | 0133 | 1-39-06 |  |  | XN62 | 79S | XN62 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN62_79UL | 23KV斗62線(XN62) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 37 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0663 |  | 0134 | 1-39-07 |  |  | XN62 | TAPS | XN62 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN62_LCO_TAP | 23KV斗62線(XN62) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 38 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XN63/T1 |  |  | 0270 |  | 0135 | 2-01-06 |  |  | XN63 | 52AS | XN63 CB (ON/OFF) |  | aadb | B2/D23_D1 | [8 empty] | 斗六DS.XN63_CB | XN63(23KV斗63線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 39 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0664 |  | 0136 | 1-39-08 |  |  | XN63 | 79S | XN63 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN63_79UL | 23KV斗63線(XN63) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 40 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0665 |  | 0137 | 1-39-09 |  |  | XN63 | TAPS | XN63 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN63_LCO_TAP | 23KV斗63線(XN63) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 41 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3ABus | L/XN64/T1 |  |  | 0274 |  | 0138 | 2-02-02 |  |  | XN64 | 52AS | XN64 CB (ON/OFF) |  | aaeb | B2/D23_D1 | [8 empty] | 斗六DS.XN64_CB | XN64(23KV斗64線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 42 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0666 |  | 0139 | 1-39-10 |  |  | XN64 | 79S | XN64 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN64_79UL | 23KV斗64線(XN64) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 43 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0667 |  | 0140 | 1-39-11 |  |  | XN64 | TAPS | XN64 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN64_LCO_TAP | 23KV斗64線(XN64) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 44 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0277 |  | 0141 | 2-02-05 |  |  | 250 | 52AS | 250 CB (ON/OFF) |  | aagb | B3/D23_A1 | [8 empty] | 斗六DS.250_CB | 250(23KV #5SC) CB | SC |  | CDC_Cmd_EMPTY |  |  |  | 45 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | A/360^T/3DTR(A) |  |  | 0125 |  | 0142 | 1-0F-05 |  |  | 350 | 52AS | 350 CB (ON/OFF) |  | aaha | ELEM/D23_A1 | [8 empty] | 斗六DS.350_CB | 350(#3DTR) CB | MTR |  | CDC_Cmd_EMPTY |  |  |  | 46 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | C/6SC |  |  | 0283 |  | 0143 | 2-03-03 |  |  | 260 | 52AS | 260 CB (ON/OFF) |  | abab | B3/D23_A1 | [8 empty] | 斗六DS.260_CB | 260(23KV #6SC) CB | SC |  | CDC_Cmd_EMPTY |  |  |  | 47 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/1SSTR |  |  | 0286 |  | 0144 | 2-03-06 |  |  | 390 | 52AS | 390 CB (ON/OFF) |  | abbb | B3/D23_A1 | [8 empty] | 斗六DS.390_CB | 390(#1SSTR) CB | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 48 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | A/350^T/3DTR(B) |  |  | 0128 |  | 0145 | 1-10-00 |  |  | 360 | 52AS | 360 CB (ON/OFF) |  | abca | ELEM/D23_A1 | [8 empty] | 斗六DS.360_CB | 360(#3DTR) CB | MTR |  | CDC_Cmd_EMPTY |  |  |  | 49 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XN65/T1 |  |  | 0293 |  | 0146 | 2-04-05 |  |  | XN65 | 52AS | XN65 CB (ON/OFF) |  | abdb | B2/D23_D1 | [8 empty] | 斗六DS.XN65_CB | XN65(23KV斗65線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 50 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0668 |  | 0147 | 1-39-12 |  |  | XN65 | 79S | XN65 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN65_79UL | 23KV斗65線(XN65) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 51 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0669 |  | 0148 | 1-39-13 |  |  | XN65 | TAPS | XN65 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN65_LCO_TAP | 23KV斗65線(XN65) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 52 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XN66/T1 |  |  | 0297 |  | 0149 | 2-05-01 |  |  | XN66 | 52AS | XN66 CB (ON/OFF) |  | abeb | B2/D23_D1 | [8 empty] | 斗六DS.XN66_CB | XN66(23KV斗66線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 53 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0670 |  | 0150 | 1-39-14 |  |  | XN66 | 79S | XN66 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN66_79UL | 23KV斗66線(XN66) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 54 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0671 |  | 0151 | 1-39-15 |  |  | XN66 | TAPS | XN66 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN66_LCO_TAP | 23KV斗66線(XN66) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 55 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XN67/T1 |  |  | 0301 |  | 0152 | 2-05-05 |  |  | XN67 | 52AS | XN67 CB (ON/OFF) |  | abgb | B2/D23_D1 | [8 empty] | 斗六DS.XN67_CB | XN67(23KV斗67線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 56 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0672 |  | 0153 | 1-3A-00 |  |  | XN67 | 79S | XN67 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN67_79UL | 23KV斗67線(XN67) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 57 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0673 |  | 0154 | 1-3A-01 |  |  | XN67 | TAPS | XN67 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN67_LCO_TAP | 23KV斗67線(XN67) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 58 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3BBus | L/XN68/T1 |  |  | 0305 |  | 0155 | 2-06-01 |  |  | XN68 | 52AS | XN68 CB (ON/OFF) |  | abhb | B2/D23_D1 | [8 empty] | 斗六DS.XN68_CB | XN68(23KV斗68線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 59 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0674 |  | 0156 | 1-3A-02 |  |  | XN68 | 79S | XN68 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN68_79UL | 23KV斗68線(XN68) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 60 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0675 |  | 0157 | 1-3A-03 |  |  | XN68 | TAPS | XN68 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN68_LCO_TAP | 23KV斗68線(XN68) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 61 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | A300/N1 |  |  | 0308 |  | 0158 | 2-06-04 |  |  | 400 | 52AS | 400 CB (ON/OFF) |  | acab | B3/D23_A1 | [8 empty] | 斗六DS.400_CB | 400(TIE) CB | TIE |  | CDC_Cmd_EMPTY |  |  |  | 62 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN71/T1 |  |  | 0312 |  | 0159 | 2-07-00 |  |  | XN71 | 52AS | XN71 CB (ON/OFF) |  | acbb | B2/D23_D1 | [8 empty] | 斗六DS.XN71_CB | XN71(23KV斗71線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 63 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0676 |  | 0160 | 1-3A-04 |  |  | XN71 | 79S | XN71 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN71_79UL | 23KV斗71線(XN71) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 64 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0677 |  | 0161 | 1-3A-05 |  |  | XN71 | TAPS | XN71 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN71_LCO_TAP | 23KV斗71線(XN71) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 65 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN72/T1 |  |  | 0316 |  | 0162 | 2-07-04 |  |  | XN72 | 52AS | XN72 CB (ON/OFF) |  | accb | B2/D23_D1 | [8 empty] | 斗六DS.XN72_CB | XN72(23KV斗72線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 66 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0678 |  | 0163 | 1-3A-06 |  |  | XN72 | 79S | XN72 復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN72_79UL | 23KV斗72線(XN72) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 67 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0679 |  | 0164 | 1-3A-07 |  |  | XN72 | TAPS | XN72 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN72_LCO_TAP | 23KV斗72線(XN72) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 68 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN73/T1 |  |  | 0320 |  | 0165 | 2-08-00 |  |  | XN73 | 52AS | XN73 CB (ON/OFF) |  | acdb | B2/D23_D1 | [8 empty] | 斗六DS.XN73_CB | XN73(23KV斗73線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 69 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0680 |  | 0166 | 1-3A-08 |  |  | XN73 | 79S | XN73復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN73_79UL | 23KV斗73線(XN73) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 70 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0681 |  | 0167 | 1-3A-09 |  |  | XN73 | TAPS | XN73 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN73_LCO_TAP | 23KV斗73線(XN73) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 71 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN74/T1 |  |  | 0324 |  | 0168 | 2-08-04 |  |  | XN74 | 52AS | XN74 CB (ON/OFF) |  | aceb | B2/D23_D1 | [8 empty] | 斗六DS.XN74_CB | XN74(23KV斗74線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 72 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0682 |  | 0169 | 1-3A-10 |  |  | XN74 | 79S | XN74復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN74_79UL | 23KV斗74線(XN74) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 73 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0683 |  | 0170 | 1-3A-11 |  |  | XN74 | TAPS | XN74 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN74_LCO_TAP | 23KV斗74線(XN74) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 74 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN75/T1 |  |  | 0328 |  | 0171 | 2-09-00 |  |  | XN75 | 52AS | XN75 8CB (ON/OFF) |  | acfb | B2/D23_D1 | [8 empty] | 斗六DS.XN75_CB | XN75(23KV斗75線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 75 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0684 |  | 0172 | 1-3A-12 |  |  | XN75 | 79S | XN75復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN75_79UL | 23KV斗75線(XN75) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 76 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0685 |  | 0173 | 1-3A-13 |  |  | XN75 | TAPS | XN75 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN75_LCO_TAP | 23KV斗75線(XN75) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 77 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN76/T1 |  |  | 0332 |  | 0174 | 2-09-04 |  |  | XN76 | 52AS | XN76 CB (ON/OFF) |  | achb | B2/D23_D1 | [8 empty] | 斗六DS.XN76_CB | XN76(23KV斗76線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 78 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0686 |  | 0175 | 1-3A-14 |  |  | XN76 | 79S | XN76復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN76_79UL | 23KV斗76線(XN76) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 79 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0687 |  | 0176 | 1-3A-15 |  |  | XN76 | TAPS | XN76 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN76_LCO_TAP | 23KV斗76線(XN76) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 80 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN77/T1 |  |  | 0336 |  | 0177 | 2-0A-00 |  |  | XN77 | 52AS | XN77 CB (ON/OFF) |  | acib | B2/D23_D1 | [8 empty] | 斗六DS.XN77_CB | XN77(23KV斗77線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 81 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0688 |  | 0178 | 1-3B-00 |  |  | XN77 | 79S | XN77復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN77_79UL | 23KV斗77線(XN77) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 82 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0689 |  | 0179 | 1-3B-01 |  |  | XN77 | TAPS | XN77 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN77_LCO_TAP | 23KV斗77線(XN77) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 83 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/4Bus | L/XN78/T1 |  |  | 0340 |  | 0180 | 2-0A-04 |  |  | XN78 | 52AS | XN78 CB (ON/OFF) |  | acjb | B2/D23_D1 | [8 empty] | 斗六DS.XN78_CB | XN78(23KV斗78線) CB | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 84 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0690 |  | 0181 | 1-3B-02 |  |  | XN78 | 79S | XN78復閉電驛閉鎖開關(使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN78_79UL | 23KV斗78線(XN78) 79RY U/L | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 85 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0691 |  | 0182 | 1-3B-03 |  |  | XN78 | TAPS | XN78 LCO TAP (使用/閉鎖) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN78_LCO_TAP | 23KV斗78線(XN78) LCO TAP | FEEDER |  | CDC_Cmd_EMPTY |  |  |  | 86 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/8SC |  |  | 0343 |  | 0183 | 2-0A-07 |  |  | 280 | 52AS | 280 CB (ON/OFF) |  | ackb | B3/D23_A1 | [8 empty] | 斗六DS.280_CB | 280(23KV #8SC) CB | SC |  | CDC_Cmd_EMPTY |  |  |  | 87 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/4DTR |  |  | 0131 |  | 0184 | 1-10-03 |  |  | 370 | 52AS | 370 CB (ON/OFF) |  | acla | ELEM/D23_A1 | [8 empty] | 斗六DS.370_CB | 370(#4DTR) CB | MTR |  | CDC_Cmd_EMPTY |  |  |  | 88 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | T/2SSTR |  |  | 0349 |  | 0185 | 2-0B-05 |  |  | 490 | 52AS | 490 CB (ON/OFF) |  | acmb | B3/D23_A1 | [8 empty] | 斗六DS.490_CB | 490(#2SSTR) CB | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 89 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4Bus | C/7SC |  |  | 0352 |  | 0186 | 2-0C-00 |  |  | 270 | 52AS | 270 CB (ON/OFF) |  | acnb | B3/D23_A1 | [8 empty] | 斗六DS.270_CB | 270(23KV #7SC) CB | SC |  | CDC_Cmd_EMPTY |  |  |  | 90 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0620 |  | 0189 | 1-36-12 |  |  | 照明控制箱 | FLA | 各區照明動作 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.開關場照明(A) | 開關場照明(A) | OTHER |  | CDC_Cmd_EMPTY |  |  |  | 91 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_A1 | [8 empty] | 斗六DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.351 | 351 (非取樣點) | MTR | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.351E | 351E (非取樣點) | MTR | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | D1 | 361(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.361 | 361 (非取樣點) | MTR | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | E1 | 361E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.361E | 361E (非取樣點) | MTR | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | D1 | 371(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.371 | 371 (非取樣點) | MTR | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | E1 | 371E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.371E | 371E (非取樣點) | MTR | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.301 | 301 (非取樣點) | TIE | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.302 | 302 (非取樣點) | TIE | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.302E | 302E(非取樣點) | OTHER | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN61_DS | XN61_DS (非取樣點) | FEEDER | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN61_ES | XN61_ES (非取樣點) | FEEDER | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN62_DS | XN62_DS (非取樣點) | FEEDER | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN62_ES | XN62_ES (非取樣點) | FEEDER | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN63_DS | XN63_DS (非取樣點) | FEEDER | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN63_ES | XN63_ES (非取樣點) | FEEDER | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN64_DS | XN64_DS (非取樣點) | FEEDER | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN64_ES | XN64_ES (非取樣點) | FEEDER | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.251E | 251E (非取樣點) | SC | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.251 | 251 (非取樣點) | SC | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.261E | 261E (非取樣點) | SC | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.261 | 261 (非取樣點) | SC | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN65_DS | XN65_DS (非取樣點) | FEEDER | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN65_ES | XN65_ES (非取樣點) | FEEDER | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN66_DS | XN66_DS (非取樣點) | FEEDER | [5 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN66_ES | XN66_ES (非取樣點) | FEEDER | [5 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN67_DS | XN67_DS (非取樣點) | FEEDER | [5 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN67_ES | XN67_ES (非取樣點) | FEEDER | [5 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN68_DS | XN68_DS (非取樣點) | FEEDER | [5 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN68_ES | XN68_ES (非取樣點) | FEEDER | [5 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.401 | 401 (非取樣點) | TIE | [5 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | D2 | 402 | DEL | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.402 | 402 (非取樣點) | TIE | [5 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.401E | 401E(非取樣點) | OTHER | [5 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | E2 | 402E | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.402E | 402E(非取樣點) | OTHER | [5 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN71_DS | XN71_DS (非取樣點) | FEEDER | [5 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN71_ES | XN71_ES (非取樣點) | FEEDER | [5 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN72_DS | XN72_DS (非取樣點) | FEEDER | [5 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN72_ES | XN72_ES (非取樣點) | FEEDER | [5 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN73_DS | XN73_DS (非取樣點) | FEEDER | [5 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN73_ES | XN73_ES (非取樣點) | FEEDER | [5 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN74_DS | XN74_DS (非取樣點) | FEEDER | [5 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN74_ES | XN74_ES (非取樣點) | FEEDER | [5 empty] | 145 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN75_DS | XN75_DS (非取樣點) | FEEDER | [5 empty] | 146 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN75_ES | XN75_ES (非取樣點) | FEEDER | [5 empty] | 147 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN76_DS | XN76_DS (非取樣點) | FEEDER | [5 empty] | 148 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN76_ES | XN76_ES (非取樣點) | FEEDER | [5 empty] | 149 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN77_DS | XN77_DS (非取樣點) | FEEDER | [5 empty] | 150 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN77_ES | XN77_ES (非取樣點) | FEEDER | [5 empty] | 151 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN78_DS | XN78_DS (非取樣點) | FEEDER | [5 empty] | 152 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D23_D1 | [8 empty] | 斗六DS.XN78_ES | XN78_ES (非取樣點) | FEEDER | [5 empty] | 153 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.281E | 281E (非取樣點) | SC | [5 empty] | 154 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.281 | 281 (非取樣點) | SC | [5 empty] | 155 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 156 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 157 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.271E | 271E (非取樣點) | SC | [5 empty] | 158 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D23_A1 | [8 empty] | 斗六DS.271 | 271 (非取樣點) | SC | [5 empty] | 159 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | M1 | ℃ | #3 DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | M1 | ℃ | #3 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | M2 | ℃ | #4 DTR 線溫指示量 0~120℃ | COIL_-120_120(-2000_2000) |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_COIL | #4DTR 線溫 | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | M2 | ℃ | #4 DTR 油溫指示量 0~120℃ | OIL_-120_120(-2000_2000) |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_OIL | #4DTR 油溫 | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | ------ | MW | 1610 雲林斗六一路瓦量 0~±4000MW | MW_-560_560(-2000_2000) |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_MW | 雲林斗六一路 MW | LINE161 | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | ------ | MVAR | 1610 雲林斗六一路乏量0~±4000MVAR | MVAR_-560_560(-2000_2000) |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_MVAR | 雲林斗六一路 MVAR | LINE161 | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | ------ | MW | 1620 雲林斗六二路瓦量 0~±4000MKW | MW_-560_560(-2000_2000) |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_MW | 雲林斗六二路 MW | LINE161 | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | ------ | MVAR | 1620 雲林斗六二路乏量 0~±4000MKVAR | MVAR_-560_560(-2000_2000) |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_MVAR | 雲林斗六二路 MVAR | LINE161 | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 1610 | KV | 1610 LPT | kV_-210_210(-2000_2000) | aaa | B2/D23_A1 | [8 empty] | 斗六DS.1610LPD_KV | 雲林斗六一路(1610) LPD KV | LINE161 | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 1620 | KV | 1620 LPT | kV_-210_210(-2000_2000) | aab | B2/D23_A1 | [8 empty] | 斗六DS.1620LPD_KV | 雲林斗六二路(1620) LPD KV | LINE161 | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D23 | 斗六DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0037 |  |  | 1-A5 |  |  | 161KV #1B BUS | KV | 161KV #1B BUS電壓量 | kV_-210_210(-2000_2000) | aaa | B2/D23_A1 | [8 empty] | 斗六DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D23 | 斗六DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0038 |  |  | 1-A6 |  |  | 161KV #2B BUS | KV | 161KV #2B BUS電壓量 | kV_-210_210(-2000_2000) | aab | B2/D23_A1 | [8 empty] | 斗六DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 1500 TIE | A | 1500 TIE R相電流量 | A_-2000_2000(-2000_2000) |  | B2/D23_A1 | [8 empty] | 斗六DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0040 |  |  | 1-A8 |  |  | 23KV #3A BUS | KV | 23KV #3A BUS電壓量 | kV_-18_18(-2000_2000) | aaa | B3/D23_A1 | [8 empty] | 斗六DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D23 | 斗六DS | 22 | 22kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0041 |  |  | 1-A9 |  |  | 23KV #3B BUS | KV | 23KV #3B BUS電壓量 | kV_-18_18(-2000_2000) | aba | B3/D23_A1 | [8 empty] | 斗六DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D23 | 斗六DS | 22 | 22kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0042 |  |  | 1-AA |  |  | 23KV #4 BUS | KV | 23KV #4 BUS電壓量 | kV_-18_18(-2000_2000) | aca | B3/D23_A1 | [8 empty] | 斗六DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 300 | A | 300 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 300 | A | 300 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 300 | A | 300 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | XN61 | KVAR | XN61 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗61線KVAR | 23KV斗61線 KVAR | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | XN61 | A | XN61 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗61線A1 | 23KV斗61線 R相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | XN61 | A | XN61 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗61線A2 | 23KV斗61線 S相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | XN61 | A | XN61 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗61線A3 | 23KV斗61線 T相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | XN61 | A | XN61 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗61線A0 | 23KV斗61線 N相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | XN62 | KVAR | XN62 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗62線KVAR | 23KV斗62線 KVAR | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | XN62 | A | XN62 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗62線A1 | 23KV斗62線 R相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | XN62 | A | XN62 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗62線A2 | 23KV斗62線 S相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | XN62 | A | XN62 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗62線A3 | 23KV斗62線 T相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | XN62 | A | XN62 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗62線A0 | 23KV斗62線 N相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | XN63 | KVAR | XN63 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗63線KVAR | 23KV斗63線 KVAR | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | XN63 | A | XN63 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗63線A1 | 23KV斗63線 R相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | XN63 | A | XN63 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗63線A2 | 23KV斗63線 S相AMP | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | XN63 | A | XN63 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗63線A3 | 23KV斗63線 T相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | XN63 | A | XN63 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗63線A0 | 23KV斗63線 N相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | XN64 | KVAR | XN64 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗64線KVAR | 23KV斗64線 KVAR | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | XN64 | A | XN64 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗64線A1 | 23KV斗64線 R相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | XN64 | A | XN64 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗64線A2 | 23KV斗64線 S相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | XN64 | A | XN64 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗64線A3 | 23KV斗64線 T相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | XN64 | A | XN64 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗64線A0 | 23KV斗64線 N相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 350 | KW | 350 瓦量 | MW_-108_108(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 350 | KVAR | 350 乏量 | MVAR_-72_72(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 350 | A | 350 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 350 | A | 350 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 350 | A | 350 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 360 | KW | 360 瓦量 | MW_-108_108(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 360 | KVAR | 360 乏量 | MVAR_-72_72(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 360 | A | 360 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 360 | A | 360 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 360 | A | 360 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | XN65 | KVAR | XN65 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗65線KVAR | 23KV斗65線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | XN65 | A | XN65 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗65線A1 | 23KV斗65線 R相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | XN65 | A | XN65 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗65線A2 | 23KV斗65線 S相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | XN65 | A | XN65 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗65線A3 | 23KV斗65線 T相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | XN65 | A | XN65 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗65線A0 | 23KV斗65線 N相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | XN66 | KVAR | XN66 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗66線KVAR | 23KV斗66線 KVAR | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | XN66 | A | XN66 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗66線A1 | 23KV斗66線 R相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | XN66 | A | XN66 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗66線A2 | 23KV斗66線 S相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | XN66 | A | XN66 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗66線A3 | 23KV斗66線 T相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | XN66 | A | XN66 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗66線A0 | 23KV斗66線 N相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | XN67 | KVAR | XN67 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗67線KVAR | 23KV斗67線 KVAR | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | XN67 | A | XN67 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗67線A1 | 23KV斗67線 R相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | XN67 | A | XN67 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗67線A2 | 23KV斗67線 S相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | XN67 | A | XN67 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗67線A3 | 23KV斗67線 T相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | XN67 | A | XN67 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗67線A0 | 23KV斗67線 N相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | XN68 | KVAR | XN68 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗68線KVAR | 23KV斗68線 KVAR | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | XN68 | A | XN68 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗68線A1 | 23KV斗68線 R相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | XN68 | A | XN68 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗68線A2 | 23KV斗68線 S相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | XN68 | A | XN68 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗68線A3 | 23KV斗68線 T相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | XN68 | A | XN68 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗68線A0 | 23KV斗68線 N相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 400 | A | 400 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_400_A1 | 23KV 400 R相AMP | TIE | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 400 | A | 400 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_400_A2 | 23KV 400 S相AMP | TIE | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 400 | A | 400 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_400_A3 | 23KV 400 T相AMP | TIE | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | XN71 | KVAR | XN71 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗71線KVAR | 23KV斗71線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | XN71 | A | XN71 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗71線A1 | 23KV斗71線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | XN71 | A | XN71 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗71線A2 | 23KV斗71線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | XN71 | A | XN71 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗71線A3 | 23KV斗71線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | XN71 | A | XN71 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗71線A0 | 23KV斗71線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | XN72 | KVAR | XN72 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗72線KVAR | 23KV斗72線 KVAR | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | XN72 | A | XN72 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗72線A1 | 23KV斗72線 R相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | XN72 | A | XN72 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗72線A2 | 23KV斗72線 S相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | XN72 | A | XN72 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗72線A3 | 23KV斗72線 T相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | XN72 | A | XN72 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗72線A0 | 23KV斗72線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | XN73 | KVAR | XN73 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗73線KVAR | 23KV斗73線 KVAR | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | XN73 | A | XN73 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗73線A1 | 23KV斗73線 R相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | XN73 | A | XN73 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗73線A2 | 23KV斗73線 S相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | XN73 | A | XN73 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗73線A3 | 23KV斗73線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | XN73 | A | XN73 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗73線A0 | 23KV斗73線 N相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | XN74 | KVAR | XN74 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗74線KVAR | 23KV斗74線 KVAR | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | XN74 | A | XN74 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗74線A1 | 23KV斗74線 R相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | XN74 | A | XN74 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗74線A2 | 23KV斗74線 S相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | XN74 | A | XN74 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗74線A3 | 23KV斗74線 T相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | XN74 | A | XN74 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗74線A0 | 23KV斗74線 N相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | XN75 | KVAR | XN75 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗75線KVAR | 23KV斗75線 KVAR | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | XN75 | A | XN75 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗75線A1 | 23KV斗75線 R相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | XN75 | A | XN75 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗75線A2 | 23KV斗75線 S相AMP | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | XN75 | A | XN75 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗75線A3 | 23KV斗75線 T相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | XN75 | A | XN75 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗75線A0 | 23KV斗75線 N相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | XN76 | KVAR | XN76 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗76線KVAR | 23KV斗76線 KVAR | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | XN76 | A | XN76 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗76線A1 | 23KV斗76線 R相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | XN76 | A | XN76 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗76線A2 | 23KV斗76線 S相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | XN76 | A | XN76 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗76線A3 | 23KV斗76線 T相AMP | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | XN76 | A | XN76 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗76線A0 | 23KV斗76線 N相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | XN77 | KVAR | XN77 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗77線KVAR | 23KV斗77線 KVAR | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | XN77 | A | XN77 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗77線A1 | 23KV斗77線 R相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | XN77 | A | XN77 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗77線A2 | 23KV斗77線 S相AMP | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | XN77 | A | XN77 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗77線A3 | 23KV斗77線 T相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | XN77 | A | XN77 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗77線A0 | 23KV斗77線 N相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | XN78 | KVAR | XN78 乏量 | KVAR_-21600_21600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗78線KVAR | 23KV斗78線 KVAR | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | XN78 | A | XN78 R相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗78線A1 | 23KV斗78線 R相AMP | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | XN78 | A | XN78 S相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗78線A2 | 23KV斗78線 S相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | XN78 | A | XN78 T相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗78線A3 | 23KV斗78線 T相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | XN78 | A | XN78 N相電流量 | A_-600_600(-2000_2000) |  | B2/D23_D1 | [8 empty] | 斗六DS.斗78線A0 | 23KV斗78線 N相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 370 | KW | 370 瓦量 | MW_-108_108(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#4DTR_MW | #4DTR二次側 MW | MTR | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 370 | KVAR | 370 乏量 | MVAR_-72_72(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 370 | A | 370 R相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 370 | A | 370 S相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 370 | A | 370 T相電流量 | A_-2000_2000(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | Locate Empty | DCP | 直流P電源電壓 | kV_-150_150(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | Locate Empty | DCN | 直流N電源電壓 | kV_-150_150(-2000_2000) |  | B3/D23_A1 | [8 empty] | 斗六DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | R5 | L187A | 1610 雲林斗六一路87RY(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_87A | 雲林斗六一路(1610) 87RY | LINE161 | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | R5 | L1PHA | 1610 雲林斗六一路相間電驛(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_PHA | 雲林斗六一路(1610) 相間RY | LINE161 | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | R5 | L1GDA | 1610 雲林斗六一路接地電驛(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_GDA | 雲林斗六一路(1610) 接地RY | LINE161 | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | R6 | L287A | 1620 雲林斗六二路87RY(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_87A | 雲林斗六二路(1620) 87RY | LINE161 | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | R6 | L2PHA | 1620 雲林斗六二路相間電驛(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_PHA | 雲林斗六二路(1620) 相間RY | LINE161 | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | R6 | L2GDA | 1620 雲林斗六二路接地電驛(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_GDA | 雲林斗六二路(1620) 接地RY | LINE161 | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | R5 | M3APHA | #3 DTR.二次側 M3-A 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | ------ | M3BPHA | #3 DTR.二次側 M3-B 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | R1 | 387A | #3 DTR.差動電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | R5 | 396A | #3 DTR.衝擊油壓電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | R5 | 351ZA | #3 DTR.中性點接地電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | R5 | T3PHA | #3 DTR.一次側相間電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | R5 | T3GDA | #3 DTR.一次側接地電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | R6 | M4APHA | #4 DTR.二次側 M4 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.370_51A | #4DTR二次側(370) 51RY | MTR | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | R2 | 487A | #4 DTR.差動電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_87A | #4DTR 87RY | MTR | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | R6 | 496A | #4 DTR.衝擊油壓電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | R6 | 451ZA | #4 DTR.中性點接地電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | R6 | T4PHA | #4 DTR.一次側相間電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_51A | #4DTR 51RY | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | R6 | T4GDA | #4 DTR.一次側接地電驛(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_51NA | #4DTR 51N RY | MTR | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | R5 | 50A | 161KV TIE 瞬時電驛 (動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | R5 | 87B1A | 161KV #1 BUS 87電驛 (動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | R5 | 87B2A | 161KV #2 BUS 87電驛 (動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | M5 | OSCA | 示波器啟動警報(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | ------ | 25TA | 161KV GIS 25電驛超時警報 (COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | ------ | RCA | 161KV 復閉電驛(動作/正常)(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0123 |  |  | 1-0F-03 |  |  | 350 | PHA | 350 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 350 | #3DTR(A)(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | 350 | GDA | 350 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | 360 | PHA | 360 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 360 | #3DTR(B)(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 360 | GDA | 360 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.360_GDA | 360開關箱IED RY GDA | OTHER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 370 | PHA | 370 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 370 | #4DTR(370) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 370 | GDA | 370 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.370_GDA | 370開關箱IED RY GDA | OTHER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | 300 | PHA | 300 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 300 | GDA | 300 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | XN61 | PHA | XN61 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN61_PHA | 23KV斗61線(XN61) 相間RY | FEEDER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | XN61 | GDA | XN61 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN61_GDA | 23KV斗61線(XN61) 接地RY | FEEDER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | XN62 | PHA | XN62 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN62_PHA | 23KV斗62線(XN62) 相間RY | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | XN62 | GDA | XN62 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN62_GDA | 23KV斗62線(XN62) 接地RY | FEEDER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | XN63 | PHA | XN63 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN63_PHA | 23KV斗63線(XN63) 相間RY | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | XN63 | GDA | XN63 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN63_GDA | 23KV斗63線(XN63) 接地RY | FEEDER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 |  |  | 2-01-07 |  |  | XN64 | PHA | XN64 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN64_PHA | 23KV斗64線(XN64) 相間RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | XN64 | GDA | XN64 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN64_GDA | 23KV斗64線(XN64) 接地RY | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | 250 | SCA | 250 相間及接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 2-02-04 |  |  | 250 | 3AUVA | 250 欠壓電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | 260 | SCA | 260 相間及接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | 260 | 3BUVA | 260 欠壓電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | 390 | PHA | 390 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | 390 | GDA | 390 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | XN65 | PHA | XN65 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN65_PHA | 23KV斗65線(XN65) 相間RY | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | XN65 | GDA | XN65 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN65_GDA | 23KV斗65線(XN65) 接地RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | XN66 | PHA | XN66 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN66_PHA | 23KV斗66線(XN66) 相間RY | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 2-04-07 |  |  | XN66 | GDA | XN66 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN66_GDA | 23KV斗66線(XN66) 接地RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0298 |  |  | 2-05-02 |  |  | XN67 | PHA | XN67 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN67_PHA | 23KV斗67線(XN67) 相間RY | FEEDER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | XN67 | GDA | XN67 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN67_GDA | 23KV斗67線(XN67) 接地RY | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | XN68 | PHA | XN68 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN68_PHA | 23KV斗68線(XN68) 相間RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | XN68 | GDA | XN68 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN68_GDA | 23KV斗68線(XN68) 接地RY | FEEDER | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | 400 | PHA | 400 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.400_51A | 23KV TIE(400) 51RY | TIE | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 2-06-03 |  |  | 400 | GDA | 400 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.400_51NA | 23KV TIE(400) 51N RY | TIE | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | XN71 | PHA | XN71 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN71_PHA | 23KV斗71線(XN71) 相間RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 2-06-06 |  |  | XN71 | GDA | XN71 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN71_GDA | 23KV斗71線(XN71) 接地RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 2-07-01 |  |  | XN72 | PHA | XN72 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN72_PHA | 23KV斗72線(XN72) 相間RY | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | XN72 | GDA | XN72 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN72_GDA | 23KV斗72線(XN72) 接地RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | XN73 | PHA | XN73 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN73_PHA | 23KV斗73線(XN73) 相間RY | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | XN73 | GDA | XN73 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN73_GDA | 23KV斗73線(XN73) 接地RY | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | XN74 | PHA | XN74 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN74_PHA | 23KV斗74線(XN74) 相間RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 |  |  | 2-08-02 |  |  | XN74 | GDA | XN74 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN74_GDA | 23KV斗74線(XN74) 接地RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 2-08-05 |  |  | XN75 | PHA | XN75 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN75_PHA | 23KV斗75線(XN75) 相間RY | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | XN75 | GDA | XN75 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN75_GDA | 23KV斗75線(XN75) 接地RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | XN76 | PHA | XN76 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN76_PHA | 23KV斗76線(XN76) 相間RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | XN76 | GDA | XN76 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN76_GDA | 23KV斗76線(XN76) 接地RY | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | XN77 | PHA | XN77 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN77_PHA | 23KV斗77線(XN77) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 |  |  | 2-09-06 |  |  | XN77 | GDA | XN77 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN77_GDA | 23KV斗77線(XN77) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-0A-01 |  |  | XN78 | PHA | XN78 相間電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN78_PHA | 23KV斗78線(XN78) 相間RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | XN78 | GDA | XN78 接地電驛(動作/正常) |  |  | B2/D23_D1 | [8 empty] | 斗六DS.XN78_GDA | 23KV斗78線(XN78) 接地RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | 280 | SCA | 280 相間及接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | 280 | 4AUVA | 280 欠壓電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | 490 | PHA | 490 相間電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | 490 | GDA | 490 接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 2-0B-06 |  |  | 270 | SCA | 270 相間及接地電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 2-0B-07 |  |  | 270 | 3BUVA | 270 欠壓電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | ComPoint |  |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | ------ | 2 RCA | 23KV 79電驛(動作/正常) (COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_RCA | 11/23KV 饋線 79RY復閉動作 | OTHER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0513 |  |  | 1-30-01 |  |  | M1 | 3TRA | #3 DTR 重故障警報(動作/正常) |  | a | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0514 |  |  | 1-30-02 |  |  | M1 | 3TRF | #3 DTR 輕故障警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | M1 | 363Q | #3 DTR ULTC 保護電驛警報 |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | M1 | 396D | #3 DTR 放壓電驛警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | M1 | 396B2 | #3 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | M1 | 396B1 | #3 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | M1 | 343RS1 | #3 DTR WIND位置(SUP/LOC) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | M1 | 396P | #3 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0524 |  |  | 1-30-12 |  |  | M2 | 4TRA | #4 DTR 重故障警報(動作/正常) |  | a | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_TRA | #4DTR 重故障 | MTR | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | M2 | 4TRF | #4 DTR 輕故障警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_TRF | #4DTR 輕故障 | MTR | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | M2 | 463Q | #4 DTR ULTC 保護電驛警報 |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_63Q | #4DTR 63Q RY | MTR | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | M2 | 496D | #4 DTR 放壓電驛警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_96D | #4DTR 96D RY | MTR | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0530 |  |  | 1-31-02 |  |  | M2 | 496B2 | #4 DTR 撲氣電驛第二段警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0531 |  |  | 1-31-03 |  |  | M2 | 496B1 | #4 DTR 撲氣電驛第一段警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | M2 | 443RS1 | #4 DTR WIND 位置(SUP/LOC) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0534 |  |  | 1-31-06 |  |  | M2 | 496P | #4 DTR 衝擊油壓電驛警報(動作/正常) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_96P | #4DTR 96P RY | MTR | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0535 |  |  | 1-31-07 |  |  | ------ | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | M5 | OSCF | 示波器故障或缺紙 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_OSCF | 161KV示波器故障 | OTHER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | M5 | 1RYFA | 1610 數位電驛故障 |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_RYFA | 雲林斗六一路(1610)數位電驛故障 | OTHER | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | M6 | 2RYFA | 1620 數位電驛故障 |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_RYFA | 雲林斗六二路(1620)數位電驛故障 | OTHER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | R1 | 387S | #3 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | R2 | 487S | #4 DTR 差動電驛鎖開關(使用/閉鎖) |  |  | B1/D23_A1 | [8 empty] | 斗六DS.#4DTR_87UL | #4DTR 87RY U/L | MTR | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | R5 | RYFA | 161KV BUS數位電驛故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | R5 | 87CTFA | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-35-04 |  |  | M5 | 60A | SC 60電驛(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | M6 | CBA | 161KV GIS 重故障(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0598 |  |  | 1-35-06 |  |  | M6 | CBF | 161KV GIS 輕故障(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | M5 | 87CFA | 1610 雲林斗六一路87RY通訊故障(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1610_87CFA | 雲林斗六一路(1610)87RY通訊故障 | OTHER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 1-35-08 |  |  | M5 | 87CFA | 1620 雲林斗六二路87RY通訊故障(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1620_87CFA | 雲林斗六二路(1620)87RY通訊故障 | OTHER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | R5 | 50SA | 1500 RY測試/正常 |  |  | B2/D23_A1 | [8 empty] | 斗六DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | M5 | CHG1 | 設備用充電機警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.直流充電機故障 | 變電所直流充電機故障 | OTHER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | M5 | CHG2 | 通訊用充電機警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | M5 | DCE | D.C接地警報 |  |  | ELEM/D23_A1 | [8 empty] | 斗六DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | 直流電源盤 | DCA | 直流NFB跳脫警報 |  |  | ELEM/D23_A1 | [8 empty] | 斗六DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Door1 | 控制室及大門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | 保全控制盤 | DOR | 控制室及大門開啟警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.無人化門禁(1) | 無人化門禁(1)建築物,控制室大門 | OTHER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | 火災警報(1) | FIR | 火災警報(1)受信總機 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | 390&490盤 | STUV | 所內變壓器欠壓警報 |  |  | ELEM/D23_A1 | [8 empty] | 斗六DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | 通訊盤 | ACF | 通訊設備AC故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | ------ | ------ | 緊急發電機運轉 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Gateway1 |  |  | Status | Gateway 1故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0623 |  |  | 1-36-15 |  |  | 通訊盤 | OLMa | 通訊設備光纖主故障 |  |  | B3/D23_A1 | [16 empty] | 398 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Gateway2 |  |  | Status | Gateway 2故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0624 |  |  | 1-37-00 |  |  | 通訊盤 | OLMi | 通訊設備光纖次故障 |  |  | B3/D23_A1 | [16 empty] | 399 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室或控制室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | 通訊盤 | TEMPA | 通訊室或控制室溫度警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0626 |  |  | 1-37-02 |  |  | M5 | VUA1 | 一號匯流排欠壓電驛(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0627 |  |  | 1-37-03 |  |  | M5 | VUA2 | 二號匯流排欠壓電驛(動作/正常) |  |  | B2/D23_A1 | [8 empty] | 斗六DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | 2A5Other | 排水泵故障1 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0628 |  |  | 1-37-04 |  |  | ------ | PUPA1 | 揚水泵故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.揚水幫浦 | 揚水幫浦故障 | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 排水泵故障2_涵洞1 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | ------ | PUPA2 | 涵洞1排水汞故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.涵洞排水泵(1) | 涵洞排水幫浦故障(1) | OTHER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | 4A5Other | 排水泵故障3_涵洞2 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0630 |  |  | 1-37-06 |  |  | ------ | PUPA3 | 涵洞2排水汞故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.涵洞排水泵(2) | 涵洞排水幫浦故障(2) | OTHER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | 5A5Other | 排水泵故障4_涵洞3 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0631 |  |  | 1-37-07 |  |  | ------ | PUPA4 | 涵洞3排水汞故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.涵洞排水泵(3) | 涵洞排水幫浦故障(3) | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Water1 | 地下室第一段 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | M5 | WP-1 | 地下室淹水警報(第一段) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Water2 | 地下室第二段 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0633 |  |  | 1-37-09 |  |  | M5 | WP-2 | 地下室淹水警報(第二段) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0634 |  |  | 1-37-10 |  |  | ACBS1 | ACB1 | 所內電源ACB1 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | ACBS2 | ACB2 | 所內電源ACB2 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0636 |  |  | 1-37-12 |  |  | ACBS3 | ACB TIE | 所內電源ACB TIE |  |  | B3/D23_A1 | [8 empty] | 斗六DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0637 |  |  | 1-37-13 |  |  | 監控主機 | SUPA | Local SCADA故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.SCADA | LOCAL SCADA故障 | OTHER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Comm_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | 通訊處理單元 | COM S/L | 通訊處理單元LOCAL//REMOTE |  |  | B3/D23_A1 | [8 empty] | 斗六DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Rem | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 22 | 22kV | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0641 |  |  | 1-38-01 |  |  | ------ | 22 CBA | 23KV GIS 重故障(COMMON) |  |  | ELEM/D23_D1 | [8 empty] | 斗六DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0642 |  |  | 1-38-02 |  |  | ------ | 22 CBF | 23KV GIS 輕故障(COMMON) |  |  | ELEM/D23_D1 | [8 empty] | 斗六DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0643 |  |  | 1-38-03 |  |  | ------ | LOA | 23KV GIS 復閉不成功閉鎖(動作/正常)(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0644 |  |  | 1-38-04 |  |  | ------ | ACBA | 所內AC電源用ACB(故障警報) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | 6A5Other | 集油池抽水泵閉鎖 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0645 |  |  | 1-38-05 |  |  | 集油池 | OWF | 集油池抽水汞閉鎖(動作/正常) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.OWFA | 洩油池抽水泵警報 | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 | 集油池 |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0646 |  |  | 1-38-06 |  |  | M5 | OW-1 | 集油池警報(第一段) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 | 集油池 |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0647 |  |  | 1-38-07 |  |  | M5 | OW-2 | 集油池警報(第二段) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | 7A5Other | 專線數據機電源故障 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0648 |  |  | 1-38-08 |  |  | ------ | RXTX | 專線數據機電源故障 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.MODEMF | 專線數據機電源故障 | OTHER | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0649 |  |  | 1-38-09 |  |  | ------ | MCCA | MCC IED ALARM |  |  | B3/D23_A1 | [8 empty] | 斗六DS.MCCA | MCC IED 故障 | OTHER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0650 |  |  | 1-38-10 |  |  | ------ | PMCCA | PMCC IED ALARM |  |  | B3/D23_A1 | [8 empty] | 斗六DS.PMCCA | PMCC IED 故障 | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | TCA |  |  | Status | 斷路器跳脫迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0651 |  |  | 1-38-11 |  |  | ------ | TCSA | 斷路器跳脫迴圈監視警報(動作/正常)(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.TCA | 斷路器跳脫回路故障 | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Water3 | 涵洞1 |  | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0652 |  |  | 1-38-12 |  |  | ------ | PUP1 | 涵洞1淹水警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.涵洞水位(1) | 涵洞淹水警報(1) | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Water4 | 涵洞2 |  | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0653 |  |  | 1-38-13 |  |  | ------ | PUP2 | 涵洞2淹水警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.涵洞水位(2) | 涵洞淹水警報(2) | OTHER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Water5 |  | Element | Status | 淹水警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0654 |  |  | 1-38-14 |  |  | ------ | PUP3 | 涵洞3淹水警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.涵洞水位(3) | 涵洞淹水警報(3) | OTHER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Burglar | 保全 |  | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0655 |  |  | 1-38-15 |  |  | ------ | ------ | 保全警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | Door | 小門開啟 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0656 |  |  | 1-39-00 |  |  | 保全控制盤 | DOR | 小門開啟警報 |  |  | B3/D23_A1 | [8 empty] | 斗六DS.無人化門禁(2) | 無人化門禁(2)小門開啟警報 | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | PMCC_R_L | PMCC Remote/Local | Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0657 |  |  | 1-39-01 |  |  | ------ | MCCA | 161KV IED非Remote位置警報(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.MCC_IED_S/L | 161KV IED SUPY/LOCAL | OTHER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 0 |  | StaDev | 所內設施 |  | PMCC_R_L |  |  | Status | PMCC Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0658 |  |  | 1-39-02 |  |  | ------ | PMCCA | 23KV IED非Remote位置警報(COMMON) |  |  | B3/D23_A1 | [8 empty] | 斗六DS.PMCC_IED_S/L | 23KV IED SUPY/LOCAL | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Rem | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E | INSERT | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus |  |  |  | 0788 | 789 |  | 2-31-04 | 2-31-05 |  | BUS PT | ES(ON) | 15B1E ES ON |  | aafz | B2/D23_A1 | [8 empty] | 斗六DS.15B1E_ES | 15B1E_ES | OTHER | [5 empty] | 432 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E | INSERT | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus |  |  |  | 0790 | 791 |  | 2-31-06 | 2-31-07 |  | BUS PT | ES(ON) | 15B2E ES ON |  | aafz | B2/D23_A1 | [8 empty] | 斗六DS.15B2E_ES | 15B2E | OTHER | [5 empty] | 433 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D23 | 斗六DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D23_A1 | [12 empty] | 斗六DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D23/161/1BUS/V; OPRD2: D23/161/2BUS/V
D23 | 斗六DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D23_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D23/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D23 | 斗六DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D23_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: D23/161/1610/MW; OPRD2: D23/161/1620/MW
D23 | 斗六DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D23_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D23/0/CalcPoint/OPRN2_MW
D23 | 斗六DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D23_A1 | [17 empty] | none
D23 | 斗六DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D23_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D23/0/CalcPoint/OPRN1; OPRD2: D23/0/CalcPoint/OPRN2; OPRD3: D23/0/CalcPoint/PRFL_UL
D23 | 斗六DS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D23_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D23/22/350/I_R; OPRD2: D23/22/360/I_R
D23 | 斗六DS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D23_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D23/22/350/I_S; OPRD2: D23/22/360/I_S
D23 | 斗六DS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D23_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D23/22/350/I_T; OPRD2: D23/22/360/I_T
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林～斗六一路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D23_A1 | [12 empty] | 斗六DS.1610_AMP | 雲林斗六一路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D23/161/1610/MW; OPRD2: D23/161/1610/MVAR; OPRD3: D23/0/CalcPoint/Vbs4
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林～斗六二路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D23_A1 | [12 empty] | 斗六DS.1620_AMP | 雲林斗六二路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D23/161/1620/MW; OPRD2: D23/161/1620/MVAR; OPRD3: D23/0/CalcPoint/Vbs4
D23 | 斗六DS | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D23_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D23/22/3ABUS/V
D23 | 斗六DS | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D23_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D23/22/3BBUS/V
D23 | 斗六DS | 22 | 22kV | 4BUS | #4BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D23_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D23/22/4BUS/V
D23 | 斗六DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D23_A1 | [12 empty] | 斗六DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D23//3DTR/SupLocal; OPRD2: D23//3DTR/Tap Chan
D23 | 斗六DS |  |  | 4DTR | #4DTR |  | TR_PERM | [9 empty] | B1/D23_A1 | [12 empty] | 斗六DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D23//4DTR/SupLocal; OPRD2: D23//4DTR/Tap Chan
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3ABUS/V; OPRD2: D23/22/XN61/I_R; OPRD3: D23/22/XN61/I_S; OPRD4: D23/22/XN61/I_T
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3ABUS/V; OPRD2: D23/22/XN62/I_R; OPRD3: D23/22/XN62/I_S; OPRD4: D23/22/XN62/I_T
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3ABUS/V; OPRD2: D23/22/XN63/I_R; OPRD3: D23/22/XN63/I_S; OPRD4: D23/22/XN63/I_T
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3ABUS/V; OPRD2: D23/22/XN64/I_R; OPRD3: D23/22/XN64/I_S; OPRD4: D23/22/XN64/I_T
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3BBUS/V; OPRD2: D23/22/XN65/I_R; OPRD3: D23/22/XN65/I_S; OPRD4: D23/22/XN65/I_T
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3BBUS/V; OPRD2: D23/22/XN66/I_R; OPRD3: D23/22/XN66/I_S; OPRD4: D23/22/XN66/I_T
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3BBUS/V; OPRD2: D23/22/XN67/I_R; OPRD3: D23/22/XN67/I_S; OPRD4: D23/22/XN67/I_T
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/3BBUS/V; OPRD2: D23/22/XN68/I_R; OPRD3: D23/22/XN68/I_S; OPRD4: D23/22/XN68/I_T
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN71/I_R; OPRD3: D23/22/XN71/I_S; OPRD4: D23/22/XN71/I_T
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN72/I_R; OPRD3: D23/22/XN72/I_S; OPRD4: D23/22/XN72/I_T
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN73/I_R; OPRD3: D23/22/XN73/I_S; OPRD4: D23/22/XN73/I_T
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN74/I_R; OPRD3: D23/22/XN74/I_S; OPRD4: D23/22/XN74/I_T
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN75/I_R; OPRD3: D23/22/XN75/I_S; OPRD4: D23/22/XN75/I_T
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN76/I_R; OPRD3: D23/22/XN76/I_S; OPRD4: D23/22/XN76/I_T
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN77/I_R; OPRD3: D23/22/XN77/I_S; OPRD4: D23/22/XN77/I_T
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D23/22/4BUS/V; OPRD2: D23/22/XN78/I_R; OPRD3: D23/22/XN78/I_S; OPRD4: D23/22/XN78/I_T
D23 | 斗六DS | 22 | 22kV | XN61 | 斗六一線(XN61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN61/kVA; OPRD2: D23/22/XN61/KVAR
D23 | 斗六DS | 22 | 22kV | XN62 | 斗六二線(XN62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN62/kVA; OPRD2: D23/22/XN62/KVAR
D23 | 斗六DS | 22 | 22kV | XN63 | 斗六三線(XN63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN63/kVA; OPRD2: D23/22/XN63/KVAR
D23 | 斗六DS | 22 | 22kV | XN64 | 斗六四線(XN64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN64/kVA; OPRD2: D23/22/XN64/KVAR
D23 | 斗六DS | 22 | 22kV | XN65 | 斗六五線(XN65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN65/kVA; OPRD2: D23/22/XN65/KVAR
D23 | 斗六DS | 22 | 22kV | XN66 | 斗六六線(XN66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN66/kVA; OPRD2: D23/22/XN66/KVAR
D23 | 斗六DS | 22 | 22kV | XN67 | 斗六七線(XN67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN67/kVA; OPRD2: D23/22/XN67/KVAR
D23 | 斗六DS | 22 | 22kV | XN68 | 斗六八線(XN68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN68/kVA; OPRD2: D23/22/XN68/KVAR
D23 | 斗六DS | 22 | 22kV | XN71 | 斗七一線(XN71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN71/kVA; OPRD2: D23/22/XN71/KVAR
D23 | 斗六DS | 22 | 22kV | XN72 | 斗七二線(XN72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN72/kVA; OPRD2: D23/22/XN72/KVAR
D23 | 斗六DS | 22 | 22kV | XN73 | 斗七三線(XN73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN73/kVA; OPRD2: D23/22/XN73/KVAR
D23 | 斗六DS | 22 | 22kV | XN74 | 斗七四線(XN74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN74/kVA; OPRD2: D23/22/XN74/KVAR
D23 | 斗六DS | 22 | 22kV | XN75 | 斗七五線(XN75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN75/kVA; OPRD2: D23/22/XN75/KVAR
D23 | 斗六DS | 22 | 22kV | XN76 | 斗七六線(XN76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN76/kVA; OPRD2: D23/22/XN76/KVAR
D23 | 斗六DS | 22 | 22kV | XN77 | 斗七七線(XN77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN77/kVA; OPRD2: D23/22/XN77/KVAR
D23 | 斗六DS | 22 | 22kV | XN78 | 斗七八線(XN78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D23_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D23/22/XN78/kVA; OPRD2: D23/22/XN78/KVAR
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D23_A1 | [12 empty] | 斗六DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D23/22/250/CB; OPRD2: 13.8; OPRD3: 0
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D23_A1 | [12 empty] | 斗六DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D23/22/260/CB; OPRD2: 13.8; OPRD3: 0
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D23_A1 | [12 empty] | 斗六DS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D23/22/270/CB; OPRD2: 13.8; OPRD3: 0
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D23_A1 | [12 empty] | 斗六DS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D23/22/280/CB; OPRD2: 13.8; OPRD3: 0
D23 | 斗六DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D23_A1 | [12 empty] | 斗六DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_25 | OPRD1: D23//3DTR/96B2; OPRD2: D23//3DTR/96B1; OPRD3: D23//3DTR/96D; OPRD4: D23//3DTR/TRA; OPRD5: D23//3DTR/63Q; OPRD6: D23//3DTR/96PA; OPRD7: D23//3DTR/87A; OPRD8: D23//3DTR/51ZA; OPRD9: D23//3DTR/GDA; OPRD10: D23//3DTR/PHA; OPRD11: D23//4DTR/96B2; OPRD12: D23//4DTR/96D; OPRD13: D23//4DTR/96B1; OPRD14: D23//4DTR/51ZA; OPRD15: D23//4DTR/96PA; OPRD16: D23//4DTR/87A; OPRD17: D23//4DTR/PHA; OPRD18: D23//4DTR/TRA; OPRD19: D23//4DTR/63Q; OPRD20: D23//4DTR/GDA; OPRD21: D23/161/1BUS/87A; OPRD22: D23/161/2BUS/87A; OPRD23: D23/22/350/GDA; OPRD24: D23/22/360/GDA; OPRD25: D23/22/370/GDA
D23 | 斗六DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D23_A1 | [12 empty] | 斗六DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D23//3DTR/TRF; OPRD2: D23//4DTR/TRF
D23 | 斗六DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/161/1770/CB
D23 | 斗六DS | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/161/1780/CB
D23 | 斗六DS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/22/350/CB
D23 | 斗六DS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/22/360/CB
D23 | 斗六DS | 22 | 22kV | 370_D1 | #4DTR(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/22/370/CB
D23 | 斗六DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/0/StaDev/DCE
D23 | 斗六DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/0/StaDev/DCA
D23 | 斗六DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D23_D1 | [17 empty] | lamp2CC | OPRD1: D23/0/StaDev/STUV

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D23 | 斗六DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D23/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗六DS.1610_AMP | 雲林斗六一路 AMP | LINE161 | D23/161/1610/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | I | [25 empty] | ADCS_N | [8 empty] | 斗六DS.1620_AMP | 雲林斗六二路 AMP | LINE161 | D23/161/1620/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗61線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗61線KVA | 23KV斗61線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗61線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗61線KW | 23KV斗61線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗62線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗62線KVA | 23KV斗62線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗62線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗62線KW | 23KV斗62線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗63線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗63線KVA | 23KV斗63線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗63線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗63線KW | 23KV斗63線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗64線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗64線KVA | 23KV斗64線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗64線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗64線KW | 23KV斗64線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗65線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗65線KVA | 23KV斗65線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗65線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗65線KW | 23KV斗65線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗66線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗66線KVA | 23KV斗66線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗66線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗66線KW | 23KV斗66線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗67線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗67線KVA | 23KV斗67線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗67線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗67線KW | 23KV斗67線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗68線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗68線KVA | 23KV斗68線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗68線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗68線KW | 23KV斗68線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗71線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗71線KVA | 23KV斗71線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗71線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗71線KW | 23KV斗71線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗72線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗72線KVA | 23KV斗72線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗72線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗72線KW | 23KV斗72線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗73線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗73線KVA | 23KV斗73線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗73線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗73線KW | 23KV斗73線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗74線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗74線KVA | 23KV斗74線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗74線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗74線KW | 23KV斗74線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗75線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗75線KVA | 23KV斗75線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗75線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗75線KW | 23KV斗75線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗76線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗76線KVA | 23KV斗76線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗76線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗76線KW | 23KV斗76線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗77線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗77線KVA | 23KV斗77線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗77線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗77線KW | 23KV斗77線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗78線KVA | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗78線KVA | 23KV斗78線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  |  |  |  | 斗78線KW | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.斗78線KW | 23KV斗78線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 38 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 41 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 44 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_PF | #4DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_MW | #3DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_MVAR | #3DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 49 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D23 | 斗六DS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗六DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D23/22/250/MVAR |  | SC_CAL_23 |  |  | 50 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗六DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D23/22/260/MVAR |  | SC_CAL_23 |  |  | 51 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 270_SC | #7SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗六DS.270_SC_MVAR | 23KV#7SC MVAR | SC | D23/22/270/MVAR |  | SC_CAL_23 |  |  | 52 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 280_SC | #8SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 斗六DS.280_SC_MVAR | 23KV#8SC MVAR | SC | D23/22/280/MVAR |  | SC_CAL_23 |  |  | 53 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  | TRTOT | 斗六主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 斗六DS.TRTOT_MW | 斗六主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 0 |  | TRTOT | 斗六主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 斗六DS.TRTOT_MVAR | 斗六主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 3BUS | #3BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 斗六DS.23KV#3BUS_KV | 23KV #3BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 56 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D23 | 斗六DS | 0 |  | 300_CB | 300(300_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.300_CB_1 | 300 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 58 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 400_CB | 400(400_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.400_CB_1 | 400 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 59 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.1770_CB_1 | 1770(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 60 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.350_CB_1 | 350(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 61 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 360_CB | #3DTR(360_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.360_CB_1 | 360(#3DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 62 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 1780_CB | #4DTR(1780_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.1780_CB_1 | 1780(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 63 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 370_CB | #4DTR(370_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.370_CB_1 | 370(#4DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 64 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.250_CB_1 | 250(23KV #5SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 65 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.260_CB_1 | 260(23KV #6SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 66 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.270_CB_1 | 270(23KV #7SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 67 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 280_CB | #8SC(280_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.280_CB_1 | 280(23KV #8SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 68 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.11/23KV_CBA_1 | 11/23KV斷路器重故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 69 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 70 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 斗六DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D23/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 71 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 斗六DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D23/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 72 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 73 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 74 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610_AMP | 雲林斗六一路 | [27 empty] | ADCS_N | [8 empty] | 斗六DS.1610_AMP_A | 雲林斗六一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620_AMP | 雲林斗六二路 | [27 empty] | ADCS_N | [8 empty] | 斗六DS.1620_AMP_A | 雲林斗六二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D23//3DTR/TR_PERM |  | DTR_PERM |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_PERM | #4DTR TAP PERMISSION POINT | MTR | D23//4DTR/TR_PERM |  | DTR_PERM |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 3DTR_MVA | #3DTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.#3DTR_MVA_1 | #3DTR MVA 點燈 (D1) | MTR |  |  | AD_LAMP_DD_2 |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | DDCS1_1 | [8 empty] | 斗六DS.#3DTR_MVA_2 | #3DTR MVA 點燈 (D1) | MTR |  |  | AD_LAMP_DD_2 |  |  | 81 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 82 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 4DTR_MVA | #4DTR |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 斗六DS.#4DTR_MVA_1 | #4DTR MVA 點燈 (D1) | MTR |  |  | AD_LAMP_DD_2 |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 斗六DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 84 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 斗六DS.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 斗六DS.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 4BUS | #4BUS |  | 23KV#4BUSC | [25 empty] | CDCS | [8 empty] | 斗六DS.23KV#4BUSC | #4BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 斗六DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T2 |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 斗六DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B3 |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D23 | 斗六DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 斗六DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 90 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 斗六DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-A5 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D23/161/1BUS/V |  |  |  | CDC | 92 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D23 | 斗六DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-A6 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D23/161/2BUS/V |  |  |  | CDC | 93 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D23 | 斗六DS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [17 empty] | 1-A8 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | D23/22/3ABUS/V |  |  |  | CDC | 94 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D23 | 斗六DS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [17 empty] | 1-A9 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | D23/22/3BBUS/V |  |  |  | CDC | 95 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D23 | 斗六DS | 22 | 22kV | 4BUS | #4BUS |  | V | [17 empty] | 1-AA | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV#4BUS_KV | 23KV #4BUS KV | BUS | D23/22/4BUS/V |  |  |  | CDC | 96 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1610_MW | 雲林斗六一路 MW | LINE161 | D23/161/1610/MW |  |  |  | CDC | 97 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1610_MVAR | 雲林斗六一路 MVAR | LINE161 | D23/161/1610/MVAR |  |  |  | CDC | 98 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1620_MW | 雲林斗六二路 MW | LINE161 | D23/161/1620/MW |  |  |  | CDC | 99 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1620_MVAR | 雲林斗六二路 MVAR | LINE161 | D23/161/1620/MVAR |  |  |  | CDC | 100 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗61線 | 斗61線 |  | 斗61線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗61線KVAR | 23KV斗61線 KVAR | FEEDER | D23/22/XN61/KVAR |  |  |  | CDC | 101 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗61線 | 斗61線 |  | 斗61線A1 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗61線A1 | 23KV斗61線 R相AMP | FEEDER | D23/22/XN61/I_R |  |  |  | CDC | 102 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗61線 | 斗61線 |  | 斗61線A2 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗61線A2 | 23KV斗61線 S相AMP | FEEDER | D23/22/XN61/I_S |  |  |  | CDC | 103 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗61線 | 斗61線 |  | 斗61線A3 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗61線A3 | 23KV斗61線 T相AMP | FEEDER | D23/22/XN61/I_T |  |  |  | CDC | 104 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗61線 | 斗61線 |  | 斗61線A0 | [17 empty] | 1-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗61線A0 | 23KV斗61線 N相AMP | FEEDER | D23/22/XN61/I_N |  |  |  | CDC | 105 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗62線 | 斗62線 |  | 斗62線KVAR | [17 empty] | 1-B3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗62線KVAR | 23KV斗62線 KVAR | FEEDER | D23/22/XN62/KVAR |  |  |  | CDC | 106 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗62線 | 斗62線 |  | 斗62線A1 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗62線A1 | 23KV斗62線 R相AMP | FEEDER | D23/22/XN62/I_R |  |  |  | CDC | 107 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗62線 | 斗62線 |  | 斗62線A2 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗62線A2 | 23KV斗62線 S相AMP | FEEDER | D23/22/XN62/I_S |  |  |  | CDC | 108 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗62線 | 斗62線 |  | 斗62線A3 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗62線A3 | 23KV斗62線 T相AMP | FEEDER | D23/22/XN62/I_T |  |  |  | CDC | 109 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗62線 | 斗62線 |  | 斗62線A0 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗62線A0 | 23KV斗62線 N相AMP | FEEDER | D23/22/XN62/I_N |  |  |  | CDC | 110 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗63線 | 斗63線 |  | 斗63線KVAR | [17 empty] | 1-B8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗63線KVAR | 23KV斗63線 KVAR | FEEDER | D23/22/XN63/KVAR |  |  |  | CDC | 111 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗63線 | 斗63線 |  | 斗63線A1 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗63線A1 | 23KV斗63線 R相AMP | FEEDER | D23/22/XN63/I_R |  |  |  | CDC | 112 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗63線 | 斗63線 |  | 斗63線A2 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗63線A2 | 23KV斗63線 S相AMP | FEEDER | D23/22/XN63/I_S |  |  |  | CDC | 113 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗63線 | 斗63線 |  | 斗63線A3 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗63線A3 | 23KV斗63線 T相AMP | FEEDER | D23/22/XN63/I_T |  |  |  | CDC | 114 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗63線 | 斗63線 |  | 斗63線A0 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗63線A0 | 23KV斗63線 N相AMP | FEEDER | D23/22/XN63/I_N |  |  |  | CDC | 115 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗64線 | 斗64線 |  | 斗64線KVAR | [17 empty] | 1-BD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗64線KVAR | 23KV斗64線 KVAR | FEEDER | D23/22/XN64/KVAR |  |  |  | CDC | 116 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗64線 | 斗64線 |  | 斗64線A1 | [17 empty] | 1-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗64線A1 | 23KV斗64線 R相AMP | FEEDER | D23/22/XN64/I_R |  |  |  | CDC | 117 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗64線 | 斗64線 |  | 斗64線A2 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗64線A2 | 23KV斗64線 S相AMP | FEEDER | D23/22/XN64/I_S |  |  |  | CDC | 118 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗64線 | 斗64線 |  | 斗64線A3 | [17 empty] | 1-C0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗64線A3 | 23KV斗64線 T相AMP | FEEDER | D23/22/XN64/I_T |  |  |  | CDC | 119 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗64線 | 斗64線 |  | 斗64線A0 | [17 empty] | 1-C1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗64線A0 | 23KV斗64線 N相AMP | FEEDER | D23/22/XN64/I_N |  |  |  | CDC | 120 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗65線 | 斗65線 |  | 斗65線KVAR | [17 empty] | 1-CC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗65線KVAR | 23KV斗65線 KVAR | FEEDER | D23/22/XN65/KVAR |  |  |  | CDC | 121 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗65線 | 斗65線 |  | 斗65線A1 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗65線A1 | 23KV斗65線 R相AMP | FEEDER | D23/22/XN65/I_R |  |  |  | CDC | 122 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗65線 | 斗65線 |  | 斗65線A2 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗65線A2 | 23KV斗65線 S相AMP | FEEDER | D23/22/XN65/I_S |  |  |  | CDC | 123 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗65線 | 斗65線 |  | 斗65線A3 | [17 empty] | 1-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗65線A3 | 23KV斗65線 T相AMP | FEEDER | D23/22/XN65/I_T |  |  |  | CDC | 124 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗65線 | 斗65線 |  | 斗65線A0 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗65線A0 | 23KV斗65線 N相AMP | FEEDER | D23/22/XN65/I_N |  |  |  | CDC | 125 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗66線 | 斗66線 |  | 斗66線KVAR | [17 empty] | 1-D1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗66線KVAR | 23KV斗66線 KVAR | FEEDER | D23/22/XN66/KVAR |  |  |  | CDC | 126 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗66線 | 斗66線 |  | 斗66線A1 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗66線A1 | 23KV斗66線 R相AMP | FEEDER | D23/22/XN66/I_R |  |  |  | CDC | 127 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗66線 | 斗66線 |  | 斗66線A2 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗66線A2 | 23KV斗66線 S相AMP | FEEDER | D23/22/XN66/I_S |  |  |  | CDC | 128 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗66線 | 斗66線 |  | 斗66線A3 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗66線A3 | 23KV斗66線 T相AMP | FEEDER | D23/22/XN66/I_T |  |  |  | CDC | 129 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗66線 | 斗66線 |  | 斗66線A0 | [17 empty] | 1-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗66線A0 | 23KV斗66線 N相AMP | FEEDER | D23/22/XN66/I_N |  |  |  | CDC | 130 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗67線 | 斗67線 |  | 斗67線KVAR | [17 empty] | 1-D6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗67線KVAR | 23KV斗67線 KVAR | FEEDER | D23/22/XN67/KVAR |  |  |  | CDC | 131 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗67線 | 斗67線 |  | 斗67線A1 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗67線A1 | 23KV斗67線 R相AMP | FEEDER | D23/22/XN67/I_R |  |  |  | CDC | 132 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗67線 | 斗67線 |  | 斗67線A2 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗67線A2 | 23KV斗67線 S相AMP | FEEDER | D23/22/XN67/I_S |  |  |  | CDC | 133 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗67線 | 斗67線 |  | 斗67線A3 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗67線A3 | 23KV斗67線 T相AMP | FEEDER | D23/22/XN67/I_T |  |  |  | CDC | 134 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗67線 | 斗67線 |  | 斗67線A0 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗67線A0 | 23KV斗67線 N相AMP | FEEDER | D23/22/XN67/I_N |  |  |  | CDC | 135 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗68線 | 斗68線 |  | 斗68線KVAR | [17 empty] | 1-DB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗68線KVAR | 23KV斗68線 KVAR | FEEDER | D23/22/XN68/KVAR |  |  |  | CDC | 136 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗68線 | 斗68線 |  | 斗68線A1 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗68線A1 | 23KV斗68線 R相AMP | FEEDER | D23/22/XN68/I_R |  |  |  | CDC | 137 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗68線 | 斗68線 |  | 斗68線A2 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗68線A2 | 23KV斗68線 S相AMP | FEEDER | D23/22/XN68/I_S |  |  |  | CDC | 138 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗68線 | 斗68線 |  | 斗68線A3 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗68線A3 | 23KV斗68線 T相AMP | FEEDER | D23/22/XN68/I_T |  |  |  | CDC | 139 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗68線 | 斗68線 |  | 斗68線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗68線A0 | 23KV斗68線 N相AMP | FEEDER | D23/22/XN68/I_N |  |  |  | CDC | 140 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗71線 | 斗71線 |  | 斗71線KVAR | [17 empty] | 1-E3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗71線KVAR | 23KV斗71線 KVAR | FEEDER | D23/22/XN71/KVAR |  |  |  | CDC | 141 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗71線 | 斗71線 |  | 斗71線A1 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗71線A1 | 23KV斗71線 R相AMP | FEEDER | D23/22/XN71/I_R |  |  |  | CDC | 142 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗71線 | 斗71線 |  | 斗71線A2 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗71線A2 | 23KV斗71線 S相AMP | FEEDER | D23/22/XN71/I_S |  |  |  | CDC | 143 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗71線 | 斗71線 |  | 斗71線A3 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗71線A3 | 23KV斗71線 T相AMP | FEEDER | D23/22/XN71/I_T |  |  |  | CDC | 144 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗71線 | 斗71線 |  | 斗71線A0 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗71線A0 | 23KV斗71線 N相AMP | FEEDER | D23/22/XN71/I_N |  |  |  | CDC | 145 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗72線 | 斗72線 |  | 斗72線KVAR | [17 empty] | 1-E8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗72線KVAR | 23KV斗72線 KVAR | FEEDER | D23/22/XN72/KVAR |  |  |  | CDC | 146 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗72線 | 斗72線 |  | 斗72線A1 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗72線A1 | 23KV斗72線 R相AMP | FEEDER | D23/22/XN72/I_R |  |  |  | CDC | 147 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗72線 | 斗72線 |  | 斗72線A2 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗72線A2 | 23KV斗72線 S相AMP | FEEDER | D23/22/XN72/I_S |  |  |  | CDC | 148 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗72線 | 斗72線 |  | 斗72線A3 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗72線A3 | 23KV斗72線 T相AMP | FEEDER | D23/22/XN72/I_T |  |  |  | CDC | 149 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗72線 | 斗72線 |  | 斗72線A0 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗72線A0 | 23KV斗72線 N相AMP | FEEDER | D23/22/XN72/I_N |  |  |  | CDC | 150 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗73線 | 斗73線 |  | 斗73線KVAR | [17 empty] | 1-ED | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗73線KVAR | 23KV斗73線 KVAR | FEEDER | D23/22/XN73/KVAR |  |  |  | CDC | 151 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗73線 | 斗73線 |  | 斗73線A1 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗73線A1 | 23KV斗73線 R相AMP | FEEDER | D23/22/XN73/I_R |  |  |  | CDC | 152 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗73線 | 斗73線 |  | 斗73線A2 | [17 empty] | 1-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗73線A2 | 23KV斗73線 S相AMP | FEEDER | D23/22/XN73/I_S |  |  |  | CDC | 153 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗73線 | 斗73線 |  | 斗73線A3 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗73線A3 | 23KV斗73線 T相AMP | FEEDER | D23/22/XN73/I_T |  |  |  | CDC | 154 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗73線 | 斗73線 |  | 斗73線A0 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗73線A0 | 23KV斗73線 N相AMP | FEEDER | D23/22/XN73/I_N |  |  |  | CDC | 155 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗74線 | 斗74線 |  | 斗74線KVAR | [17 empty] | 1-F2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗74線KVAR | 23KV斗74線 KVAR | FEEDER | D23/22/XN74/KVAR |  |  |  | CDC | 156 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗74線 | 斗74線 |  | 斗74線A1 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗74線A1 | 23KV斗74線 R相AMP | FEEDER | D23/22/XN74/I_R |  |  |  | CDC | 157 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗74線 | 斗74線 |  | 斗74線A2 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗74線A2 | 23KV斗74線 S相AMP | FEEDER | D23/22/XN74/I_S |  |  |  | CDC | 158 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗74線 | 斗74線 |  | 斗74線A3 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗74線A3 | 23KV斗74線 T相AMP | FEEDER | D23/22/XN74/I_T |  |  |  | CDC | 159 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗74線 | 斗74線 |  | 斗74線A0 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗74線A0 | 23KV斗74線 N相AMP | FEEDER | D23/22/XN74/I_N |  |  |  | CDC | 160 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗75線 | 斗75線 |  | 斗75線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗75線KVAR | 23KV斗75線 KVAR | FEEDER | D23/22/XN75/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗75線 | 斗75線 |  | 斗75線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗75線A1 | 23KV斗75線 R相AMP | FEEDER | D23/22/XN75/I_R |  |  |  | CDC | 162 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗75線 | 斗75線 |  | 斗75線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗75線A2 | 23KV斗75線 S相AMP | FEEDER | D23/22/XN75/I_S |  |  |  | CDC | 163 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗75線 | 斗75線 |  | 斗75線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗75線A3 | 23KV斗75線 T相AMP | FEEDER | D23/22/XN75/I_T |  |  |  | CDC | 164 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗75線 | 斗75線 |  | 斗75線A0 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗75線A0 | 23KV斗75線 N相AMP | FEEDER | D23/22/XN75/I_N |  |  |  | CDC | 165 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗76線 | 斗76線 |  | 斗76線KVAR | [17 empty] | 1-FC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗76線KVAR | 23KV斗76線 KVAR | FEEDER | D23/22/XN76/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗76線 | 斗76線 |  | 斗76線A1 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗76線A1 | 23KV斗76線 R相AMP | FEEDER | D23/22/XN76/I_R |  |  |  | CDC | 167 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗76線 | 斗76線 |  | 斗76線A2 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗76線A2 | 23KV斗76線 S相AMP | FEEDER | D23/22/XN76/I_S |  |  |  | CDC | 168 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗76線 | 斗76線 |  | 斗76線A3 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗76線A3 | 23KV斗76線 T相AMP | FEEDER | D23/22/XN76/I_T |  |  |  | CDC | 169 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗76線 | 斗76線 |  | 斗76線A0 | [17 empty] | 2-80 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗76線A0 | 23KV斗76線 N相AMP | FEEDER | D23/22/XN76/I_N |  |  |  | CDC | 170 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗77線 | 斗77線 |  | 斗77線KVAR | [17 empty] | 2-81 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗77線KVAR | 23KV斗77線 KVAR | FEEDER | D23/22/XN77/KVAR |  |  |  | CDC | 171 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗77線 | 斗77線 |  | 斗77線A1 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗77線A1 | 23KV斗77線 R相AMP | FEEDER | D23/22/XN77/I_R |  |  |  | CDC | 172 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗77線 | 斗77線 |  | 斗77線A2 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗77線A2 | 23KV斗77線 S相AMP | FEEDER | D23/22/XN77/I_S |  |  |  | CDC | 173 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗77線 | 斗77線 |  | 斗77線A3 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗77線A3 | 23KV斗77線 T相AMP | FEEDER | D23/22/XN77/I_T |  |  |  | CDC | 174 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗77線 | 斗77線 |  | 斗77線A0 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗77線A0 | 23KV斗77線 N相AMP | FEEDER | D23/22/XN77/I_N |  |  |  | CDC | 175 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗78線 | 斗78線 |  | 斗78線KVAR | [17 empty] | 2-86 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗78線KVAR | 23KV斗78線 KVAR | FEEDER | D23/22/XN78/KVAR |  |  |  | CDC | 176 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗78線 | 斗78線 |  | 斗78線A1 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗78線A1 | 23KV斗78線 R相AMP | FEEDER | D23/22/XN78/I_R |  |  |  | CDC | 177 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗78線 | 斗78線 |  | 斗78線A2 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗78線A2 | 23KV斗78線 S相AMP | FEEDER | D23/22/XN78/I_S |  |  |  | CDC | 178 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗78線 | 斗78線 |  | 斗78線A3 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗78線A3 | 23KV斗78線 T相AMP | FEEDER | D23/22/XN78/I_T |  |  |  | CDC | 179 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | 斗78線 | 斗78線 |  | 斗78線A0 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 斗六DS.斗78線A0 | 23KV斗78線 N相AMP | FEEDER | D23/22/XN78/I_N |  |  |  | CDC | 180 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1500TIE_AMP | 1500TIE AMP | TIE | D23/161/1500/I_R |  |  |  | CDC | 181 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D23/22/300/I_R |  |  |  | CDC | 182 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D23/22/300/I_S |  |  |  | CDC | 183 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D23/22/300/I_T |  |  |  | CDC | 184 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | _400 | 400 |  | I_R | [17 empty] | 1-E0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV_400_A1 | 23KV 400 R相AMP | TIE | D23/22/400/I_R |  |  |  | CDC | 185 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | _400 | 400 |  | I_S | [17 empty] | 1-E1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV_400_A2 | 23KV 400 S相AMP | TIE | D23/22/400/I_S |  |  |  | CDC | 186 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 22 | 22kV | _400 | 400 |  | I_T | [17 empty] | 1-E2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.23KV_400_A3 | 23KV 400 T相AMP | TIE | D23/22/400/I_T |  |  |  | CDC | 187 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-84 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR_OIL | #3DTR 油溫 | MTR | D23//3DTR/OilTemp |  |  |  | CDC | 188 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-82 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR_COIL | #3DTR 線溫 | MTR | D23//3DTR/CoilTemp |  |  |  | CDC | 189 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-80 |  | 1-02 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D23//3DTR/TapPosMv |  |  |  | CDC | 190 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | D23/22/350/KW |  |  |  | CDC | 191 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | D23/22/350/KVAR |  |  |  | CDC | 192 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [17 empty] | 1-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | D23/22/350/I_R |  |  |  | CDC | 193 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [17 empty] | 1-C5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | D23/22/350/I_S |  |  |  | CDC | 194 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [17 empty] | 1-C6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | D23/22/350/I_T |  |  |  | CDC | 195 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [17 empty] | 1-C7 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | D23/22/360/KW |  |  |  | CDC | 196 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [17 empty] | 1-C8 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | D23/22/360/KVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [17 empty] | 1-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | D23/22/360/I_R |  |  |  | CDC | 198 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | D23/22/360/I_S |  |  |  | CDC | 199 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | D23/22/360/I_T |  |  |  | CDC | 200 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR二次側 |  | MW | [17 empty] | 2-8B | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_MW | #4DTR二次側 MW | MTR | D23/22/370/KW |  |  |  | CDC | 201 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR二次側 |  | MVAR | [17 empty] | 2-8C | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_MVAR | #4DTR二次側 MVAR | MTR | D23/22/370/KVAR |  |  |  | CDC | 202 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR二次側 |  | I_R | [17 empty] | 2-8D | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_A1 | #4DTR二次側 R相AMP | MTR | D23/22/370/I_R |  |  |  | CDC | 203 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR二次側 |  | I_S | [17 empty] | 2-8E | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_A2 | #4DTR二次側 S相AMP | MTR | D23/22/370/I_S |  |  |  | CDC | 204 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR二次側 |  | I_T | [17 empty] | 2-8F | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_A3 | #4DTR二次側 T相AMP | MTR | D23/22/370/I_T |  |  |  | CDC | 205 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | OilTemp | [17 empty] | 1-89 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_OIL | #4DTR 油溫 | MTR | D23//4DTR/OilTemp |  |  |  | CDC | 206 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | CoilTemp | [17 empty] | 1-87 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_COIL | #4DTR 線溫 | MTR | D23//4DTR/CoilTemp |  |  |  | CDC | 207 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | TapPosMv | [17 empty] | 1-85 |  | 1-06 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 斗六DS.#4DTR_TAP | #4DTR OLTC TAP | MTR | D23//4DTR/TapPosMv |  |  |  | CDC | 208 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D23 | 斗六DS | 161 | 161kV | 1610LPD | 雲林斗六一路(1610) |  | V | [17 empty] | 1-A3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1610LPD_KV | 雲林斗六一路(1610) LPD KV | LINE161 | D23/161/1610/V |  |  |  | CDC | 209 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D23 | 斗六DS | 161 | 161kV | 1620LPD | 雲林斗六二路(1620) |  | V | [17 empty] | 1-A4 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.1620LPD_KV | 雲林斗六二路(1620) LPD KV | LINE161 | D23/161/1620/V |  |  |  | CDC | 210 | GENERICAIPoint | DS049_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D23 | 斗六DS | 0 |  |  |  |  | DCV_N | [17 empty] | 2-91 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D23/0/StaDev/DCV_N |  |  |  | CDC | 211 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D23 | 斗六DS | 0 |  |  |  |  | DCV_P | [17 empty] | 2-90 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 斗六DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D23/0/StaDev/DCV_P |  |  |  | CDC | 212 | GENERICAIPoint | DS049_L2 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | PHA | [17 empty] | 1-00-02 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1610_PHA | 雲林斗六一路(1610) 相間RY | LINE161 | D23/161/1610/PHA |  |  |  | CDC | 213 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | GDA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1610_GDA | 雲林斗六一路(1610) 接地RY | LINE161 | D23/161/1610/GDA |  |  |  | CDC | 214 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1610_87A | 雲林斗六一路(1610) 87RY | LINE161 | D23/161/1610/87A |  |  |  | CDC | 215 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | 87UL | [17 empty] | 1-32-09 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1610_87UL | 雲林斗六一路(1610) 87RY U/L | LINE161 | D23/161/1610/87UL |  |  |  | CDC | 216 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | CB | [17 empty] | 1-0E-06 |  | 1-38 | [5 empty] | 161KV_N | [8 empty] | 斗六DS.1610_CB | 1610(雲林斗六一路) CB | LINE161 | D23/161/1610/CB |  |  |  | CDC | 217 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | 79UL | [17 empty] | 1-32-11 |  | 1-13 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1610_79UL | 雲林斗六一路(1610) 79RY U/L | LINE161 | D23/161/1610/79UL |  |  |  | CDC | 218 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | DS1 | 1611 | [16 empty] | 2-30-04 | 2-30-05 | 1-39 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1611_DS | 1611(雲林斗六一路) DS | LINE161 | D23/161/1610/DS1 |  |  |  | CDC | 219 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | DS2 | 1612 | [16 empty] | 2-30-06 | 2-30-07 | 1-3A | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1612_DS | 1612(雲林斗六一路) DS | LINE161 | D23/161/1610/DS2 |  |  |  | CDC | 220 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | DS3 | 1613 | [16 empty] | 2-30-08 | 2-30-09 | 1-3B | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1613_DS | 1613(雲林斗六一路) DS | LINE161 | D23/161/1610/DS3 |  |  |  | CDC | 221 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | E3 | 1613E | [16 empty] | 2-30-10 | 2-30-11 | 1-3C | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1613E_ES | 1613E(雲林斗六一路) ES | LINE161 | D23/161/1610/ES3 |  |  |  | CDC | 222 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | PHA | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1620_PHA | 雲林斗六二路(1620) 相間RY | LINE161 | D23/161/1620/PHA |  |  |  | CDC | 223 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1620_GDA | 雲林斗六二路(1620) 接地RY | LINE161 | D23/161/1620/GDA |  |  |  | CDC | 224 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | 87A | [17 empty] | 1-00-05 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1620_87A | 雲林斗六二路(1620) 87RY | LINE161 | D23/161/1620/87A |  |  |  | CDC | 225 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | 87UL | [17 empty] | 1-32-10 |  | 1-14 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1620_87UL | 雲林斗六二路(1620) 87RY U/L | LINE161 | D23/161/1620/87UL |  |  |  | CDC | 226 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | CB | [17 empty] | 1-0E-07 |  | 1-3D | [5 empty] | 161KV_N | [8 empty] | 斗六DS.1620_CB | 1620(雲林斗六二路) CB | LINE161 | D23/161/1620/CB |  |  |  | CDC | 227 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | 79UL | [17 empty] | 1-32-12 |  | 1-16 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1620_79UL | 雲林斗六二路(1620) 79RY U/L | LINE161 | D23/161/1620/79UL |  |  |  | CDC | 228 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | DS1 | 1621 | [16 empty] | 2-30-12 | 2-30-13 | 1-3E | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1621_DS | 1621(雲林斗六二路) DS | LINE161 | D23/161/1620/DS1 |  |  |  | CDC | 229 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | DS2 | 1622 | [16 empty] | 2-30-14 | 2-30-15 | 1-3F | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1622_DS | 1622(雲林斗六二路) DS | LINE161 | D23/161/1620/DS2 |  |  |  | CDC | 230 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | DS3 | 1623 | [16 empty] | 2-31-00 | 2-31-01 | 1-40 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1623_DS | 1623(雲林斗六二路) DS | LINE161 | D23/161/1620/DS3 |  |  |  | CDC | 231 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | E3 | 1623E | [16 empty] | 2-31-02 | 2-31-03 | 1-41 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1623E_ES | 1623E(雲林斗六二路) ES | LINE161 | D23/161/1620/ES3 |  |  |  | CDC | 232 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 22 | 22kV | XN61 | 斗61線(XN61) |  | PHA | [17 empty] | 2-00-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_PHA | 23KV斗61線(XN61) 相間RY | FEEDER | D23/22/XN61/PHA |  |  |  | CDC | 233 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN61 | 斗61線(XN61) |  | GDA | [17 empty] | 2-00-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_GDA | 23KV斗61線(XN61) 接地RY | FEEDER | D23/22/XN61/GDA |  |  |  | CDC | 234 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN61 | 斗61線(XN61) 79RY |  | 79UL | [17 empty] | 1-39-04 |  | 2-02 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_79UL | 23KV斗61線(XN61) 79RY U/L | FEEDER | D23/22/XN61/79UL |  |  |  | CDC | 235 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN61_LCO | 斗61線(XN61) LCO |  | TapPosMv | [17 empty] | 1-39-05 |  | 2-03 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_LCO_TAP | 23KV斗61線(XN61) LCO TAP | FEEDER | D23/22/XN61/ADJ |  |  |  | CDC | 236 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN61 | XN61(23KV斗61線) |  | CB | [17 empty] | 2-00-06 |  | 2-01 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_CB | XN61(23KV斗61線) CB | FEEDER | D23/22/XN61/CB |  |  |  | CDC | 237 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN62 | 斗62線(XN62) |  | PHA | [17 empty] | 2-00-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_PHA | 23KV斗62線(XN62) 相間RY | FEEDER | D23/22/XN62/PHA |  |  |  | CDC | 238 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN62 | 斗62線(XN62) |  | GDA | [17 empty] | 2-01-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_GDA | 23KV斗62線(XN62) 接地RY | FEEDER | D23/22/XN62/GDA |  |  |  | CDC | 239 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN62 | 斗62線(XN62) 79RY |  | 79UL | [17 empty] | 1-39-06 |  | 2-05 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_79UL | 23KV斗62線(XN62) 79RY U/L | FEEDER | D23/22/XN62/79UL |  |  |  | CDC | 240 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN62_LCO | 斗62線(XN62) LCO |  | TapPosMv | [17 empty] | 1-39-07 |  | 2-06 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_LCO_TAP | 23KV斗62線(XN62) LCO TAP | FEEDER | D23/22/XN62/ADJ |  |  |  | CDC | 241 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN62 | XN62(23KV斗62線) |  | CB | [17 empty] | 2-01-02 |  | 2-04 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_CB | XN62(23KV斗62線) CB | FEEDER | D23/22/XN62/CB |  |  |  | CDC | 242 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN63 | 斗63線(XN63) |  | PHA | [17 empty] | 2-01-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_PHA | 23KV斗63線(XN63) 相間RY | FEEDER | D23/22/XN63/PHA |  |  |  | CDC | 243 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN63 | 斗63線(XN63) |  | GDA | [17 empty] | 2-01-04 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_GDA | 23KV斗63線(XN63) 接地RY | FEEDER | D23/22/XN63/GDA |  |  |  | CDC | 244 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN63 | 斗63線(XN63) 79RY |  | 79UL | [17 empty] | 1-39-08 |  | 2-08 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_79UL | 23KV斗63線(XN63) 79RY U/L | FEEDER | D23/22/XN63/79UL |  |  |  | CDC | 245 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN63_LCO | 斗63線(XN63) LCO |  | TapPosMv | [17 empty] | 1-39-09 |  | 2-09 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_LCO_TAP | 23KV斗63線(XN63) LCO TAP | FEEDER | D23/22/XN63/ADJ |  |  |  | CDC | 246 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN63 | XN63(23KV斗63線) |  | CB | [17 empty] | 2-01-06 |  | 2-07 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_CB | XN63(23KV斗63線) CB | FEEDER | D23/22/XN63/CB |  |  |  | CDC | 247 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN64 | 斗64線(XN64) |  | PHA | [17 empty] | 2-01-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_PHA | 23KV斗64線(XN64) 相間RY | FEEDER | D23/22/XN64/PHA |  |  |  | CDC | 248 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN64 | 斗64線(XN64) |  | GDA | [17 empty] | 2-02-00 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_GDA | 23KV斗64線(XN64) 接地RY | FEEDER | D23/22/XN64/GDA |  |  |  | CDC | 249 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN64 | 斗64線(XN64) 79RY |  | 79UL | [17 empty] | 1-39-10 |  | 2-0B | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_79UL | 23KV斗64線(XN64) 79RY U/L | FEEDER | D23/22/XN64/79UL |  |  |  | CDC | 250 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN64_LCO | 斗64線(XN64) LCO |  | TapPosMv | [17 empty] | 1-39-11 |  | 2-0C | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_LCO_TAP | 23KV斗64線(XN64) LCO TAP | FEEDER | D23/22/XN64/ADJ |  |  |  | CDC | 251 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN64 | XN64(23KV斗64線) |  | CB | [17 empty] | 2-02-02 |  | 2-0A | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_CB | XN64(23KV斗64線) CB | FEEDER | D23/22/XN64/CB |  |  |  | CDC | 252 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN65 | 斗65線(XN65) |  | PHA | [17 empty] | 2-04-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_PHA | 23KV斗65線(XN65) 相間RY | FEEDER | D23/22/XN65/PHA |  |  |  | CDC | 253 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN65 | 斗65線(XN65) |  | GDA | [17 empty] | 2-04-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_GDA | 23KV斗65線(XN65) 接地RY | FEEDER | D23/22/XN65/GDA |  |  |  | CDC | 254 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN65 | 斗65線(XN65) 79RY |  | 79UL | [17 empty] | 1-39-12 |  | 2-13 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_79UL | 23KV斗65線(XN65) 79RY U/L | FEEDER | D23/22/XN65/79UL |  |  |  | CDC | 255 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN65_LCO | 斗65線(XN65) LCO |  | TapPosMv | [17 empty] | 1-39-13 |  | 2-14 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_LCO_TAP | 23KV斗65線(XN65) LCO TAP | FEEDER | D23/22/XN65/ADJ |  |  |  | CDC | 256 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN65 | XN65(23KV斗65線) |  | CB | [17 empty] | 2-04-05 |  | 2-12 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_CB | XN65(23KV斗65線) CB | FEEDER | D23/22/XN65/CB |  |  |  | CDC | 257 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN66 | 斗66線(XN66) |  | PHA | [17 empty] | 2-04-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_PHA | 23KV斗66線(XN66) 相間RY | FEEDER | D23/22/XN66/PHA |  |  |  | CDC | 258 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN66 | 斗66線(XN66) |  | GDA | [17 empty] | 2-04-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_GDA | 23KV斗66線(XN66) 接地RY | FEEDER | D23/22/XN66/GDA |  |  |  | CDC | 259 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN66 | 斗66線(XN66) 79RY |  | 79UL | [17 empty] | 1-39-14 |  | 2-16 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_79UL | 23KV斗66線(XN66) 79RY U/L | FEEDER | D23/22/XN66/79UL |  |  |  | CDC | 260 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN66_LCO | 斗66線(XN66) LCO |  | TapPosMv | [17 empty] | 1-39-15 |  | 2-17 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_LCO_TAP | 23KV斗66線(XN66) LCO TAP | FEEDER | D23/22/XN66/ADJ |  |  |  | CDC | 261 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN66 | XN66(23KV斗66線) |  | CB | [17 empty] | 2-05-01 |  | 2-15 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_CB | XN66(23KV斗66線) CB | FEEDER | D23/22/XN66/CB |  |  |  | CDC | 262 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN67 | 斗67線(XN67) |  | PHA | [17 empty] | 2-05-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_PHA | 23KV斗67線(XN67) 相間RY | FEEDER | D23/22/XN67/PHA |  |  |  | CDC | 263 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN67 | 斗67線(XN67) |  | GDA | [17 empty] | 2-05-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_GDA | 23KV斗67線(XN67) 接地RY | FEEDER | D23/22/XN67/GDA |  |  |  | CDC | 264 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN67 | 斗67線(XN67) 79RY |  | 79UL | [17 empty] | 1-3A-00 |  | 2-19 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_79UL | 23KV斗67線(XN67) 79RY U/L | FEEDER | D23/22/XN67/79UL |  |  |  | CDC | 265 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN67_LCO | 斗67線(XN67) LCO |  | TapPosMv | [17 empty] | 1-3A-01 |  | 2-1A | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_LCO_TAP | 23KV斗67線(XN67) LCO TAP | FEEDER | D23/22/XN67/ADJ |  |  |  | CDC | 266 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN67 | XN67(23KV斗67線) |  | CB | [17 empty] | 2-05-05 |  | 2-18 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_CB | XN67(23KV斗67線) CB | FEEDER | D23/22/XN67/CB |  |  |  | CDC | 267 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN68 | 斗68線(XN68) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_PHA | 23KV斗68線(XN68) 相間RY | FEEDER | D23/22/XN68/PHA |  |  |  | CDC | 268 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN68 | 斗68線(XN68) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_GDA | 23KV斗68線(XN68) 接地RY | FEEDER | D23/22/XN68/GDA |  |  |  | CDC | 269 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN68 | 斗68線(XN68) 79RY |  | 79UL | [17 empty] | 1-3A-02 |  | 2-1C | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_79UL | 23KV斗68線(XN68) 79RY U/L | FEEDER | D23/22/XN68/79UL |  |  |  | CDC | 270 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN68_LCO | 斗68線(XN68) LCO |  | TapPosMv | [17 empty] | 1-3A-03 |  | 2-1D | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_LCO_TAP | 23KV斗68線(XN68) LCO TAP | FEEDER | D23/22/XN68/ADJ |  |  |  | CDC | 271 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN68 | XN68(23KV斗68線) |  | CB | [17 empty] | 2-06-01 |  | 2-1B | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_CB | XN68(23KV斗68線) CB | FEEDER | D23/22/XN68/CB |  |  |  | CDC | 272 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN71 | 斗71線(XN71) |  | PHA | [17 empty] | 2-06-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_PHA | 23KV斗71線(XN71) 相間RY | FEEDER | D23/22/XN71/PHA |  |  |  | CDC | 273 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN71 | 斗71線(XN71) |  | GDA | [17 empty] | 2-06-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_GDA | 23KV斗71線(XN71) 接地RY | FEEDER | D23/22/XN71/GDA |  |  |  | CDC | 274 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN71 | 斗71線(XN71) 79RY |  | 79UL | [17 empty] | 1-3A-04 |  | 2-20 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_79UL | 23KV斗71線(XN71) 79RY U/L | FEEDER | D23/22/XN71/79UL |  |  |  | CDC | 275 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN71_LCO | 斗71線(XN71) LCO |  | TapPosMv | [17 empty] | 1-3A-05 |  | 2-21 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_LCO_TAP | 23KV斗71線(XN71) LCO TAP | FEEDER | D23/22/XN71/ADJ |  |  |  | CDC | 276 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN71 | XN71(23KV斗71線) |  | CB | [17 empty] | 2-07-00 |  | 2-1F | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_CB | XN71(23KV斗71線) CB | FEEDER | D23/22/XN71/CB |  |  |  | CDC | 277 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN72 | 斗72線(XN72) |  | PHA | [17 empty] | 2-07-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_PHA | 23KV斗72線(XN72) 相間RY | FEEDER | D23/22/XN72/PHA |  |  |  | CDC | 278 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN72 | 斗72線(XN72) |  | GDA | [17 empty] | 2-07-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_GDA | 23KV斗72線(XN72) 接地RY | FEEDER | D23/22/XN72/GDA |  |  |  | CDC | 279 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN72 | 斗72線(XN72) 79RY |  | 79UL | [17 empty] | 1-3A-06 |  | 2-23 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_79UL | 23KV斗72線(XN72) 79RY U/L | FEEDER | D23/22/XN72/79UL |  |  |  | CDC | 280 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN72_LCO | 斗72線(XN72) LCO |  | TapPosMv | [17 empty] | 1-3A-07 |  | 2-24 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_LCO_TAP | 23KV斗72線(XN72) LCO TAP | FEEDER | D23/22/XN72/ADJ |  |  |  | CDC | 281 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN72 | XN72(23KV斗72線) |  | CB | [17 empty] | 2-07-04 |  | 2-22 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_CB | XN72(23KV斗72線) CB | FEEDER | D23/22/XN72/CB |  |  |  | CDC | 282 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN73 | 斗73線(XN73) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_PHA | 23KV斗73線(XN73) 相間RY | FEEDER | D23/22/XN73/PHA |  |  |  | CDC | 283 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN73 | 斗73線(XN73) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_GDA | 23KV斗73線(XN73) 接地RY | FEEDER | D23/22/XN73/GDA |  |  |  | CDC | 284 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN73 | 斗73線(XN73) 79RY |  | 79UL | [17 empty] | 1-3A-08 |  | 2-26 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_79UL | 23KV斗73線(XN73) 79RY U/L | FEEDER | D23/22/XN73/79UL |  |  |  | CDC | 285 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN73_LCO | 斗73線(XN73) LCO |  | TapPosMv | [17 empty] | 1-3A-09 |  | 2-27 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_LCO_TAP | 23KV斗73線(XN73) LCO TAP | FEEDER | D23/22/XN73/ADJ |  |  |  | CDC | 286 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN73 | XN73(23KV斗73線) |  | CB | [17 empty] | 2-08-00 |  | 2-25 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_CB | XN73(23KV斗73線) CB | FEEDER | D23/22/XN73/CB |  |  |  | CDC | 287 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN74 | 斗74線(XN74) |  | PHA | [17 empty] | 2-08-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_PHA | 23KV斗74線(XN74) 相間RY | FEEDER | D23/22/XN74/PHA |  |  |  | CDC | 288 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN74 | 斗74線(XN74) |  | GDA | [17 empty] | 2-08-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_GDA | 23KV斗74線(XN74) 接地RY | FEEDER | D23/22/XN74/GDA |  |  |  | CDC | 289 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN74 | 斗74線(XN74) 79RY |  | 79UL | [17 empty] | 1-3A-10 |  | 2-29 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_79UL | 23KV斗74線(XN74) 79RY U/L | FEEDER | D23/22/XN74/79UL |  |  |  | CDC | 290 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN74_LCO | 斗74線(XN74) LCO |  | TapPosMv | [17 empty] | 1-3A-11 |  | 2-2A | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_LCO_TAP | 23KV斗74線(XN74) LCO TAP | FEEDER | D23/22/XN74/ADJ |  |  |  | CDC | 291 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN74 | XN74(23KV斗74線) |  | CB | [17 empty] | 2-08-04 |  | 2-28 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_CB | XN74(23KV斗74線) CB | FEEDER | D23/22/XN74/CB |  |  |  | CDC | 292 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN75 | 斗75線(XN75) |  | PHA | [17 empty] | 2-08-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_PHA | 23KV斗75線(XN75) 相間RY | FEEDER | D23/22/XN75/PHA |  |  |  | CDC | 293 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN75 | 斗75線(XN75) |  | GDA | [17 empty] | 2-08-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_GDA | 23KV斗75線(XN75) 接地RY | FEEDER | D23/22/XN75/GDA |  |  |  | CDC | 294 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN75 | 斗75線(XN75) 79RY |  | 79UL | [17 empty] | 1-3A-12 |  | 2-2C | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_79UL | 23KV斗75線(XN75) 79RY U/L | FEEDER | D23/22/XN75/79UL |  |  |  | CDC | 295 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN75_LCO | 斗75線(XN75) LCO |  | TapPosMv | [17 empty] | 1-3A-13 |  | 2-2D | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_LCO_TAP | 23KV斗75線(XN75) LCO TAP | FEEDER | D23/22/XN75/ADJ |  |  |  | CDC | 296 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN75 | XN75(23KV斗75線) |  | CB | [17 empty] | 2-09-00 |  | 2-2B | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_CB | XN75(23KV斗75線) CB | FEEDER | D23/22/XN75/CB |  |  |  | CDC | 297 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN76 | 斗76線(XN76) |  | PHA | [17 empty] | 2-09-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_PHA | 23KV斗76線(XN76) 相間RY | FEEDER | D23/22/XN76/PHA |  |  |  | CDC | 298 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN76 | 斗76線(XN76) |  | GDA | [17 empty] | 2-09-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_GDA | 23KV斗76線(XN76) 接地RY | FEEDER | D23/22/XN76/GDA |  |  |  | CDC | 299 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN76 | 斗76線(XN76) 79RY |  | 79UL | [17 empty] | 1-3A-14 |  | 2-2F | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_79UL | 23KV斗76線(XN76) 79RY U/L | FEEDER | D23/22/XN76/79UL |  |  |  | CDC | 300 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN76_LCO | 斗76線(XN76) LCO |  | TapPosMv | [17 empty] | 1-3A-15 |  | 2-30 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_LCO_TAP | 23KV斗76線(XN76) LCO TAP | FEEDER | D23/22/XN76/ADJ |  |  |  | CDC | 301 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN76 | XN76(23KV斗76線) |  | CB | [17 empty] | 2-09-04 |  | 2-2E | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_CB | XN76(23KV斗76線) CB | FEEDER | D23/22/XN76/CB |  |  |  | CDC | 302 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN77 | 斗77線(XN77) |  | PHA | [17 empty] | 2-09-05 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_PHA | 23KV斗77線(XN77) 相間RY | FEEDER | D23/22/XN77/PHA |  |  |  | CDC | 303 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN77 | 斗77線(XN77) |  | GDA | [17 empty] | 2-09-06 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_GDA | 23KV斗77線(XN77) 接地RY | FEEDER | D23/22/XN77/GDA |  |  |  | CDC | 304 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN77 | 斗77線(XN77) 79RY |  | 79UL | [17 empty] | 1-3B-00 |  | 2-32 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_79UL | 23KV斗77線(XN77) 79RY U/L | FEEDER | D23/22/XN77/79UL |  |  |  | CDC | 305 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN77_LCO | 斗77線(XN77) LCO |  | TapPosMv | [17 empty] | 1-3B-01 |  | 2-33 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_LCO_TAP | 23KV斗77線(XN77) LCO TAP | FEEDER | D23/22/XN77/ADJ |  |  |  | CDC | 306 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN77 | XN77(23KV斗77線) |  | CB | [17 empty] | 2-0A-00 |  | 2-31 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_CB | XN77(23KV斗77線) CB | FEEDER | D23/22/XN77/CB |  |  |  | CDC | 307 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | XN78 | 斗78線(XN78) |  | PHA | [17 empty] | 2-0A-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_PHA | 23KV斗78線(XN78) 相間RY | FEEDER | D23/22/XN78/PHA |  |  |  | CDC | 308 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN78 | 斗78線(XN78) |  | GDA | [17 empty] | 2-0A-02 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_GDA | 23KV斗78線(XN78) 接地RY | FEEDER | D23/22/XN78/GDA |  |  |  | CDC | 309 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | XN78 | 斗78線(XN78) 79RY |  | 79UL | [17 empty] | 1-3B-02 |  | 2-35 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_79UL | 23KV斗78線(XN78) 79RY U/L | FEEDER | D23/22/XN78/79UL |  |  |  | CDC | 310 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | XN78_LCO | 斗78線(XN78) LCO |  | TapPosMv | [17 empty] | 1-3B-03 |  | 2-36 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_LCO_TAP | 23KV斗78線(XN78) LCO TAP | FEEDER | D23/22/XN78/ADJ |  |  |  | CDC | 311 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D23 | 斗六DS | 22 | 22kV | XN78 | XN78(23KV斗78線) |  | CB | [17 empty] | 2-0A-04 |  | 2-34 | [5 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_CB | XN78(23KV斗78線) CB | FEEDER | D23/22/XN78/CB |  |  |  | CDC | 312 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-0F-02 |  | 1-35 | [5 empty] | 161KV_N | [8 empty] | 斗六DS.1500_CB | 1500(TIE) CB | TIE | D23/161/1500/CB |  |  |  | CDC | 313 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-0B-00 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D23/161/1500/50A |  |  |  | CDC | 314 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-30-00 | 2-30-01 | 1-36 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1501_DS | 1501(TIE) DS | TIE | D23/161/1500/DS1 |  |  |  | CDC | 315 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-30-02 | 2-30-03 | 1-37 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1502_DS | 1502(TIE) DS | TIE | D23/161/1500/DS2 |  |  |  | CDC | 316 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 2-00-02 |  | 2-00 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.300_CB | 300(TIE) CB | TIE | D23/22/300/CB |  |  |  | CDC | 317 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 2-00-00 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.300_51A | 23KV TIE(300) 51RY | TIE | D23/22/300/PHA |  |  |  | CDC | 318 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 2-00-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D23/22/300/GDA |  |  |  | CDC | 319 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 2-06-04 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 斗六DS.400_CB | 400(TIE) CB | TIE | D23/22/400/CB |  |  |  | CDC | 320 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 2-06-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.400_51A | 23KV TIE(400) 51RY | TIE | D23/22/400/PHA |  |  |  | CDC | 321 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 2-06-03 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.400_51NA | 23KV TIE(400) 51N RY | TIE | D23/22/400/GDA |  |  |  | CDC | 322 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 2-03-06 |  | 2-10 | [5 empty] | 161KV_N | [8 empty] | 斗六DS.390_CB | 390(#1SSTR) CB | OTHER | D23/22/390/CB |  |  |  | CDC | 323 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 2-03-04 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D23/22/390/PHA |  |  |  | CDC | 324 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 2-03-05 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D23/22/390/GDA |  |  |  | CDC | 325 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 2-0B-05 |  | 2-39 | [5 empty] | 161KV_N | [8 empty] | 斗六DS.490_CB | 490(#2SSTR) CB | OTHER | D23/22/490/CB |  |  |  | CDC | 326 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-0B-03 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D23/22/490/PHA |  |  |  | CDC | 327 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-0B-04 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D23/22/490/GDA |  |  |  | CDC | 328 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-0F-00 |  | 1-74 | [5 empty] | 161KV_N | [8 empty] | 斗六DS.1770_CB | 1770(#3DTR) CB | MTR | D23/161/1770/CB |  |  |  | CDC | 329 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0F-05 |  | 2-0E | [5 empty] | ADCS_N | [8 empty] | 斗六DS.350_CB | 350(#3DTR) CB | MTR | D23/22/350/CB |  |  |  | CDC | 330 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 360 | #3DTR(360) |  | CB | [17 empty] | 1-10-00 |  | 2-11 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.360_CB | 360(#3DTR) CB | MTR | D23/22/360/CB |  |  |  | CDC | 331 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#3DTR_51A | #3DTR 51RY | MTR | D23//3DTR/PHA |  |  |  | CDC | 332 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-06-06 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#3DTR_51NA | #3DTR 51N RY | MTR | D23//3DTR/GDA |  |  |  | CDC | 333 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D23//3DTR/51ZA |  |  |  | CDC | 334 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-06-02 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#3DTR_87A | #3DTR 87RY | MTR | D23//3DTR/87A |  |  |  | CDC | 335 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 87UL | [17 empty] | 1-34-13 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_87UL | #3DTR 87RY U/L | MTR | D23//3DTR/87UL |  |  |  | CDC | 336 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-06-00 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.350_51A | #3DTR二次側(350) 51RY | MTR | D23/22/350/PHA1 |  |  |  | CDC | 337 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 360 | #3DTR(360) |  | 51A | [17 empty] | 1-06-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.360_51A | #3DTR二次側(360) 51RY | MTR | D23/22/360/PHA1 |  |  |  | CDC | 338 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D23//3DTR/96PA |  |  |  | CDC | 339 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-30-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_96D | #3DTR 96D RY | MTR | D23//3DTR/96D |  |  |  | CDC | 340 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-30-11 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_96P | #3DTR 96P RY | MTR | D23//3DTR/96P |  |  |  | CDC | 341 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-30-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D23//3DTR/63Q |  |  |  | CDC | 342 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-30-08 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D23//3DTR/96B1 |  |  |  | CDC | 343 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-30-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D23//3DTR/96B2 |  |  |  | CDC | 344 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_TRA | #3DTR 重故障 | MTR | D23//3DTR/TRA |  |  |  | CDC | 345 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-30-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D23//3DTR/TRF |  |  |  | CDC | 346 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-30-09 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D23//3DTR/SupLocal |  |  |  | CDC | 347 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-30-03 |  | 1-01 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D23//3DTR/Tap Chan |  |  |  | CDC | 348 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 2-36-04 | 2-36-05 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1771_DS | 1771(#3DTR) DS | MTR | D23/161/1770/DS1 |  |  |  | CDC | 349 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 2-36-06 | 2-36-07 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1772_DS | 1772(#3DTR) DS | MTR | D23/161/1770/DS2 |  |  |  | CDC | 350 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [17 empty] | 1-0F-01 |  | 1-77 | [5 empty] | 161KV_N | [8 empty] | 斗六DS.1780_CB | 1780(#4DTR) CB | MTR | D23/161/1780/CB |  |  |  | CDC | 351 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 370 | #4DTR(370) |  | CB | [17 empty] | 1-10-03 |  | 2-38 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.370_CB | 370(#4DTR) CB | MTR | D23/22/370/CB |  |  |  | CDC | 352 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 51A | [17 empty] | 1-07-06 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#4DTR_51A | #4DTR 51RY | MTR | D23//4DTR/PHA |  |  |  | CDC | 353 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 51NA | [17 empty] | 1-07-07 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#4DTR_51NA | #4DTR 51N RY | MTR | D23//4DTR/GDA |  |  |  | CDC | 354 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 51ZA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#4DTR_51ZA | #4DTR 51Z RY | MTR | D23//4DTR/51ZA |  |  |  | CDC | 355 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 87A | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#4DTR_87A | #4DTR 87RY | MTR | D23//4DTR/87A |  |  |  | CDC | 356 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 87UL | [17 empty] | 1-34-14 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_87UL | #4DTR 87RY U/L | MTR | D23//4DTR/87UL |  |  |  | CDC | 357 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 0 |  | 370 | #4DTR(370) |  | 51A | [17 empty] | 1-07-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.370_51A | #4DTR二次側(370) 51RY | MTR | D23/22/370/PHA1 |  |  |  | CDC | 358 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 96PA | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.#4DTR_96PA | #4DTR 機械保護動作 | MTR | D23//4DTR/96PA |  |  |  | CDC | 359 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 96D | [17 empty] | 1-31-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_96D | #4DTR 96D RY | MTR | D23//4DTR/96D |  |  |  | CDC | 360 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 96P | [17 empty] | 1-31-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_96P | #4DTR 96P RY | MTR | D23//4DTR/96P |  |  |  | CDC | 361 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 63Q | [17 empty] | 1-31-00 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_63Q | #4DTR 63Q RY | MTR | D23//4DTR/63Q |  |  |  | CDC | 362 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 96B1 | [17 empty] | 1-31-03 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_96B1 | #4DTR 96B1 RY | MTR | D23//4DTR/96B1 |  |  |  | CDC | 363 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | 96B2 | [17 empty] | 1-31-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_96B2 | #4DTR 96B2 RY | MTR | D23//4DTR/96B2 |  |  |  | CDC | 364 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | TRA | [17 empty] | 1-30-12 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_TRA | #4DTR 重故障 | MTR | D23//4DTR/TRA |  |  |  | CDC | 365 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | TRF | [17 empty] | 1-30-13 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_TRF | #4DTR 輕故障 | MTR | D23//4DTR/TRF |  |  |  | CDC | 366 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | SupLocal | [17 empty] | 1-31-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_S/L | #4DTR OLTC S/L | MTR | D23//4DTR/SupLocal |  |  |  | CDC | 367 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 0 |  | 4DTR | #4DTR |  | A_M | [17 empty] | 1-30-14 |  | 1-05 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.#4DTR_A/M | #4DTR OLTC A/M | MTR | D23//4DTR/Tap Chan |  |  |  | CDC | 368 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [16 empty] | 2-36-08 | 2-36-09 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1781_DS | 1781(#4DTR) DS | MTR | D23/161/1780/DS1 |  |  |  | CDC | 369 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [16 empty] | 2-36-10 | 2-36-11 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.1782_DS | 1782(#4DTR) DS | MTR | D23/161/1780/DS2 |  |  |  | CDC | 370 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-02-05 |  | 2-0D | [5 empty] | ADCS_N | [8 empty] | 斗六DS.250_CB | 250(23KV #5SC) CB | SC | D23/22/250/CB |  |  |  | CDC | 371 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-02-03 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.250_SCA | 23KV #5SC 51,51N RY | SC | D23/22/250/SCA |  |  |  | CDC | 372 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-02-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D23/22/250/UVA |  |  |  | CDC | 373 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-03-03 |  | 2-0F | [5 empty] | ADCS_N | [8 empty] | 斗六DS.260_CB | 260(23KV #6SC) CB | SC | D23/22/260/CB |  |  |  | CDC | 374 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-03-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.260_SCA | 23KV #6SC 51,51N RY | SC | D23/22/260/SCA |  |  |  | CDC | 375 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-03-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D23/22/260/UVA |  |  |  | CDC | 376 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 2-0C-00 |  | 2-3A | [5 empty] | ADCS_N | [8 empty] | 斗六DS.270_CB | 270(23KV #7SC) CB | SC | D23/22/270/CB |  |  |  | CDC | 377 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 2-0B-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.270_SCA | 23KV #7SC 51,51N RY | SC | D23/22/270/SCA |  |  |  | CDC | 378 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 2-0B-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | D23/22/270/UVA |  |  |  | CDC | 379 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | CB | [17 empty] | 2-0A-07 |  | 2-37 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.280_CB | 280(23KV #8SC) CB | SC | D23/22/280/CB |  |  |  | CDC | 380 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [17 empty] | 2-0A-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.280_SCA | 23KV #8SC 51,51N RY | SC | D23/22/280/SCA |  |  |  | CDC | 381 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [17 empty] | 2-0A-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | D23/22/280/UVA |  |  |  | CDC | 382 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D23/161/1BUS/BUS_VUA |  |  |  | CDC | 383 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-0B-01 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D23/161/1BUS/87A |  |  |  | CDC | 384 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-35-01 |  | 1-17 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D23/161/1BUS/87UL |  |  |  | CDC | 385 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D23/161/2BUS/BUS_VUA |  |  |  | CDC | 386 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-0B-02 | [7 empty] | 161KV_N | [8 empty] | 斗六DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D23/161/2BUS/87A |  |  |  | CDC | 387 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-35-02 |  | 1-18 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D23/161/2BUS/87UL |  |  |  | CDC | 388 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D23 | 斗六DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-38-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D23/22/ComPoint/FDR_CBA |  |  |  | CDC | 389 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-38-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D23/22/ComPoint/FDR_CBF |  |  |  | CDC | 390 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D23/161/ComPoint/CBA |  |  |  | CDC | 391 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D23/161/ComPoint/CBF |  |  |  | CDC | 392 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0E-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D23/161/ComPoint/RCA |  |  |  | CDC | 393 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | _SC | 11/ SC |  | 60A | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.23KV_SC_60A | 11/23KV SC 60A | OTHER | D23/0/ComPoint/FDR_60A |  |  |  | CDC | 394 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 斗六DS.TEST_CB | TEST CB | OTHER | D23/0/RTU/Test_CB |  |  |  | CDC | 395 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D23/0/StaDev/Fire1 |  |  |  | CDC | 396 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 25TA | [17 empty] | 1-0E-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D23/161/ComPoint/25TA |  |  |  | CDC | 397 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-37-10 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D23/0/StaDev/ACB1 |  |  |  | CDC | 398 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D23 | 斗六DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-37-11 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D23/0/StaDev/ACB2 |  |  |  | CDC | 399 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D23 | 斗六DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-38-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.所內電源ACBA | 所內電源故障警報 | OTHER | D23/0/StaDev/ACBA |  |  |  | CDC | 400 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-37-12 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D23/0/StaDev/ACBT |  |  |  | CDC | 401 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D23 | 斗六DS | 0 |  |  |  |  | STUV | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D23/0/StaDev/STUV |  |  |  | CDC | 402 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-36-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.直流充電機故障 | 變電所直流充電機故障 | OTHER | D23/0/StaDev/CHG1 |  |  |  | CDC | 403 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | DCA | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.直流電源DCA | 直流電源故障警報 | OTHER | D23/0/StaDev/DCA |  |  |  | CDC | 404 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | DCE | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D23/0/StaDev/DCE |  |  |  | CDC | 405 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D23/0/StaDev/CHG2 |  |  |  | CDC | 406 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D23/0/StaDev/CommACF |  |  |  | CDC | 407 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-36-09 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.無人化門禁(1) | 無人化門禁(1)建築物,控制室大門 | OTHER | D23/0/StaDev/Door1 |  |  |  | CDC | 408 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-36-12 |  | 2-3D | [5 empty] | ADCS_N | [8 empty] | 斗六DS.開關場照明(A) | 開關場照明(A) | OTHER | D23/0/StaDev/Lights1 |  |  |  | CDC | 409 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D23 | 斗六DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 1-38-03 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.11/23KV_LOA | 11/23KV饋線復閉失敗閉鎖 | OTHER | D23/22/ComPoint/LOA |  |  |  | CDC | 410 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D23/161/1500/50SA |  |  |  | CDC | 411 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 1610 | 雲林斗六一路(1610) |  | 87CFA | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.1610_87CFA | 雲林斗六一路(1610)87RY通訊故障 | OTHER | D23/161/1610/87CFA |  |  |  | CDC | 412 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 1610 | 雲林斗六一路(1610) |  | RYFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.1610_RYFA | 雲林斗六一路(1610)數位電驛故障 | OTHER | D23/161/1610/RYFA |  |  |  | CDC | 413 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-0B-03 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D23/161/ComPoint/OSCA |  |  |  | CDC | 414 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_OSCF | 161KV示波器故障 | OTHER | D23/161/ComPoint/OSCF |  |  |  | CDC | 415 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 1620 | 雲林斗六二路(1620) |  | 87CFA | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.1620_87CFA | 雲林斗六二路(1620)87RY通訊故障 | OTHER | D23/161/1620/87CFA |  |  |  | CDC | 416 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 1620 | 雲林斗六二路(1620) |  | RYFA | [17 empty] | 1-33-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.1620_RYFA | 雲林斗六二路(1620)數位電驛故障 | OTHER | D23/161/1620/RYFA |  |  |  | CDC | 417 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 11_ | 11/ 饋線 |  | RCA | [17 empty] | 2-0C-01 | [7 empty] | DDCS1_1 | [8 empty] | 斗六DS.23KV_RCA | 11/23KV 饋線 79RY復閉動作 | OTHER | D23/22/ComPoint/FDR_RCA |  |  |  | CDC | 418 | GENERICDIPoint | DS049_L2 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0F-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.350_GDA | 350開關箱IED RY GDA | OTHER | D23/22/350/GDA |  |  |  | CDC | 419 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0F-03 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D23/22/350/PHA2 |  |  |  | CDC | 420 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 360 | #3DTR(360) |  | GDA | [17 empty] | 1-0F-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.360_GDA | 360開關箱IED RY GDA | OTHER | D23/22/360/GDA |  |  |  | CDC | 421 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 360 | #3DTR(360) |  | PHA2 | [17 empty] | 1-0F-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.360_PHA2 | 360開關箱IED RY PHA | OTHER | D23/22/360/PHA2 |  |  |  | CDC | 422 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 370 | #4DTR(370) |  | GDA | [17 empty] | 1-10-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.370_GDA | 370開關箱IED RY GDA | OTHER | D23/22/370/GDA |  |  |  | CDC | 423 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | 370 | #4DTR(370) |  | PHA2 | [17 empty] | 1-10-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.370_PHA2 | 370開關箱IED RY PHA | OTHER | D23/22/370/PHA2 |  |  |  | CDC | 424 | GENERICDIPoint | DS049_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER | D23/0/StaDev/Comm_R_L |  |  |  | CDC | 425 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 0 |  | MCC | MCC |  | MCCA | [17 empty] | 1-38-09 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.MCCA | MCC IED 故障 | OTHER | D23/0/StaDev/MCC |  |  |  | CDC | 426 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | MODEMF | [17 empty] | 1-38-08 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.MODEMF | 專線數據機電源故障 | OTHER | D23/0/StaDev/7A5Other |  |  |  | CDC | 427 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | OWFA | [17 empty] | 1-38-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.OWFA | 洩油池抽水泵警報 | OTHER | D23/0/StaDev/6A5Other |  |  |  | CDC | 428 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | PMCC | PMCC |  | PMCCA | [17 empty] | 1-38-10 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.PMCCA | PMCC IED 故障 | OTHER | D23/0/StaDev/PMCC |  |  |  | CDC | 429 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | LOCAL | LOCAL |  | SCADA | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.SCADA | LOCAL SCADA故障 | OTHER | D23/0/StaDev/SCADAA |  |  |  | CDC | 430 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | TCA | [17 empty] | 1-38-11 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.TCA | 斷路器跳脫回路故障 | OTHER | D23/0/StaDev/TCA |  |  |  | CDC | 431 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-37-08 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.水位警報(1) | 地下室水位警報(1) | OTHER | D23/0/StaDev/Water1 |  |  |  | CDC | 432 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-37-09 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.水位警報(2) | 地下室水位警報(2) | OTHER | D23/0/StaDev/Water2 |  |  |  | CDC | 433 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 1-38-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D23/0/StaDev/OilLeak1 |  |  |  | CDC | 434 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 1-38-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D23/0/StaDev/OilLeak2 |  |  |  | CDC | 435 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 涵洞水位(1) | [17 empty] | 1-38-12 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.涵洞水位(1) | 涵洞淹水警報(1) | OTHER | D23/0/StaDev/Water3 |  |  |  | CDC | 436 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 涵洞水位(2) | [17 empty] | 1-38-13 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.涵洞水位(2) | 涵洞淹水警報(2) | OTHER | D23/0/StaDev/Water4 |  |  |  | CDC | 437 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 涵洞水位(3) | [17 empty] | 1-38-14 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.涵洞水位(3) | 涵洞淹水警報(3) | OTHER | D23/0/StaDev/Water5 |  |  |  | CDC | 438 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 涵洞排水泵(1) | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.涵洞排水泵(1) | 涵洞排水幫浦故障(1) | OTHER | D23/0/StaDev/3A5Other |  |  |  | CDC | 439 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 涵洞排水泵(2) | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.涵洞排水泵(2) | 涵洞排水幫浦故障(2) | OTHER | D23/0/StaDev/4A5Other |  |  |  | CDC | 440 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 涵洞排水泵(3) | [17 empty] | 1-37-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.涵洞排水泵(3) | 涵洞排水幫浦故障(3) | OTHER | D23/0/StaDev/5A5Other |  |  |  | CDC | 441 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-37-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D23/0/StaDev/R_Temp |  |  |  | CDC | 442 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | 揚水幫浦 | [17 empty] | 1-37-04 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.揚水幫浦 | 揚水幫浦故障 | OTHER | D23/0/StaDev/2A5Other |  |  |  | CDC | 443 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | MCC_IED | IED |  | SupLocal | [17 empty] | 1-39-01 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.MCC_IED_S/L | 161KV IED SUPY/LOCAL | OTHER | D23/0/StaDev/8A5Other |  |  |  | CDC | 444 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 22 | 22kV | PMCC_IED | IED |  | SupLocal | [17 empty] | 1-39-02 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.PMCC_IED_S/L | 23KV IED SUPY/LOCAL | OTHER | D23/0/StaDev/PMCC_R_L |  |  |  | CDC | 445 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D23 | 斗六DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [16 empty] | 2-31-04 | 2-31-05 | [6 empty] | ADCS_N | [8 empty] | 斗六DS.15B1E_ES | 15B1E_ES | OTHER | D23/161/1BUS/BE1 |  |  |  | CDC | 446 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [16 empty] | 2-31-06 | 2-31-07 | [6 empty] | ADCS_N | [8 empty] | 斗六DS.15B2E_ES | 15B2E | OTHER | D23/161/2BUS/BE2 |  |  |  | CDC | 447 | GENERICDIPoint | DS049_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D23 | 斗六DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-38-15 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D23/0/StaDev/Burglar |  |  |  | CDC | 448 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-39-00 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.無人化門禁(2) | 無人化門禁(2)小門開啟警報 | OTHER | D23/0/StaDev/Door |  |  |  | CDC | 449 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  |  |  |  | GEN | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.GEN | 緊急發電機運轉 | OTHER | D23/0/StaDev/1A5Other |  |  |  | CDC | 450 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D23 | 斗六DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D23/161/ComPoint/12B_CTFA |  |  |  | CDC | 451 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-34-15 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D23/161/ComPoint/BUS_RYFA |  |  |  | CDC | 452 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D23 | 斗六DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-31-07 | [7 empty] | ADCS_N | [8 empty] | 斗六DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D23/0/ComPoint/OLTC_A |  |  |  | CDC | 453 | GENERICDIPoint | DS049_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D23 | 斗六DS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗六DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 454 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗六DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 455 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 270_SC | #7SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗六DS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 456 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 22 | 22kV | 280_SC | #8SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 斗六DS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 457 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1610LE | 1610LE (非取樣點) | LINE161 | D23/161/1610/LE0 |  |  |  |  | 458 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1610 | 雲林斗六一路(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1610BE | 1610BE (非取樣點) | LINE161 | D23/161/1610/BE0 |  |  |  |  | 459 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1620LE | 1620LE (非取樣點) | LINE161 | D23/161/1620/LE0 |  |  |  |  | 460 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1620 | 雲林斗六二路(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1620BE | 1620BE (非取樣點) | LINE161 | D23/161/1620/BE0 |  |  |  |  | 461 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN61 | XN61_DS |  | DS1 | XN61_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_DS | XN61_DS (非取樣點) | FEEDER | D23/22/XN61/DS |  |  |  |  | 462 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN61 | XN61_ES |  | LE0 | XN61_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN61_ES | XN61_ES (非取樣點) | FEEDER | D23/22/XN61/ES |  |  |  |  | 463 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN62 | XN62_DS |  | DS1 | XN62_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_DS | XN62_DS (非取樣點) | FEEDER | D23/22/XN62/DS |  |  |  |  | 464 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN62 | XN62_ES |  | LE0 | XN62_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN62_ES | XN62_ES (非取樣點) | FEEDER | D23/22/XN62/ES |  |  |  |  | 465 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN63 | XN63_DS |  | DS1 | XN63_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_DS | XN63_DS (非取樣點) | FEEDER | D23/22/XN63/DS |  |  |  |  | 466 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN63 | XN63_ES |  | LE0 | XN63_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN63_ES | XN63_ES (非取樣點) | FEEDER | D23/22/XN63/ES |  |  |  |  | 467 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN64 | XN64_DS |  | DS1 | XN64_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_DS | XN64_DS (非取樣點) | FEEDER | D23/22/XN64/DS |  |  |  |  | 468 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN64 | XN64_ES |  | LE0 | XN64_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN64_ES | XN64_ES (非取樣點) | FEEDER | D23/22/XN64/ES |  |  |  |  | 469 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN65 | XN65_DS |  | DS1 | XN65_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_DS | XN65_DS (非取樣點) | FEEDER | D23/22/XN65/DS |  |  |  |  | 470 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN65 | XN65_ES |  | LE0 | XN65_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN65_ES | XN65_ES (非取樣點) | FEEDER | D23/22/XN65/ES |  |  |  |  | 471 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN66 | XN66_DS |  | DS1 | XN66_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_DS | XN66_DS (非取樣點) | FEEDER | D23/22/XN66/DS |  |  |  |  | 472 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN66 | XN66_ES |  | LE0 | XN66_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN66_ES | XN66_ES (非取樣點) | FEEDER | D23/22/XN66/ES |  |  |  |  | 473 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN67 | XN67_DS |  | DS1 | XN67_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_DS | XN67_DS (非取樣點) | FEEDER | D23/22/XN67/DS |  |  |  |  | 474 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN67 | XN67_ES |  | LE0 | XN67_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN67_ES | XN67_ES (非取樣點) | FEEDER | D23/22/XN67/ES |  |  |  |  | 475 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN68 | XN68_DS |  | DS1 | XN68_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_DS | XN68_DS (非取樣點) | FEEDER | D23/22/XN68/DS |  |  |  |  | 476 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN68 | XN68_ES |  | LE0 | XN68_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN68_ES | XN68_ES (非取樣點) | FEEDER | D23/22/XN68/ES |  |  |  |  | 477 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN71 | XN71_DS |  | DS1 | XN71_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_DS | XN71_DS (非取樣點) | FEEDER | D23/22/XN71/DS |  |  |  |  | 478 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN71 | XN71_ES |  | LE0 | XN71_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN71_ES | XN71_ES (非取樣點) | FEEDER | D23/22/XN71/ES |  |  |  |  | 479 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN72 | XN72_DS |  | DS1 | XN72_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_DS | XN72_DS (非取樣點) | FEEDER | D23/22/XN72/DS |  |  |  |  | 480 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN72 | XN72_ES |  | LE0 | XN72_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN72_ES | XN72_ES (非取樣點) | FEEDER | D23/22/XN72/ES |  |  |  |  | 481 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN73 | XN73_DS |  | DS1 | XN73_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_DS | XN73_DS (非取樣點) | FEEDER | D23/22/XN73/DS |  |  |  |  | 482 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN73 | XN73_ES |  | LE0 | XN73_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN73_ES | XN73_ES (非取樣點) | FEEDER | D23/22/XN73/ES |  |  |  |  | 483 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN74 | XN74_DS |  | DS1 | XN74_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_DS | XN74_DS (非取樣點) | FEEDER | D23/22/XN74/DS |  |  |  |  | 484 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN74 | XN74_ES |  | LE0 | XN74_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN74_ES | XN74_ES (非取樣點) | FEEDER | D23/22/XN74/ES |  |  |  |  | 485 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN75 | XN75_DS |  | DS1 | XN75_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_DS | XN75_DS (非取樣點) | FEEDER | D23/22/XN75/DS |  |  |  |  | 486 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN75 | XN75_ES |  | LE0 | XN75_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN75_ES | XN75_ES (非取樣點) | FEEDER | D23/22/XN75/ES |  |  |  |  | 487 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN76 | XN76_DS |  | DS1 | XN76_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_DS | XN76_DS (非取樣點) | FEEDER | D23/22/XN76/DS |  |  |  |  | 488 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN76 | XN76_ES |  | LE0 | XN76_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN76_ES | XN76_ES (非取樣點) | FEEDER | D23/22/XN76/ES |  |  |  |  | 489 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN77 | XN77_DS |  | DS1 | XN77_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_DS | XN77_DS (非取樣點) | FEEDER | D23/22/XN77/DS |  |  |  |  | 490 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN77 | XN77_ES |  | LE0 | XN77_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN77_ES | XN77_ES (非取樣點) | FEEDER | D23/22/XN77/ES |  |  |  |  | 491 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | XN78 | XN78_DS |  | DS1 | XN78_DS | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_DS | XN78_DS (非取樣點) | FEEDER | D23/22/XN78/DS |  |  |  |  | 492 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | XN78 | XN78_ES |  | LE0 | XN78_ES | [24 empty] | DDCS1_1 | [8 empty] | 斗六DS.XN78_ES | XN78_ES (非取樣點) | FEEDER | D23/22/XN78/ES |  |  |  |  | 493 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1501E | 1501E (非取樣點) | TIE | D23/161/1500/E1 |  |  |  |  | 494 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1502E | 1502E (非取樣點) | TIE | D23/161/1500/E2 |  |  |  |  | 495 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.301 | 301 (非取樣點) | TIE | D23/22/300/D1 |  |  |  |  | 496 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.302 | 302 (非取樣點) | TIE | D23/22/300/D2 |  |  |  |  | 497 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.401 | 401 (非取樣點) | TIE | D23/22/400/D1 |  |  |  |  | 498 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 402 | 402 |  | 402 | 402 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.402 | 402 (非取樣點) | TIE | D23/22/400/D2 |  |  |  |  | 499 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.391 | 391 (非取樣點) | OTHER | D23/22/390/D1 |  |  |  |  | 500 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.391E | 391E (非取樣點) | OTHER | D23/22/390/E1 |  |  |  |  | 501 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.491 | 491 (非取樣點) | OTHER | D23/22/490/D1 |  |  |  |  | 502 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.491E | 491E (非取樣點) | OTHER | D23/22/490/E1 |  |  |  |  | 503 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1770TE | 1770TE (非取樣點) | MTR | D23/161/1770/TE0 |  |  |  |  | 504 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1770BE | 1770BE (非取樣點) | MTR | D23/161/1770/BE0 |  |  |  |  | 505 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.351 | 351 (非取樣點) | MTR | D23/22/350/D1 |  |  |  |  | 506 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.351E | 351E (非取樣點) | MTR | D23/22/350/E1 |  |  |  |  | 507 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.361 | 361 (非取樣點) | MTR | D23/22/360/D1 |  |  |  |  | 508 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 360 | #3DTR(360) |  | E1 | 361E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.361E | 361E (非取樣點) | MTR | D23/22/360/E1 |  |  |  |  | 509 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | 1780TE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1780TE | 1780TE (非取樣點) | MTR | D23/161/1780/TE0 |  |  |  |  | 510 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | 1780BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.1780BE | 1780BE (非取樣點) | MTR | D23/161/1780/BE0 |  |  |  |  | 511 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.371 | 371 (非取樣點) | MTR | D23/22/370/D1 |  |  |  |  | 512 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 370 | #4DTR(370) |  | E1 | 371E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.371E | 371E (非取樣點) | MTR | D23/22/370/E1 |  |  |  |  | 513 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.251E | 251E (非取樣點) | SC | D23/22/250/E1 |  |  |  |  | 514 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.251 | 251 (非取樣點) | SC | D23/22/250/D1 |  |  |  |  | 515 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.261E | 261E (非取樣點) | SC | D23/22/260/E1 |  |  |  |  | 516 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.261 | 261 (非取樣點) | SC | D23/22/260/D1 |  |  |  |  | 517 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.271E | 271E (非取樣點) | SC | D23/22/270/E1 |  |  |  |  | 518 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.271 | 271 (非取樣點) | SC | D23/22/270/D1 |  |  |  |  | 519 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.281E | 281E (非取樣點) | SC | D23/22/280/E1 |  |  |  |  | 520 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_N | [8 empty] | 斗六DS.281 | 281 (非取樣點) | SC | D23/22/280/D1 |  |  |  |  | 521 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 522 | NotelDIPoint | [38 empty] | START/STOP | STOP
D23 | 斗六DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.301E | 301E(非取樣點) | OTHER | D23/22/300/E1 |  |  |  |  | 523 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  |  |  |  | 302E | 302E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.302E | 302E(非取樣點) | OTHER | D23/22/300/E2 |  |  |  |  | 524 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  |  |  |  | 401E | 401E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.401E | 401E(非取樣點) | OTHER | D23/22/400/E1 |  |  |  |  | 525 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  |  |  |  | 402E | 402E | [24 empty] | ADCS_N | [8 empty] | 斗六DS.402E | 402E(非取樣點) | OTHER | D23/22/400/E2 |  |  |  |  | 526 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 3A | #3A |  | BE | #3A_BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.#3A_BE | #3A BE(非取樣點) | OTHER | [5 empty] | 527 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 3B | #3B |  | BE | #3B_BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.#3B_BE | #3B BE(非取樣點) | OTHER | [5 empty] | 528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 4 | #4 |  | BE | #4_BE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.#4_BE | #4 BE(非取樣點) | OTHER | [5 empty] | 529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 斗六DS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 3ABUS | 3ABUS |  | PTE | 3ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.3ABUS_PTE | #3ABUS_PTE(非取樣點) | OTHER | [5 empty] | 531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 斗六DS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 3BBUS | 3BBUS |  | PTE | 3BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.3BBUS_PTE | #3BBUS_PTE(非取樣點) | OTHER | [5 empty] | 533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D23 | 斗六DS | 0 |  | 4BUS | 4BUS |  | PTD | 4BUS_PTD | [24 empty] | ADCS_N | [8 empty] | 斗六DS.4BUS_PTD | #4BUS_PTD(非取樣點) | OTHER | [5 empty] | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D23 | 斗六DS | 0 |  | 4BUS | 4BUS |  | PTE | 4BUS_PTE | [24 empty] | ADCS_N | [8 empty] | 斗六DS.4BUS_PTE | #4BUS_PTE(非取樣點) | OTHER | [5 empty] | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo