## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 | [10 empty] | B3/D24_A1 | [16 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 | [10 empty] | B3/D24_A1 | [16 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 | [8 empty] | kV_-210_210(-2000_2000) | aaa | B2/D24_A1 | [8 empty] | 虎菁DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 4 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D24 | 虎菁DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 | [8 empty] | kV_-210_210(-2000_2000) | aab | B2/D24_A1 | [8 empty] | 虎菁DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 5 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 | [8 empty] | MW_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1510_MW | 斗南虎菁一路 MW | LINE161 | [5 empty] | 6 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 | [8 empty] | MVAR_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1510_MVAR | 斗南虎菁一路 MVAR | LINE161 | [5 empty] | 7 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 | [8 empty] | MW_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1520_MW | 斗南虎菁二路 MW | LINE161 | [5 empty] | 8 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 | [8 empty] | MVAR_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1520_MVAR | 斗南虎菁二路 MVAR | LINE161 | [5 empty] | 9 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 | [8 empty] | MW_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1530_MW | 虎科虎菁一路 MW | LINE161 | [5 empty] | 10 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 | [8 empty] | MVAR_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1530_MVAR | 虎科虎菁一路 MVAR | LINE161 | [5 empty] | 11 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 | [8 empty] | MW_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1540_MW | 虎科虎菁二路 MW | LINE161 | [5 empty] | 12 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 | [8 empty] | MVAR_-560_560(-2000_2000) |  | B2/D24_A1 | [8 empty] | 虎菁DS.1540_MVAR | 虎科虎菁二路 MVAR | LINE161 | [5 empty] | 13 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0020 | [10 empty] | B2/D24_A1 | [16 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0021 | [10 empty] | B2/D24_A1 | [16 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0022 | [10 empty] | B2/D24_A1 | [16 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0023 | [10 empty] | B2/D24_A1 | [16 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 | [10 empty] | B2/D24_A1 | [16 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0025 |  | 0092 | [8 empty] | B1/D24_A1 | [16 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0026 |  | 0094 | [8 empty] | B1/D24_A1 | [16 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0027 | [10 empty] | B1/D24_A1 | [16 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 | [10 empty] | B1/D24_A1 | [16 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0029 | [10 empty] | B1/D24_A1 | [16 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0030 |  | 0096 | [8 empty] | B1/D24_A1 | [16 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0031 |  | 0098 | [8 empty] | B1/D24_A1 | [16 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 | [10 empty] | B1/D24_A1 | [16 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 | [10 empty] | B1/D24_A1 | [16 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0034 | [10 empty] | B1/D24_A1 | [16 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0045 | [8 empty] | kV_-18_18(-2000_2000) | aaa | B3/D24_A1 | [8 empty] | 虎菁DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | [5 empty] | 29 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0046 | [10 empty] | B3/D24_A1 | [16 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0047 | [10 empty] | B3/D24_A1 | [16 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0048 | [10 empty] | B3/D24_A1 | [16 empty] | 32 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0049 | [10 empty] | B3/D24_A1 | [16 empty] | 33 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0050 | [10 empty] | B3/D24_A1 | [16 empty] | 34 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0051 | [10 empty] | B2/D24_D1 | [16 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0052 | [10 empty] | B2/D24_D1 | [16 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0053 | [10 empty] | B2/D24_D1 | [16 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0054 | [10 empty] | B2/D24_D1 | [16 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0055 | [10 empty] | B2/D24_D1 | [16 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0056 | [10 empty] | B2/D24_D1 | [16 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0057 | [10 empty] | B2/D24_D1 | [16 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 | [10 empty] | B2/D24_D1 | [16 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 | [10 empty] | B2/D24_D1 | [16 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 | [10 empty] | B2/D24_D1 | [16 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 | [10 empty] | B2/D24_D1 | [16 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0062 | [10 empty] | B2/D24_D1 | [16 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0063 | [10 empty] | B2/D24_D1 | [16 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 | [10 empty] | B3/D24_A1 | [16 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 | [10 empty] | B3/D24_A1 | [16 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0066 | [10 empty] | B2/D24_D1 | [16 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0067 | [10 empty] | B2/D24_D1 | [16 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0068 | [10 empty] | B2/D24_D1 | [16 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0069 | [10 empty] | B2/D24_D1 | [16 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0070 | [10 empty] | B2/D24_D1 | [16 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0071 | [10 empty] | B2/D24_D1 | [16 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0072 | [10 empty] | B2/D24_D1 | [16 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 | [10 empty] | B2/D24_D1 | [16 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 | [10 empty] | B2/D24_D1 | [16 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 | [10 empty] | B2/D24_D1 | [16 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0076 | [10 empty] | B2/D24_D1 | [16 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0077 | [10 empty] | B2/D24_D1 | [16 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 | [10 empty] | B2/D24_D1 | [16 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 | [10 empty] | B2/D24_D1 | [16 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 | [10 empty] | B2/D24_D1 | [16 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 | [10 empty] | B2/D24_D1 | [16 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0082 | [10 empty] | B2/D24_D1 | [16 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0083 | [10 empty] | B3/D24_A1 | [16 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0084 | [10 empty] | B3/D24_A1 | [16 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0085 | [10 empty] | B3/D24_A1 | [16 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0086 | [8 empty] | kV_-9_9(-2000_2000) | aca | B3/D24_A1 | [8 empty] | 虎菁DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 70 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0087 | [10 empty] | B3/D24_A1 | [16 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 | [10 empty] | B3/D24_A1 | [16 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 | [10 empty] | B3/D24_A1 | [16 empty] | 73 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 | [10 empty] | B3/D24_A1 | [16 empty] | 74 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 | [10 empty] | B3/D24_A1 | [16 empty] | 75 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0092 | [10 empty] | B2/D24_D1 | [16 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 | [10 empty] | B2/D24_D1 | [16 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 | [10 empty] | B2/D24_D1 | [16 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 | [10 empty] | B2/D24_D1 | [16 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 | [10 empty] | B2/D24_D1 | [16 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 | [10 empty] | B2/D24_D1 | [16 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0098 | [10 empty] | B2/D24_D1 | [16 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 | [10 empty] | B2/D24_D1 | [16 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 | [10 empty] | B2/D24_D1 | [16 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 | [10 empty] | B2/D24_D1 | [16 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 | [10 empty] | B2/D24_D1 | [16 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0103 | [10 empty] | B2/D24_D1 | [16 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0104 | [10 empty] | B2/D24_D1 | [16 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0105 | [10 empty] | B2/D24_D1 | [16 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 | [10 empty] | B2/D24_D1 | [16 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 | [10 empty] | B2/D24_D1 | [16 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 | [10 empty] | B2/D24_D1 | [16 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0109 | [10 empty] | B2/D24_D1 | [16 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0110 | [10 empty] | B2/D24_D1 | [16 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 | [10 empty] | B2/D24_D1 | [16 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 | [10 empty] | B2/D24_D1 | [16 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 | [10 empty] | B2/D24_D1 | [16 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 | [10 empty] | B2/D24_D1 | [16 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0115 | [10 empty] | B2/D24_D1 | [16 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0116 | [10 empty] | B2/D24_D1 | [16 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0117 | [10 empty] | B2/D24_D1 | [16 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0118 | [10 empty] | B2/D24_D1 | [16 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0119 | [10 empty] | B2/D24_D1 | [16 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0120 | [10 empty] | B2/D24_D1 | [16 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0121 | [10 empty] | B2/D24_D1 | [16 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 | [10 empty] | B3/D24_A1 | [16 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 | [10 empty] | B3/D24_A1 | [16 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 | [10 empty] | B3/D24_A1 | [16 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0125 | [8 empty] | kV_-18_18(-2000_2000) | aba | B3/D24_A1 | [8 empty] | 虎菁DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0126 | [10 empty] | B3/D24_A1 | [16 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0127 | [10 empty] | B3/D24_A1 | [16 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 | [10 empty] | B3/D24_A1 | [16 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 | [10 empty] | B3/D24_A1 | [16 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0130 | [10 empty] | B3/D24_A1 | [16 empty] | 114 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0131 | [10 empty] | B3/D24_A1 | [16 empty] | 115 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0132 | [10 empty] | B3/D24_A1 | [16 empty] | 116 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0133 | [10 empty] | B2/D24_D1 | [16 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0134 | [10 empty] | B2/D24_D1 | [16 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0135 | [10 empty] | B2/D24_D1 | [16 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0136 | [10 empty] | B2/D24_D1 | [16 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0137 | [10 empty] | B2/D24_D1 | [16 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0138 | [10 empty] | B2/D24_D1 | [16 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0139 | [10 empty] | B2/D24_D1 | [16 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0140 | [10 empty] | B2/D24_D1 | [16 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0141 | [10 empty] | B2/D24_D1 | [16 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0142 | [10 empty] | B2/D24_D1 | [16 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0143 | [10 empty] | B2/D24_D1 | [16 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0144 | [10 empty] | B2/D24_D1 | [16 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0145 | [10 empty] | B2/D24_D1 | [16 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 | [10 empty] | B2/D24_D1 | [16 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 | [10 empty] | B2/D24_D1 | [16 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 | [10 empty] | B2/D24_D1 | [16 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 | [10 empty] | B2/D24_D1 | [16 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 | [10 empty] | B2/D24_D1 | [16 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0151 | [10 empty] | B2/D24_D1 | [16 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0152 | [10 empty] | B2/D24_D1 | [16 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0153 | [10 empty] | B2/D24_D1 | [16 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0154 | [10 empty] | B2/D24_D1 | [16 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0155 | [10 empty] | B2/D24_D1 | [16 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 | [10 empty] | B2/D24_D1 | [16 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0157 | [10 empty] | B2/D24_D1 | [16 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 | [10 empty] | B2/D24_D1 | [16 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 | [10 empty] | B2/D24_D1 | [16 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 | [10 empty] | B2/D24_D1 | [16 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 | [10 empty] | B2/D24_D1 | [16 empty] | 145 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 | [10 empty] | B2/D24_D1 | [16 empty] | 146 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0163 | [8 empty] | kV_-9_9(-2000_2000) | ada | B3/D24_A1 | [8 empty] | 虎菁DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0164 | [10 empty] | B3/D24_A1 | [16 empty] | 148 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0165 | [10 empty] | B3/D24_A1 | [16 empty] | 149 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 | [10 empty] | B3/D24_A1 | [16 empty] | 150 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 | [10 empty] | B3/D24_A1 | [16 empty] | 151 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 | [10 empty] | B3/D24_A1 | [16 empty] | 152 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0169 | [10 empty] | B2/D24_D1 | [16 empty] | 153 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0170 | [10 empty] | B2/D24_D1 | [16 empty] | 154 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 | [10 empty] | B2/D24_D1 | [16 empty] | 155 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 | [10 empty] | B2/D24_D1 | [16 empty] | 156 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 | [10 empty] | B2/D24_D1 | [16 empty] | 157 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 | [10 empty] | B2/D24_D1 | [16 empty] | 158 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0175 | [10 empty] | B2/D24_D1 | [16 empty] | 159 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0176 | [10 empty] | B2/D24_D1 | [16 empty] | 160 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 | [10 empty] | B2/D24_D1 | [16 empty] | 161 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 | [10 empty] | B2/D24_D1 | [16 empty] | 162 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 | [10 empty] | B2/D24_D1 | [16 empty] | 163 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0180 | [10 empty] | B2/D24_D1 | [16 empty] | 164 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0181 | [10 empty] | B2/D24_D1 | [16 empty] | 165 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 | [10 empty] | B2/D24_D1 | [16 empty] | 166 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 | [10 empty] | B2/D24_D1 | [16 empty] | 167 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 | [10 empty] | B2/D24_D1 | [16 empty] | 168 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 | [10 empty] | B2/D24_D1 | [16 empty] | 169 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0186 | [10 empty] | B2/D24_D1 | [16 empty] | 170 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0187 | [10 empty] | B2/D24_D1 | [16 empty] | 171 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0188 | [10 empty] | B2/D24_D1 | [16 empty] | 172 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0189 | [10 empty] | B2/D24_D1 | [16 empty] | 173 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0190 | [10 empty] | B2/D24_D1 | [16 empty] | 174 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0191 | [10 empty] | B2/D24_D1 | [16 empty] | 175 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 | [10 empty] | B3/D24_A1 | [16 empty] | 176 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 | [10 empty] | B3/D24_A1 | [16 empty] | 177 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0194 | [10 empty] | B2/D24_D1 | [16 empty] | 178 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0195 | [10 empty] | B2/D24_D1 | [16 empty] | 179 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0196 | [10 empty] | B2/D24_D1 | [16 empty] | 180 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 | [10 empty] | B2/D24_D1 | [16 empty] | 181 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 | [10 empty] | B2/D24_D1 | [16 empty] | 182 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 | [10 empty] | B2/D24_D1 | [16 empty] | 183 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0200 | [10 empty] | B2/D24_D1 | [16 empty] | 184 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0201 | [10 empty] | B3/D24_A1 | [16 empty] | 185 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0202 | [10 empty] | B3/D24_A1 | [16 empty] | 186 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0203 | [10 empty] | B3/D24_A1 | [16 empty] | 187 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0204 | [10 empty] | B3/D24_A1 | [16 empty] | 188 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0205 | [10 empty] | B3/D24_A1 | [16 empty] | 189 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0206 | [10 empty] | B3/D24_A1 | [16 empty] | 190 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0207 | [10 empty] | B3/D24_A1 | [16 empty] | 191 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0208 | [10 empty] | B3/D24_A1 | [16 empty] | 192 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 | [10 empty] | B3/D24_A1 | [16 empty] | 193 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 | [10 empty] | B3/D24_A1 | [16 empty] | 194 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 | [10 empty] | B3/D24_A1 | [16 empty] | 195 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 | [10 empty] | B3/D24_A1 | [16 empty] | 196 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 | [10 empty] | B3/D24_A1 | [16 empty] | 197 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 | [10 empty] | B3/D24_A1 | [16 empty] | 198 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCL6 | [14 empty] | 0320 | [10 empty] | B3/D24_A1 | [16 empty] | 199 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | ADCH6 | [14 empty] | 0321 | [10 empty] | B3/D24_A1 | [16 empty] | 200 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0328 | [10 empty] | B3/D24_A1 | [16 empty] | 201 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0329 | [10 empty] | B3/D24_A1 | [16 empty] | 202 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0000 | [8 empty] | ELEM/ALL | [16 empty] | 203 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510_87A | 斗南虎菁一路(1510) 87RY | LINE161 | [5 empty] | 204 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 | [10 empty] | B2/D24_A1 | [16 empty] | 205 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510_PHA | 斗南虎菁一路(1510) 相間RY | LINE161 | [5 empty] | 206 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510_GDA | 斗南虎菁一路(1510) 接地RY | LINE161 | [5 empty] | 207 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D08D241/T2 |  | 0000 |  | 0001 | [7 empty] | aaba | B2/D24_A1 | [8 empty] | 虎菁DS.1510_CB | 1510(斗南虎菁一路) CB | LINE161 | [5 empty] | 208 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520_87A | 斗南虎菁二路(1520) 87RY | LINE161 | [5 empty] | 209 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 | [10 empty] | B2/D24_A1 | [16 empty] | 210 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520_PHA | 斗南虎菁二路(1520) 相間RY | LINE161 | [5 empty] | 211 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520_GDA | 斗南虎菁二路(1520) 接地RY | LINE161 | [5 empty] | 212 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D08D242/T2 |  | 0005 |  | 0002 | [7 empty] | aaea | B2/D24_A1 | [8 empty] | 虎菁DS.1520_CB | 1520(斗南虎菁二路) CB | LINE161 | [5 empty] | 213 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530_87A | 虎科虎菁一路(1530) 87RY | LINE161 | [5 empty] | 214 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 | [10 empty] | B2/D24_A1 | [16 empty] | 215 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530_PHA | 虎科虎菁一路(1530) 相間RY | LINE161 | [5 empty] | 216 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530_GDA | 虎科虎菁一路(1530) 接地RY | LINE161 | [5 empty] | 217 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D13D241/T2 |  | 0010 |  | 0003 | [7 empty] | aagb | B2/D24_A1 | [8 empty] | 虎菁DS.1530_CB | 1530(虎科虎菁一路) CB | LINE161 | [5 empty] | 218 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540_87A | 虎科虎菁二路(1540) 87RY | LINE161 | [5 empty] | 219 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 | [10 empty] | B2/D24_A1 | [16 empty] | 220 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540_PHA | 虎科虎菁二路(1540) 相間RY | LINE161 | [5 empty] | 221 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 | [10 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540_GDA | 虎科虎菁二路(1540) 接地RY | LINE161 | [5 empty] | 222 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0046 | [10 empty] | B2/D24_A1 | [16 empty] | 223 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0047 | [10 empty] | B2/D24_A1 | [16 empty] | 224 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0048 | [10 empty] | B2/D24_A1 | [16 empty] | 225 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0049 | [10 empty] | B2/D24_A1 | [16 empty] | 226 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D13D242/T2 |  | 0015 |  | 0004 | [7 empty] | aahb | B2/D24_A1 | [8 empty] | 虎菁DS.1540_CB | 1540(虎科虎菁二路) CB | LINE161 | [5 empty] | 227 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 | [10 empty] | B2/D24_A1 | [16 empty] | 228 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 | [10 empty] | B2/D24_A1 | [16 empty] | 229 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 | [10 empty] | B2/D24_A1 | [16 empty] | 230 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0056 | [10 empty] | B3/D24_A1 | [16 empty] | 231 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0057 | [10 empty] | B3/D24_A1 | [16 empty] | 232 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0050 |  | 0011 | [7 empty] | aadz | B2/D24_A1 | [8 empty] | 虎菁DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 233 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 | [10 empty] | B1/D24_A1 | [16 empty] | 234 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 | [10 empty] | B1/D24_A1 | [16 empty] | 235 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 51ZA | 1A & 1B |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 | [10 empty] | B1/D24_A1 | [16 empty] | 236 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 | [10 empty] | B1/D24_A1 | [16 empty] | 237 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 | [10 empty] | B1/D24_A1 | [16 empty] | 238 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0059 |  | 0012 | [7 empty] | aacb | ELEM/D24_A1 | [8 empty] | 虎菁DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 239 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 | [10 empty] | B3/D24_A1 | [16 empty] | 240 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 | [10 empty] | B3/D24_A1 | [16 empty] | 241 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0072 |  | 0013 | [7 empty] | aafb | ELEM/D24_A1 | [8 empty] | 虎菁DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 | [10 empty] | B3/D24_A1 | [16 empty] | 243 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 | [10 empty] | B3/D24_A1 | [16 empty] | 244 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0066 |  | 0016 | [7 empty] | aaaa | ELEM/D24_A1 | [16 empty] | 245 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 | [10 empty] | B1/D24_A1 | [16 empty] | 246 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 | [10 empty] | B1/D24_A1 | [16 empty] | 247 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 51ZA | 2A & 2B |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 | [10 empty] | B1/D24_A1 | [16 empty] | 248 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 | [10 empty] | B1/D24_A1 | [16 empty] | 249 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 | [10 empty] | B1/D24_A1 | [16 empty] | 250 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/LBS210^C/1SC(A) |  |  | 0160 |  | 0017 | [7 empty] | aaib | B3/D24_A1 | [8 empty] | 虎菁DS.210_CB | 210(23KV #1SC) CB | SC | [5 empty] | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 | [10 empty] | B3/D24_A1 | [16 empty] | 252 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 | [10 empty] | B3/D24_A1 | [16 empty] | 253 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0163 |  | 0018 | [7 empty] | aabb | B3/D24_A1 | [16 empty] | 254 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 | [10 empty] | B3/D24_A1 | [16 empty] | 255 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 | [10 empty] | B3/D24_A1 | [16 empty] | 256 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0110 | [10 empty] | B2/D24_A1 | [16 empty] | 257 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0112 | [10 empty] | B2/D24_A1 | [16 empty] | 258 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0114 | [10 empty] | B2/D24_A1 | [16 empty] | 259 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0116 | [10 empty] | B2/D24_A1 | [16 empty] | 260 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 | [10 empty] | B2/D24_A1 | [16 empty] | 261 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 | [10 empty] | B2/D24_A1 | [16 empty] | 262 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0132 | [10 empty] | B2/D24_A1 | [16 empty] | 263 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 | [10 empty] | B2/D24_A1 | [16 empty] | 264 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0140 | [10 empty] | B3/D24_A1 | [16 empty] | 265 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XJ51/T1 |  |  | 0166 |  | 0019 | [7 empty] | aacb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ51_CB | XJ51(23KV虎51線) CB | FEEDER | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0161 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.210_SCA | 23KV #1SC 51,51N RY | SC | [5 empty] | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0162 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.210_UVA | 23KV #1SC 27RY(欠壓) | SC | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XJ52/T1 |  |  | 0169 |  | 0020 | [7 empty] | aadb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ52_CB | XJ52(23KV虎52線) CB | FEEDER | [5 empty] | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 390 | SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 | [10 empty] | B3/D24_A1 | [16 empty] | 270 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 390 | SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 | [10 empty] | B3/D24_A1 | [16 empty] | 271 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XJ53/T1 |  |  | 0172 |  | 0021 | [7 empty] | aaeb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ53_CB | XJ53(23KV虎53線) CB | FEEDER | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ51_PHA | 23KV虎51線(XJ51) 相間RY | FEEDER | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ51_GDA | 23KV虎51線(XJ51) 接地RY | FEEDER | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XJ54/T1 |  |  | 0175 |  | 0022 | [7 empty] | aafb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ54_CB | XJ54(23KV虎54線) CB | FEEDER | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ52_PHA | 23KV虎52線(XJ52) 相間RY | FEEDER | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ52_GDA | 23KV虎52線(XJ52) 接地RY | FEEDER | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/XJ55/T1 |  |  | 0178 |  | 0023 | [7 empty] | aahb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ55_CB | XJ55(23KV虎55線) CB | FEEDER | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ53_PHA | 23KV虎53線(XJ53) 相間RY | FEEDER | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ53_GDA | 23KV虎53線(XJ53) 接地RY | FEEDER | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0181 |  | 0024 | [7 empty] | aajb | B3/D24_A1 | [16 empty] | 281 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ54_PHA | 23KV虎54線(XJ54) 相間RY | FEEDER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ54_GDA | 23KV虎54線(XJ54) 接地RY | FEEDER | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0069 |  | 0025 | [7 empty] | acaa | ELEM/D24_A1 | [16 empty] | 284 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ55_PHA | 23KV虎55線(XJ55) 相間RY | FEEDER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ55_GDA | 23KV虎55線(XJ55) 接地RY | FEEDER | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0184 |  | 0026 | [7 empty] | acbb | B3/D24_A1 | [8 empty] | 虎菁DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 | [10 empty] | B3/D24_A1 | [16 empty] | 288 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 | [10 empty] | B3/D24_A1 | [16 empty] | 289 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XJ25/T1 |  |  | 0187 |  | 0027 | [7 empty] | acgb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ25_CB | XJ25(11KV虎五線) CB | FEEDER | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0185 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0186 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XJ24/T1 |  |  | 0190 |  | 0028 | [7 empty] | acfb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ24_CB | XJ24(11KV虎四線) CB | FEEDER | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ25_PHA | 11KV虎五線(XJ25) 相間RY | FEEDER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ25_GDA | 11KV虎五線(XJ25) 接地RY | FEEDER | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XJ23/T1 |  |  | 0193 |  | 0029 | [7 empty] | aceb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ23_CB | XJ23(11KV虎三線) CB | FEEDER | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ24_PHA | 11KV虎四線(XJ24) 相間RY | FEEDER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ24_GDA | 11KV虎四線(XJ24) 接地RY | FEEDER | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XJ22/T1 |  |  | 0196 |  | 0030 | [7 empty] | acdb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ22_CB | XJ22(11KV虎二線) CB | FEEDER | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ23_PHA | 11KV虎三線(XJ23) 相間RY | FEEDER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ23_GDA | 11KV虎三線(XJ23) 接地RY | FEEDER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/XJ21/T1 |  |  | 0199 |  | 0031 | [7 empty] | accb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ21_CB | XJ21(11KV虎一線) CB | FEEDER | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ22_PHA | 11KV虎二線(XJ22) 相間RY | FEEDER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ22_GDA | 11KV虎二線(XJ22) 接地RY | FEEDER | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0202 |  | 0032 | [7 empty] | adab | B3/D24_A1 | [16 empty] | 305 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ21_PHA | 11KV虎一線(XJ21) 相間RY | FEEDER | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ21_GDA | 11KV虎一線(XJ21) 接地RY | FEEDER | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0079 |  | 0033 | [7 empty] | abaa | ELEM/D24_A1 | [16 empty] | 308 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 | [10 empty] | B3/D24_A1 | [16 empty] | 309 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 | [10 empty] | B3/D24_A1 | [16 empty] | 310 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/LBS230^C/3SC(A) |  |  | 0205 |  | 0034 | [7 empty] | abbb | B3/D24_A1 | [8 empty] | 虎菁DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0206 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0207 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XJ56/T1 |  |  | 0208 |  | 0035 | [7 empty] | abcb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ56_CB | XJ56(23KV虎56線) CB | FEEDER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ56_PHA | 23KV虎56線(XJ56) 相間RY | FEEDER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ56_GDA | 23KV虎56線(XJ56) 接地RY | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XJ57/T1 |  |  | 0211 |  | 0036 | [7 empty] | abdb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ57_CB | XJ57(23KV虎57線) CB | FEEDER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ57_PHA | 23KV虎57線(XJ57) 相間RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ57_GDA | 23KV虎57線(XJ57) 接地RY | FEEDER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XJ58/T1 |  |  | 0214 |  | 0037 | [7 empty] | abeb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ58_CB | XJ58(23KV虎58線) CB | FEEDER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ58_PHA | 23KV虎58線(XJ58) 相間RY | FEEDER | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ58_GDA | 23KV虎58線(XJ58) 接地RY | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XJ59/T1 |  |  | 0217 |  | 0038 | [7 empty] | abgb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ59_CB | XJ59(23KV虎59線) CB | FEEDER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ59_PHA | 23KV虎59線(XJ59) 相間RY | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ59_GDA | 23KV虎59線(XJ59) 接地RY | FEEDER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/XJ60/T1 |  |  | 0220 |  | 0039 | [7 empty] | abhb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ60_CB | XJ60(23KV虎60線) CB | FEEDER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ60_PHA | 23KV虎60線(XJ60) 相間RY | FEEDER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ60_GDA | 23KV虎60線(XJ60) 接地RY | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0082 |  | 0040 | [7 empty] | adba | ELEM/D24_A1 | [16 empty] | 329 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0224 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0225 | [10 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/LBS240^C/4SC(A) |  |  | 0223 |  | 0041 | [7 empty] | adjb | B3/D24_A1 | [8 empty] | 虎菁DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 490 | SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 | [10 empty] | B3/D24_A1 | [16 empty] | 333 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 | [10 empty] | B3/D24_A1 | [16 empty] | 334 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0226 |  | 0042 | [7 empty] | adcb | B3/D24_A1 | [16 empty] | 335 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ30_PHA | 11KV虎十線(XJ30) 相間RY | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ30_GDA | 11KV虎十線(XJ30) 接地RY | FEEDER | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XJ30/T1 |  |  | 0229 |  | 0043 | [7 empty] | adhb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ30_CB | XJ30(11KV虎十線) CB | FEEDER | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ29_PHA | 11KV虎九線(XJ29) 相間RY | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ29_GDA | 11KV虎九線(XJ29) 接地RY | FEEDER | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XJ29/T1 |  |  | 0232 |  | 0044 | [7 empty] | adgb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ29_CB | XJ29(11KV虎九線) CB | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ28_PHA | 11KV虎八線(XJ28) 相間RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ28_GDA | 11KV虎八線(XJ28) 接地RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XJ28/T1 |  |  | 0235 |  | 0045 | [7 empty] | adfb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ28_CB | XJ28(11KV虎八線) CB | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ27_PHA | 11KV虎七線(XJ27) 相間RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ27_GDA | 11KV虎七線(XJ27) 接地RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XJ27/T1 |  |  | 0238 |  | 0046 | [7 empty] | adeb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ27_CB | XJ27(11KV虎七線) CB | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ26_PHA | 11KV虎六線(XJ26) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 | [10 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ26_GDA | 11KV虎六線(XJ26) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/XJ26/T1 |  |  | 0241 |  | 0047 | [7 empty] | addb | B2/D24_D1 | [8 empty] | 虎菁DS.XJ26_CB | XJ26(11KV虎六線) CB | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0069 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510_87UL | 斗南虎菁一路(1510) 87RY U/L | LINE161 | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0070 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510_79UL | 斗南虎菁一路(1510) 79RY U/L | LINE161 | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0071 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520_87UL | 斗南虎菁二路(1520) 87RY U/L | LINE161 | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 0 |  | ComPoint |  |  | 81AS1 |  |  | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0307 | [10 empty] | B3/D24_A1 | [16 empty] | 354 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | ComPoint |  |  | 81AS2 |  |  | Status | 81RY A/S(2) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0308 | [10 empty] | B3/D24_A1 | [16 empty] | 355 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0072 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520_79UL | 斗南虎菁二路(1520) 79RY U/L | LINE161 | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0073 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530_87UL | 虎科虎菁一路(1530) 87RY U/L | LINE161 | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 21_UL |  |  | Status | 21RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 | [10 empty] | B2/D24_A1 | [16 empty] | 358 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0074 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530_79UL | 虎科虎菁一路(1530) 79RY U/L | LINE161 | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0075 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540_87UL | 虎科虎菁二路(1540) 87RY U/L | LINE161 | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 21_UL |  |  | Status | 21RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 | [10 empty] | B2/D24_A1 | [16 empty] | 361 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0076 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540_79UL | 虎科虎菁二路(1540) 79RY U/L | LINE161 | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0806 |  | 0091 | [8 empty] | B1/D24_A1 | [16 empty] | 363 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 21_UL |  |  | Status | 21RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 | [10 empty] | B2/D24_A1 | [16 empty] | 364 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0807 |  | 0093 | [8 empty] | B1/D24_A1 | [16 empty] | 365 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0095 | [8 empty] | B1/D24_A1 | [16 empty] | 366 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 21_UL |  |  | Status | 21RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 | [10 empty] | B2/D24_A1 | [16 empty] | 367 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0097 | [8 empty] | B1/D24_A1 | [16 empty] | 368 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0800 | [10 empty] | B2/D24_A1 | [16 empty] | 369 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0101 | [8 empty] | B2/D24_A1 | [16 empty] | 370 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  | 0102 | [8 empty] | B2/D24_A1 | [16 empty] | 371 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0803 | [10 empty] | B1/D24_A1 | [16 empty] | 372 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0804 | [10 empty] | B1/D24_A1 | [16 empty] | 373 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0805 | [10 empty] | B1/D24_A1 | [16 empty] | 374 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 景觀 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0864 |  | 0107 | [8 empty] | B3/D24_A1 | [16 empty] | 375 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0865 |  | 0108 | [8 empty] | B3/D24_A1 | [16 empty] | 376 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0808 | [9 empty] | a | B1/D24_A1 | [16 empty] | 377 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0809 | [10 empty] | B1/D24_A1 | [16 empty] | 378 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0810 | [10 empty] | B1/D24_A1 | [16 empty] | 379 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0811 | [10 empty] | B1/D24_A1 | [16 empty] | 380 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0812 | [10 empty] | B1/D24_A1 | [16 empty] | 381 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0866 |  | 0109 | [8 empty] | B3/D24_A1 | [16 empty] | 382 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0110 | [8 empty] | B3/D24_A1 | [16 empty] | 383 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0815 | [9 empty] | a | B1/D24_A1 | [16 empty] | 384 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0816 | [10 empty] | B1/D24_A1 | [16 empty] | 385 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0831 | [10 empty] | B2/D24_A1 | [16 empty] | 386 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0832 | [10 empty] | B2/D24_A1 | [16 empty] | 387 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0833 | [10 empty] | B2/D24_A1 | [16 empty] | 388 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0834 | [10 empty] | B2/D24_A1 | [16 empty] | 389 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0835 | [10 empty] | B2/D24_A1 | [16 empty] | 390 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0836 | [10 empty] | B2/D24_A1 | [16 empty] | 391 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0837 | [10 empty] | B2/D24_A1 | [16 empty] | 392 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0838 | [10 empty] | B2/D24_A1 | [16 empty] | 393 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0851 | [10 empty] | B3/D24_A1 | [16 empty] | 394 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | NULL | NULL |  | 待新增!!__BUS_87CTFA | [14 empty] | 0852 | [10 empty] | B2/D24_A1 | [16 empty] | 395 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0853 | [10 empty] | B3/D24_A1 | [16 empty] | 396 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0854 | [10 empty] | B3/D24_A1 | [16 empty] | 397 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0855 | [10 empty] | B3/D24_A1 | [16 empty] | 398 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0856 | [10 empty] | B3/D24_A1 | [16 empty] | 399 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | NFBA |  |  | Status | NFB 跳脫監視 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0857 | [10 empty] | B3/D24_A1 | [16 empty] | 400 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0858 | [10 empty] | B3/D24_A1 | [16 empty] | 401 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0859 | [10 empty] | ELEM/D24_A1 | [16 empty] | 402 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 | [10 empty] | B3/D24_A1 | [16 empty] | 403 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | ComPoint |  |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0861 | [10 empty] | B3/D24_A1 | [16 empty] | 404 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | ACB |  |  | Status | ACB | Close/Open | Y | 3 | DI-SP | [6 empty] | 0862 | [10 empty] | B3/D24_A1 | [16 empty] | 405 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0863 | [10 empty] | ELEM/D24_A1 | [16 empty] | 406 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | ABS1 | 1511 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 | 0111 | [8 empty] | B2/D24_A1 | [16 empty] | 407 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | ABS2 | 1512 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 | 0112 | [8 empty] | B2/D24_A1 | [16 empty] | 408 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | ABS3 | 1513 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 | 0113 | [8 empty] | B2/D24_A1 | [16 empty] | 409 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | ES3 | 1513E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0902 | 903 | 0114 | [8 empty] | B2/D24_A1 | [16 empty] | 410 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | SCADAA |  |  | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0868 | [10 empty] | B3/D24_A1 | [16 empty] | 411 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | ABS1 | 1521 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0904 | 905 | 0115 | [8 empty] | B2/D24_A1 | [16 empty] | 412 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | NULL | NULL |  | 待新增!!__排水泵故障1 | 涵洞 | [13 empty] | 0870 | [10 empty] | B1/D24_A1 | [16 empty] | 413 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0871 | [10 empty] | B3/D24_A1 | [16 empty] | 414 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | NULL | NULL |  | 待新增!!__揚水泵警報 | [14 empty] | 0872 | [10 empty] | B1/D24_A1 | [16 empty] | 415 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | NULL | NULL |  | 待新增!!__污水泵故障 | [14 empty] | 0873 | [10 empty] | B1/D24_A1 | [16 empty] | 416 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0874 | [10 empty] | B2/D24_A1 | [16 empty] | 417 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0875 | [10 empty] | B2/D24_A1 | [16 empty] | 418 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0876 | [10 empty] | B3/D24_A1 | [16 empty] | 419 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0877 | [10 empty] | B3/D24_A1 | [16 empty] | 420 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0878 | [10 empty] | B3/D24_A1 | [16 empty] | 421 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0879 | [10 empty] | B3/D24_A1 | [16 empty] | 422 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 | [10 empty] | B3/D24_A1 | [16 empty] | 423 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0881 | [10 empty] | B3/D24_A1 | [16 empty] | 424 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | ComPoint |  |  | FDR_CBA |  |  | Status | 11/22kV斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 | [10 empty] | ELEM/D24_D1 | [16 empty] | 425 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | ComPoint |  |  | FDR_CBF |  |  | Status | 11/22kV斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0883 | [10 empty] | ELEM/D24_D1 | [16 empty] | 426 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 | [10 empty] | B3/D24_A1 | [16 empty] | 427 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0888 | [10 empty] | B3/D24_A1 | [16 empty] | 428 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | UPSA |  |  | Status | UPS故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0889 | [10 empty] | B3/D24_A1 | [16 empty] | 429 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | DCA1 | DC電壓過低 |  | Status | 直流電源故障1 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0890 | [10 empty] | B3/D24_A1 | [16 empty] | 430 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | DCA2 | DC電壓過高 |  | Status | 直流電源故障2 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0891 | [10 empty] | B3/D24_A1 | [16 empty] | 431 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全警報 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0892 | [10 empty] | B3/D24_A1 | [16 empty] | 432 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0893 | [10 empty] | B3/D24_A1 | [16 empty] | 433 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Door1 | 建築物 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0894 | [10 empty] | B3/D24_A1 | [16 empty] | 434 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Door2 | 外圍 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0895 | [10 empty] | B3/D24_A1 | [16 empty] | 435 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | ABS2 | 1522 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0906 | 907 | 0116 | [8 empty] | B2/D24_A1 | [16 empty] | 436 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | ABS3 | 1523 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0117 | [8 empty] | B2/D24_A1 | [16 empty] | 437 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | ES3 | 1523E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0910 | 911 | 0118 | [8 empty] | B2/D24_A1 | [16 empty] | 438 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | ABS1 | 1531 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 | 0119 | [8 empty] | B2/D24_A1 | [16 empty] | 439 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | ABS2 | 1532 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0120 | [8 empty] | B2/D24_A1 | [16 empty] | 440 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | ABS3 | 1533 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0916 | 917 | 0121 | [8 empty] | B2/D24_A1 | [16 empty] | 441 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | ES3 | 1533E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0918 | 919 | 0122 | [8 empty] | B2/D24_A1 | [16 empty] | 442 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | ABS1 | 1541 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 | 0123 | [8 empty] | B2/D24_A1 | [16 empty] | 443 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | ABS2 | 1542 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 | 0124 | [8 empty] | B2/D24_A1 | [16 empty] | 444 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | ABS3 | 1543 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0924 | 925 | 0125 | [8 empty] | B2/D24_A1 | [16 empty] | 445 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | ES3 | 1543E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0926 | 927 | 0126 | [8 empty] | B2/D24_A1 | [16 empty] | 446 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 977 | 0151 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 979 | 0152 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 981 | 0153 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 983 | 0154 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 985 | 0155 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 987 | 0156 | [8 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1024 |  | 0214 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ51_79UL | 23KV虎51線(XJ51) 79RY U/L | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1025 |  | 0215 | [8 empty] | B2/D24_D1 | [16 empty] | 454 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1026 |  | 0216 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ52_79UL | 23KV虎52線(XJ52) 79RY U/L | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1027 |  | 0217 | [8 empty] | B2/D24_D1 | [16 empty] | 456 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1028 |  | 0218 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ53_79UL | 23KV虎53線(XJ53) 79RY U/L | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1029 |  | 0219 | [8 empty] | B2/D24_D1 | [16 empty] | 458 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1030 |  | 0220 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ54_79UL | 23KV虎54線(XJ54) 79RY U/L | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1031 |  | 0221 | [8 empty] | B2/D24_D1 | [16 empty] | 460 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1032 |  | 0222 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ55_79UL | 23KV虎55線(XJ55) 79RY U/L | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1033 |  | 0223 | [8 empty] | B2/D24_D1 | [16 empty] | 462 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1034 |  | 0224 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ25_79UL | 11KV虎五線(XJ25) 79RY U/L | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1035 |  | 0225 | [8 empty] | B2/D24_D1 | [16 empty] | 464 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1036 |  | 0226 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ24_79UL | 11KV虎四線(XJ24) 79RY U/L | FEEDER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1037 |  | 0227 | [8 empty] | B2/D24_D1 | [16 empty] | 466 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1038 |  | 0228 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ23_79UL | 11KV虎三線(XJ23) 79RY U/L | FEEDER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1039 |  | 0229 | [8 empty] | B2/D24_D1 | [16 empty] | 468 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1040 |  | 0230 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ22_79UL | 11KV虎二線(XJ22) 79RY U/L | FEEDER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1041 |  | 0231 | [8 empty] | B2/D24_D1 | [16 empty] | 470 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1042 |  | 0232 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ21_79UL | 11KV虎一線(XJ21) 79RY U/L | FEEDER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1043 |  | 0233 | [8 empty] | B2/D24_D1 | [16 empty] | 472 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1044 |  | 0234 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ56_79UL | 23KV虎56線(XJ56) 79RY U/L | FEEDER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1045 |  | 0235 | [8 empty] | B2/D24_D1 | [16 empty] | 474 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1046 |  | 0236 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ57_79UL | 23KV虎57線(XJ57) 79RY U/L | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | 1_BPT_FR |  |  | Status | #1 BUS PT鐵磁共振 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1096 | [10 empty] | B3/D24_A1 | [16 empty] | 476 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 1097 | [10 empty] | ELEM/D24_A1 | [16 empty] | 477 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | NULL | NULL |  | 待新增!!__斷路器跳脫迴圈監視警報TCSA | [14 empty] | 1098 | [10 empty] | B1/D24_A1 | [16 empty] | 478 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1099 | [10 empty] | B3/D24_A1 | [16 empty] | 479 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1100 | [10 empty] | B3/D24_A1 | [16 empty] | 480 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | 2_BPT_FR |  |  | Status | #2 BUS PT鐵磁共振 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1101 | [10 empty] | B3/D24_A1 | [16 empty] | 481 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | NULL | NULL |  | 待新增!!__緊急發電機運轉 | [14 empty] | 1102 | [10 empty] | B1/D24_A1 | [16 empty] | 482 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1106 | [10 empty] | B1/D24_A1 | [16 empty] | 483 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1107 | [10 empty] | B1/D24_A1 | [16 empty] | 484 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1108 | [10 empty] | B1/D24_A1 | [16 empty] | 485 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1109 | [10 empty] | B1/D24_A1 | [16 empty] | 486 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1110 | [10 empty] | B1/D24_A1 | [16 empty] | 487 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1111 | [10 empty] | B1/D24_A1 | [16 empty] | 488 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1112 | [10 empty] | B1/D24_A1 | [16 empty] | 489 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1113 | [10 empty] | B1/D24_A1 | [16 empty] | 490 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1114 | [10 empty] | B1/D24_A1 | [16 empty] | 491 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1115 | [10 empty] | B1/D24_A1 | [16 empty] | 492 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1126 | [10 empty] | B3/D24_A1 | [16 empty] | 493 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1127 | [10 empty] | B3/D24_A1 | [16 empty] | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1128 | [10 empty] | B3/D24_A1 | [16 empty] | 495 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1129 | [10 empty] | B3/D24_A1 | [16 empty] | 496 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1047 |  | 0237 | [8 empty] | B2/D24_D1 | [16 empty] | 497 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1048 |  | 0238 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ58_79UL | 23KV虎58線(XJ58) 79RY U/L | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1049 |  | 0239 | [8 empty] | B2/D24_D1 | [16 empty] | 499 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1050 |  | 0240 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ59_79UL | 23KV虎59線(XJ59) 79RY U/L | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1051 |  | 0241 | [8 empty] | B2/D24_D1 | [16 empty] | 501 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1052 |  | 0242 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ60_79UL | 23KV虎60線(XJ60) 79RY U/L | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1053 |  | 0243 | [8 empty] | B2/D24_D1 | [16 empty] | 503 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1054 |  | 0244 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ30_79UL | 11KV虎十線(XJ30) 79RY U/L | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1055 |  | 0245 | [8 empty] | B2/D24_D1 | [16 empty] | 505 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1056 |  | 0246 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ29_79UL | 11KV虎九線(XJ29) 79RY U/L | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1057 |  | 0247 | [8 empty] | B2/D24_D1 | [16 empty] | 507 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1058 |  | 0248 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ28_79UL | 11KV虎八線(XJ28) 79RY U/L | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1059 |  | 0249 | [8 empty] | B2/D24_D1 | [16 empty] | 509 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1060 |  | 0250 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ27_79UL | 11KV虎七線(XJ27) 79RY U/L | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1061 |  | 0251 | [8 empty] | B2/D24_D1 | [16 empty] | 511 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1062 |  | 0252 | [8 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ26_79UL | 11KV虎六線(XJ26) 79RY U/L | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1063 |  | 0253 | [8 empty] | B2/D24_D1 | [16 empty] | 513 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0869 |  | 0286 | [8 empty] | B3/D24_A1 | [16 empty] | 514 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | LBS210 | #1SC(210) |  | LBS | [9 empty] | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0301 |  | 0296 | [8 empty] | B3/D24_A1 | [16 empty] | 515 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS | [9 empty] | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0302 |  | 0297 | [8 empty] | B3/D24_A1 | [16 empty] | 516 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | LBS230 | #3SC(230) |  | LBS | [9 empty] | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0303 |  | 0298 | [8 empty] | B3/D24_A1 | [16 empty] | 517 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 11 | 11kV | LBS240 | #4SC(240) |  | LBS | [9 empty] | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 0304 |  | 0299 | [8 empty] | B3/D24_A1 | [16 empty] | 518 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | DS1 | 311(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.311 | 311 (非取樣點) | MTR | [5 empty] | 519 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.311E | 311E (非取樣點) | MTR | [5 empty] | 520 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.211 | 211 (非取樣點) | SC | [5 empty] | 521 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.211E | 211E (非取樣點) | SC | [5 empty] | 522 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | DS1 | 101(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.101 | 101 (非取樣點) | TIE | [5 empty] | 523 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 524 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | DS1 | 321(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.321 | 321 (非取樣點) | MTR | [5 empty] | 525 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.321E | 321E (非取樣點) | MTR | [5 empty] | 526 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.221 | 221 (非取樣點) | SC | [5 empty] | 527 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.221E | 221E (非取樣點) | SC | [5 empty] | 528 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | DS1 | 201(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.201 | 201 (非取樣點) | TIE | [5 empty] | 529 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 530 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | DS1 | 331(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.331 | 331 (非取樣點) | MTR | [5 empty] | 531 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.331E | 331E (非取樣點) | MTR | [5 empty] | 532 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | DS1 | 231(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.231 | 231 (非取樣點) | SC | [5 empty] | 533 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.231E | 231E (非取樣點) | SC | [5 empty] | 534 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | DS1 | 341(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.341 | 341 (非取樣點) | MTR | [5 empty] | 535 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.341E | 341E (非取樣點) | MTR | [5 empty] | 536 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | DS1 | 241(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.241 | 241 (非取樣點) | SC | [5 empty] | 537 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.241E | 241E (非取樣點) | SC | [5 empty] | 538 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | DS1 | 391(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 539 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 540 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | DS1 | 491(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 541 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 542 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | DS2 | 102(非取樣點) |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.102 | 102 (非取樣點) | TIE | [5 empty] | 543 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 544 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | DS2 | 202(非取樣點) |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.202 | 202 (非取樣點) | TIE | [5 empty] | 545 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B3/D24_A1 | [8 empty] | 虎菁DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 546 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 547 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 548 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 549 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 550 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 551 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 552 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 553 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 554 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 555 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 556 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 557 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 558 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 559 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_A1 | [8 empty] | 虎菁DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 560 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ51_DS | XJ51_DS (非取樣點) | FEEDER | [5 empty] | 561 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ51_ES | XJ51_ES (非取樣點) | FEEDER | [5 empty] | 562 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ52_DS | XJ52_DS (非取樣點) | FEEDER | [5 empty] | 563 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ52_ES | XJ52_ES (非取樣點) | FEEDER | [5 empty] | 564 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ53_DS | XJ53_DS (非取樣點) | FEEDER | [5 empty] | 565 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ53_ES | XJ53_ES (非取樣點) | FEEDER | [5 empty] | 566 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ54_DS | XJ54_DS (非取樣點) | FEEDER | [5 empty] | 567 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ54_ES | XJ54_ES (非取樣點) | FEEDER | [5 empty] | 568 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ55_DS | XJ55_DS (非取樣點) | FEEDER | [5 empty] | 569 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ55_ES | XJ55_ES (非取樣點) | FEEDER | [5 empty] | 570 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ25_DS | XJ25_DS (非取樣點) | FEEDER | [5 empty] | 571 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ25_ES | XJ25_ES (非取樣點) | FEEDER | [5 empty] | 572 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ24_DS | XJ24_DS (非取樣點) | FEEDER | [5 empty] | 573 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ24_ES | XJ24_ES (非取樣點) | FEEDER | [5 empty] | 574 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ23_DS | XJ23_DS (非取樣點) | FEEDER | [5 empty] | 575 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ23_ES | XJ23_ES (非取樣點) | FEEDER | [5 empty] | 576 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ22_DS | XJ22_DS (非取樣點) | FEEDER | [5 empty] | 577 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ22_ES | XJ22_ES (非取樣點) | FEEDER | [5 empty] | 578 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ21_DS | XJ21_DS (非取樣點) | FEEDER | [5 empty] | 579 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ21_ES | XJ21_ES (非取樣點) | FEEDER | [5 empty] | 580 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ56_DS | XJ56_DS (非取樣點) | FEEDER | [5 empty] | 581 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ56_ES | XJ56_ES (非取樣點) | FEEDER | [5 empty] | 582 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ57_DS | XJ57_DS (非取樣點) | FEEDER | [5 empty] | 583 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ57_ES | XJ57_ES (非取樣點) | FEEDER | [5 empty] | 584 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ58_DS | XJ58_DS (非取樣點) | FEEDER | [5 empty] | 585 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ58_ES | XJ58_ES (非取樣點) | FEEDER | [5 empty] | 586 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ59_DS | XJ59_DS (非取樣點) | FEEDER | [5 empty] | 587 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ59_ES | XJ59_ES (非取樣點) | FEEDER | [5 empty] | 588 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ60_DS | XJ60_DS (非取樣點) | FEEDER | [5 empty] | 589 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ60_ES | XJ60_ES (非取樣點) | FEEDER | [5 empty] | 590 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ30_DS | XJ30_DS (非取樣點) | FEEDER | [5 empty] | 591 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ30_ES | XJ30_ES (非取樣點) | FEEDER | [5 empty] | 592 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ29_DS | XJ29_DS (非取樣點) | FEEDER | [5 empty] | 593 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ29_ES | XJ29_ES (非取樣點) | FEEDER | [5 empty] | 594 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ28_DS | XJ28_DS (非取樣點) | FEEDER | [5 empty] | 595 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ28_ES | XJ28_ES (非取樣點) | FEEDER | [5 empty] | 596 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ27_DS | XJ27_DS (非取樣點) | FEEDER | [5 empty] | 597 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ27_ES | XJ27_ES (非取樣點) | FEEDER | [5 empty] | 598 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ26_DS | XJ26_DS (非取樣點) | FEEDER | [5 empty] | 599 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D24_D1 | [8 empty] | 虎菁DS.XJ26_ES | XJ26_ES (非取樣點) | FEEDER | [5 empty] | 600 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D24_A1 | [8 empty] | 虎菁DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 601 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D24_A1 | [8 empty] | 虎菁DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 602 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D24_A1 | [12 empty] | 虎菁DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D24/161/1BUS/V; OPRD2: D24/161/2BUS/V
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D24_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D24/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D24_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D24/161/1510/MW; OPRD2: D24/161/1520/MW; OPRD3: D24/161/1530/MW; OPRD4: D24/161/1540/MW
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D24_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D24/0/CalcPoint/OPRN2_MW
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D24_A1 | [17 empty] | none
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D24_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D24/0/CalcPoint/OPRN1; OPRD2: D24/0/CalcPoint/OPRN2; OPRD3: D24/0/CalcPoint/PRFL_UL
D24 | 虎菁DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D24_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D24/22/310/I_R; OPRD2: D24/11/320/I_R
D24 | 虎菁DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D24_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D24/22/310/I_S; OPRD2: D24/11/320/I_S
D24 | 虎菁DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D24_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D24/22/310/I_T; OPRD2: D24/11/320/I_T
D24 | 虎菁DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D24_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D24/22/330/I_R; OPRD2: D24/11/340/I_R
D24 | 虎菁DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D24_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D24/22/330/I_S; OPRD2: D24/11/340/I_S
D24 | 虎菁DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D24_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D24/22/330/I_T; OPRD2: D24/11/340/I_T
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南～虎菁一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D24_A1 | [12 empty] | 虎菁DS.1510_AMP | 斗南虎菁一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D24/161/1510/MW; OPRD2: D24/161/1510/MVAR; OPRD3: NULL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南～虎菁二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D24_A1 | [12 empty] | 虎菁DS.1520_AMP | 斗南虎菁二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: D24/161/1520/MW; OPRD2: D24/161/1520/MVAR; OPRD3: NULL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科～虎菁一路(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D24_A1 | [12 empty] | 虎菁DS.1530_AMP | 虎科虎菁一路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D24/161/1530/MW; OPRD2: D24/161/1530/MVAR; OPRD3: NULL
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科～虎菁二路(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D24_A1 | [12 empty] | 虎菁DS.1540_AMP | 虎科虎菁二路 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: D24/161/1540/MW; OPRD2: D24/161/1540/MVAR; OPRD3: NULL
D24 | 虎菁DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D24_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D24/11/1BBUS/V
D24 | 虎菁DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D24_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D24/11/2BBUS/V
D24 | 虎菁DS | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D24_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D24/22/1ABUS/V
D24 | 虎菁DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D24_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D24/22/2ABUS/V
D24 | 虎菁DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D24_A1 | [12 empty] | 虎菁DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D24//1DTR(A)/SupLocal; OPRD2: D24//1DTR(A)/Tap Chan
D24 | 虎菁DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D24_A1 | [12 empty] | 虎菁DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D24//1DTR(B)/SupLocal; OPRD2: D24//1DTR(B)/Tap Chan
D24 | 虎菁DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D24_A1 | [12 empty] | 虎菁DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D24//2DTR(A)/SupLocal; OPRD2: D24//2DTR(A)/Tap Chan
D24 | 虎菁DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D24_A1 | [12 empty] | 虎菁DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D24//2DTR(B)/SupLocal; OPRD2: D24//2DTR(B)/Tap Chan
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ21/I_R; OPRD3: D24/11/XJ21/I_S; OPRD4: D24/11/XJ21/I_T
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ22/I_R; OPRD3: D24/11/XJ22/I_S; OPRD4: D24/11/XJ22/I_T
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ23/I_R; OPRD3: D24/11/XJ23/I_S; OPRD4: D24/11/XJ23/I_T
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ24/I_R; OPRD3: D24/11/XJ24/I_S; OPRD4: D24/11/XJ24/I_T
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ25/I_R; OPRD3: D24/11/XJ25/I_S; OPRD4: D24/11/XJ25/I_T
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ26/I_R; OPRD3: D24/11/XJ26/I_S; OPRD4: D24/11/XJ26/I_T
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ27/I_R; OPRD3: D24/11/XJ27/I_S; OPRD4: D24/11/XJ27/I_T
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ28/I_R; OPRD3: D24/11/XJ28/I_S; OPRD4: D24/11/XJ28/I_T
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ29/I_R; OPRD3: D24/11/XJ29/I_S; OPRD4: D24/11/XJ29/I_T
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/11/XJ30/I_R; OPRD3: D24/11/XJ30/I_S; OPRD4: D24/11/XJ30/I_T
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ51/I_R; OPRD3: D24/22/XJ51/I_S; OPRD4: D24/22/XJ51/I_T
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ52/I_R; OPRD3: D24/22/XJ52/I_S; OPRD4: D24/22/XJ52/I_T
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ53/I_R; OPRD3: D24/22/XJ53/I_S; OPRD4: D24/22/XJ53/I_T
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ54/I_R; OPRD3: D24/22/XJ54/I_S; OPRD4: D24/22/XJ54/I_T
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ55/I_R; OPRD3: D24/22/XJ55/I_S; OPRD4: D24/22/XJ55/I_T
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ56/I_R; OPRD3: D24/22/XJ56/I_S; OPRD4: D24/22/XJ56/I_T
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ57/I_R; OPRD3: D24/22/XJ57/I_S; OPRD4: D24/22/XJ57/I_T
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ58/I_R; OPRD3: D24/22/XJ58/I_S; OPRD4: D24/22/XJ58/I_T
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ59/I_R; OPRD3: D24/22/XJ59/I_S; OPRD4: D24/22/XJ59/I_T
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D24/22/XJ60/I_R; OPRD3: D24/22/XJ60/I_S; OPRD4: D24/22/XJ60/I_T
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ21/kVA; OPRD2: D24/11/XJ21/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ22/kVA; OPRD2: D24/11/XJ22/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ23/kVA; OPRD2: D24/11/XJ23/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ24/kVA; OPRD2: D24/11/XJ24/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ25/kVA; OPRD2: D24/11/XJ25/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ26/kVA; OPRD2: D24/11/XJ26/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ27/kVA; OPRD2: D24/11/XJ27/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ28/kVA; OPRD2: D24/11/XJ28/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ29/kVA; OPRD2: D24/11/XJ29/KVAR
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/11/XJ30/kVA; OPRD2: D24/11/XJ30/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎五一線(XJ51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ51/kVA; OPRD2: D24/22/XJ51/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎五二線(XJ52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ52/kVA; OPRD2: D24/22/XJ52/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎五三線(XJ53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ53/kVA; OPRD2: D24/22/XJ53/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎五四線(XJ54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ54/kVA; OPRD2: D24/22/XJ54/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎五五線(XJ55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ55/kVA; OPRD2: D24/22/XJ55/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎五六線(XJ56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ56/kVA; OPRD2: D24/22/XJ56/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎五七線(XJ57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ57/kVA; OPRD2: D24/22/XJ57/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎五八線(XJ58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ58/kVA; OPRD2: D24/22/XJ58/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎五九線(XJ59) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ59/kVA; OPRD2: D24/22/XJ59/KVAR
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎六十線(XJ60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D24_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D24/22/XJ60/kVA; OPRD2: D24/22/XJ60/KVAR
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D24_A1 | [12 empty] | 虎菁DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D24/11/220/CB; OPRD2: 6.9; OPRD3: 0
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D24_A1 | [12 empty] | 虎菁DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D24/11/240/CB; OPRD2: 6.9; OPRD3: 0
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D24_A1 | [12 empty] | 虎菁DS.210_SC_MVAR | 23KV#1SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D24/22/210/CB; OPRD2: 13.8; OPRD3: 0
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D24_A1 | [12 empty] | 虎菁DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D24/22/230/CB; OPRD2: 13.8; OPRD3: 0
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D24_A1 | [12 empty] | 虎菁DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_26 | OPRD1: D24//1DTR/63Q; OPRD2: D24//1DTR/GDA; OPRD3: D24//1DTR/96D; OPRD4: D24//1DTR/96B1; OPRD5: D24//1DTR/96B2; OPRD6: D24//1DTR/PHA; OPRD7: D24//1DTR/87A; OPRD8: D24//1DTR/TRA; OPRD9: D24//1DTR/51ZA; OPRD10: D24//1DTR/96PA; OPRD11: D24//2DTR/TRA; OPRD12: D24//2DTR/96B1; OPRD13: D24//2DTR/96B2; OPRD14: D24//2DTR/63Q; OPRD15: D24//2DTR/96D; OPRD16: D24//2DTR/51ZA; OPRD17: D24//2DTR/96PA; OPRD18: D24//2DTR/87A; OPRD19: D24//2DTR/PHA; OPRD20: D24//2DTR/GDA; OPRD21: D24/11/320/GDA; OPRD22: D24/11/340/GDA; OPRD23: D24/161/1BUS/87A; OPRD24: D24/161/2BUS/87A; OPRD25: D24/22/310/GDA; OPRD26: D24/22/330/GDA
D24 | 虎菁DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D24_A1 | [12 empty] | 虎菁DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D24//1DTR/TRF; OPRD2: D24//2DTR/TRF
D24 | 虎菁DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/161/1750/CB
D24 | 虎菁DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/161/1760/CB
D24 | 虎菁DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/22/310/CB
D24 | 虎菁DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/11/320/CB
D24 | 虎菁DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/22/330/CB
D24 | 虎菁DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/11/340/CB
D24 | 虎菁DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/0/StaDev/DCE
D24 | 虎菁DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/0/StaDev/STUV
D24 | 虎菁DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D24_D1 | [17 empty] | lamp2CC | OPRD1: D24/0/RTU/RTU_R_L

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D24 | 虎菁DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D24/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_AMP | 斗南虎菁一路 AMP | LINE161 | D24/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_AMP | 斗南虎菁二路 AMP | LINE161 | D24/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎一線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎一線KVA | 11KV虎一線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎一線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎一線KW | 11KV虎一線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎七線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎七線KVA | 11KV虎七線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎七線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎七線KW | 11KV虎七線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎九線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎九線KVA | 11KV虎九線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎九線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎九線KW | 11KV虎九線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎二線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎二線KVA | 11KV虎二線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎二線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎二線KW | 11KV虎二線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎八線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎八線KVA | 11KV虎八線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎八線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎八線KW | 11KV虎八線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎十線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎十線KVA | 11KV虎十線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎十線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎十線KW | 11KV虎十線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎三線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎三線KVA | 11KV虎三線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎三線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎三線KW | 11KV虎三線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎五線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎五線KVA | 11KV虎五線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎五線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎五線KW | 11KV虎五線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎六線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎六線KVA | 11KV虎六線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎六線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎六線KW | 11KV虎六線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎四線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎四線KVA | 11KV虎四線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎四線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎四線KW | 11KV虎四線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎51線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎51線KVA | 23KV虎51線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎51線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎51線KW | 23KV虎51線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎52線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎52線KVA | 23KV虎52線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎52線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎52線KW | 23KV虎52線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎53線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎53線KVA | 23KV虎53線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎53線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎53線KW | 23KV虎53線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎54線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎54線KVA | 23KV虎54線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎54線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎54線KW | 23KV虎54線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎55線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎55線KVA | 23KV虎55線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎55線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎55線KW | 23KV虎55線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎56線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎56線KVA | 23KV虎56線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎56線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎56線KW | 23KV虎56線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎57線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎57線KVA | 23KV虎57線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎57線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎57線KW | 23KV虎57線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎58線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎58線KVA | 23KV虎58線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎58線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎58線KW | 23KV虎58線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎59線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎59線KVA | 23KV虎59線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎59線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎59線KW | 23KV虎59線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎60線KVA | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎60線KVA | 23KV虎60線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  |  |  |  | 虎60線KW | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.虎60線KW | 23KV虎60線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 46 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 49 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 55 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 60 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D24 | 虎菁DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D24/11/220/MVAR |  | SC_CAL_11 |  |  | 65 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D24/11/240/MVAR |  | SC_CAL_11 |  |  | 66 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 22 | 22kV | 210_SC | #1SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.210_SC_MVAR | 23KV#1SC MVAR | SC | D24/22/210/MVAR |  | SC_CAL_23 |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D24/22/230/MVAR |  | SC_CAL_23 |  |  | 68 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | TRTOT | 虎菁主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 虎菁DS.TRTOT_MW | 虎菁主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 0 |  | TRTOT | 虎菁主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 虎菁DS.TRTOT_MVAR | 虎菁主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_AMP | 虎科虎菁一路 AMP | LINE161 | D24/161/1530/I |  | AMP_CAL |  |  | 71 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_AMP | 虎科虎菁二路 AMP | LINE161 | D24/161/1540/I |  | AMP_CAL |  |  | 72 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
D24 | 虎菁DS | 0 |  | 100_CB | 100(100_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.100_CB_1 | 100 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 73 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 200_CB | 200(200_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.200_CB_1 | 200 CB (D1) | TIE |  |  | AD_LAMP_DD_1 |  |  | 74 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.1750_CB_1 | 1750(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 75 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.310_CB_1 | 310(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.320_CB_1 | 320(#1DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.1760_CB_1 | 1760(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.330_CB_1 | 330(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.340_CB_1 | 340(#2DTR) CB (D1) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.220_CB_1 | 220(11KV #2SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.240_CB_1 | 240(11KV #4SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 210_CB | #1SC(210_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.210_CB_1 | 210(23KV #1SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.230_CB_1 | 230(23KV #3SC) CB (D1) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.11/23KV_CBA_1 | 11/23KV斷路器重故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 85 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.11/23KV_CBF_1 | 11/23KV斷路器輕故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 86 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | _OSCA | 11/示波器啟動警報 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.23KV_OSCA_1 | 11/23KV示波器啟動警報 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 87 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D24/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 88 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D24/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 89 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 90 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510_AMP | 斗南虎菁一路 | [27 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_AMP_A | 斗南虎菁一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520_AMP | 斗南虎菁二路 | [27 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_AMP_A | 斗南虎菁二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D24//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D24//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D24//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D24//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.#1DTR_MVA_1 | #1DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR_MVA | #1DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 虎菁DS.#1DTR_MVA_2 | #1DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 100 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.#2DTR_MVA_1 | #2DTR(A) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR_MVA | #2DTR(B) | [27 empty] | DDCS1_1 | [8 empty] | 虎菁DS.#2DTR_MVA_2 | #2DTR(B) MVA 點燈 (D1) | MTR |  |  | MAP_SET |  |  | 103 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 104 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530_AMP | 虎科虎菁一路 | [27 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_AMP_A | 虎科虎菁一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1540_AMP | 虎科虎菁二路 | [27 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_AMP_A | 虎科虎菁二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | COMM_S_L | 通訊處理單元 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.COMM_S/L_1 | 通訊處理單元 SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 107 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D24 | 虎菁DS | 0 |  | PMCCA | PMCC電驛故障 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.PMCCA_1 | PMCC電驛故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 108 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | TCA | 斷路器跳脫回路故障 |  | 1 | [25 empty] | DDCS1_1 | [8 empty] | 虎菁DS.TCA_1 | 斷路器跳脫回路故障 (D1) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 109 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1ABUS | #1ABUS |  | 23KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 虎菁DS.23KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 虎菁DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 虎菁DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 虎菁DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D24 | 虎菁DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 117 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D24/161/1BUS/V |  |  |  | CDC | 118 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D24 | 虎菁DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D24/161/2BUS/V |  |  |  | CDC | 119 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D24 | 虎菁DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-D6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D24/11/1BBUS/V |  |  |  | CDC | 120 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D24 | 虎菁DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-A3 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D24/11/2BBUS/V |  |  |  | CDC | 121 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D24 | 虎菁DS | 22 | 22kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-AD | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | D24/22/1ABUS/V |  |  |  | CDC | 122 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D24 | 虎菁DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-FD | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D24/22/2ABUS/V |  |  |  | CDC | 123 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1510_MW | 斗南虎菁一路 MW | LINE161 | D24/161/1510/MW |  |  |  | CDC | 124 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1510_MVAR | 斗南虎菁一路 MVAR | LINE161 | D24/161/1510/MVAR |  |  |  | CDC | 125 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1520_MW | 斗南虎菁二路 MW | LINE161 | D24/161/1520/MW |  |  |  | CDC | 126 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1520_MVAR | 斗南虎菁二路 MVAR | LINE161 | D24/161/1520/MVAR |  |  |  | CDC | 127 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎一線 | 虎一線 |  | 虎一線KVAR | [17 empty] | 1-F5 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎一線KVAR | 11KV虎一線 KVAR | FEEDER |  |  |  |  | CDC | 128 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎一線 | 虎一線 |  | 虎一線A1 | [17 empty] | 1-F6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎一線A1 | 11KV虎一線 R相AMP | FEEDER |  |  |  |  | CDC | 129 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎一線 | 虎一線 |  | 虎一線A2 | [17 empty] | 1-F7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎一線A2 | 11KV虎一線 S相AMP | FEEDER |  |  |  |  | CDC | 130 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎一線 | 虎一線 |  | 虎一線A3 | [17 empty] | 1-F8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎一線A3 | 11KV虎一線 T相AMP | FEEDER |  |  |  |  | CDC | 131 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎一線 | 虎一線 |  | 虎一線A0 | [17 empty] | 1-F9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎一線A0 | 11KV虎一線 N相AMP | FEEDER |  |  |  |  | CDC | 132 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎七線 | 虎七線 |  | 虎七線KVAR | [17 empty] | 2-BC | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎七線KVAR | 11KV虎七線 KVAR | FEEDER |  |  |  |  | CDC | 133 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎七線 | 虎七線 |  | 虎七線A1 | [17 empty] | 2-BD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎七線A1 | 11KV虎七線 R相AMP | FEEDER |  |  |  |  | CDC | 134 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎七線 | 虎七線 |  | 虎七線A2 | [17 empty] | 2-BE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎七線A2 | 11KV虎七線 S相AMP | FEEDER |  |  |  |  | CDC | 135 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎七線 | 虎七線 |  | 虎七線A3 | [17 empty] | 2-BF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎七線A3 | 11KV虎七線 T相AMP | FEEDER |  |  |  |  | CDC | 136 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎七線 | 虎七線 |  | 虎七線A0 | [17 empty] | 2-C2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎七線A0 | 11KV虎七線 N相AMP | FEEDER |  |  |  |  | CDC | 137 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎九線 | 虎九線 |  | 虎九線KVAR | [17 empty] | 2-B0 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎九線KVAR | 11KV虎九線 KVAR | FEEDER |  |  |  |  | CDC | 138 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎九線 | 虎九線 |  | 虎九線A1 | [17 empty] | 2-B1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎九線A1 | 11KV虎九線 R相AMP | FEEDER |  |  |  |  | CDC | 139 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎九線 | 虎九線 |  | 虎九線A2 | [17 empty] | 2-B2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎九線A2 | 11KV虎九線 S相AMP | FEEDER |  |  |  |  | CDC | 140 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎九線 | 虎九線 |  | 虎九線A3 | [17 empty] | 2-B3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎九線A3 | 11KV虎九線 T相AMP | FEEDER |  |  |  |  | CDC | 141 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎九線 | 虎九線 |  | 虎九線A0 | [17 empty] | 2-B4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎九線A0 | 11KV虎九線 N相AMP | FEEDER |  |  |  |  | CDC | 142 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎二線 | 虎二線 |  | 虎二線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎二線KVAR | 11KV虎二線 KVAR | FEEDER |  |  |  |  | CDC | 143 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎二線 | 虎二線 |  | 虎二線A1 | [17 empty] | 1-F0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎二線A1 | 11KV虎二線 R相AMP | FEEDER |  |  |  |  | CDC | 144 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎二線 | 虎二線 |  | 虎二線A2 | [17 empty] | 1-F1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎二線A2 | 11KV虎二線 S相AMP | FEEDER |  |  |  |  | CDC | 145 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎二線 | 虎二線 |  | 虎二線A3 | [17 empty] | 1-F2 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎二線A3 | 11KV虎二線 T相AMP | FEEDER |  |  |  |  | CDC | 146 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎二線 | 虎二線 |  | 虎二線A0 | [17 empty] | 1-F3 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎二線A0 | 11KV虎二線 N相AMP | FEEDER |  |  |  |  | CDC | 147 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎八線 | 虎八線 |  | 虎八線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎八線KVAR | 11KV虎八線 KVAR | FEEDER |  |  |  |  | CDC | 148 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎八線 | 虎八線 |  | 虎八線A1 | [17 empty] | 2-B7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎八線A1 | 11KV虎八線 R相AMP | FEEDER |  |  |  |  | CDC | 149 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎八線 | 虎八線 |  | 虎八線A2 | [17 empty] | 2-B8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎八線A2 | 11KV虎八線 S相AMP | FEEDER |  |  |  |  | CDC | 150 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎八線 | 虎八線 |  | 虎八線A3 | [17 empty] | 2-B9 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎八線A3 | 11KV虎八線 T相AMP | FEEDER |  |  |  |  | CDC | 151 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎八線 | 虎八線 |  | 虎八線A0 | [17 empty] | 2-BA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎八線A0 | 11KV虎八線 N相AMP | FEEDER |  |  |  |  | CDC | 152 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎十線 | 虎十線 |  | 虎十線KVAR | [17 empty] | 2-AA | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎十線KVAR | 11KV虎十線 KVAR | FEEDER |  |  |  |  | CDC | 153 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎十線 | 虎十線 |  | 虎十線A1 | [17 empty] | 2-AB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎十線A1 | 11KV虎十線 R相AMP | FEEDER |  |  |  |  | CDC | 154 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎十線 | 虎十線 |  | 虎十線A2 | [17 empty] | 2-AC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎十線A2 | 11KV虎十線 S相AMP | FEEDER |  |  |  |  | CDC | 155 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎十線 | 虎十線 |  | 虎十線A3 | [17 empty] | 2-AD | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎十線A3 | 11KV虎十線 T相AMP | FEEDER |  |  |  |  | CDC | 156 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎十線 | 虎十線 |  | 虎十線A0 | [17 empty] | 2-AE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎十線A0 | 11KV虎十線 N相AMP | FEEDER |  |  |  |  | CDC | 157 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎三線 | 虎三線 |  | 虎三線KVAR | [17 empty] | 1-E9 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎三線KVAR | 11KV虎三線 KVAR | FEEDER |  |  |  |  | CDC | 158 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎三線 | 虎三線 |  | 虎三線A1 | [17 empty] | 1-EA | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎三線A1 | 11KV虎三線 R相AMP | FEEDER |  |  |  |  | CDC | 159 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎三線 | 虎三線 |  | 虎三線A2 | [17 empty] | 1-EB | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎三線A2 | 11KV虎三線 S相AMP | FEEDER |  |  |  |  | CDC | 160 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎三線 | 虎三線 |  | 虎三線A3 | [17 empty] | 1-EC | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎三線A3 | 11KV虎三線 T相AMP | FEEDER |  |  |  |  | CDC | 161 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎三線 | 虎三線 |  | 虎三線A0 | [17 empty] | 1-ED | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎三線A0 | 11KV虎三線 N相AMP | FEEDER |  |  |  |  | CDC | 162 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎五線 | 虎五線 |  | 虎五線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎五線KVAR | 11KV虎五線 KVAR | FEEDER |  |  |  |  | CDC | 163 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎五線 | 虎五線 |  | 虎五線A1 | [17 empty] | 1-DE | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎五線A1 | 11KV虎五線 R相AMP | FEEDER |  |  |  |  | CDC | 164 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎五線 | 虎五線 |  | 虎五線A2 | [17 empty] | 1-DF | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎五線A2 | 11KV虎五線 S相AMP | FEEDER |  |  |  |  | CDC | 165 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎五線 | 虎五線 |  | 虎五線A3 | [17 empty] | 1-E0 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎五線A3 | 11KV虎五線 T相AMP | FEEDER |  |  |  |  | CDC | 166 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎五線 | 虎五線 |  | 虎五線A0 | [17 empty] | 1-E1 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎五線A0 | 11KV虎五線 N相AMP | FEEDER |  |  |  |  | CDC | 167 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎六線 | 虎六線 |  | 虎六線KVAR | [17 empty] | 2-C4 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎六線KVAR | 11KV虎六線 KVAR | FEEDER |  |  |  |  | CDC | 168 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎六線 | 虎六線 |  | 虎六線A1 | [17 empty] | 2-C5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎六線A1 | 11KV虎六線 R相AMP | FEEDER |  |  |  |  | CDC | 169 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎六線 | 虎六線 |  | 虎六線A2 | [17 empty] | 2-C6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎六線A2 | 11KV虎六線 S相AMP | FEEDER |  |  |  |  | CDC | 170 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎六線 | 虎六線 |  | 虎六線A3 | [17 empty] | 2-C7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎六線A3 | 11KV虎六線 T相AMP | FEEDER |  |  |  |  | CDC | 171 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎六線 | 虎六線 |  | 虎六線A0 | [17 empty] | 2-C8 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎六線A0 | 11KV虎六線 N相AMP | FEEDER |  |  |  |  | CDC | 172 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎四線 | 虎四線 |  | 虎四線KVAR | [17 empty] | 1-E3 | [5 empty] | KVAR_-9000_9000(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎四線KVAR | 11KV虎四線 KVAR | FEEDER |  |  |  |  | CDC | 173 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 9.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎四線 | 虎四線 |  | 虎四線A1 | [17 empty] | 1-E4 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎四線A1 | 11KV虎四線 R相AMP | FEEDER |  |  |  |  | CDC | 174 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R480R | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎四線 | 虎四線 |  | 虎四線A2 | [17 empty] | 1-E5 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎四線A2 | 11KV虎四線 S相AMP | FEEDER |  |  |  |  | CDC | 175 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎四線 | 虎四線 |  | 虎四線A3 | [17 empty] | 1-E6 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎四線A3 | 11KV虎四線 T相AMP | FEEDER |  |  |  |  | CDC | 176 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C05R0480 | 432.000000 | 432.000000 | 480.000000 | 500.000000 | 1.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | 虎四線 | 虎四線 |  | 虎四線A0 | [17 empty] | 1-E7 | [5 empty] | A_-500_500(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎四線A0 | 11KV虎四線 N相AMP | FEEDER |  |  |  |  | CDC | 177 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎51線 | 虎51線 |  | 虎51線KVAR | [17 empty] | 1-B4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎51線KVAR | 23KV虎51線 KVAR | FEEDER |  |  |  |  | CDC | 178 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎51線 | 虎51線 |  | 虎51線A1 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎51線A1 | 23KV虎51線 R相AMP | FEEDER |  |  |  |  | CDC | 179 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎51線 | 虎51線 |  | 虎51線A2 | [17 empty] | 1-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎51線A2 | 23KV虎51線 S相AMP | FEEDER |  |  |  |  | CDC | 180 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎51線 | 虎51線 |  | 虎51線A3 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎51線A3 | 23KV虎51線 T相AMP | FEEDER |  |  |  |  | CDC | 181 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎51線 | 虎51線 |  | 虎51線A0 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎51線A0 | 23KV虎51線 N相AMP | FEEDER |  |  |  |  | CDC | 182 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎52線 | 虎52線 |  | 虎52線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎52線KVAR | 23KV虎52線 KVAR | FEEDER |  |  |  |  | CDC | 183 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎52線 | 虎52線 |  | 虎52線A1 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎52線A1 | 23KV虎52線 R相AMP | FEEDER |  |  |  |  | CDC | 184 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎52線 | 虎52線 |  | 虎52線A2 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎52線A2 | 23KV虎52線 S相AMP | FEEDER |  |  |  |  | CDC | 185 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎52線 | 虎52線 |  | 虎52線A3 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎52線A3 | 23KV虎52線 T相AMP | FEEDER |  |  |  |  | CDC | 186 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎52線 | 虎52線 |  | 虎52線A0 | [17 empty] | 1-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎52線A0 | 23KV虎52線 N相AMP | FEEDER |  |  |  |  | CDC | 187 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎53線 | 虎53線 |  | 虎53線KVAR | [17 empty] | 1-C2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎53線KVAR | 23KV虎53線 KVAR | FEEDER |  |  |  |  | CDC | 188 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎53線 | 虎53線 |  | 虎53線A1 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎53線A1 | 23KV虎53線 R相AMP | FEEDER |  |  |  |  | CDC | 189 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎53線 | 虎53線 |  | 虎53線A2 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎53線A2 | 23KV虎53線 S相AMP | FEEDER |  |  |  |  | CDC | 190 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎53線 | 虎53線 |  | 虎53線A3 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎53線A3 | 23KV虎53線 T相AMP | FEEDER |  |  |  |  | CDC | 191 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎53線 | 虎53線 |  | 虎53線A0 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎53線A0 | 23KV虎53線 N相AMP | FEEDER |  |  |  |  | CDC | 192 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎54線 | 虎54線 |  | 虎54線KVAR | [17 empty] | 1-C8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎54線KVAR | 23KV虎54線 KVAR | FEEDER |  |  |  |  | CDC | 193 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎54線 | 虎54線 |  | 虎54線A1 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎54線A1 | 23KV虎54線 R相AMP | FEEDER |  |  |  |  | CDC | 194 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎54線 | 虎54線 |  | 虎54線A2 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎54線A2 | 23KV虎54線 S相AMP | FEEDER |  |  |  |  | CDC | 195 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎54線 | 虎54線 |  | 虎54線A3 | [17 empty] | 1-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎54線A3 | 23KV虎54線 T相AMP | FEEDER |  |  |  |  | CDC | 196 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎54線 | 虎54線 |  | 虎54線A0 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎54線A0 | 23KV虎54線 N相AMP | FEEDER |  |  |  |  | CDC | 197 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎55線 | 虎55線 |  | 虎55線KVAR | [17 empty] | 1-CE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎55線KVAR | 23KV虎55線 KVAR | FEEDER |  |  |  |  | CDC | 198 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎55線 | 虎55線 |  | 虎55線A1 | [17 empty] | 1-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎55線A1 | 23KV虎55線 R相AMP | FEEDER |  |  |  |  | CDC | 199 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎55線 | 虎55線 |  | 虎55線A2 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎55線A2 | 23KV虎55線 S相AMP | FEEDER |  |  |  |  | CDC | 200 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎55線 | 虎55線 |  | 虎55線A3 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎55線A3 | 23KV虎55線 T相AMP | FEEDER |  |  |  |  | CDC | 201 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎55線 | 虎55線 |  | 虎55線A0 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎55線A0 | 23KV虎55線 N相AMP | FEEDER |  |  |  |  | CDC | 202 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎56線 | 虎56線 |  | 虎56線KVAR | [17 empty] | 2-86 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎56線KVAR | 23KV虎56線 KVAR | FEEDER |  |  |  |  | CDC | 203 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎56線 | 虎56線 |  | 虎56線A1 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎56線A1 | 23KV虎56線 R相AMP | FEEDER |  |  |  |  | CDC | 204 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎56線 | 虎56線 |  | 虎56線A2 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎56線A2 | 23KV虎56線 S相AMP | FEEDER |  |  |  |  | CDC | 205 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎56線 | 虎56線 |  | 虎56線A3 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎56線A3 | 23KV虎56線 T相AMP | FEEDER |  |  |  |  | CDC | 206 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎56線 | 虎56線 |  | 虎56線A0 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎56線A0 | 23KV虎56線 N相AMP | FEEDER |  |  |  |  | CDC | 207 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎57線 | 虎57線 |  | 虎57線KVAR | [17 empty] | 2-8C | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎57線KVAR | 23KV虎57線 KVAR | FEEDER |  |  |  |  | CDC | 208 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎57線 | 虎57線 |  | 虎57線A1 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎57線A1 | 23KV虎57線 R相AMP | FEEDER |  |  |  |  | CDC | 209 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎57線 | 虎57線 |  | 虎57線A2 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎57線A2 | 23KV虎57線 S相AMP | FEEDER |  |  |  |  | CDC | 210 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎57線 | 虎57線 |  | 虎57線A3 | [17 empty] | 2-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎57線A3 | 23KV虎57線 T相AMP | FEEDER |  |  |  |  | CDC | 211 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎57線 | 虎57線 |  | 虎57線A0 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎57線A0 | 23KV虎57線 N相AMP | FEEDER |  |  |  |  | CDC | 212 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎58線 | 虎58線 |  | 虎58線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎58線KVAR | 23KV虎58線 KVAR | FEEDER |  |  |  |  | CDC | 213 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎58線 | 虎58線 |  | 虎58線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎58線A1 | 23KV虎58線 R相AMP | FEEDER |  |  |  |  | CDC | 214 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎58線 | 虎58線 |  | 虎58線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎58線A2 | 23KV虎58線 S相AMP | FEEDER |  |  |  |  | CDC | 215 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎58線 | 虎58線 |  | 虎58線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎58線A3 | 23KV虎58線 T相AMP | FEEDER |  |  |  |  | CDC | 216 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎58線 | 虎58線 |  | 虎58線A0 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎58線A0 | 23KV虎58線 N相AMP | FEEDER |  |  |  |  | CDC | 217 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎59線 | 虎59線 |  | 虎59線KVAR | [17 empty] | 2-98 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎59線KVAR | 23KV虎59線 KVAR | FEEDER |  |  |  |  | CDC | 218 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎59線 | 虎59線 |  | 虎59線A1 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎59線A1 | 23KV虎59線 R相AMP | FEEDER |  |  |  |  | CDC | 219 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎59線 | 虎59線 |  | 虎59線A2 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎59線A2 | 23KV虎59線 S相AMP | FEEDER |  |  |  |  | CDC | 220 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎59線 | 虎59線 |  | 虎59線A3 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎59線A3 | 23KV虎59線 T相AMP | FEEDER |  |  |  |  | CDC | 221 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎59線 | 虎59線 |  | 虎59線A0 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎59線A0 | 23KV虎59線 N相AMP | FEEDER |  |  |  |  | CDC | 222 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎60線 | 虎60線 |  | 虎60線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎60線KVAR | 23KV虎60線 KVAR | FEEDER |  |  |  |  | CDC | 223 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎60線 | 虎60線 |  | 虎60線A1 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎60線A1 | 23KV虎60線 R相AMP | FEEDER |  |  |  |  | CDC | 224 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎60線 | 虎60線 |  | 虎60線A2 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎60線A2 | 23KV虎60線 S相AMP | FEEDER |  |  |  |  | CDC | 225 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎60線 | 虎60線 |  | 虎60線A3 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎60線A3 | 23KV虎60線 T相AMP | FEEDER |  |  |  |  | CDC | 226 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | 虎60線 | 虎60線 |  | 虎60線A0 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS1_1 | [8 empty] | 虎菁DS.虎60線A0 | 23KV虎60線 N相AMP | FEEDER |  |  |  |  | CDC | 227 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-98 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 228 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-FA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.11KV_200_A1 | 11KV 200 R相AMP | TIE |  |  |  |  | CDC | 229 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-FB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.11KV_200_A2 | 11KV 200 S相AMP | TIE |  |  |  |  | CDC | 230 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-FC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.11KV_200_A3 | 11KV 200 T相AMP | TIE |  |  |  |  | CDC | 231 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | _100 | 100 |  | I_R | [17 empty] | 1-D3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.23KV_100_A1 | 23KV 100 R相AMP | TIE |  |  |  |  | CDC | 232 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | _100 | 100 |  | I_S | [17 empty] | 1-D4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.23KV_100_A2 | 23KV 100 S相AMP | TIE |  |  |  |  | CDC | 233 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 22 | 22kV | _100 | 100 |  | I_T | [17 empty] | 1-D5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.23KV_100_A3 | 23KV 100 T相AMP | TIE |  |  |  |  | CDC | 234 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-AE | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR |  |  |  |  | CDC | 235 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AF | [5 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR |  |  |  |  | CDC | 236 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-B0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR |  |  |  |  | CDC | 237 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-B1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR |  |  |  |  | CDC | 238 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-B2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR |  |  |  |  | CDC | 239 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-9B | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR_OIL | #1DTR 油溫 | MTR |  |  |  |  | CDC | 240 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR |  |  |  |  | CDC | 241 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-99 |  | 1-5C |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR |  |  |  |  | CDC | 242 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-D7 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR |  |  |  |  | CDC | 243 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-D8 | [5 empty] | MVAR_-24_24(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR |  |  |  |  | CDC | 244 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-D9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR |  |  |  |  | CDC | 245 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-DA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR |  |  |  |  | CDC | 246 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-DB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR |  |  |  |  | CDC | 247 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-9D | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR |  |  |  |  | CDC | 248 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-9A |  | 1-5E |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR |  |  |  |  | CDC | 249 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-FE | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR |  |  |  |  | CDC | 250 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-FF | [5 empty] | MVAR_-48_48(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR |  |  |  |  | CDC | 251 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.096000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR |  |  |  |  | CDC | 252 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR |  |  |  |  | CDC | 253 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR |  |  |  |  | CDC | 254 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-A0 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR_OIL | #2DTR 油溫 | MTR |  |  |  |  | CDC | 255 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-A1 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR |  |  |  |  | CDC | 256 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9E |  | 1-60 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR |  |  |  |  | CDC | 257 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-A4 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR |  |  |  |  | CDC | 258 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-A5 | [5 empty] | MVAR_-24_24(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR |  |  |  |  | CDC | 259 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.048000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-A6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR |  |  |  |  | CDC | 260 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR |  |  |  |  | CDC | 261 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-A8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR |  |  |  |  | CDC | 262 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR |  |  |  |  | CDC | 263 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9F |  | 1-62 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR |  |  |  |  | CDC | 264 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D24 | 虎菁DS | 0 |  | AI | AI90%參考點 |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCH1 | AI90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 265 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI90%參考點 |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCH2 | AI90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 266 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI90%參考點 |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCH3 | AI90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 267 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI90%參考點 |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCH4 | AI90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 268 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI10%參考點 |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCL1 | AI10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 269 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI10%參考點 |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCL2 | AI10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 270 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI10%參考點 |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCL3 | AI10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 271 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 0 |  | AI | AI10%參考點 |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.AI_ADCL4 | AI10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 272 | GENERICAIPoint | DS046_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1510LPD | 斗南虎菁一路(1510) |  | V | [17 empty] | 1-94 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1510LPD_KV | 斗南虎菁一路(1510) LPD KV | LINE161 |  |  |  |  | CDC | 273 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D24 | 虎菁DS | 161 | 161kV | 1520LPD | 斗南虎菁二路(1520) |  | V | [17 empty] | 1-95 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1520LPD_KV | 斗南虎菁二路(1520) LPD KV | LINE161 |  |  |  |  | CDC | 274 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1530_MW | 虎科虎菁一路 MW | LINE161 | D24/161/1530/MW |  |  |  | CDC | 275 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1530_MVAR | 虎科虎菁一路 MVAR | LINE161 | D24/161/1530/MVAR |  |  |  | CDC | 276 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1530LPD | 虎科虎菁一路(1530) |  | V | [17 empty] | 1-96 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1530LPD_KV | 虎科虎菁一路(1530) LPD KV | LINE161 |  |  |  |  | CDC | 277 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1540_MW | 虎科虎菁二路 MW | LINE161 | D24/161/1540/MW |  |  |  | CDC | 278 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1540_MVAR | 虎科虎菁二路 MVAR | LINE161 | D24/161/1540/MVAR |  |  |  | CDC | 279 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1540LPD | 虎科虎菁二路(1540) |  | V | [17 empty] | 1-97 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.1540LPD_KV | 虎科虎菁二路(1540) LPD KV | LINE161 |  |  |  |  | CDC | 280 | GENERICAIPoint | DS046_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D24 | 虎菁DS | 0 |  |  |  |  | DCV_N | [17 empty] | 3-C9 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.直流N電源電壓 | 直流N電源電壓 | OTHER |  |  |  |  | CDC | 281 | GENERICAIPoint | DS046_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D24 | 虎菁DS | 0 |  |  |  |  | DCV_P | [17 empty] | 3-C8 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 虎菁DS.直流P電源電壓 | 直流P電源電壓 | OTHER |  |  |  |  | CDC | 282 | GENERICAIPoint | DS046_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1510_PHA | 斗南虎菁一路(1510) 相間RY | LINE161 | D24/161/1510/PHA |  |  |  | CDC | 283 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1510_GDA | 斗南虎菁一路(1510) 接地RY | LINE161 | D24/161/1510/GDA |  |  |  | CDC | 284 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | 87UL | [17 empty] | 1-30-02 |  | 1-45 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_87UL | 斗南虎菁一路(1510) 87RY U/L | LINE161 | D24/161/1510/87UL |  |  |  | CDC | 285 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1510_CB | 1510(斗南虎菁一路) CB | LINE161 | D24/161/1510/CB |  |  |  | CDC | 286 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | 79UL | [17 empty] | 1-30-04 |  | 1-46 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_79UL | 斗南虎菁一路(1510) 79RY U/L | LINE161 | D24/161/1510/79UL |  |  |  | CDC | 287 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | DS1 | 1511 | [16 empty] | 1-38-00 | 1-38-01 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1511_DS | 1511(斗南虎菁一路) DS | LINE161 |  |  |  |  | CDC | 288 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | DS2 | 1512 | [16 empty] | 1-38-02 | 1-38-03 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1512_DS | 1512(斗南虎菁一路) DS | LINE161 |  |  |  |  | CDC | 289 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | DS3 | 1513 | [16 empty] | 1-38-04 | 1-38-05 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1513_DS | 1513(斗南虎菁一路) DS | LINE161 |  |  |  |  | CDC | 290 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | E3 | 1513E | [16 empty] | 1-38-06 | 1-38-07 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1513E_ES | 1513E(斗南虎菁一路) ES | LINE161 |  |  |  |  | CDC | 291 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1520_PHA | 斗南虎菁二路(1520) 相間RY | LINE161 | D24/161/1520/PHA |  |  |  | CDC | 292 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1520_GDA | 斗南虎菁二路(1520) 接地RY | LINE161 | D24/161/1520/GDA |  |  |  | CDC | 293 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | 87UL | [17 empty] | 1-30-05 |  | 1-47 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_87UL | 斗南虎菁二路(1520) 87RY U/L | LINE161 | D24/161/1520/87UL |  |  |  | CDC | 294 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1520_CB | 1520(斗南虎菁二路) CB | LINE161 | D24/161/1520/CB |  |  |  | CDC | 295 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | 79UL | [17 empty] | 1-30-07 |  | 1-48 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_79UL | 斗南虎菁二路(1520) 79RY U/L | LINE161 | D24/161/1520/79UL |  |  |  | CDC | 296 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | DS1 | 1521 | [16 empty] | 1-38-08 | 1-38-09 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1521_DS | 1521(斗南虎菁二路) DS | LINE161 |  |  |  |  | CDC | 297 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | DS2 | 1522 | [16 empty] | 1-38-10 | 1-38-11 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1522_DS | 1522(斗南虎菁二路) DS | LINE161 |  |  |  |  | CDC | 298 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | DS3 | 1523 | [16 empty] | 1-38-12 | 1-38-13 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1523_DS | 1523(斗南虎菁二路) DS | LINE161 |  |  |  |  | CDC | 299 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | E3 | 1523E | [16 empty] | 1-38-14 | 1-38-15 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1523E_ES | 1523E(斗南虎菁二路) ES | LINE161 |  |  |  |  | CDC | 300 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | PHA | [17 empty] | 1-19-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_PHA | 11KV虎一線(XJ21) 相間RY | FEEDER | D24/11/XJ21/PHA |  |  |  | CDC | 301 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) |  | GDA | [17 empty] | 1-19-01 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_GDA | 11KV虎一線(XJ21) 接地RY | FEEDER | D24/11/XJ21/GDA |  |  |  | CDC | 302 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ21 | 虎一線(XJ21) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-68 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_79UL | 11KV虎一線(XJ21) 79RY U/L | FEEDER | D24/11/XJ21/79UL |  |  |  | CDC | 303 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ21_LCO | 虎一線(XJ21) LCO |  | TapPosMv | [17 empty] | 2-31-03 |  | 2-69 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_LCO_TAP | 11KV虎一線(XJ21) LCO TAP | FEEDER |  |  |  |  | CDC | 304 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ21 | XJ21(11KV虎一線) |  | CB | [17 empty] | 1-18-07 |  | 1-1F | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_CB | XJ21(11KV虎一線) CB | FEEDER | D24/11/XJ21/CB |  |  |  | CDC | 305 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_PHA | 11KV虎二線(XJ22) 相間RY | FEEDER | D24/11/XJ22/PHA |  |  |  | CDC | 306 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_GDA | 11KV虎二線(XJ22) 接地RY | FEEDER | D24/11/XJ22/GDA |  |  |  | CDC | 307 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ22 | 虎二線(XJ22) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-66 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_79UL | 11KV虎二線(XJ22) 79RY U/L | FEEDER | D24/11/XJ22/79UL |  |  |  | CDC | 308 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ22_LCO | 虎二線(XJ22) LCO |  | TapPosMv | [17 empty] | 2-31-01 |  | 2-67 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_LCO_TAP | 11KV虎二線(XJ22) LCO TAP | FEEDER |  |  |  |  | CDC | 309 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ22 | XJ22(11KV虎二線) |  | CB | [17 empty] | 1-18-04 |  | 1-1E | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_CB | XJ22(11KV虎二線) CB | FEEDER | D24/11/XJ22/CB |  |  |  | CDC | 310 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_PHA | 11KV虎三線(XJ23) 相間RY | FEEDER | D24/11/XJ23/PHA |  |  |  | CDC | 311 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_GDA | 11KV虎三線(XJ23) 接地RY | FEEDER | D24/11/XJ23/GDA |  |  |  | CDC | 312 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ23 | 虎三線(XJ23) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-64 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_79UL | 11KV虎三線(XJ23) 79RY U/L | FEEDER | D24/11/XJ23/79UL |  |  |  | CDC | 313 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ23_LCO | 虎三線(XJ23) LCO |  | TapPosMv | [17 empty] | 2-30-15 |  | 2-65 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_LCO_TAP | 11KV虎三線(XJ23) LCO TAP | FEEDER |  |  |  |  | CDC | 314 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ23 | XJ23(11KV虎三線) |  | CB | [17 empty] | 1-18-01 |  | 1-1D | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_CB | XJ23(11KV虎三線) CB | FEEDER | D24/11/XJ23/CB |  |  |  | CDC | 315 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_PHA | 11KV虎四線(XJ24) 相間RY | FEEDER | D24/11/XJ24/PHA |  |  |  | CDC | 316 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_GDA | 11KV虎四線(XJ24) 接地RY | FEEDER | D24/11/XJ24/GDA |  |  |  | CDC | 317 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ24 | 虎四線(XJ24) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-62 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_79UL | 11KV虎四線(XJ24) 79RY U/L | FEEDER | D24/11/XJ24/79UL |  |  |  | CDC | 318 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ24_LCO | 虎四線(XJ24) LCO |  | TapPosMv | [17 empty] | 2-30-13 |  | 2-63 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_LCO_TAP | 11KV虎四線(XJ24) LCO TAP | FEEDER |  |  |  |  | CDC | 319 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ24 | XJ24(11KV虎四線) |  | CB | [17 empty] | 1-17-06 |  | 1-1C | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_CB | XJ24(11KV虎四線) CB | FEEDER | D24/11/XJ24/CB |  |  |  | CDC | 320 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | PHA | [17 empty] | 1-17-04 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_PHA | 11KV虎五線(XJ25) 相間RY | FEEDER | D24/11/XJ25/PHA |  |  |  | CDC | 321 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_GDA | 11KV虎五線(XJ25) 接地RY | FEEDER | D24/11/XJ25/GDA |  |  |  | CDC | 322 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ25 | 虎五線(XJ25) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-60 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_79UL | 11KV虎五線(XJ25) 79RY U/L | FEEDER | D24/11/XJ25/79UL |  |  |  | CDC | 323 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ25_LCO | 虎五線(XJ25) LCO |  | TapPosMv | [17 empty] | 2-30-11 |  | 2-61 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_LCO_TAP | 11KV虎五線(XJ25) LCO TAP | FEEDER |  |  |  |  | CDC | 324 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ25 | XJ25(11KV虎五線) |  | CB | [17 empty] | 1-17-03 |  | 1-1B | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_CB | XJ25(11KV虎五線) CB | FEEDER | D24/11/XJ25/CB |  |  |  | CDC | 325 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | PHA | [17 empty] | 1-1E-02 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_PHA | 11KV虎六線(XJ26) 相間RY | FEEDER | D24/11/XJ26/PHA |  |  |  | CDC | 326 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) |  | GDA | [17 empty] | 1-1E-03 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_GDA | 11KV虎六線(XJ26) 接地RY | FEEDER | D24/11/XJ26/GDA |  |  |  | CDC | 327 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ26 | 虎六線(XJ26) 79RY |  | 79UL | [17 empty] | 2-32-06 |  | 2-7C | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_79UL | 11KV虎六線(XJ26) 79RY U/L | FEEDER | D24/11/XJ26/79UL |  |  |  | CDC | 328 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ26_LCO | 虎六線(XJ26) LCO |  | TapPosMv | [17 empty] | 2-32-07 |  | 2-7D | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_LCO_TAP | 11KV虎六線(XJ26) LCO TAP | FEEDER |  |  |  |  | CDC | 329 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ26 | XJ26(11KV虎六線) |  | CB | [17 empty] | 1-1E-01 |  | 1-2F | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_CB | XJ26(11KV虎六線) CB | FEEDER | D24/11/XJ26/CB |  |  |  | CDC | 330 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | PHA | [17 empty] | 1-1D-07 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_PHA | 11KV虎七線(XJ27) 相間RY | FEEDER | D24/11/XJ27/PHA |  |  |  | CDC | 331 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) |  | GDA | [17 empty] | 1-1E-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_GDA | 11KV虎七線(XJ27) 接地RY | FEEDER | D24/11/XJ27/GDA |  |  |  | CDC | 332 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ27 | 虎七線(XJ27) 79RY |  | 79UL | [17 empty] | 2-32-04 |  | 2-7A | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_79UL | 11KV虎七線(XJ27) 79RY U/L | FEEDER | D24/11/XJ27/79UL |  |  |  | CDC | 333 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ27_LCO | 虎七線(XJ27) LCO |  | TapPosMv | [17 empty] | 2-32-05 |  | 2-7B | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_LCO_TAP | 11KV虎七線(XJ27) LCO TAP | FEEDER |  |  |  |  | CDC | 334 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ27 | XJ27(11KV虎七線) |  | CB | [17 empty] | 1-1D-06 |  | 1-2E | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_CB | XJ27(11KV虎七線) CB | FEEDER | D24/11/XJ27/CB |  |  |  | CDC | 335 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | PHA | [17 empty] | 1-1D-04 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_PHA | 11KV虎八線(XJ28) 相間RY | FEEDER | D24/11/XJ28/PHA |  |  |  | CDC | 336 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) |  | GDA | [17 empty] | 1-1D-05 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_GDA | 11KV虎八線(XJ28) 接地RY | FEEDER | D24/11/XJ28/GDA |  |  |  | CDC | 337 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ28 | 虎八線(XJ28) 79RY |  | 79UL | [17 empty] | 2-32-02 |  | 2-78 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_79UL | 11KV虎八線(XJ28) 79RY U/L | FEEDER | D24/11/XJ28/79UL |  |  |  | CDC | 338 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ28_LCO | 虎八線(XJ28) LCO |  | TapPosMv | [17 empty] | 2-32-03 |  | 2-79 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_LCO_TAP | 11KV虎八線(XJ28) LCO TAP | FEEDER |  |  |  |  | CDC | 339 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ28 | XJ28(11KV虎八線) |  | CB | [17 empty] | 1-1D-03 |  | 1-2D | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_CB | XJ28(11KV虎八線) CB | FEEDER | D24/11/XJ28/CB |  |  |  | CDC | 340 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | PHA | [17 empty] | 1-1D-01 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_PHA | 11KV虎九線(XJ29) 相間RY | FEEDER | D24/11/XJ29/PHA |  |  |  | CDC | 341 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) |  | GDA | [17 empty] | 1-1D-02 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_GDA | 11KV虎九線(XJ29) 接地RY | FEEDER | D24/11/XJ29/GDA |  |  |  | CDC | 342 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ29 | 虎九線(XJ29) 79RY |  | 79UL | [17 empty] | 2-32-00 |  | 2-76 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_79UL | 11KV虎九線(XJ29) 79RY U/L | FEEDER | D24/11/XJ29/79UL |  |  |  | CDC | 343 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ29_LCO | 虎九線(XJ29) LCO |  | TapPosMv | [17 empty] | 2-32-01 |  | 2-77 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_LCO_TAP | 11KV虎九線(XJ29) LCO TAP | FEEDER |  |  |  |  | CDC | 344 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ29 | XJ29(11KV虎九線) |  | CB | [17 empty] | 1-1D-00 |  | 1-2C | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_CB | XJ29(11KV虎九線) CB | FEEDER | D24/11/XJ29/CB |  |  |  | CDC | 345 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | PHA | [17 empty] | 1-1C-06 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_PHA | 11KV虎十線(XJ30) 相間RY | FEEDER | D24/11/XJ30/PHA |  |  |  | CDC | 346 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) |  | GDA | [17 empty] | 1-1C-07 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_GDA | 11KV虎十線(XJ30) 接地RY | FEEDER | D24/11/XJ30/GDA |  |  |  | CDC | 347 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | XJ30 | 虎十線(XJ30) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-74 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_79UL | 11KV虎十線(XJ30) 79RY U/L | FEEDER | D24/11/XJ30/79UL |  |  |  | CDC | 348 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 11 | 11kV | XJ30_LCO | 虎十線(XJ30) LCO |  | TapPosMv | [17 empty] | 2-31-15 |  | 2-75 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_LCO_TAP | 11KV虎十線(XJ30) LCO TAP | FEEDER |  |  |  |  | CDC | 349 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 11 | 11kV | XJ30 | XJ30(11KV虎十線) |  | CB | [17 empty] | 1-1C-05 |  | 1-2B | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_CB | XJ30(11KV虎十線) CB | FEEDER | D24/11/XJ30/CB |  |  |  | CDC | 350 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎51線(XJ51) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_PHA | 23KV虎51線(XJ51) 相間RY | FEEDER | D24/22/XJ51/PHA |  |  |  | CDC | 351 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎51線(XJ51) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_GDA | 23KV虎51線(XJ51) 接地RY | FEEDER | D24/22/XJ51/GDA |  |  |  | CDC | 352 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ51 | 虎51線(XJ51) 79RY |  | 79UL | [17 empty] | 2-30-00 |  | 2-56 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_79UL | 23KV虎51線(XJ51) 79RY U/L | FEEDER | D24/22/XJ51/79UL |  |  |  | CDC | 353 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ51_LCO | 虎51線(XJ51) LCO |  | TapPosMv | [17 empty] | 2-30-01 |  | 2-57 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_LCO_TAP | 23KV虎51線(XJ51) LCO TAP | FEEDER |  |  |  |  | CDC | 354 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ51 | XJ51(23KV虎51線) |  | CB | [17 empty] | 1-14-06 |  | 1-13 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_CB | XJ51(23KV虎51線) CB | FEEDER | D24/22/XJ51/CB |  |  |  | CDC | 355 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎52線(XJ52) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_PHA | 23KV虎52線(XJ52) 相間RY | FEEDER | D24/22/XJ52/PHA |  |  |  | CDC | 356 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎52線(XJ52) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_GDA | 23KV虎52線(XJ52) 接地RY | FEEDER | D24/22/XJ52/GDA |  |  |  | CDC | 357 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ52 | 虎52線(XJ52) 79RY |  | 79UL | [17 empty] | 2-30-02 |  | 2-58 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_79UL | 23KV虎52線(XJ52) 79RY U/L | FEEDER | D24/22/XJ52/79UL |  |  |  | CDC | 358 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ52_LCO | 虎52線(XJ52) LCO |  | TapPosMv | [17 empty] | 2-30-03 |  | 2-59 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_LCO_TAP | 23KV虎52線(XJ52) LCO TAP | FEEDER |  |  |  |  | CDC | 359 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ52 | XJ52(23KV虎52線) |  | CB | [17 empty] | 1-15-01 |  | 1-14 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_CB | XJ52(23KV虎52線) CB | FEEDER | D24/22/XJ52/CB |  |  |  | CDC | 360 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎53線(XJ53) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_PHA | 23KV虎53線(XJ53) 相間RY | FEEDER | D24/22/XJ53/PHA |  |  |  | CDC | 361 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎53線(XJ53) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_GDA | 23KV虎53線(XJ53) 接地RY | FEEDER | D24/22/XJ53/GDA |  |  |  | CDC | 362 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ53 | 虎53線(XJ53) 79RY |  | 79UL | [17 empty] | 2-30-04 |  | 2-5A | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_79UL | 23KV虎53線(XJ53) 79RY U/L | FEEDER | D24/22/XJ53/79UL |  |  |  | CDC | 363 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ53_LCO | 虎53線(XJ53) LCO |  | TapPosMv | [17 empty] | 2-30-05 |  | 2-5B | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_LCO_TAP | 23KV虎53線(XJ53) LCO TAP | FEEDER |  |  |  |  | CDC | 364 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ53 | XJ53(23KV虎53線) |  | CB | [17 empty] | 1-15-04 |  | 1-15 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_CB | XJ53(23KV虎53線) CB | FEEDER | D24/22/XJ53/CB |  |  |  | CDC | 365 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎54線(XJ54) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_PHA | 23KV虎54線(XJ54) 相間RY | FEEDER | D24/22/XJ54/PHA |  |  |  | CDC | 366 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎54線(XJ54) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_GDA | 23KV虎54線(XJ54) 接地RY | FEEDER | D24/22/XJ54/GDA |  |  |  | CDC | 367 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ54 | 虎54線(XJ54) 79RY |  | 79UL | [17 empty] | 2-30-06 |  | 2-5C | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_79UL | 23KV虎54線(XJ54) 79RY U/L | FEEDER | D24/22/XJ54/79UL |  |  |  | CDC | 368 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ54_LCO | 虎54線(XJ54) LCO |  | TapPosMv | [17 empty] | 2-30-07 |  | 2-5D | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_LCO_TAP | 23KV虎54線(XJ54) LCO TAP | FEEDER |  |  |  |  | CDC | 369 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ54 | XJ54(23KV虎54線) |  | CB | [17 empty] | 1-15-07 |  | 1-16 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_CB | XJ54(23KV虎54線) CB | FEEDER | D24/22/XJ54/CB |  |  |  | CDC | 370 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎55線(XJ55) |  | PHA | [17 empty] | 1-16-03 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_PHA | 23KV虎55線(XJ55) 相間RY | FEEDER | D24/22/XJ55/PHA |  |  |  | CDC | 371 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎55線(XJ55) |  | GDA | [17 empty] | 1-16-04 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_GDA | 23KV虎55線(XJ55) 接地RY | FEEDER | D24/22/XJ55/GDA |  |  |  | CDC | 372 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ55 | 虎55線(XJ55) 79RY |  | 79UL | [17 empty] | 2-30-08 |  | 2-5E | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_79UL | 23KV虎55線(XJ55) 79RY U/L | FEEDER | D24/22/XJ55/79UL |  |  |  | CDC | 373 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ55_LCO | 虎55線(XJ55) LCO |  | TapPosMv | [17 empty] | 2-30-09 |  | 2-5F | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_LCO_TAP | 23KV虎55線(XJ55) LCO TAP | FEEDER |  |  |  |  | CDC | 374 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ55 | XJ55(23KV虎55線) |  | CB | [17 empty] | 1-16-02 |  | 1-17 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_CB | XJ55(23KV虎55線) CB | FEEDER | D24/22/XJ55/CB |  |  |  | CDC | 375 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎56線(XJ56) |  | PHA | [17 empty] | 1-1A-01 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_PHA | 23KV虎56線(XJ56) 相間RY | FEEDER | D24/22/XJ56/PHA |  |  |  | CDC | 376 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎56線(XJ56) |  | GDA | [17 empty] | 1-1A-02 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_GDA | 23KV虎56線(XJ56) 接地RY | FEEDER | D24/22/XJ56/GDA |  |  |  | CDC | 377 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ56 | 虎56線(XJ56) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-6A | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_79UL | 23KV虎56線(XJ56) 79RY U/L | FEEDER | D24/22/XJ56/79UL |  |  |  | CDC | 378 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ56_LCO | 虎56線(XJ56) LCO |  | TapPosMv | [17 empty] | 2-31-05 |  | 2-6B | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_LCO_TAP | 23KV虎56線(XJ56) LCO TAP | FEEDER |  |  |  |  | CDC | 379 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ56 | XJ56(23KV虎56線) |  | CB | [17 empty] | 1-1A-00 |  | 1-23 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_CB | XJ56(23KV虎56線) CB | FEEDER | D24/22/XJ56/CB |  |  |  | CDC | 380 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎57線(XJ57) |  | PHA | [17 empty] | 1-1A-04 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_PHA | 23KV虎57線(XJ57) 相間RY | FEEDER | D24/22/XJ57/PHA |  |  |  | CDC | 381 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎57線(XJ57) |  | GDA | [17 empty] | 1-1A-05 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_GDA | 23KV虎57線(XJ57) 接地RY | FEEDER | D24/22/XJ57/GDA |  |  |  | CDC | 382 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ57 | 虎57線(XJ57) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-6C | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_79UL | 23KV虎57線(XJ57) 79RY U/L | FEEDER | D24/22/XJ57/79UL |  |  |  | CDC | 383 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ57_LCO | 虎57線(XJ57) LCO |  | TapPosMv | [17 empty] | 2-31-07 |  | 2-6D | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_LCO_TAP | 23KV虎57線(XJ57) LCO TAP | FEEDER |  |  |  |  | CDC | 384 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ57 | XJ57(23KV虎57線) |  | CB | [17 empty] | 1-1A-03 |  | 1-24 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_CB | XJ57(23KV虎57線) CB | FEEDER | D24/22/XJ57/CB |  |  |  | CDC | 385 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎58線(XJ58) |  | PHA | [17 empty] | 1-1A-07 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_PHA | 23KV虎58線(XJ58) 相間RY | FEEDER | D24/22/XJ58/PHA |  |  |  | CDC | 386 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎58線(XJ58) |  | GDA | [17 empty] | 1-1B-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_GDA | 23KV虎58線(XJ58) 接地RY | FEEDER | D24/22/XJ58/GDA |  |  |  | CDC | 387 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ58 | 虎58線(XJ58) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-6E | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_79UL | 23KV虎58線(XJ58) 79RY U/L | FEEDER | D24/22/XJ58/79UL |  |  |  | CDC | 388 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ58_LCO | 虎58線(XJ58) LCO |  | TapPosMv | [17 empty] | 2-31-09 |  | 2-6F | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_LCO_TAP | 23KV虎58線(XJ58) LCO TAP | FEEDER |  |  |  |  | CDC | 389 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ58 | XJ58(23KV虎58線) |  | CB | [17 empty] | 1-1A-06 |  | 1-25 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_CB | XJ58(23KV虎58線) CB | FEEDER | D24/22/XJ58/CB |  |  |  | CDC | 390 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎59線(XJ59) |  | PHA | [17 empty] | 1-1B-02 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_PHA | 23KV虎59線(XJ59) 相間RY | FEEDER | D24/22/XJ59/PHA |  |  |  | CDC | 391 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎59線(XJ59) |  | GDA | [17 empty] | 1-1B-03 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_GDA | 23KV虎59線(XJ59) 接地RY | FEEDER | D24/22/XJ59/GDA |  |  |  | CDC | 392 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ59 | 虎59線(XJ59) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-70 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_79UL | 23KV虎59線(XJ59) 79RY U/L | FEEDER | D24/22/XJ59/79UL |  |  |  | CDC | 393 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ59_LCO | 虎59線(XJ59) LCO |  | TapPosMv | [17 empty] | 2-31-11 |  | 2-71 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_LCO_TAP | 23KV虎59線(XJ59) LCO TAP | FEEDER |  |  |  |  | CDC | 394 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ59 | XJ59(23KV虎59線) |  | CB | [17 empty] | 1-1B-01 |  | 1-26 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_CB | XJ59(23KV虎59線) CB | FEEDER | D24/22/XJ59/CB |  |  |  | CDC | 395 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎60線(XJ60) |  | PHA | [17 empty] | 1-1B-05 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_PHA | 23KV虎60線(XJ60) 相間RY | FEEDER | D24/22/XJ60/PHA |  |  |  | CDC | 396 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎60線(XJ60) |  | GDA | [17 empty] | 1-1B-06 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_GDA | 23KV虎60線(XJ60) 接地RY | FEEDER | D24/22/XJ60/GDA |  |  |  | CDC | 397 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | XJ60 | 虎60線(XJ60) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-72 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_79UL | 23KV虎60線(XJ60) 79RY U/L | FEEDER | D24/22/XJ60/79UL |  |  |  | CDC | 398 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | XJ60_LCO | 虎60線(XJ60) LCO |  | TapPosMv | [17 empty] | 2-31-13 |  | 2-73 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_LCO_TAP | 23KV虎60線(XJ60) LCO TAP | FEEDER |  |  |  |  | CDC | 399 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D24 | 虎菁DS | 22 | 22kV | XJ60 | XJ60(23KV虎60線) |  | CB | [17 empty] | 1-1B-04 |  | 1-27 | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_CB | XJ60(23KV虎60線) CB | FEEDER | D24/22/XJ60/CB |  |  |  | CDC | 400 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-16-05 |  | 1-18 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.100_CB | 100(TIE) CB | TIE |  |  |  |  | CDC | 401 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-16-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.100_51A | 11KV TIE(100) 51RY | TIE |  |  |  |  | CDC | 402 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-16-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.100_51NA | 11KV TIE(100) 51N RY | TIE |  |  |  |  | CDC | 403 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-06-02 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1500_CB | 1500(TIE) CB | TIE | D24/161/1500/CB |  |  |  | CDC | 404 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1500_50A | 161KV TIE(1500) 50RY | TIE |  |  |  |  | CDC | 405 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3D-00 | 1-3D-01 | 2-17 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1501_DS | 1501(TIE) DS | TIE | D24/161/1500/DS1 |  |  |  | CDC | 406 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3D-02 | 1-3D-03 | 2-18 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1502_DS | 1502(TIE) DS | TIE | D24/161/1500/DS2 |  |  |  | CDC | 407 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-19-02 |  | 1-20 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.200_CB | 200(TIE) CB | TIE |  |  |  |  | CDC | 408 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-19-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.200_51A | 11KV TIE(200) 51RY | TIE |  |  |  |  | CDC | 409 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-19-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.200_51NA | 11KV TIE(200) 51N RY | TIE |  |  |  |  | CDC | 410 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-14-03 |  | 1-12 | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.390_CB | 390(#1SSTR) CB | OTHER |  |  |  |  | CDC | 411 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-14-04 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 412 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-14-05 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER |  |  |  |  | CDC | 413 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-1C-02 |  | 1-2A | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.490_CB | 490(#2SSTR) CB | OTHER |  |  |  |  | CDC | 414 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-1C-03 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 415 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-1C-04 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER |  |  |  |  | CDC | 416 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-03 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1750_CB | 1750(#1DTR) CB | MTR | D24/161/1750/CB |  |  |  | CDC | 417 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-08-02 |  | 1-10 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.310_CB | 310(#1DTR) CB | MTR |  |  |  |  | CDC | 418 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-05 |  | 1-19 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.320_CB | 320(#1DTR) CB | MTR |  |  |  |  | CDC | 419 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-08-00 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1DTR_51A | #1DTR 51RY | MTR |  |  |  |  | CDC | 420 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-08-01 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1DTR_51NA | #1DTR 51N RY | MTR |  |  |  |  | CDC | 421 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-06 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1DTR_51ZA | #1DTR 51Z RY | MTR |  |  |  |  | CDC | 422 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-04 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1DTR_87A | #1DTR 87RY | MTR |  |  |  |  | CDC | 423 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 87UL | [17 empty] | 1-32-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_87UL | #1DTR 87RY U/L | MTR |  |  |  |  | CDC | 424 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-08-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.310_51A | #1DTR二次側(310) 51RY | MTR |  |  |  |  | CDC | 425 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.320_51A | #1DTR二次側(320) 51RY | MTR |  |  |  |  | CDC | 426 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR |  |  |  |  | CDC | 427 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_96D | #1DTR 96D RY | MTR |  |  |  |  | CDC | 428 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 2-35-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_96P | #1DTR 96P RY | MTR |  |  |  |  | CDC | 429 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 2-35-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_63Q | #1DTR 63Q RY | MTR |  |  |  |  | CDC | 430 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR |  |  |  |  | CDC | 431 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 2-35-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR |  |  |  |  | CDC | 432 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_TRA | #1DTR 重故障 | MTR |  |  |  |  | CDC | 433 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR_TRF | #1DTR 輕故障 | MTR |  |  |  |  | CDC | 434 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-32-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR |  |  |  |  | CDC | 435 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D24 | 虎菁DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-32-06 |  | 1-5B | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR |  |  |  |  | CDC | 436 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-32-05 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR |  |  |  |  | CDC | 437 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D24 | 虎菁DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-32-07 |  | 1-5D | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR |  |  |  |  | CDC | 438 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3D-04 | 1-3D-05 | 2-19 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1751_DS | 1751(#1DTR) DS | MTR | D24/161/1750/DS1 |  |  |  | CDC | 439 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3D-06 | 1-3D-07 | 2-1A | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1752_DS | 1752(#1DTR) DS | MTR | D24/161/1750/DS2 |  |  |  | CDC | 440 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-09-00 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1760_CB | 1760(#2DTR) CB | MTR | D24/161/1760/CB |  |  |  | CDC | 441 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-09-07 |  | 1-21 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.330_CB | 330(#2DTR) CB | MTR |  |  |  |  | CDC | 442 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0A-02 |  | 1-28 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.340_CB | 340(#2DTR) CB | MTR |  |  |  |  | CDC | 443 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-09-05 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2DTR_51A | #2DTR 51RY | MTR |  |  |  |  | CDC | 444 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2DTR_51NA | #2DTR 51N RY | MTR |  |  |  |  | CDC | 445 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-09-03 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2DTR_51ZA | #2DTR 51Z RY | MTR |  |  |  |  | CDC | 446 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2DTR_87A | #2DTR 87RY | MTR |  |  |  |  | CDC | 447 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 87UL | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_87UL | #2DTR 87RY U/L | MTR |  |  |  |  | CDC | 448 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-0A-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.330_51A | #2DTR二次側(330) 51RY | MTR |  |  |  |  | CDC | 449 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-0A-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.340_51A | #2DTR二次側(340) 51RY | MTR |  |  |  |  | CDC | 450 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-09-02 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR |  |  |  |  | CDC | 451 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-35-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_96D | #2DTR 96D RY | MTR |  |  |  |  | CDC | 452 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-35-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_96P | #2DTR 96P RY | MTR |  |  |  |  | CDC | 453 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-35-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_63Q | #2DTR 63Q RY | MTR |  |  |  |  | CDC | 454 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-35-10 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR |  |  |  |  | CDC | 455 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-35-11 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR |  |  |  |  | CDC | 456 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_TRA | #2DTR 重故障 | MTR |  |  |  |  | CDC | 457 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR_TRF | #2DTR 輕故障 | MTR |  |  |  |  | CDC | 458 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR |  |  |  |  | CDC | 459 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D24 | 虎菁DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-32-13 |  | 1-5F | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR |  |  |  |  | CDC | 460 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR |  |  |  |  | CDC | 461 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D24 | 虎菁DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-32-14 |  | 1-61 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR |  |  |  |  | CDC | 462 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3D-08 | 1-3D-09 | 2-1B | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1761_DS | 1761(#2DTR) DS | MTR | D24/161/1760/DS1 |  |  |  | CDC | 463 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3D-10 | 1-3D-11 | 2-1C | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1762_DS | 1762(#2DTR) DS | MTR | D24/161/1760/DS2 |  |  |  | CDC | 464 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-17-00 |  | 1-1A | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.220_CB | 220(11KV #2SC) CB | SC | D24/11/220/CB |  |  |  | CDC | 465 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-17-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.220_SCA | 11KV #2SC 51,51N RY | SC | D24/11/220/SCA |  |  |  | CDC | 466 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-17-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D24/11/220/UVA |  |  |  | CDC | 467 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-1B-07 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.240_CB | 240(11KV #4SC) CB | SC | D24/11/240/CB |  |  |  | CDC | 468 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-1C-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.240_SCA | 11KV #4SC 51,51N RY | SC | D24/11/240/SCA |  |  |  | CDC | 469 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-1C-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D24/11/240/UVA |  |  |  | CDC | 470 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-14-00 |  | 1-11 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.210_CB | 210(23KV #1SC) CB | SC | D24/22/210/CB |  |  |  | CDC | 471 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.210_SCA | 23KV #1SC 51,51N RY | SC | D24/22/210/SCA |  |  |  | CDC | 472 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-14-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.210_UVA | 23KV #1SC 27RY(欠壓) | SC | D24/22/210/UVA |  |  |  | CDC | 473 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-19-05 |  | 1-22 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.230_CB | 230(23KV #3SC) CB | SC | D24/22/230/CB |  |  |  | CDC | 474 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-19-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.230_SCA | 23KV #3SC 51,51N RY | SC | D24/22/230/SCA |  |  |  | CDC | 475 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-19-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | D24/22/230/UVA |  |  |  | CDC | 476 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 477 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS |  |  |  |  | CDC | 478 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-01 |  | 1-65 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 479 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 480 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS |  |  |  |  | CDC | 481 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-02 |  | 1-66 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 482 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER |  |  |  |  | CDC | 483 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 484 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | _SC | 11/ SC |  | 60A | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.11KV_SC_60A | 11/23KV SC 60A | OTHER |  |  |  |  | CDC | 485 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_CBA | 161KV斷路器重故障 | OTHER |  |  |  |  | CDC | 486 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-37-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_CBF | 161KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 487 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 488 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.火災警報(1) | 火災警報(1)受信總機 | OTHER |  |  |  |  | CDC | 489 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-36-01 |  | 1-6C | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 490 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D24 | 虎菁DS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-36-02 |  | 1-6D | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 491 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D24 | 虎菁DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 492 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-36-03 |  | 1-6E | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER |  |  |  |  | CDC | 493 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D24 | 虎菁DS | 0 |  |  |  |  | STUV | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 494 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER |  |  |  |  | CDC | 495 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | DCA | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 496 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | DCE | [17 empty] | 1-35-11 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 497 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 498 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 499 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | Door1 | [17 empty] | 1-37-15 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.無人化門禁(1) | 無人化門禁(1)圍牆大門 | OTHER |  |  |  |  | CDC | 500 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
D24 | 虎菁DS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-36-00 |  | 1-6B | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.開關場照明(A) | 景觀照明 | OTHER |  |  |  |  | CDC | 501 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D24 | 虎菁DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-32-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 502 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | 25TA | [17 empty] | 1-0D-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_25TA | 1510 同步校核電驛超時動作 | OTHER |  |  |  |  | CDC | 503 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | DTTA | [17 empty] | 1-10-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_DTTA | 斗南虎菁一路(1510) 遠方遙跳 | OTHER |  |  |  |  | CDC | 504 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | 25TA | [17 empty] | 1-0E-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_25TA | 1520 同步校核電驛超時動作 | OTHER |  |  |  |  | CDC | 505 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | DTTA | [17 empty] | 1-10-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_DTTA | 斗南虎菁一路(1520) 遠方遙跳 | OTHER |  |  |  |  | CDC | 506 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-07-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER |  |  |  |  | CDC | 507 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 2-05-06 |  | 3-29 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.220_LBS | 220(11KV #2SC) LBS | OTHER |  |  |  |  | CDC | 508 | GENERICDIPoint | DS046_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 22 | 22kV |  |  |  | OSCA | [17 empty] | 1-07-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.23KV_OSCA | 11/23KV示波器啟動警報 | OTHER |  |  |  |  | CDC | 509 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 240 | #4SC(240) |  | LBS | [17 empty] | 2-06-00 |  | 3-2B | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.240_LBS | 240(11KV #4SC) LBS | OTHER |  |  |  |  | CDC | 510 | GENERICDIPoint | DS046_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.310_GDA | 310開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 511 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 2-36-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.310_PHA2 | 310開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 512 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.320_GDA | 320開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 513 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 2-36-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.320_PHA2 | 320開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 514 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-0A-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.330_GDA | 330開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 515 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 2-36-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.330_PHA2 | 330開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 516 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0A-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.340_GDA | 340開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 517 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 2-36-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.340_PHA2 | 340開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 518 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | BUS | BUS |  | SUBA | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.BPT重故障 | BUS PT BAY重故障 | OTHER |  |  |  |  | CDC | 519 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | BUS | BUS |  | SUBF | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.BPT輕故障 | BUS PT BAY輕故障 | OTHER |  |  |  |  | CDC | 520 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | DC電壓過低 | [17 empty] | 1-37-10 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.DC電壓過低 | DC電壓過低警報(120V) | OTHER |  |  |  |  | CDC | 521 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | DC電壓過高 | [17 empty] | 1-37-11 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.DC電壓過高 | DC電壓過高警報(140V) | OTHER |  |  |  |  | CDC | 522 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | SCADA | [17 empty] | 1-36-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.SCADA | 變電所SCADA故障 | OTHER |  |  |  |  | CDC | 523 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D24 | 虎菁DS | 0 |  | SCADA | SCADA |  | UPS | [17 empty] | 1-37-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.SCADA_UPS | SCADA UPS故障 | OTHER |  |  |  |  | CDC | 524 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | SEL電驛故障 | [17 empty] | 1-35-13 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.SEL電驛故障 | 1750或1760或1500SEL電驛故障 | OTHER |  |  |  |  | CDC | 525 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.水位警報(1) | 地下室水位警報(1) | OTHER |  |  |  |  | CDC | 526 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.水位警報(2) | 地下室水位警報(2) | OTHER |  |  |  |  | CDC | 527 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 污水幫浦 | [17 empty] | 1-36-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.污水幫浦 | 污水幫浦故障 | OTHER |  |  |  |  | CDC | 528 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 涵洞排水幫浦 | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.涵洞排水幫浦 | 涵洞排水幫浦故障 | OTHER |  |  |  |  | CDC | 529 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 揚水幫浦 | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.揚水幫浦 | 揚水幫浦故障 | OTHER |  |  |  |  | CDC | 530 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1510_87A | 斗南虎菁一路(1510) 87RY | LINE161 | D24/161/1510/87A |  |  |  | CDC | 531 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1520_87A | 斗南虎菁二路(1520) 87RY | LINE161 | D24/161/1520/87A |  |  |  | CDC | 532 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1530_PHA | 虎科虎菁一路(1530) 相間RY | LINE161 | D24/161/1530/PHA |  |  |  | CDC | 533 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1530_GDA | 虎科虎菁一路(1530) 接地RY | LINE161 | D24/161/1530/GDA |  |  |  | CDC | 534 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1530_87A | 虎科虎菁一路(1530) 87RY | LINE161 | D24/161/1530/87A |  |  |  | CDC | 535 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | 87UL | [17 empty] | 1-30-08 |  | 1-49 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_87UL | 虎科虎菁一路(1530) 87RY U/L | LINE161 | D24/161/1530/87UL |  |  |  | CDC | 536 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1530_CB | 1530(虎科虎菁一路) CB | LINE161 | D24/161/1530/CB |  |  |  | CDC | 537 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | 79UL | [17 empty] | 1-30-10 |  | 1-4A | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_79UL | 虎科虎菁一路(1530) 79RY U/L | LINE161 | D24/161/1530/79UL |  |  |  | CDC | 538 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | DS1 | 1531 | [16 empty] | 1-39-00 | 1-39-01 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1531_DS | 1531(虎科虎菁一路) DS | LINE161 |  |  |  |  | CDC | 539 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | DS2 | 1532 | [16 empty] | 1-39-02 | 1-39-03 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1532_DS | 1532(虎科虎菁一路) DS | LINE161 |  |  |  |  | CDC | 540 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | DS3 | 1533 | [16 empty] | 1-39-04 | 1-39-05 | 1-79 | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1533_DS | 1533(虎科虎菁一路) DS | LINE161 |  |  |  |  | CDC | 541 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | E3 | 1533E | [16 empty] | 1-39-06 | 1-39-07 | 1-7A | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1533E_ES | 1533E(虎科虎菁一路) ES | LINE161 |  |  |  |  | CDC | 542 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1540_PHA | 虎科虎菁二路(1540) 相間RY | LINE161 | D24/161/1540/PHA |  |  |  | CDC | 543 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1540_GDA | 虎科虎菁二路(1540) 接地RY | LINE161 | D24/161/1540/GDA |  |  |  | CDC | 544 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 虎菁DS.1540_87A | 虎科虎菁二路(1540) 87RY | LINE161 | D24/161/1540/87A |  |  |  | CDC | 545 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | 87UL | [17 empty] | 1-30-11 |  | 1-4B | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_87UL | 虎科虎菁二路(1540) 87RY U/L | LINE161 | D24/161/1540/87UL |  |  |  | CDC | 546 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 虎菁DS.1540_CB | 1540(虎科虎菁二路) CB | LINE161 | D24/161/1540/CB |  |  |  | CDC | 547 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | 79UL | [17 empty] | 1-30-13 |  | 1-4C | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_79UL | 虎科虎菁二路(1540) 79RY U/L | LINE161 | D24/161/1540/79UL |  |  |  | CDC | 548 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | DS1 | 1541 | [16 empty] | 1-39-08 | 1-39-09 | 1-7B | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1541_DS | 1541(虎科虎菁二路) DS | LINE161 |  |  |  |  | CDC | 549 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | DS2 | 1542 | [16 empty] | 1-39-10 | 1-39-11 | 1-7C | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1542_DS | 1542(虎科虎菁二路) DS | LINE161 |  |  |  |  | CDC | 550 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | DS3 | 1543 | [16 empty] | 1-39-12 | 1-39-13 | 1-7D | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1543_DS | 1543(虎科虎菁二路) DS | LINE161 |  |  |  |  | CDC | 551 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | E3 | 1543E | [16 empty] | 1-39-14 | 1-39-15 | 1-7E | [5 empty] | ADCS_N | [8 empty] | 虎菁DS.1543E_ES | 1543E(虎科虎菁二路) ES | LINE161 |  |  |  |  | CDC | 552 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D24 | 虎菁DS | 0 |  | 1530 | 虎科虎菁一路(1530) |  | 25TA | [17 empty] | 1-0E-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_25TA | 1530 同步校核電驛超時動作 | OTHER |  |  |  |  | CDC | 553 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1530 | 虎科虎菁一路(1530) |  | 87CFA | [17 empty] | 1-34-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_87CFA | 虎科虎菁一路(1530)87RY通訊故障 | OTHER |  |  |  |  | CDC | 554 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1530 | 虎科虎菁一路(1530) |  | DTTA | [17 empty] | 1-10-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_DTTA | 虎科虎菁一路(1530) 遠方遙跳 | OTHER |  |  |  |  | CDC | 555 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1530 | 虎科虎菁一路(1530) |  | RYFA | [17 empty] | 1-34-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_RYFA | 虎科虎菁一路(1530)數位電驛故障 | OTHER |  |  |  |  | CDC | 556 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1540 | 虎科虎菁二路(1540) |  | 25TA | [17 empty] | 1-0E-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_25TA | 1540 同步校核電驛超時動作 | OTHER |  |  |  |  | CDC | 557 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1540 | 虎科虎菁二路(1540) |  | 87CFA | [17 empty] | 1-34-05 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_87CFA | 虎科虎菁二路(1540)87RY通訊故障 | OTHER |  |  |  |  | CDC | 558 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1540 | 虎科虎菁二路(1540) |  | DTTA | [17 empty] | 1-10-05 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_DTTA | 虎科虎菁二路(1540) 遠方遙跳 | OTHER |  |  |  |  | CDC | 559 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1540 | 虎科虎菁二路(1540) |  | RYFA | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_RYFA | 虎科虎菁二路(1540)數位電驛故障 | OTHER |  |  |  |  | CDC | 560 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-37-12 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER |  |  |  |  | CDC | 561 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | 87CFA | [17 empty] | 1-33-15 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_87CFA | 斗南虎菁一路(1510)87RY通訊故障 | OTHER |  |  |  |  | CDC | 562 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | RYFA | [17 empty] | 1-34-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_RYFA | 斗南虎菁一路(1510)數位電驛故障 | OTHER |  |  |  |  | CDC | 563 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | 87CFA | [17 empty] | 1-34-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_87CFA | 斗南虎菁二路(1520)87RY通訊故障 | OTHER |  |  |  |  | CDC | 564 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | RYFA | [17 empty] | 1-34-02 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_RYFA | 斗南虎菁二路(1520)數位電驛故障 | OTHER |  |  |  |  | CDC | 565 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER |  |  |  |  | CDC | 566 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | COMM | 通訊處理單元 |  | SupLocal | [17 empty] | 2-34-09 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.COMM_S/L | 通訊處理單元 SUPY/LOCAL | OTHER |  |  |  |  | CDC | 567 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D24 | 虎菁DS | 0 |  | FEEDER | FEEDER |  | LOA | [17 empty] | 1-07-00 | [7 empty] | DDCS1_1 | [8 empty] | 虎菁DS.FEEDER_LOA | 饋線復閉失敗閉鎖警報 | OTHER |  |  |  |  | CDC | 568 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | MCCA | [17 empty] | 2-34-12 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.MCCA | MCC電驛故障 | OTHER |  |  |  |  | CDC | 569 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | PMCCA | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.PMCCA | PMCC電驛故障 | OTHER |  |  |  |  | CDC | 570 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | TCA | [17 empty] | 2-34-10 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.TCA | 斷路器跳脫回路故障 | OTHER |  |  |  |  | CDC | 571 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-37-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER |  |  |  |  | CDC | 572 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 集油池警報(1) | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.集油池警報(1) | 集油池水位警報(1) | OTHER |  |  |  |  | CDC | 573 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | 集油池警報(2) | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.集油池警報(2) | 集油池水位警報(2) | OTHER |  |  |  |  | CDC | 574 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | Door2 | [17 empty] | 1-37-14 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.無人化門禁(2) | 無人化門禁(2)建築物大小門 | OTHER |  |  |  |  | CDC | 575 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
D24 | 虎菁DS | 0 |  | 1510 | 斗南虎菁一路(1510) |  | RCA | [17 empty] | 1-05-06 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1510_RCA | 斗南虎菁一路 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 576 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1520 | 斗南虎菁二路(1520) |  | RCA | [17 empty] | 1-05-07 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1520_RCA | 斗南虎菁二路 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 577 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1530 | 虎科虎菁一路(1530) |  | RCA | [17 empty] | 1-06-00 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1530_RCA | 虎科虎菁一路 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 578 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | 1540 | 虎科虎菁二路(1540) |  | RCA | [17 empty] | 1-06-01 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.1540_RCA | 虎科虎菁二路 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 579 | GENERICDIPoint | DS046_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-36-05 |  | 3-1E | [5 empty] | DDCS1_1 | [8 empty] | 虎菁DS.開關場照明(B) | 路燈照明 | OTHER |  |  |  |  | CDC | 580 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D24 | 虎菁DS | 0 |  |  |  |  | GEN | [17 empty] | 2-34-14 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.GEN | 緊急發電機運轉 | OTHER |  |  |  |  | CDC | 581 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D24 | 虎菁DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER |  |  |  |  | CDC | 582 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER |  |  |  |  | CDC | 583 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D24 | 虎菁DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.OLTCA | OLTC 15分鐘連動3次 | OTHER |  |  |  |  | CDC | 584 | GENERICDIPoint | DS046_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | _1BPT | #1 |  | FR | [17 empty] | 2-34-08 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_#1BPT_FR | 161KV #1 BPT鐵磁共振警報 | OTHER |  |  |  |  | CDC | 585 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 161 | 161kV | _2BPT | #2 |  | FR | [17 empty] | 2-34-13 | [7 empty] | ADCS_N | [8 empty] | 虎菁DS.161KV_#2BPT_FR | 161KV #2 BPT鐵磁共振警報 | OTHER |  |  |  |  | CDC | 586 | GENERICDIPoint | DS046_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D24 | 虎菁DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 587 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 588 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 22 | 22kV | 210_SC | #1SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.210_SC_CAP | 23KV#1SC 容量 | SC | [5 empty] | 589 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 虎菁DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 590 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1510LE | 1510LE (非取樣點) | LINE161 | D24/161/1510/LE0 |  |  |  |  | 591 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1510 | 斗南虎菁一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1510BE | 1510BE (非取樣點) | LINE161 | D24/161/1510/BE0 |  |  |  |  | 592 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1520LE | 1520LE (非取樣點) | LINE161 | D24/161/1520/LE0 |  |  |  |  | 593 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1520 | 斗南虎菁二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1520BE | 1520BE (非取樣點) | LINE161 | D24/161/1520/BE0 |  |  |  |  | 594 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ21 | XJ21_DS |  | DS1 | XJ21_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_DS | XJ21_DS (非取樣點) | FEEDER | D24/11/XJ21/DS |  |  |  |  | 595 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ21 | XJ21_ES |  | LE0 | XJ21_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ21_ES | XJ21_ES (非取樣點) | FEEDER | D24/11/XJ21/ES |  |  |  |  | 596 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ22 | XJ22_DS |  | DS1 | XJ22_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_DS | XJ22_DS (非取樣點) | FEEDER | D24/11/XJ22/DS |  |  |  |  | 597 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ22 | XJ22_ES |  | LE0 | XJ22_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ22_ES | XJ22_ES (非取樣點) | FEEDER | D24/11/XJ22/ES |  |  |  |  | 598 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ23 | XJ23_DS |  | DS1 | XJ23_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_DS | XJ23_DS (非取樣點) | FEEDER | D24/11/XJ23/DS |  |  |  |  | 599 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ23 | XJ23_ES |  | LE0 | XJ23_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ23_ES | XJ23_ES (非取樣點) | FEEDER | D24/11/XJ23/ES |  |  |  |  | 600 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ24 | XJ24_DS |  | DS1 | XJ24_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_DS | XJ24_DS (非取樣點) | FEEDER | D24/11/XJ24/DS |  |  |  |  | 601 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ24 | XJ24_ES |  | LE0 | XJ24_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ24_ES | XJ24_ES (非取樣點) | FEEDER | D24/11/XJ24/ES |  |  |  |  | 602 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ25 | XJ25_DS |  | DS1 | XJ25_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_DS | XJ25_DS (非取樣點) | FEEDER | D24/11/XJ25/DS |  |  |  |  | 603 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ25 | XJ25_ES |  | LE0 | XJ25_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ25_ES | XJ25_ES (非取樣點) | FEEDER | D24/11/XJ25/ES |  |  |  |  | 604 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ26 | XJ26_DS |  | DS1 | XJ26_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_DS | XJ26_DS (非取樣點) | FEEDER | D24/11/XJ26/DS |  |  |  |  | 605 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ26 | XJ26_ES |  | LE0 | XJ26_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ26_ES | XJ26_ES (非取樣點) | FEEDER | D24/11/XJ26/ES |  |  |  |  | 606 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ27 | XJ27_DS |  | DS1 | XJ27_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_DS | XJ27_DS (非取樣點) | FEEDER | D24/11/XJ27/DS |  |  |  |  | 607 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ27 | XJ27_ES |  | LE0 | XJ27_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ27_ES | XJ27_ES (非取樣點) | FEEDER | D24/11/XJ27/ES |  |  |  |  | 608 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ28 | XJ28_DS |  | DS1 | XJ28_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_DS | XJ28_DS (非取樣點) | FEEDER | D24/11/XJ28/DS |  |  |  |  | 609 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ28 | XJ28_ES |  | LE0 | XJ28_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ28_ES | XJ28_ES (非取樣點) | FEEDER | D24/11/XJ28/ES |  |  |  |  | 610 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ29 | XJ29_DS |  | DS1 | XJ29_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_DS | XJ29_DS (非取樣點) | FEEDER | D24/11/XJ29/DS |  |  |  |  | 611 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ29 | XJ29_ES |  | LE0 | XJ29_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ29_ES | XJ29_ES (非取樣點) | FEEDER | D24/11/XJ29/ES |  |  |  |  | 612 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ30 | XJ30_DS |  | DS1 | XJ30_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_DS | XJ30_DS (非取樣點) | FEEDER | D24/11/XJ30/DS |  |  |  |  | 613 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ30 | XJ30_ES |  | LE0 | XJ30_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ30_ES | XJ30_ES (非取樣點) | FEEDER | D24/11/XJ30/ES |  |  |  |  | 614 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ51 | XJ51_DS |  | DS1 | XJ51_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_DS | XJ51_DS (非取樣點) | FEEDER | D24/22/XJ51/DS |  |  |  |  | 615 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ51 | XJ51_ES |  | LE0 | XJ51_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ51_ES | XJ51_ES (非取樣點) | FEEDER | D24/22/XJ51/ES |  |  |  |  | 616 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ52 | XJ52_DS |  | DS1 | XJ52_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_DS | XJ52_DS (非取樣點) | FEEDER | D24/22/XJ52/DS |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ52 | XJ52_ES |  | LE0 | XJ52_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ52_ES | XJ52_ES (非取樣點) | FEEDER | D24/22/XJ52/ES |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ53 | XJ53_DS |  | DS1 | XJ53_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_DS | XJ53_DS (非取樣點) | FEEDER | D24/22/XJ53/DS |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ53 | XJ53_ES |  | LE0 | XJ53_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ53_ES | XJ53_ES (非取樣點) | FEEDER | D24/22/XJ53/ES |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ54 | XJ54_DS |  | DS1 | XJ54_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_DS | XJ54_DS (非取樣點) | FEEDER | D24/22/XJ54/DS |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ54 | XJ54_ES |  | LE0 | XJ54_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ54_ES | XJ54_ES (非取樣點) | FEEDER | D24/22/XJ54/ES |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ55 | XJ55_DS |  | DS1 | XJ55_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_DS | XJ55_DS (非取樣點) | FEEDER | D24/22/XJ55/DS |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ55 | XJ55_ES |  | LE0 | XJ55_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ55_ES | XJ55_ES (非取樣點) | FEEDER | D24/22/XJ55/ES |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ56 | XJ56_DS |  | DS1 | XJ56_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_DS | XJ56_DS (非取樣點) | FEEDER | D24/22/XJ56/DS |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ56 | XJ56_ES |  | LE0 | XJ56_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ56_ES | XJ56_ES (非取樣點) | FEEDER | D24/22/XJ56/ES |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ57 | XJ57_DS |  | DS1 | XJ57_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_DS | XJ57_DS (非取樣點) | FEEDER | D24/22/XJ57/DS |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ57 | XJ57_ES |  | LE0 | XJ57_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ57_ES | XJ57_ES (非取樣點) | FEEDER | D24/22/XJ57/ES |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ58 | XJ58_DS |  | DS1 | XJ58_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_DS | XJ58_DS (非取樣點) | FEEDER | D24/22/XJ58/DS |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ58 | XJ58_ES |  | LE0 | XJ58_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ58_ES | XJ58_ES (非取樣點) | FEEDER | D24/22/XJ58/ES |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ59 | XJ59_DS |  | DS1 | XJ59_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_DS | XJ59_DS (非取樣點) | FEEDER | D24/22/XJ59/DS |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ59 | XJ59_ES |  | LE0 | XJ59_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ59_ES | XJ59_ES (非取樣點) | FEEDER | D24/22/XJ59/ES |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | XJ60 | XJ60_DS |  | DS1 | XJ60_DS | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_DS | XJ60_DS (非取樣點) | FEEDER | D24/22/XJ60/DS |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | XJ60 | XJ60_ES |  | LE0 | XJ60_ES | [24 empty] | DDCS1_1 | [8 empty] | 虎菁DS.XJ60_ES | XJ60_ES (非取樣點) | FEEDER | D24/22/XJ60/ES |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.101 | 101 (非取樣點) | TIE | D24/22/100/DS1 |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.102 | 102 (非取樣點) | TIE | D24/22/100/DS2 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1501E | 1501E (非取樣點) | TIE | D24/161/1500/ES1 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1502E | 1502E (非取樣點) | TIE | D24/161/1500/ES2 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.201 | 201 (非取樣點) | TIE | D24/11/200/DS1 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.202 | 202 (非取樣點) | TIE | D24/11/200/DS2 |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.391 | 391 (非取樣點) | OTHER | D24/22/390/DS1 |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.391E | 391E (非取樣點) | OTHER | D24/22/390/ES1 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.491 | 491 (非取樣點) | OTHER | D24/11/490/DS1 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.491E | 491E (非取樣點) | OTHER | D24/11/490/ES1 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1750TE | 1750TE (非取樣點) | MTR | D24/161/1750/TE0 |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1750BE | 1750BE (非取樣點) | MTR | D24/161/1750/BE0 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.311 | 311 (非取樣點) | MTR | D24/22/310/DS1 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.311E | 311E (非取樣點) | MTR | D24/22/310/ES1 |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.321 | 321 (非取樣點) | MTR | D24/11/320/DS1 |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.321E | 321E (非取樣點) | MTR | D24/11/320/ES1 |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1760TE | 1760TE (非取樣點) | MTR | D24/161/1760/TE0 |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1760BE | 1760BE (非取樣點) | MTR | D24/161/1760/BE0 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.331 | 331 (非取樣點) | MTR | D24/22/330/DS1 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.331E | 331E (非取樣點) | MTR | D24/22/330/ES1 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.341 | 341 (非取樣點) | MTR | D24/11/340/DS1 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.341E | 341E (非取樣點) | MTR | D24/11/340/ES1 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.221E | 221E (非取樣點) | SC | D24/11/220/ES1 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.221 | 221 (非取樣點) | SC | D24/11/220/DS1 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.241E | 241E (非取樣點) | SC | D24/11/240/ES1 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.241 | 241 (非取樣點) | SC | D24/11/240/DS1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.211E | 211E (非取樣點) | SC | D24/22/210/ES1 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.211 | 211 (非取樣點) | SC | D24/22/210/DS1 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.231E | 231E (非取樣點) | SC | D24/22/230/ES1 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.231 | 231 (非取樣點) | SC | D24/22/230/DS1 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.15B1E | 15B1E (非取樣點) | BUS | D24/161/1BUS/ES |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.15B2E | 15B2E (非取樣點) | BUS | D24/161/2BUS/ES |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 667 | NotelDIPoint | [38 empty] | START/STOP | STOP
D24 | 虎菁DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.101E | 101E(非取樣點) | OTHER | D24/22/100/ES1 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.102E | 102E(非取樣點) | OTHER | D24/22/100/ES2 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.201E | 201E(非取樣點) | OTHER | D24/11/200/ES1 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.202E | 202E(非取樣點) | OTHER | D24/11/200/ES2 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1530LE | 1530LE (非取樣點) | LINE161 | D24/161/1530/LE0 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1530 | 虎科虎菁一路(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1530BE | 1530BE (非取樣點) | LINE161 | D24/161/1530/BE0 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1540LE | 1540LE (非取樣點) | LINE161 | D24/161/1540/LE0 |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 161 | 161kV | 1540 | 虎科虎菁二路(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1540BE | 1540BE (非取樣點) | LINE161 | D24/161/1540/BE0 |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D24 | 虎菁DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D24 | 虎菁DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_N | [8 empty] | 虎菁DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo