## 版本
版本 | 20190702 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D25 | 延平DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | T/1SSTR |  | v | 0128 |  | 0015 | 1-10-00 |  | 1-0F | 390 | ON/OFF | 1SSTR 390 CB |  | aaab | B3/D25_A1 | [8 empty] | 延平DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 2 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | C/1SC |  | v | 0131 |  | 0017 | 2-00-03 |  | 1-11 | Locate Empty |  |  |  | aacb | B3/D25_A1 | [8 empty] | 延平DS.210_CB | 210(23KV #1SC) CB | SC | [5 empty] | 3 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA51/T1 |  | v | 0134 |  | 0018 | 1-10-06 |  | 1-12 | 平51線 | ON/OFF | 平51線 F1 KA51 CB |  | aadb | B2/D25_D1 | [8 empty] | 延平DS.KA51_CB | KA51(23KV平五一線) CB | FEEDER | [5 empty] | 4 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA52/T1 |  | v | 0137 |  | 0019 | 1-11-01 |  | 1-13 | 平52線 | ON/OFF | 平52線 F2 KA52 CB |  | aaeb | B2/D25_D1 | [8 empty] | 延平DS.KA52_CB | KA52(23KV平五二線) CB | FEEDER | [5 empty] | 5 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA53/T1 |  | v | 0140 |  | 0020 | 1-11-04 |  | 1-14 | 平53線 | ON/OFF | 平53線 F3 KA53 CB |  | aagb | B2/D25_D1 | [8 empty] | 延平DS.KA53_CB | KA53(23KV平五三線) CB | FEEDER | [5 empty] | 6 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA54/T1 |  | v | 0143 |  | 0021 | 1-11-07 |  | 1-15 | 平54線 | ON/OFF | 平54線 F4 KA54 CB |  | aahb | B2/D25_D1 | [8 empty] | 延平DS.KA54_CB | KA54(23KV平五四線) CB | FEEDER | [5 empty] | 7 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA55/T1 |  | v | 0146 |  | 0022 | 2-02-02 |  | 1-16 | Locate Empty |  |  |  | aaib | B2/D25_D1 | [8 empty] | 延平DS.KA55_CB | KA55(23KV平五五線) CB | FEEDER | [5 empty] | 8 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA56/T1 |  | v | 0149 |  | 0023 | 1-12-05 |  | 1-17 | 平56線 | ON/OFF | 平56線 F6 KA56 CB |  | aajb | B2/D25_D1 | [8 empty] | 延平DS.KA56_CB | KA56(23KV平五六線) CB | FEEDER | [5 empty] | 9 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA57/T1 |  | v | 0152 |  | 0024 | 2-03-00 |  | 1-18 | Locate Empty |  |  |  | aakb | B2/D25_D1 | [8 empty] | 延平DS.KA57_CB | KA57(23KV平五七線) CB | FEEDER | [5 empty] | 10 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1Bus | L/KA58/T1 |  | v | 0155 |  | 0025 | 2-03-03 |  | 1-19 | Locate Empty |  |  |  | aalb | B2/D25_D1 | [8 empty] | 延平DS.KA58_CB | KA58(23KV平五八線) CB | FEEDER | [5 empty] | 11 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | C/2SC |  | v | 0158 |  | 0026 | 2-03-06 |  | 1-1A | Locate Empty |  |  |  | aamb | B3/D25_A1 | [8 empty] | 延平DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 12 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1Bus | B/2ABus |  | v | 0161 |  | 0027 | 1-10-01 |  | 1-1B | 390 | PHA | 1SSTR 390 PHA |  | aanb | B3/D25_A1 | [8 empty] | 延平DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 13 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KA61/T1 |  | v | 0164 |  | 0028 | 1-14-04 |  | 1-1C | 平61線 | ON/OFF | 平61線 F9 KA61 CB |  | abab | B2/D25_D1 | [8 empty] | 延平DS.KA61_CB | KA61(23KV平六一線) CB | FEEDER | [5 empty] | 14 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KA62/T1 |  | v | 0167 |  | 0029 | 1-14-07 |  | 1-1D | 平62線 | ON/OFF | 平62線 F10 KA62 CB |  | abcb | B2/D25_D1 | [8 empty] | 延平DS.KA62_CB | KA62(23KV平六二線) CB | FEEDER | [5 empty] | 15 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KA63/T1 |  | v | 0170 |  | 0030 | 1-15-02 |  | 1-1E | 平63線 | ON/OFF | 平63線 F11 KA63 CB |  | abdb | B2/D25_D1 | [8 empty] | 延平DS.KA63_CB | KA63(23KV平六三線) CB | FEEDER | [5 empty] | 16 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KA64/T1 |  | v | 0173 |  | 0031 | 1-11-05 |  | 1-1F | 平53線 | PHA | 平53線 F3 KA53 PHA |  | abeb | B2/D25_D1 | [8 empty] | 延平DS.KA53_PHA | 23KV平五三線(KA53) 相間RY | FEEDER | [5 empty] | 17 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  | v | 0176 |  | 0032 | 1-12-00 |  | 1-20 | 平54線 | PHA | 平54線 F4 KA54 PHA |  | abfb | B3/D25_A1 | [8 empty] | 延平DS.KA54_PHA | 23KV平五四線(KA54) 相間RY | FEEDER | [5 empty] | 18 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  | v | 0179 |  | 0035 | 1-12-03 |  | 1-23 | 平55線 | PHA | 平55線 F5 KA55 PHA |  | acbb | B3/D25_A1 | [8 empty] | 延平DS.KA55_PHA | 23KV平五五線(KA55) 相間RY | FEEDER | [5 empty] | 19 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KA65/T1 |  | v | 0182 |  | 0036 | 1-16-06 |  | 1-24 | 平65線 | ON/OFF | 平65線 F13 KA65 CB |  | accb | B2/D25_D1 | [8 empty] | 延平DS.KA65_CB | KA65(23KV平六五線) CB | FEEDER | [5 empty] | 20 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KA66/T1 |  | v | 0185 |  | 0037 | 1-17-01 |  | 1-25 | 平66線 | ON/OFF | 平66線 F14 KA66 CB |  | acdb | B2/D25_D1 | [8 empty] | 延平DS.KA66_CB | KA66(23KV平六六線) CB | FEEDER | [5 empty] | 21 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KA67/T1 |  | v | 0188 |  | 0038 | 1-13-04 |  | 1-26 | 平58線 | PHA | 平58線 F8 KA58 PHA |  | aceb | B2/D25_D1 | [8 empty] | 延平DS.KA58_PHA | 23KV平五八線(KA58) 相間RY | FEEDER | [5 empty] | 22 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KA68/T1 |  | v | 0191 |  | 0039 | 1-13-07 |  | 1-27 | 220 | SCA | #2SC 220 SCA |  | acgb | B2/D25_D1 | [8 empty] | 延平DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 23 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/3Bus |  | v | 0194 |  | 0040 | 1-14-02 |  | 1-28 | #1TIE | PHA | #1TIE 100 PHA |  | achb | B3/D25_A1 | [8 empty] | 延平DS.100_51A | 23KV TIE(100) 51RY | TIE | [5 empty] | 24 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  | v | 0197 |  | 0041 | 1-14-05 |  | 1-29 | 平61線 | PHA | 平61線 F9 KA61 PHA |  | adab | B3/D25_A1 | [8 empty] | 延平DS.KA61_PHA | 23KV平六一線(KA61) 相間RY | FEEDER | [5 empty] | 25 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA71/T1 |  | v | 0200 |  | 0042 | 1-19-00 |  | 1-2A | 平71線 | ON/OFF | 平71線 F17 KA71 CB |  | adbb | B2/D25_D1 | [8 empty] | 延平DS.KA71_CB | KA71(23KV平七一線) CB | FEEDER | [5 empty] | 26 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA72/T1 |  | v | 0203 |  | 0043 | 1-19-03 |  | 1-2B | 平72線 | ON/OFF | 平72線 F18 KA72 CB |  | adcb | B2/D25_D1 | [8 empty] | 延平DS.KA72_CB | KA72(23KV平七二線) CB | FEEDER | [5 empty] | 27 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA73/T1 |  | v | 0206 |  | 0044 | 1-15-06 |  | 1-2C | 平64線 | PHA | 平64線 F12 KA64 PHA |  | addb | B2/D25_D1 | [8 empty] | 延平DS.KA64_PHA | 23KV平六四線(KA64) 相間RY | FEEDER | [5 empty] | 28 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA74/T1 |  | v | 0209 |  | 0045 | 1-16-01 |  | 1-2D | 230 | SCA | #3SC 230 SCA |  | adeb | B2/D25_D1 | [8 empty] | 延平DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 29 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA75/T1 |  | v | 0212 |  | 0046 | 1-16-04 |  | 1-2E | 240 | SCA | #4SC 240 SCA |  | adfb | B2/D25_D1 | [8 empty] | 延平DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 30 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA76/T1 |  | v | 0215 |  | 0047 | 1-1A-07 |  | 1-2F | 平76線 | ON/OFF | 平76線 F22 KA76 CB |  | adgb | B2/D25_D1 | [8 empty] | 延平DS.KA76_CB | KA76(23KV平七六線) CB | FEEDER | [5 empty] | 31 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA77/T1 |  | v | 0218 |  | 0048 | 1-1B-02 |  | 1-30 | 平77線 | ON/OFF | 平77線 F23 KA77 CB |  | adib | B2/D25_D1 | [8 empty] | 延平DS.KA77_CB | KA77(23KV平七七線) CB | FEEDER | [5 empty] | 32 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KA78/T1 |  | v | 0221 |  | 0049 | 1-1B-05 |  | 1-31 | 平78線 | ON/OFF | 平78線 F24 KA78 CB |  | adjb | B2/D25_D1 | [8 empty] | 延平DS.KA78_CB | KA78(23KV平七八線) CB | FEEDER | [5 empty] | 33 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  | v | 0224 |  | 0050 | 1-18-00 |  | 1-32 | 平68線 | PHA | 平68線 F16 KA68 PHA |  | adkb | B3/D25_A1 | [8 empty] | 延平DS.KA68_PHA | 23KV平六八線(KA68) 相間RY | FEEDER | [5 empty] | 34 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR |  | v | 0069 |  | 0051 | 1-08-05 |  | 1-33 | 350 | ON/OFF | #3DTR 350 CB |  | adla | ELEM/D25_A1 | [8 empty] | 延平DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 35 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/2SSTR |  | v | 0227 |  | 0052 | 1-1C-03 |  | 1-34 | 490 | ON/OFF | 2SSTR 490 CB |  | admb | B3/D25_A1 | [8 empty] | 延平DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 36 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | DS1 | 1561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0576 | 577 | 0112 | 1-34-00 | 1-34-01 | 1-70 | 1561 | ON/OFF | 忠孝延平線 1561 DS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1561_DS | 1561(忠孝延平線) DS | LINE161 | [5 empty] | 37 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | DS2 | 1562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0578 | 579 | 0113 | 1-34-02 | 1-34-03 | 1-71 | 1562 | ON/OFF | 忠孝延平線 1562 DS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1562_DS | 1562(忠孝延平線) DS | LINE161 | [5 empty] | 38 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | DS3 | 1563 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0580 | 581 | 0114 | 1-34-04 | 1-34-05 | 1-72 | 1563 | ON/OFF | 忠孝延平線 1563 DS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1563_DS | 1563(忠孝延平線) DS | LINE161 | [5 empty] | 39 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0584 | 585 | 0116 | 1-34-08 | 1-34-09 | 1-74 | 1551 | ON/OFF | 台南延平線 1551 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1551_DS | 1551(台南延平線) DS | LINE161 | [5 empty] | 40 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0586 | 587 | 0117 | 1-34-10 | 1-34-11 | 1-75 | 1552 | ON/OFF | 台南延平線 1552 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1552_DS | 1552(台南延平線) DS | LINE161 | [5 empty] | 41 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0588 | 589 | 0118 | 1-34-12 | 1-34-13 | 1-76 | 1553 | ON/OFF | 台南延平線 1553 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1553_DS | 1553(台南延平線) DS | LINE161 | [5 empty] | 42 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | DS1 | 1511 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0592 | 593 | 0120 | 1-35-00 | 1-35-01 | 1-78 | 1511 | ON/OFF | 延平健康線 1511 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1511_DS | 1511(健康線) DS | LINE161 | [5 empty] | 43 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | DS2 | 1512 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0594 | 595 | 0121 | 1-35-02 | 1-35-03 | 1-79 | 1512 | ON/OFF | 延平健康線 1512 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1512_DS | 1512(健康線) DS | LINE161 | [5 empty] | 44 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | DS3 | 1513 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0596 | 597 | 0122 | 1-35-04 | 1-35-05 | 1-7A | 1513 | ON/OFF | 延平健康線 1513 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1513_DS | 1513(健康線) DS | LINE161 | [5 empty] | 45 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0778 |  | 0160 | 2-32-10 |  | 2-20 | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D25_A1 | [8 empty] | 延平DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 46 |  |  |  |  | DI | [29 empty] | Auto/Man | Man | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0779 |  | 0161 | 2-32-11 |  | 2-21 | 火災警報(2) | A/N | 火災警報(2) |  |  | B3/D25_A1 | [8 empty] | 延平DS.火災警報(2) | 火災警報(2) | OTHER | [5 empty] | 47 |  |  |  |  | DI | [29 empty] | Auto/Man | Man | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0780 |  | 0162 | 2-32-12 |  | 2-22 | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/D25_A1 | [8 empty] | 延平DS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 48 |  |  |  |  | DI | [29 empty] | Auto/Man | Man | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0781 |  | 0163 | 2-32-13 |  | 2-23 | Locate Empty | A/N | 保全系統 |  |  | B3/D25_A1 | [8 empty] | 延平DS.無人化防盜(1) | 無人化防盜(1)保全 | OTHER | [5 empty] | 49 |  |  |  |  | DI | [29 empty] | Auto/Man | Man | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0783 |  | 0165 | 2-32-15 |  | 2-25 | Locate Empty | A/N | #2DTR變壓器監視用IED故障（資產管理） |  |  | B3/D25_A1 | [8 empty] | 延平DS.IEDA | 變壓器資產管理監視IED故障 | OTHER | [5 empty] | 50 |  |  |  |  | DI | [29 empty] | Auto/Man | Man | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [5 empty] | v | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 延平DS.TEST_CB | TEST CB | OTHER | [5 empty] | 51 |  |  |  |  | DI | [29 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D18D25/T2 | v | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1560 | ON/OFF | 忠孝延平線 1560 CB |  | aaba | B2/D25_A1 | [8 empty] | 延平DS.1560_CB | 1560(忠孝延平線) CB | LINE161 | [5 empty] | 52 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P07D25/T2 | v | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1550 | ON/OFF | 台南延平線 1550 CB |  | aaea | B2/D25_A1 | [8 empty] | 延平DS.1550_CB | 1550(台南延平線) CB | LINE161 | [5 empty] | 53 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 | v | 0010 |  | 0003 | 1-01-02 |  | 1-03 | 1510 | ON/OFF | 延平健康線 1510 CB |  | aaha | B2/D25_A1 | [8 empty] | 延平DS.1510_CB | 1510(健康線) CB | LINE161 | [5 empty] | 54 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  | v | 0040 |  | 0009 | 1-05-00 |  | 1-09 | 1500 | ON/OFF | 161KV TIE 1500 CB |  | aafz | B2/D25_A1 | [8 empty] | 延平DS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 55 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR | v | 0045 |  | 0010 | 1-05-05 |  | 1-0A | 1750 | ON/OFF | #1DTR 1750 CB |  | aaab | ELEM/D25_A1 | [8 empty] | 延平DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 56 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR | v | 0053 |  | 0011 | 1-06-05 |  | 1-0B | #2DTR | ON/OFF | #2DTR 1760 CB |  | aadb | ELEM/D25_A1 | [8 empty] | 延平DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 57 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR | v | 0063 |  | 0012 | 1-07-07 |  | 1-0C | #3DTR | ON/OFF | #3DTR 1770 CB |  | aagb | ELEM/D25_A1 | [8 empty] | 延平DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 58 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1Bus | T/1DTR |  | v | 0051 |  | 0016 | 1-06-03 |  | 1-10 | 310 | ON/OFF | #1DTR 310 CB |  | aaba | ELEM/D25_A1 | [8 empty] | 延平DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 59 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/340^T/2DTR(A) |  | v | 0059 |  | 0033 | 1-07-03 |  | 1-21 | 330 | ON/OFF | #2DTR 2A 330 CB |  | abga | ELEM/D25_A1 | [8 empty] | 延平DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 60 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/330^T/2DTR(B) |  | v | 0061 |  | 0034 | 1-07-05 |  | 1-22 | 340 | ON/OFF | #2DTR 2B 340 CB |  | acaa | ELEM/D25_A1 | [8 empty] | 延平DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 61 |  |  |  |  | DI | [29 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0514 |  | 0064 | 1-30-02 |  | 1-40 | 1560 | U/L | 忠孝延平線 1560 #1 87RY U/L |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_87UL1 | 忠孝延平線(1560)#1 87RY U/L | OTHER | [5 empty] | 62 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0515 |  | 0065 | 1-30-03 |  | 1-41 | 1560 | U/L | 忠孝延平線 1560 79 RY U/L |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_79UL | 忠孝延平線(1560) 79RY U/L | LINE161 | [5 empty] | 63 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0516 |  | 0066 | 1-30-04 |  | 1-42 | 1550 | U/L | 台南延平線 1550 87RY U/L |  |  | B2/D25_A1 | [8 empty] | 延平DS.1550_87UL | 台南延平線(1550) 87RY U/L | LINE161 | [5 empty] | 64 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0517 |  | 0067 | 1-30-05 |  | 1-43 | 1550 | U/L | 台南延平線 1550 79 RY U/L |  |  | B2/D25_A1 | [8 empty] | 延平DS.1550_79UL | 台南延平線(1550) 79RY U/L | LINE161 | [5 empty] | 65 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0518 |  | 0068 | 1-30-06 |  | 1-44 | 1510 | U/L | 延平健康線 1510 85MRY U/L |  |  | B2/D25_A1 | [8 empty] | 延平DS.1510_85UL | 健康線(1510) 85RY U/L | LINE161 | [5 empty] | 66 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0519 |  | 0069 | 1-30-07 |  | 1-45 | 1560 | U/L | 忠孝延平線 1560 #2 87RY U/L |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_87UL2 | 忠孝延平線(1560)#2 87RY U/L | OTHER | [5 empty] | 67 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0552 |  | 0070 | 1-32-08 |  | 1-46 | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/D25_A1 | [8 empty] | 延平DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 68 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0553 |  | 0071 | 1-32-09 |  | 1-47 | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/D25_A1 | [8 empty] | 延平DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 69 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS |  |  | 1DTR | #1DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [5 empty] | v | 0556 |  | 0096 | 1-97 |  | 1-61 | #1DTR | 升/降 | #1DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | [5 empty] | 70 |  |  |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS |  |  | 1DTR | #1DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [5 empty] | v | 0023 |  | 0097 | 1-97 |  | 1-61 | #1DTR | 升/降 | #1DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | [5 empty] | 71 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS |  |  | 2DTR | #2DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [5 empty] | v | 0561 |  | 0098 | 1-9A |  | 1-63 | #2DTR | 升/降 | #2DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | [5 empty] | 72 |  |  |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [5 empty] | v | 0026 |  | 0099 | 1-9A |  | 1-63 | #2DTR | 升/降 | #2DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | [5 empty] | 73 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [5 empty] | v | 0566 |  | 0100 | 1-9D |  | 1-65 | #3DTR | 升/降 | #3DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 74 |  |  |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [5 empty] | v | 0029 |  | 0101 | 1-9D |  | 1-65 | #3DTR | 升/降 | #3DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 75 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0554 |  | 0102 | 1-32-10 |  | 1-66 | #1DTR | U/L | #1DTR 87 閉鎖開關 |  |  | B1/D25_A1 | [8 empty] | 延平DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | [5 empty] | 76 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0768 |  | 0103 | 2-32-00 |  | 1-67 | 平71線 | U/L | 平71線 F17 KA71 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA71_LCO_TAP | 23KV平七一線(KA71) LCO TAP | FEEDER | [5 empty] | 77 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0769 |  | 0104 | 2-32-01 |  | 1-68 | 平72線 | U/L | 平72線 F18 KA72 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA72_LCO_TAP | 23KV平七二線(KA72) LCO TAP | FEEDER | [5 empty] | 78 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0559 |  | 0105 | 1-32-15 |  | 1-69 | #2DTR | U/L | #2DTR 87 閉鎖開關 |  |  | B1/D25_A1 | [8 empty] | 延平DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | [5 empty] | 79 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0771 |  | 0106 | 2-32-03 |  | 1-6A | 平74線 | U/L | 平74線F20 KA74 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA74_LCO_TAP | 23KV平七四線(KA74) LCO TAP | FEEDER | [5 empty] | 80 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0772 |  | 0107 | 2-32-04 |  | 1-6B | 平75線 | U/L | 平75線 F21 KA75 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA75_LCO_TAP | 23KV平七五線(KA75) LCO TAP | FEEDER | [5 empty] | 81 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0564 |  | 0108 | 1-33-04 |  | 1-6C | #3DTR | U/L | #3DTR 87 閉鎖開關 |  |  | B1/D25_A1 | [8 empty] | 延平DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | [5 empty] | 82 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0774 |  | 0109 | 2-32-06 |  | 1-6D | 平77線 | U/L | 平77線 F23 KA77 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA77_LCO_TAP | 23KV平七七線(KA77) LCO TAP | FEEDER | [5 empty] | 83 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [5 empty] | v | 0775 |  | 0110 | 2-32-07 |  | 1-6E | 平78線 | U/L | 平78線 F24 KA78 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA78_LCO_TAP | 23KV平七八線(KA78) LCO TAP | FEEDER | [5 empty] | 84 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0582 | 583 | 0115 | 1-34-06 | 1-34-07 | 1-73 | 1563E | ON/OFF | 忠孝延平線 1563E DS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1563E_ES | 1563E(忠孝延平線) ES | LINE161 | [5 empty] | 85 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0590 | 591 | 0119 | 1-34-14 | 1-34-15 | 1-77 | 1553E | ON/OFF | 台南延平線 1553E ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1553E_ES | 1553E(台南延平線) ES | LINE161 | [5 empty] | 86 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0598 | 599 | 0123 | 1-35-06 | 1-35-07 | 1-7B | 1513E | ON/OFF | 延平健康線 1513E ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1513E_ES | 1513E(健康線) ES | LINE161 | [5 empty] | 87 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0896 | 897 | 0144 | 2-38-00 | 2-38-01 | 2-10 | 1501 | ON/OFF | 161KV 1501 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 88 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0898 | 899 | 0145 | 2-38-02 | 2-38-03 | 2-11 | 1502 | ON/OFF | 161KV 1502 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 89 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0900 | 901 | 0146 | 2-38-04 | 2-38-05 | 2-12 | 1751 | ON/OFF | #1DTR 1751 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 90 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0902 | 903 | 0147 | 2-38-06 | 2-38-07 | 2-13 | 1752 | ON/OFF | #1DTR 1752 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 91 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0904 | 905 | 0148 | 2-38-08 | 2-38-09 | 2-14 | 1761 | ON/OFF | #2DTR 1761 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 92 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0906 | 907 | 0149 | 2-38-10 | 2-38-11 | 2-15 | 1762 | ON/OFF | #2DTR 1762 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 93 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0908 | 909 | 0150 | 2-38-12 | 2-38-13 | 2-16 | 1771 | ON/OFF | #3DTR 1771 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 94 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [5 empty] | v | 0910 | 911 | 0151 | 2-38-14 | 2-38-15 | 2-17 | 1772 | ON/OFF | #3DTR 1772 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 95 |  |  |  |  | DI | [29 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [5 empty] | v | 0782 |  | 0164 | 2-32-14 |  | 2-24 | Locate Empty | A/N | 無人化防盜(2) |  |  | B3/D25_A1 | [8 empty] | 延平DS.無人化防盜(2) | 無人化防盜(2) | OTHER | [5 empty] | 96 |  |  |  |  | DI | [29 empty] | Auto/Man | Man | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0784 |  | 0166 | 2-33-00 |  | 2-26 | Locate Empty | A/N | 圍牆小門(1) |  |  | B2/D25_D1 | [8 empty] | 延平DS.無人化門禁(1) | 無人化門禁(1)圍牆小門 | OTHER | [5 empty] | 97 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0785 |  | 0167 | 2-31-01 |  | 2-27 | 平52線 | U/L | 平52線 F2 KA52 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA52_LCO_TAP | 23KV平五二線(KA52) LCO TAP | FEEDER | [5 empty] | 98 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0786 |  | 0168 | 2-31-02 |  | 2-28 | 平53線 | U/L | 平53線 F3 KA53 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA53_LCO_TAP | 23KV平五三線(KA53) LCO TAP | FEEDER | [5 empty] | 99 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0787 |  | 0169 | 2-31-03 |  | 2-29 | 平54線 | U/L | 平54線 F4 KA54 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA54_LCO_TAP | 23KV平五四線(KA54) LCO TAP | FEEDER | [5 empty] | 100 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0788 |  | 0170 | 2-33-04 |  | 2-2A | Locate Empty | ON/OFF | 開關場照明(B) |  |  | B2/D25_D1 | [8 empty] | 延平DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 101 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | ON/OFF | OFF
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0789 |  | 0171 | 2-31-05 |  | 2-2B | 平56線 | U/L | 平56線 F6 KA56 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA56_LCO_TAP | 23KV平五六線(KA56) LCO TAP | FEEDER | [5 empty] | 102 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0790 |  | 0172 | 2-33-06 |  | 2-2C | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B2/D25_D1 | [8 empty] | 延平DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 103 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | ON/OFF | ON
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0791 |  | 0173 | 2-33-07 |  | 2-2D | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B2/D25_D1 | [8 empty] | 延平DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 104 |  |  |  |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | ON/OFF | ON
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0792 |  | 0174 | 2-31-08 |  | 2-2E | 平61線 | U/L | 平61線 F9 KA61 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA61_LCO_TAP | 23KV平六一線(KA61) LCO TAP | FEEDER | [5 empty] | 105 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0793 |  | 0175 | 2-31-09 |  | 2-2F | 平62線 | U/L | 平62線 F10 KA62 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA62_LCO_TAP | 23KV平六二線(KA62) LCO TAP | FEEDER | [5 empty] | 106 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0794 |  | 0176 | 2-31-10 |  | 2-30 | 平63線 | U/L | 平63線 F11 KA63 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA63_LCO_TAP | 23KV平六三線(KA63) LCO TAP | FEEDER | [5 empty] | 107 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0795 |  | 0177 | 2-33-11 |  | 2-31 | DCA | A/N | 直流電源故障 (DCA) |  |  | B2/D25_D1 | [8 empty] | 延平DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 108 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0796 |  | 0178 | 2-31-12 |  | 2-32 | 平65線 | U/L | 平65線 F13 KA65 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA65_LCO_TAP | 23KV平六五線(KA65) LCO TAP | FEEDER | [5 empty] | 109 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0797 |  | 0179 | 2-31-13 |  | 2-33 | 平66線 | U/L | 平66線 F14 KA66 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA66_LCO_TAP | 23KV平六六線(KA66) LCO TAP | FEEDER | [5 empty] | 110 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0798 |  | 0180 | 2-33-14 |  | 2-34 | DCE | A/N | 直流接地 (DCE) |  |  | B2/D25_D1 | [8 empty] | 延平DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 111 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0799 |  | 0181 | 2-33-15 |  | 2-35 | Locate Empty | A/N | 空壓機超時 |  |  | B2/D25_D1 | [8 empty] | 延平DS.空壓機COMT | 空壓機運轉超時警報 | OTHER | [5 empty] | 112 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0800 |  | 0182 | 2-32-00 |  | 2-36 | 平71線 | U/L | 平71線 F17 KA71 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA71_LCO_TAP | 23KV平七一線(KA71) LCO TAP | FEEDER | [5 empty] | 113 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0801 |  | 0183 | 2-32-01 |  | 2-37 | 平72線 | U/L | 平72線 F18 KA72 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA72_LCO_TAP | 23KV平七二線(KA72) LCO TAP | FEEDER | [5 empty] | 114 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0802 |  | 0184 | 2-34-02 |  | 2-38 | A/N |  | 22KV CB重故障 |  |  | B2/D25_D1 | [8 empty] | 延平DS.23KV_CBA | 23KV斷路器重故障 | OTHER | [5 empty] | 115 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0803 |  | 0185 | 2-34-03 |  | 2-39 | A/N |  | 22KV CB輕故障 |  |  | B2/D25_D1 | [8 empty] | 延平DS.23KV_CBF | 23KV斷路器輕故障 | OTHER | [5 empty] | 116 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0804 |  | 0186 | 2-34-04 |  | 2-3A | A/N |  | 其他重故障 |  |  | B2/D25_D1 | [8 empty] | 延平DS.其他重故障 | 變電所內其他重故障 | OTHER | [5 empty] | 117 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0805 |  | 0187 | 2-32-05 |  | 2-3B | 平76線 | U/L | 平76線 F22 KA76 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA76_LCO_TAP | 23KV平七六線(KA76) LCO TAP | FEEDER | [5 empty] | 118 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0806 |  | 0188 | 2-32-06 |  | 2-3C | 平77線 | U/L | 平77線 F23 KA77 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA77_LCO_TAP | 23KV平七七線(KA77) LCO TAP | FEEDER | [5 empty] | 119 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [5 empty] | v | 0807 |  | 0189 | 2-32-07 |  | 2-3D | 平78線 | U/L | 平78線 F24 KA78 LCO分流器 |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA78_LCO_TAP | 23KV平七八線(KA78) LCO TAP | FEEDER | [5 empty] | 120 |  |  |  |  | DI | [29 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 390 | PHA | 1SSTR 390 PHA |  |  | B3/D25_A1 | [8 empty] | 延平DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 121 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0132 |  |  | 2-00-04 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | 延平DS.210_SCA | 23KV #1SC 51,51N RY | SC | [5 empty] | 122 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 平51線 | PHA | 平51線 F1 KA51 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA51_PHA | 23KV平五一線(KA51) 相間RY | FEEDER | [5 empty] | 123 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 1-11-02 |  |  | 平52線 | PHA | 平52線 F2 KA52 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA52_PHA | 23KV平五二線(KA52) 相間RY | FEEDER | [5 empty] | 124 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | 平53線 | PHA | 平53線 F3 KA53 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA53_PHA | 23KV平五三線(KA53) 相間RY | FEEDER | [5 empty] | 125 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 1-12-00 |  |  | 平54線 | PHA | 平54線 F4 KA54 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA54_PHA | 23KV平五四線(KA54) 相間RY | FEEDER | [5 empty] | 126 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 2-02-03 |  |  | Locate Empty |  |  |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA55_PHA | 23KV平五五線(KA55) 相間RY | FEEDER | [5 empty] | 127 |  |  |  |  | DI | D_P_KEY | [28 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 平56線 | PHA | 平56線 F6 KA56 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA56_PHA | 23KV平五六線(KA56) 相間RY | FEEDER | [5 empty] | 128 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0153 |  |  | 1-13-01 |  |  | Locate Empty |  |  |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA57_PHA | 23KV平五七線(KA57) 相間RY | FEEDER | [5 empty] | 129 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 2-03-04 |  |  | Locate Empty |  |  |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA58_PHA | 23KV平五八線(KA58) 相間RY | FEEDER | [5 empty] | 130 |  |  |  |  | DI | D_P_KEY | [28 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0159 |  |  | 2-03-07 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | 延平DS.220_SCA | 23KV #2SC 51,51N RY | SC | [5 empty] | 131 |  |  |  |  | DI | D_P_KEY | [28 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-10-02 |  |  | 390 | GDA | 1SSTR 390 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 132 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 平61線 | PHA | 平61線 F9 KA61 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA61_PHA | 23KV平六一線(KA61) 相間RY | FEEDER | [5 empty] | 133 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 平62線 | PHA | 平62線 F10 KA62 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA62_PHA | 23KV平六二線(KA62) 相間RY | FEEDER | [5 empty] | 134 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 平63線 | PHA | 平63線 F11 KA63 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA63_PHA | 23KV平六三線(KA63) 相間RY | FEEDER | [5 empty] | 135 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-11-06 |  |  | 平53線 | GDA | 平53線 F3 KA53 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA53_GDA | 23KV平五三線(KA53) 接地RY | FEEDER | [5 empty] | 136 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0177 |  |  | 1-12-01 |  |  | 平54線 | GDA | 平54線 F4 KA54 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA54_GDA | 23KV平五四線(KA54) 接地RY | FEEDER | [5 empty] | 137 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0180 |  |  | 1-12-04 |  |  | 平55線 | GDA | 平55線 F5 KA55 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA55_GDA | 23KV平五五線(KA55) 接地RY | FEEDER | [5 empty] | 138 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 平65線 | PHA | 平65線 F13 KA65 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA65_PHA | 23KV平六五線(KA65) 相間RY | FEEDER | [5 empty] | 139 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 平66線 | PHA | 平66線 F14 KA66 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA66_PHA | 23KV平六六線(KA66) 相間RY | FEEDER | [5 empty] | 140 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-13-05 |  |  | 平58線 | GDA | 平58線 F8 KA58 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA58_GDA | 23KV平五八線(KA58) 接地RY | FEEDER | [5 empty] | 141 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-14-00 |  |  | 220 | UVA | #2SC 220 UVA |  |  | B2/D25_D1 | [8 empty] | 延平DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | [5 empty] | 142 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-14-03 |  |  | #1TIE | GDA | #1TIE 100 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.100_51NA | 23KV TIE(100) 51N RY | TIE | [5 empty] | 143 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | 1512 | ON/OFF | 延平健康線 1512 ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1512_DS | 1512(健康線) DS | LINE161 | [5 empty] | 144 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | 1513 | ON/OFF | 延平健康線 1513 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1513_DS | 1513(健康線) DS | LINE161 | [5 empty] | 145 |  |  |  |  | DI | [29 empty] | Normal/Fault |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-34-10 |  |  | PCM |  | 通信室溫控警報 |  |  | B3/D25_A1 | [8 empty] | 延平DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 146 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 2-34-11 |  |  | OW1 |  | OW1水位警報1 |  |  | B3/D25_A1 | [8 empty] | 延平DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | [5 empty] | 147 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 148 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 149 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 150 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 151 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 152 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 153 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 154 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 155 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 156 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 157 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | DS1 | 311(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.311 | 311 (非取樣點) | MTR | [5 empty] | 158 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.311E | 311E (非取樣點) | MTR | [5 empty] | 159 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 160 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 161 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | DS1 | 331(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.331 | 331 (非取樣點) | MTR | [5 empty] | 162 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.331E | 331E (非取樣點) | MTR | [5 empty] | 163 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | DS1 | 341(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.341 | 341 (非取樣點) | MTR | [5 empty] | 164 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.341E | 341E (非取樣點) | MTR | [5 empty] | 165 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 166 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_A1 | [8 empty] | 延平DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 167 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | DS1 | 351(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.351 | 351 (非取樣點) | MTR | [5 empty] | 168 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.351E | 351E (非取樣點) | MTR | [5 empty] | 169 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 390 | #1SSTR(390) |  | DS1 | 391(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 170 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 171 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.211E | 211E (非取樣點) | SC | [5 empty] | 172 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | ES | 210_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.210SC_ES | 210SC_ES (非取樣點) | SC | [5 empty] | 173 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | DS1 | 211(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.211 | 211 (非取樣點) | SC | [5 empty] | 174 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA51_DS | KA51_DS (非取樣點) | FEEDER | [5 empty] | 175 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA51_ES | KA51_ES (非取樣點) | FEEDER | [5 empty] | 176 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA52_DS | KA52_DS (非取樣點) | FEEDER | [5 empty] | 177 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA52_ES | KA52_ES (非取樣點) | FEEDER | [5 empty] | 178 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA53_DS | KA53_DS (非取樣點) | FEEDER | [5 empty] | 179 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA53_ES | KA53_ES (非取樣點) | FEEDER | [5 empty] | 180 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA54_DS | KA54_DS (非取樣點) | FEEDER | [5 empty] | 181 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA54_ES | KA54_ES (非取樣點) | FEEDER | [5 empty] | 182 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA55_DS | KA55_DS (非取樣點) | FEEDER | [5 empty] | 183 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA55_ES | KA55_ES (非取樣點) | FEEDER | [5 empty] | 184 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA56_DS | KA56_DS (非取樣點) | FEEDER | [5 empty] | 185 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA56_ES | KA56_ES (非取樣點) | FEEDER | [5 empty] | 186 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA57_DS | KA57_DS (非取樣點) | FEEDER | [5 empty] | 187 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA57_ES | KA57_ES (非取樣點) | FEEDER | [5 empty] | 188 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | DS | (非取樣點) | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA58_DS | KA58_DS (非取樣點) | FEEDER | [5 empty] | 189 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA58_ES | KA58_ES (非取樣點) | FEEDER | [5 empty] | 190 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.221E | 221E (非取樣點) | SC | [5 empty] | 191 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | ES | 220_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.220SC_ES | 220SC_ES (非取樣點) | SC | [5 empty] | 192 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | DS1 | 221(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.221 | 221 (非取樣點) | SC | [5 empty] | 193 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | DS1 | 101(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.101 | 101 (非取樣點) | TIE | [5 empty] | 194 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | DS2 | 102(非取樣點) |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.102 | 102 (非取樣點) | TIE | [5 empty] | 195 | [34 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 196 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 197 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA61_DS | KA61_DS (非取樣點) | FEEDER | [5 empty] | 198 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA61_ES | KA61_ES (非取樣點) | FEEDER | [5 empty] | 199 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA62_DS | KA62_DS (非取樣點) | FEEDER | [5 empty] | 200 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA62_ES | KA62_ES (非取樣點) | FEEDER | [5 empty] | 201 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA63_DS | KA63_DS (非取樣點) | FEEDER | [5 empty] | 202 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA63_ES | KA63_ES (非取樣點) | FEEDER | [5 empty] | 203 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA64_DS | KA64_DS (非取樣點) | FEEDER | [5 empty] | 204 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA64_ES | KA64_ES (非取樣點) | FEEDER | [5 empty] | 205 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.231E | 231E (非取樣點) | SC | [5 empty] | 206 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | ES | 230_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.230SC_ES | 230SC_ES (非取樣點) | SC | [5 empty] | 207 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.231 | 231 (非取樣點) | SC | [5 empty] | 208 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.241E | 241E (非取樣點) | SC | [5 empty] | 209 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | ES | 240_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.240SC_ES | 240SC_ES (非取樣點) | SC | [5 empty] | 210 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.241 | 241 (非取樣點) | SC | [5 empty] | 211 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA65_DS | KA65_DS (非取樣點) | FEEDER | [5 empty] | 212 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA65_ES | KA65_ES (非取樣點) | FEEDER | [5 empty] | 213 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA66_DS | KA66_DS (非取樣點) | FEEDER | [5 empty] | 214 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA66_ES | KA66_ES (非取樣點) | FEEDER | [5 empty] | 215 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA67_DS | KA67_DS (非取樣點) | FEEDER | [5 empty] | 216 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA67_ES | KA67_ES (非取樣點) | FEEDER | [5 empty] | 217 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA68_DS | KA68_DS (非取樣點) | FEEDER | [5 empty] | 218 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA68_ES | KA68_ES (非取樣點) | FEEDER | [5 empty] | 219 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.201 | 201 (非取樣點) | TIE | [5 empty] | 220 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.202 | 202 (非取樣點) | TIE | [5 empty] | 221 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 222 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.202E | 202E(非取樣點) | OTHER | [5 empty] | 223 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.261E | 261E (非取樣點) | SC | [5 empty] | 224 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | ES | 260_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 225 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.261 | 261 (非取樣點) | SC | [5 empty] | 226 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA71_DS | KA71_DS (非取樣點) | FEEDER | [5 empty] | 227 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA71_ES | KA71_ES (非取樣點) | FEEDER | [5 empty] | 228 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA72_DS | KA72_DS (非取樣點) | FEEDER | [5 empty] | 229 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA72_ES | KA72_ES (非取樣點) | FEEDER | [5 empty] | 230 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA73_DS | KA73_DS (非取樣點) | FEEDER | [5 empty] | 231 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA73_ES | KA73_ES (非取樣點) | FEEDER | [5 empty] | 232 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA74_DS | KA74_DS (非取樣點) | FEEDER | [5 empty] | 233 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA74_ES | KA74_ES (非取樣點) | FEEDER | [5 empty] | 234 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA75_DS | KA75_DS (非取樣點) | FEEDER | [5 empty] | 235 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA75_ES | KA75_ES (非取樣點) | FEEDER | [5 empty] | 236 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA76_DS | KA76_DS (非取樣點) | FEEDER | [5 empty] | 237 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA76_ES | KA76_ES (非取樣點) | FEEDER | [5 empty] | 238 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA77_DS | KA77_DS (非取樣點) | FEEDER | [5 empty] | 239 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA77_ES | KA77_ES (非取樣點) | FEEDER | [5 empty] | 240 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA78_DS | KA78_DS (非取樣點) | FEEDER | [5 empty] | 241 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D25_D1 | [8 empty] | 延平DS.KA78_ES | KA78_ES (非取樣點) | FEEDER | [5 empty] | 242 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.251E | 251E (非取樣點) | SC | [5 empty] | 243 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | ES | 250_ES | DEL | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 244 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.251 | 251 (非取樣點) | SC | [5 empty] | 245 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 246 | [34 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D25_A1 | [8 empty] | 延平DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 247 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aacz | B2/D25_A1 | [8 empty] | 延平DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 248 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aacz | B2/D25_A1 | [8 empty] | 延平DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 249 | [34 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-34-12 |  |  | OW1 |  | OW1水位警報2 |  |  | B3/D25_A1 | [8 empty] | 延平DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | [5 empty] | 250 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全系統 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0813 |  |  | 2-34-13 |  |  | 1560 | A/N | 忠孝延平線 1560 87CFA (87L通訊故障) |  |  | B3/D25_A1 | [8 empty] | 延平DS.1560_87CFA | 忠孝延平線(1560)87RY通訊故障 | OTHER | [5 empty] | 251 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | ComPoint |  |  | IRFA | 資產管理 |  | Status | IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0815 |  |  | 2-34-15 |  |  | 1510 R7 |  | 延平健康線 74A |  |  | B3/D25_A1 | [8 empty] | 延平DS.1510_74A | 健康線(1510) 74RY | LINE161 | [5 empty] | 252 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 221 | 232 | 243 | 10 | 190 | 179 | 168 | 157 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1821 | 1832 | 1843 | 10 | 1790 | 1779 | 1768 | 1757 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/D25_A1 | [8 empty] | 延平DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168.5 | 170 | 210 | 0.5 | 155 | 153.5 | 152 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D25 | 延平DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/D25_A1 | [8 empty] | 延平DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168.5 | 170 | 210 | 0.5 | 155 | 153.5 | 152 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1560 | MW | 忠孝延平線 1560 瓦 | MW_-560_560(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1560_MW | 忠孝延平線 MW | LINE161 | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1560 | MVAR | 忠孝延平線 1560 乏 | MVAR_-560_560(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1560_MVAR | 忠孝延平線 MVAR | LINE161 | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1550 | MW | 台南延平線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1550_MW | 台南延平線 MW | LINE161 | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1550 | MVAR | 台南延平線 1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1550_MVAR | 台南延平線 MVAR | LINE161 | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1510 | MW | 延平健康線 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1510_MW | 健康線 MW | LINE161 | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1510 | MVAR | 延平健康線 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1510_MVAR | 健康線 MVAR | LINE161 | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0010 | 10 |  | 1-8A | 1-8A |  | 1550 | KG | 1550 台南延平線 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1550_OF_R | 台南延平線 R相 油壓 | OTHER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0011 | 11 |  | 1-8B | 1-8B |  | 1550 | KG | 1550 台南延平線 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1550_OF_S | 台南延平線 S相 油壓 | OTHER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0012 | 12 |  | 1-8C | 1-8C |  | 1550 | KG | 1550 台南延平線 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1550_OF_T | 台南延平線 T相 油壓 | OTHER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1560 |  | 1560 忠孝延平線 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1560_OF_R | 忠孝延平線 R相 油壓 | OTHER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1560 |  | 1560 忠孝延平線 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1560_OF_S | 忠孝延平線 S相 油壓 | OTHER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1560 |  | 1560 忠孝延平線 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1560_OF_T | 忠孝延平線 T相 油壓 | OTHER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | DC | V | P-E (DC) | kV_-150_150(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71.2 | 75 | 150 | 0.2 | 60 | 58.8 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | DC | V | N-E (DC) | kV_-150_150(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -58.8 | -55 | 150 | 0.2 | -70 | -71.2 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1500 | A | 161KV TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/D25_A1 | [8 empty] | 延平DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001.3 | 2002.6 | 0.3 | -1900 | -2000 | -2001.3 | -2002.6 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
D25 | 延平DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 78 | 83 | 90 | 2 | -10 | -13 | -16 | -19 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS |  |  | 1DTR | #1DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | #1DTR | ℃ | #1DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_COIL | #1DTR 線溫 | MTR | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 102.7 | 110 | 1.7 | -10 | -12.7 | -15.4 | -18.1 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 78 | 83 | 90 | 2 | -10 | -13 | -16 | -19 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #2DTR | ℃ | #2DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_COIL | #2DTR 線溫 | MTR | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 102.7 | 110 | 1.7 | -10 | -12.7 | -15.4 | -18.1 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #3DTR | ℃ | #3DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 78 | 83 | 90 | 2 | -10 | -13 | -16 | -19 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #3DTR | ℃ | #3DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 102.7 | 110 | 1.7 | -10 | -12.7 | -15.4 | -18.1 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | #1DTR | MW | #1DTR 310瓦 | MW_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#1DTR_MW | #1DTR二次側 MW | MTR | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | #1DTR | MVAR | #1DTR 310 乏 | MVAR_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#1DTR_MVAR | #1DTR二次側 MVAR | MTR | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | #1DTR | A | #1DTR 310 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#1DTR_A1 | #1DTR二次側 R相AMP | MTR | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | #1DTR | A | #1DTR 310 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#1DTR_A2 | #1DTR二次側 S相AMP | MTR | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | #1DTR | A | #1DTR 310 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#1DTR_A3 | #1DTR二次側 T相AMP | MTR | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0045 |  |  | 1-AD |  |  | PT-1 | KV | #1BUS PT 電壓 | kV_-18_18(-2000_2000) | aaa | B3/D25_A1 | [8 empty] | 延平DS.23KV#1BUS_KV | 23KV #1BUS KV | BUS | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.4 | 16.6 | 18 | 0.2 | 12.4 | 11.2 | 10 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 平51線 | MVAR | 平51線F1 KA51 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五一線KVAR | 23KV平五一線 KVAR | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 平51線 | A | 平51線F1 KA51 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五一線A1 | 23KV平五一線 R相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 平51線 | A | 平51線F1 KA51 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五一線A2 | 23KV平五一線 S相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 平51線 | A | 平51線F1 KA51 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五一線A3 | 23KV平五一線 T相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 平52線 | MVAR | 平52線F2 KA52 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五二線KVAR | 23KV平五二線 KVAR | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 平52線 | A | 平52線F2 KA52 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五二線A1 | 23KV平五二線 R相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 平52線 | A | 平52線F2 KA52 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五二線A2 | 23KV平五二線 S相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 平52線 | A | 平52線F2 KA52 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五二線A3 | 23KV平五二線 T相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 平53線 | MVAR | 平53線F3 KA53 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五三線KVAR | 23KV平五三線 KVAR | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 平53線 | A | 平53線F3 KA53 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五三線A1 | 23KV平五三線 R相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 平53線 | A | 平53線F3 KA53 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五三線A2 | 23KV平五三線 S相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 平53線 | A | 平53線F3 KA53 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五三線A3 | 23KV平五三線 T相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 平54線 | MVAR | 平54線F4 KA54 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五四線KVAR | 23KV平五四線 KVAR | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 平54線 | A | 平54線F4 KA54 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五四線A1 | 23KV平五四線 R相AMP | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 平54線 | A | 平54線F4 KA54 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五四線A2 | 23KV平五四線 S相AMP | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 平54線 | A | 平54線F4 KA54 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五四線A3 | 23KV平五四線 T相AMP | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 平55線 | MVAR | 平55線F5 KA55 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五五線KVAR | 23KV平五五線 KVAR | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 平55線 | A | 平55線F5 KA55 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五五線A1 | 23KV平五五線 R相AMP | FEEDER | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 221 | 232 | 243 | 10 | 190 | 179 | 168 | 157 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1821 | 1832 | 1843 | 10 | 1790 | 1779 | 1768 | 1757 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 平55線 | A | 平55線F5 KA55 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五五線A2 | 23KV平五五線 S相AMP | FEEDER | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 平55線 | A | 平55線F5 KA55 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五五線A3 | 23KV平五五線 T相AMP | FEEDER | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 平56線 | MVAR | 平56線F6 KA56 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五六線KVAR | 23KV平五六線 KVAR | FEEDER | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 平56線 | A | 平56線F6 KA56 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五六線A1 | 23KV平五六線 R相AMP | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 平56線 | A | 平56線F6 KA56 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五六線A2 | 23KV平五六線 S相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 平56線 | A | 平56線F6 KA56 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五六線A3 | 23KV平五六線 T相AMP | FEEDER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 平57線 | MVAR | 平57線F7 KA57乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五七線KVAR | 23KV平五七線 KVAR | FEEDER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 平57線 | A | 平57線F7 KA57R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五七線A1 | 23KV平五七線 R相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 平57線 | A | 平57線F7 KA57S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五七線A2 | 23KV平五七線 S相AMP | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 平57線 | A | 平57線F7 KA57T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五七線A3 | 23KV平五七線 T相AMP | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 平58線 | MVAR | 平58線F8 KA58乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五八線KVAR | 23KV平五八線 KVAR | FEEDER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 平58線 | A | 平58線F8 KA58R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五八線A1 | 23KV平五八線 R相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 平58線 | A | 平58線F8 KA58S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五八線A2 | 23KV平五八線 S相AMP | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 平58線 | A | 平58線F8 KA58T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五八線A3 | 23KV平五八線 T相AMP | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | #1TIE | A | #1TIE 100 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | #1TIE | A | #1TIE 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | #1TIE | A | #1TIE 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | #2 DTR | MW | #2 DTR 2A 330 瓦 | MW_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | #2 DTR | MVAR | #2 DTR 2A 330 乏 | MVAR_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | #2 DTR | A | #2 DTR 2A 330 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | None | [11 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | #2 DTR | A | #2 DTR 2A 330 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | None | [11 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | #2 DTR | A | #2 DTR 2A 330 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | None | [11 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0088 |  |  | 1-D8 |  |  | PT-2A | KV | #2A BUS PT 電壓 | kV_-18_18(-2000_2000) | aba | B3/D25_A1 | [8 empty] | 延平DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.4 | 16.6 | 18 | 0.2 | 12.4 | 11.2 | 10 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 平61線 | MVAR | 平61線 F9 KA61乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六一線KVAR | 23KV平六一線 KVAR | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 平61線 | A | 平61線 F9 KA61 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六一線A1 | 23KV平六一線 R相AMP | FEEDER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 平61線 | A | 平61線 F9 KA61 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六一線A2 | 23KV平六一線 S相AMP | FEEDER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 平61線 | A | 平61線 F9 KA61 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六一線A3 | 23KV平六一線 T相AMP | FEEDER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 平62線 | MVAR | 平62線F10 KA62乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六二線KVAR | 23KV平六二線 KVAR | FEEDER | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 平62線 | A | 平62線F10 KAR2 相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六二線A1 | 23KV平六二線 R相AMP | FEEDER | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 平62線 | A | 平62線F10 KA62 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六二線A2 | 23KV平六二線 S相AMP | FEEDER | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 平62線 | A | 平62線F10 KA62 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六二線A3 | 23KV平六二線 T相AMP | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 平63線 | MVAR | 平63線F11 KA63 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六三線KVAR | 23KV平六三線 KVAR | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 平63線 | A | 平63線F11 KA63 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六三線A1 | 23KV平六三線 R相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 平63線 | A | 平63線F11 KA63 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六三線A2 | 23KV平六三線 S相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 平63線 | A | 平63線F11 KA63 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六三線A3 | 23KV平六三線 T相AMP | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 平64線 | MVAR | 平64線F12 KA64 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六四線KVAR | 23KV平六四線 KVAR | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 平64線 | A | 平64線F12 KA64 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六四線A1 | 23KV平六四線 R相AMP | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 平64線 | A | 平64線F12 KA64 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六四線A2 | 23KV平六四線 S相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 平64線 | A | 平64線F12 KA64 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六四線A3 | 23KV平六四線 T相AMP | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #2 DTR | MW | #2 DTR 2B 340 瓦 | MW_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #2 DTR | MVAR | #2 DTR 2B 340 乏 | MVAR_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | #2 DTR | A | #2 DTR 2B 340 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | None | [11 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | #2 DTR | A | #2 DTR 2B 340 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | None | [11 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | #2 DTR | A | #2 DTR 2B 340 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | None | [11 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0110 |  |  | 1-EE |  |  | PT-2B | KV | #2B BUS PT 電壓 | kV_-18_18(-2000_2000) | aca | B3/D25_A1 | [8 empty] | 延平DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.4 | 16.6 | 18 | 0.2 | 12.4 | 11.2 | 10 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 平65線 | AMVAR | 平65線F13 KA65 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六五線KVAR | 23KV平六五線 KVAR | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 平65線 | A | 平65線F13 KA65 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六五線A1 | 23KV平六五線 R相AMP | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 平65線 | A | 平65線F13 KA65 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六五線A2 | 23KV平六五線 S相AMP | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 平65線 | A | 平65線F13 KA65T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六五線A3 | 23KV平六五線 T相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 平66線 | MVAR | 平66線F14 KA66 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六六線KVAR | 23KV平六六線 KVAR | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 平66線 | A | 平66線F14 KA66 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六六線A1 | 23KV平六六線 R相AMP | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 平66線 | A | 平66線F14 KA66 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六六線A2 | 23KV平六六線 S相AMP | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 平66線 | A | 平66線F14 KA66 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六六線A3 | 23KV平六六線 T相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 平67線 | MVAR | 平67線F15 KA67 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六七線KVAR | 23KV平六七線 KVAR | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 平67線 | A | 平67線F15 KA67 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六七線A1 | 23KV平六七線 R相AMP | FEEDER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 平67線 | A | 平67線F15 KA67 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六七線A2 | 23KV平六七線 S相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 平67線 | A | 平67線F15 KA67 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六七線A3 | 23KV平六七線 T相AMP | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 平68線 | MVAR | 平68線F16 KA68 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六八線KVAR | 23KV平六八線 KVAR | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 平68線 | A | 平68線F16 KA68 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六八線A1 | 23KV平六八線 R相AMP | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 平68線 | A | 平68線F16 KA68 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六八線A2 | 23KV平六八線 S相AMP | FEEDER | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 平68線 | A | 平68線F16 KA68 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六八線A3 | 23KV平六八線 T相AMP | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | #2TIE | A | #2TIE 200 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 221 | 232 | 243 | 10 | 190 | 179 | 168 | 157 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1821 | 1832 | 1843 | 10 | 1790 | 1779 | 1768 | 1757 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | #2TIE | A | #2TIE 200 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | #2TIE | A | #2TIE 200 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | #3 DTR | MW | #3 DTR 350 瓦 | MW_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | #3 DTR | MVAR | #3 DTR 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | #3 DTR | A | #3 DTR 350 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | #3 DTR | A | #3 DTR 350 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | #3 DTR | A | #3 DTR 350 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0137 |  |  | 2-89 |  |  | PT-3 | KV | #3 BUS PT 電壓 | kV_-18_18(-2000_2000) | ada | B3/D25_A1 | [8 empty] | 延平DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.4 | 16.6 | 18 | 0.2 | 12.4 | 11.2 | 10 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 平71線 | MVAR | 平71線F17 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七一線KVAR | 23KV平七一線 KVAR | FEEDER | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 平71線 | A | 平71線F17 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七一線A1 | 23KV平七一線 R相AMP | FEEDER | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 平71線 | A | 平71線F17 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七一線A2 | 23KV平七一線 S相AMP | FEEDER | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 平71線 | A | 平71線F17 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七一線A3 | 23KV平七一線 T相AMP | FEEDER | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 平72線 | MVAR | 平72線F18 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七二線KVAR | 23KV平七二線 KVAR | FEEDER | [5 empty] | 380 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 平72線 | A | 平72線F18 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七二線A1 | 23KV平七二線 R相AMP | FEEDER | [5 empty] | 381 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 平72線 | A | 平72線F18 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七二線A2 | 23KV平七二線 S相AMP | FEEDER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 平72線 | A | 平72線F18 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七二線A3 | 23KV平七二線 T相AMP | FEEDER | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 平73線 | MVAR | 平73線F19 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七三線KVAR | 23KV平七三線 KVAR | FEEDER | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 平73線 | A | 平73線F19 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七三線A1 | 23KV平七三線 R相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 平73線 | A | 平73線F19 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七三線A2 | 23KV平七三線 S相AMP | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 平73線 | A | 平73線F19 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七三線A3 | 23KV平七三線 T相AMP | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 平74線 | MVAR | 平74線F20 KA74 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七四線KVAR | 23KV平七四線 KVAR | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 平74線 | A | 平74線F20 KA74 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七四線A1 | 23KV平七四線 R相AMP | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 平74線 | A | 平74線F20 KA74 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七四線A2 | 23KV平七四線 S相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 平74線 | A | 平74線F20 KA74 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七四線A3 | 23KV平七四線 T相AMP | FEEDER | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 平75線 | MVAR | 平75線F21 KA75 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七五線KVAR | 23KV平七五線 KVAR | FEEDER | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 平75線 | A | 平75線F21 KA75 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七五線A1 | 23KV平七五線 R相AMP | FEEDER | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 平75線 | A | 平75線F21 KA75 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七五線A2 | 23KV平七五線 S相AMP | FEEDER | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 平75線 | A | 平75線F21 KA75 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七五線A3 | 23KV平七五線 T相AMP | FEEDER | [5 empty] | 395 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 平76線 | MVAR | 平76線F22 KA76 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七六線KVAR | 23KV平七六線 KVAR | FEEDER | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 平76線 | A | 平76線F22 KA76 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七六線A1 | 23KV平七六線 R相AMP | FEEDER | [5 empty] | 397 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 平76線 | A | 平76線F22 KA76 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七六線A2 | 23KV平七六線 S相AMP | FEEDER | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 平76線 | A | 平76線F22 KA76 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七六線A3 | 23KV平七六線 T相AMP | FEEDER | [5 empty] | 399 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 平77線 | MVAR | 平77線F23 KA77 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七七線KVAR | 23KV平七七線 KVAR | FEEDER | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 平77線 | A | 平77線F23 KA77 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七七線A1 | 23KV平七七線 R相AMP | FEEDER | [5 empty] | 401 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 平77線 | A | 平77線F23 KA77 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七七線A2 | 23KV平七七線 S相AMP | FEEDER | [5 empty] | 402 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 平77線 | A | 平77線F23 KA77 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七七線A3 | 23KV平七七線 T相AMP | FEEDER | [5 empty] | 403 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 平78線 | MVAR | 平78線F24 KA78 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七八線KVAR | 23KV平七八線 KVAR | FEEDER | [5 empty] | 404 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20002 | 20004 | 20006 | 1 | -20000 | -20002 | -20004 | -20006 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 平78線 | A | 平78線F24 KA78 R相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七八線A1 | 23KV平七八線 R相AMP | FEEDER | [5 empty] | 405 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 434.25 | 480 | 600 | 1.25 | 8 | -200 | -202.25 | -204.5 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 平78線 | A | 平78線F24 KA78 S相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七八線A2 | 23KV平七八線 S相AMP | FEEDER | [5 empty] | 406 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | 平78線 | A | 平78線F24 KA78 T相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七八線A3 | 23KV平七八線 T相AMP | FEEDER | [5 empty] | 407 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | SSTR2 | A | #490 SSTR2 R相電流 |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 408
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | SSTR2 | A | #490 SSTR2 S相電流 |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 409
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | SSTR2 | A | #490 SSTR2 T相電流 |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 410
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 平51線 | A | 平51線F1 KA51 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五一線A0 | 23KV平五一線 N相AMP | FEEDER | [5 empty] | 411 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 平52線 | A | 平52線F2 KA52 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五二線A0 | 23KV平五二線 N相AMP | FEEDER | [5 empty] | 412 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 平53線 | A | 平53線F3 KA53 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五三線A0 | 23KV平五三線 N相AMP | FEEDER | [5 empty] | 413 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 平54線 | A | 平54線F4 KA54 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五四線A0 | 23KV平五四線 N相AMP | FEEDER | [5 empty] | 414 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 平55線 | A | 平55線F5 KA55 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五五線A0 | 23KV平五五線 N相AMP | FEEDER | [5 empty] | 415 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 平56線 | A | 平56線F6 KA56 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五六線A0 | 23KV平五六線 N相AMP | FEEDER | [5 empty] | 416 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 平57線 | A | 平57線F7 KA57 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五七線A0 | 23KV平五七線 N相AMP | FEEDER | [5 empty] | 417 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 平58線 | A | 平58線F8 KA58 零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平五八線A0 | 23KV平五八線 N相AMP | FEEDER | [5 empty] | 418 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 平61線 | A | 平61線F9 KA61零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六一線A0 | 23KV平六一線 N相AMP | FEEDER | [5 empty] | 419 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 平62線 | A | 平62線F10 KA62零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六二線A0 | 23KV平六二線 N相AMP | FEEDER | [5 empty] | 420 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 平63線 | A | 平63線F11 KA63零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六三線A0 | 23KV平六三線 N相AMP | FEEDER | [5 empty] | 421 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 平64線 | A | 平64線F12 KA64零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六四線A0 | 23KV平六四線 N相AMP | FEEDER | [5 empty] | 422 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 平65線 | A | 平65線F13 KA65零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六五線A0 | 23KV平六五線 N相AMP | FEEDER | [5 empty] | 423 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 平66線 | A | 平66線F14 KA66零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六六線A0 | 23KV平六六線 N相AMP | FEEDER | [5 empty] | 424 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 平67線 | A | 平67線F15 KA67零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六七線A0 | 23KV平六七線 N相AMP | FEEDER | [5 empty] | 425 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 平68線 | A | 平68線F16 KA68零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平六八線A0 | 23KV平六八線 N相AMP | FEEDER | [5 empty] | 426 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 平71線 | A | 平71線F17 KA71零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七一線A0 | 23KV平七一線 N相AMP | FEEDER | [5 empty] | 427 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 平72線 | A | 平72線F18 KA72零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七二線A0 | 23KV平七二線 N相AMP | FEEDER | [5 empty] | 428 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 平73線 | A | 平73線F19 KA73零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七三線A0 | 23KV平七三線 N相AMP | FEEDER | [5 empty] | 429 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No4AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 430 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1821 | 1832 | 1843 | 10 | 1790 | 1779 | 1768 | 1757 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D25_A1 | [8 empty] | 延平DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 431 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 221 | 232 | 243 | 10 | 190 | 179 | 168 | 157 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 平74線 | A | 平74線F20 KA74零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七四線A0 | 23KV平七四線 N相AMP | FEEDER | [5 empty] | 432 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 平75線 | A | 平75線F21 KA75零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七五線A0 | 23KV平七五線 N相AMP | FEEDER | [5 empty] | 433 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 平76線 | A | 平76線F22 KA76零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七六線A0 | 23KV平七六線 N相AMP | FEEDER | [5 empty] | 434 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 平77線 | A | 平77線F23 KA77零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七七線A0 | 23KV平七七線 N相AMP | FEEDER | [5 empty] | 435 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 平78線 | A | 平78線F24 KA78零相電流 | A_-600_600(-2000_2000) |  | B2/D25_D1 | [8 empty] | 延平DS.平七八線A0 | 23KV平七八線 N相AMP | FEEDER | [5 empty] | 436 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201.5 | -203 | -204.5 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1560 | 87A1 | 忠孝延平線 1560 87A1 |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_87A1 | 忠孝延平線(1560)第一套87RY | OTHER | [5 empty] | 437 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 1560 | 87A2 | 忠孝延平線 1560 87A2 |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_87A2 | 忠孝延平線(1560)第二套87RY | OTHER | [5 empty] | 438 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1560 | PHA | 忠孝延平線 1560 PHA |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_PHA | 忠孝延平線(1560) 相間RY | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1560 | GDA | 忠孝延平線 1560 GDA |  |  | B2/D25_A1 | [8 empty] | 延平DS.1560_GDA | 忠孝延平線(1560) 接地RY | LINE161 | [5 empty] | 440 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1550 | 87A | 台南延平線 1550 87A |  |  | B2/D25_A1 | [8 empty] | 延平DS.1550_87A | 台南延平線(1550) 87RY | LINE161 | [5 empty] | 441 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 | 8 |  | 1-01-00 | 1-01-00 |  | 1550 | PHA | 台南延平線 1550 PHA |  |  | B2/D25_A1 | [8 empty] | 延平DS.1550_PHA | 台南延平線(1550) 相間RY | LINE161 | [5 empty] | 442 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 | 9 |  | 1-01-01 | 1-01-01 |  | 1550 | GDA | 台南延平線 1550 GDA |  |  | B2/D25_A1 | [8 empty] | 延平DS.1550_GDA | 台南延平線(1550) 接地RY | LINE161 | [5 empty] | 443 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1510 | 85A | 延平健康線 1510 85A |  |  | B2/D25_A1 | [8 empty] | 延平DS.1510_85A | 健康線(1510) 85RY | LINE161 | [5 empty] | 444 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1510 | PHA | 延平健康線 1510 PHA |  |  | B2/D25_A1 | [8 empty] | 延平DS.1510_PHA | 健康線(1510) 相間RY | LINE161 | [5 empty] | 445 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1510 | GDA | 延平健康線 1510 GDA |  |  | B2/D25_A1 | [8 empty] | 延平DS.1510_GDA | 健康線(1510) 接地RY | LINE161 | [5 empty] | 446 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1500 | 50A | 161KV TIE 1500 50A |  |  | B2/D25_A1 | [8 empty] | 延平DS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 447 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/D25_A1 | [8 empty] | 延平DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 448 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/D25_A1 | [8 empty] | 延平DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 449 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | Locate Empty | A/N | 161KV 79RY復閉失敗 RCA |  |  | B3/D25_A1 | [8 empty] | 延平DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 450 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1DTR | 87A | #1DTR 87A |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 451 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 452 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1DTR | 51ZA | #1DTR 51ZA |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 453 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #1DTR | PHA | #1DTR 1750 PHA |  |  | B2/D25_A1 | [8 empty] | 延平DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 454 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #1DTR | GDA | #1DTR 1750 GDA |  |  | B2/D25_A1 | [8 empty] | 延平DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 455 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 310 | PHA | #1DTR 310 PHA |  |  | B3/D25_A1 | [8 empty] | 延平DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 456 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #2DTR | 87A | #2DTR 87A |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 457 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 458 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #2DTR | 51ZA | #2DTR 51ZA |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 459 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #2DTR | PHA | #2DTR 1760 PHA |  |  | B2/D25_A1 | [8 empty] | 延平DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 460 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #2DTR | GDA | #2DTR 1760 GDA |  |  | B2/D25_A1 | [8 empty] | 延平DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 461 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | 330 | PHA | #2DTR 2A 330 PHA |  |  | B3/D25_A1 | [8 empty] | 延平DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 462 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 340 | PHA | #2DTR 2B 340 PHA |  |  | B3/D25_A1 | [8 empty] | 延平DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 463 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | #3DTR | 87A | #3DTR 87A |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 464 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | #3DTR | 96PA | #3DTR 機械保護動作(96PA) |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 465 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #3DTR | 51ZA | #3DTR 51ZA |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 466 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #3DTR | PHA | #3DTR 1770 PHA |  |  | B2/D25_A1 | [8 empty] | 延平DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 467 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #3DTR | GDA | #3DTR 1770 GDA |  |  | B2/D25_A1 | [8 empty] | 延平DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 468 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 350 | PHA | #3DTR 350 PHA |  |  | B3/D25_A1 | [8 empty] | 延平DS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 469 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D25_A1 | [8 empty] | 延平DS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 310 | #1DTR(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 310 | GDA | #1DTR 310 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.310_GDA | 310開關箱IED RY GDA | OTHER | [5 empty] | 471 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 330 | GDA | #2DTR 330 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.330_GDA | 330開關箱IED RY GDA | OTHER | [5 empty] | 472 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 340 | GDA | #2DTR 340 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.340_GDA | 340開關箱IED RY GDA | OTHER | [5 empty] | 473 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | 350 | GDA | #3DTR 350 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.350_GDA | 350開關箱IED RY GDA | OTHER | [5 empty] | 474 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 475
D25 | 延平DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 390 | GDA | 1SSTR 390 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 476 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0133 |  |  | 2-00-05 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | 延平DS.210_UVA | 23KV #1SC 27RY(欠壓) | SC | [5 empty] | 477 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0136 |  |  | 1-11-00 |  |  | 平51線 | GDA | 平51線 F1 KA51 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA51_GDA | 23KV平五一線(KA51) 接地RY | FEEDER | [5 empty] | 478 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | 平52線 | GDA | 平52線 F2 KA52 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA52_GDA | 23KV平五二線(KA52) 接地RY | FEEDER | [5 empty] | 479 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | 平53線 | GDA | 平53線 F3 KA53 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA53_GDA | 23KV平五三線(KA53) 接地RY | FEEDER | [5 empty] | 480 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | 平54線 | GDA | 平54線 F4 KA54 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA54_GDA | 23KV平五四線(KA54) 接地RY | FEEDER | [5 empty] | 481 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0148 |  |  | 2-02-04 |  |  | Locate Empty |  |  |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA55_GDA | 23KV平五五線(KA55) 接地RY | FEEDER | [5 empty] | 482 |  |  |  |  | DI | D_P_KEY | [28 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | 平56線 | GDA | 平56線 F6 KA56 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA56_GDA | 23KV平五六線(KA56) 接地RY | FEEDER | [5 empty] | 483 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0154 |  |  | 1-13-02 |  |  | Locate Empty |  |  |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA57_GDA | 23KV平五七線(KA57) 接地RY | FEEDER | [5 empty] | 484 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 2-03-05 |  |  | Locate Empty |  |  |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA58_GDA | 23KV平五八線(KA58) 接地RY | FEEDER | [5 empty] | 485 |  |  |  |  | DI | D_P_KEY | [28 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0160 |  |  | 1-10-00 |  |  | 390 | ON/OFF | 1SSTR 390 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 486 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-10-03 |  |  | 210 | ON/OFF | #1SC 210 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.210_CB | 210(23KV #1SC) CB | SC | [5 empty] | 487 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | 平61線 | GDA | 平61線 F9 KA61 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA61_GDA | 23KV平六一線(KA61) 接地RY | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 平62線 | GDA | 平62線 F10 KA62 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA62_GDA | 23KV平六二線(KA62) 接地RY | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 平63線 | GDA | 平63線 F11 KA63 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA63_GDA | 23KV平六三線(KA63) 接地RY | FEEDER | [5 empty] | 490 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-11-07 |  |  | 平54線 | ON/OFF | 平54線 F4 KA54 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA54_CB | KA54(23KV平五四線) CB | FEEDER | [5 empty] | 491 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0178 |  |  | 1-12-02 |  |  | 平55線 | ON/OFF | 平55線 F5 KA55 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA55_CB | KA55(23KV平五五線) CB | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0181 |  |  | 1-12-05 |  |  | 平56線 | ON/OFF | 平56線 F6 KA56 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA56_CB | KA56(23KV平五六線) CB | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 1-17-00 |  |  | 平65線 | GDA | 平65線 F13 KA65 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA65_GDA | 23KV平六五線(KA65) 接地RY | FEEDER | [5 empty] | 494 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | 平66線 | GDA | 平66線 F14 KA66 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA66_GDA | 23KV平六六線(KA66) 接地RY | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-13-06 |  |  | 220 | ON/OFF | #2SC 220 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.220_CB | 220(23KV #2SC) CB | SC | [5 empty] | 496 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-14-01 |  |  | #1TIE | ON/OFF | #1TIE 100 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 497 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-14-04 |  |  | 平61線 | ON/OFF | 平61線 F9 KA61 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA61_CB | KA61(23KV平六一線) CB | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0198 |  |  | 1-14-06 |  |  | 平61線 | GDA | 平61線 F9 KA61 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA61_GDA | 23KV平六一線(KA61) 接地RY | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0199 |  |  | 1-14-07 |  |  | 平62線 | ON/OFF | 平62線 F10 KA62 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA62_CB | KA62(23KV平六二線) CB | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 平71線 | PHA | 平71線 F17 KA71 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA71_PHA | 23KV平七一線(KA71) 相間RY | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 平71線 | GDA | 平71線 F17 KA71 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA71_GDA | 23KV平七一線(KA71) 接地RY | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | 平72線 | PHA | 平72線 F18 KA72 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA72_PHA | 23KV平七二線(KA72) 相間RY | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | 平72線 | GDA | 平72線 F18 KA72 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA72_GDA | 23KV平七二線(KA72) 接地RY | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-15-07 |  |  | 平64線 | GDA | 平64線 F12 KA64 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA64_GDA | 23KV平六四線(KA64) 接地RY | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 |  |  | 1-16-00 |  |  | 230 | ON/OFF | #3SC 230 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 506 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-16-02 |  |  | 230 | UVA | #3SC 230 UVA |  |  | B2/D25_D1 | [8 empty] | 延平DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 507 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-16-03 |  |  | 240 | ON/OFF | #4SC 240 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 508 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-16-05 |  |  | 240 | UVA | #4SC 240 UVA |  |  | B2/D25_D1 | [8 empty] | 延平DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 509 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-16-06 |  |  | 平65線 | ON/OFF | 平65線 F13 KA65 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA65_CB | KA65(23KV平六五線) CB | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 平76線 | PHA | 平76線 F22 KA76 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA76_PHA | 23KV平七六線(KA76) 相間RY | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 平76線 | GDA | 平76線 F22 KA76 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA76_GDA | 23KV平七六線(KA76) 接地RY | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-17-03 |  | 1-1B-03 | 平66線 | GDA | 平66線 F14 KA66 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA66_GDA | 23KV平六六線(KA66) 接地RY | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-17-04 |  | 1-1B-04 | 平67線 | ON/OFF | 平67線F15 KA67 CB |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA67_CB | KA67(23KV平六七線) CB | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [29 empty] | Normal/Trip | Normal | 0 |  |  | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 平78線 | PHA | 平78線 F24 KA78 PHA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA78_PHA | 23KV平七八線(KA78) 相間RY | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | 平78線 | GDA | 平78線 F24 KA78 GDA |  |  | B2/D25_D1 | [8 empty] | 延平DS.KA78_GDA | 23KV平七八線(KA78) 接地RY | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0225 |  |  | 1-18-01 |  |  | 平68線 | GDA | 平68線 F16 KA68 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.KA68_GDA | 23KV平六八線(KA68) 接地RY | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0226 |  |  | 1-18-02 |  |  | 400 | ON/OFF | #2TIE 200 CB |  |  | B3/D25_A1 | [8 empty] | 延平DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 518 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 490 | PHA | 2SSTR 490 PHA |  |  | B3/D25_A1 | [8 empty] | 延平DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 519 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 490 | GDA | 2SSTR 490 GDA |  |  | B3/D25_A1 | [8 empty] | 延平DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 520 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | STATUS | L/R | L/R STATUS |  |  | ELEM/D25_A1 | [8 empty] | 延平DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 521 |  |  |  |  | DI | [29 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | #1DTR | 96D | #1DTR 96D |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 522 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | #1DTR | 96P | #1DTR 96P |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 523 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0546 |  |  | 1-32-02 |  |  | #1DTR | 63Q | #1DTR 63Q |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 524 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0547 |  |  | 1-32-03 |  |  | #1DTR | 96B1 | #1DTR 96B1 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 525 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | #1DTR | 96B2 | #1DTR 96B2 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 526 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | #2DTR | 96D | #2DTR 96D |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 527 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | #2DTR | 96P | #2DTR 96P |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 528 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | #2DTR | 63Q | #2DTR 63Q |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 529 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | #1DTR | S/L | #1DTR OLTC S/L |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_S/L | #1DTR OLTC S/L | MTR | [5 empty] | 530 |  |  |  |  | DI | [29 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D25 | 延平DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0557 |  |  | 1-32-13 |  |  | #1DTR | A/N | #1DTR 重故障 |  | a | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 531 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | #1DTR | A/N | #1DTR 輕故障 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 532 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | #2DTR | S/L | #2DTR OLTC S/L |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | [5 empty] | 533 |  |  |  |  | DI | [29 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D25 | 延平DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0562 |  |  | 1-33-02 |  |  | #2DTR | A/N | #2DTR 重故障 |  | a | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 534 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | #2DTR | A/N | #2DTR 輕故障 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 535 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #3DTR | S/L | #3DTR OLTC S/L |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 536 |  |  |  |  | DI | [29 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D25 | 延平DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0567 |  |  | 1-33-07 |  |  | #3DTR | A/N | #3DTR 重故障 |  | a | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 537 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0568 |  |  | 1-33-08 |  |  | #3DTR | A/N | #3DTR 輕故障 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 538 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | #2DTR | 96B1 | #2DTR 96B1 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 539 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | #2DTR | 96B2 | #2DTR 96B2 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 540 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | #3DTR | 96D | #3DTR 96D |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 541 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | #3DTR | 96P | #3DTR 96P |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 542 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | #3DTR | 63Q | #3DTR 63Q |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 543 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | #3DTR | 96B1 | #3DTR 96B1 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 544 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | #3DTR | 96B2 | #3DTR 96B2 |  |  | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 545 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0808 |  |  | 2-34-08 |  |  | A/N |  | 通訊設備 光纖主故障(備用) |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 546
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0809 |  |  | 2-34-09 |  |  | A/N |  | 通訊設備 光纖次故障(備用) |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 547
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0814 |  |  | 2-34-14 |  |  | 1550 | A/N | 台南延平線 1550 87CFA (87L通訊故障) |  |  | B3/D25_A1 | [8 empty] | 延平DS.1550_87CFA | 台南延平線(1550)87RY通訊故障 | OTHER | [5 empty] | 548 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Door1 | 圍牆小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 2-35-00 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B3/D25_A1 | [8 empty] | 延平DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 549 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Door2 | 鐵捲門 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0817 |  |  | 2-35-01 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B3/D25_A1 | [8 empty] | 延平DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 550 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Door3 | 控制室大門 |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0818 |  |  | 2-35-02 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B3/D25_A1 | [8 empty] | 延平DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 551 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | TEST/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0819 |  | 0158 | 2-35-03 |  | 2-1E | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D25_A1 | [8 empty] | 延平DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 552 |  |  |  |  | DI | [29 empty] | OFF/ON | ON | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0820 |  | 0159 | 2-35-04 |  | 2-1F | 1550 | A/N | 台南延平線 1550 RYFA(電驛故障) |  |  | B3/D25_A1 | [8 empty] | 延平DS.1550_RYFA | 台南延平線(1550)數位電驛故障 | OTHER | [5 empty] | 553 |  |  |  |  | DI | [29 empty] | OFF/ON | ON | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 2-35-05 |  |  | 1560 | A/N | 忠孝延平線 1560 RYFA(電驛故障) |  |  | B3/D25_A1 | [8 empty] | 延平DS.1560_RYFA | 忠孝延平線(1560)數位電驛故障 | OTHER | [5 empty] | 554 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 2-35-06 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D25_A1 | [8 empty] | 延平DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 555 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 2-35-07 |  |  | PMA | A/N | 電力量測表計故障 |  |  | B3/D25_A1 | [8 empty] | 延平DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 556 |  |  |  |  | DI | [29 empty] | Close/Open | Open | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 2-35-08 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | ELEM/D25_A1 | [8 empty] | 延平DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 557 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 2-35-09 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B2/D25_A1 | [8 empty] | 延平DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | [5 empty] | 558 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 2-35-10 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B2/D25_A1 | [8 empty] | 延平DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 559 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 2-35-11 |  |  | Locate Empty |  |  |  |  | ELEM/D25_A1 | [8 empty] | Point Empty | [7 empty] | 560
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-35-12 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 561
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 2-35-13 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 562
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 2-35-14 |  |  | Locate Empty |  |  |  |  | ELEM/D25_A1 | [8 empty] | Point Empty | [7 empty] | 563
D25 | 延平DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 2-35-15 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 564
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0832 |  |  | 1-34-00 |  |  | 1561 | ON/OFF | 忠孝延平線 1561 DS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1561_DS | 1561(忠孝延平線) DS | LINE161 | [5 empty] | 565 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0833 |  |  | 1-34-01 |  |  | 1561 | ON/OFF | 忠孝延平線 1561 DS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1561_DS | 1561(忠孝延平線) DS | LINE161 | [5 empty] | 566 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0834 |  |  | 1-34-02 |  |  | 1562 | ON/OFF | 忠孝延平線 1562 DS |  |  | ELEM/D25_A1 | [8 empty] | 延平DS.1562_DS | 1562(忠孝延平線) DS | LINE161 | [5 empty] | 567 |  |  |  |  | DI | [29 empty] | Normal/Fault |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0835 |  |  | 1-34-03 |  |  | 1562 | ON/OFF | 忠孝延平線 1562 DS |  |  | ELEM/D25_A1 | [8 empty] | 延平DS.1562_DS | 1562(忠孝延平線) DS | LINE161 | [5 empty] | 568 |  |  |  |  | DI | [29 empty] | Normal/Fault |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | 1563 | ON/OFF | 忠孝延平線 1563 DS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1563_DS | 1563(忠孝延平線) DS | LINE161 | [5 empty] | 569 |  |  |  |  | DI | [29 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0837 |  |  | 1-34-05 |  |  | 1563 | ON/OFF | 忠孝延平線 1563 DS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1563_DS | 1563(忠孝延平線) DS | LINE161 | [5 empty] | 570 |  |  |  |  | DI | [29 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | 1563E | ON/OFF | 忠孝延平線 1563E DS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1563E_ES | 1563E(忠孝延平線) ES | LINE161 | [5 empty] | 571 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | 1563E | ON/OFF | 忠孝延平線 1563E DS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1563E_ES | 1563E(忠孝延平線) ES | LINE161 | [5 empty] | 572 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | 1552 | ON/OFF | 台南延平線 1552 ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1552_DS | 1552(台南延平線) DS | LINE161 | [5 empty] | 573 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | 1552 | ON/OFF | 台南延平線 1552 ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1552_DS | 1552(台南延平線) DS | LINE161 | [5 empty] | 574 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0844 |  |  | 1-34-12 |  |  | 1553 | ON/OFF | 台南延平線 1553 ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1553_DS | 1553(台南延平線) DS | LINE161 | [5 empty] | 575 |  |  |  |  | DI | [29 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | 1553 | ON/OFF | 台南延平線 1553 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1553_DS | 1553(台南延平線) DS | LINE161 | [5 empty] | 576 |  |  |  |  | DI | [29 empty] | Normal/Fault |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南～延平線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0846 |  |  | 1-34-14 |  |  | 1553E | ON/OFF | 台南延平線 1553E ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1553E_ES | 1553E(台南延平線) ES | LINE161 | [5 empty] | 577 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0847 |  |  | 2-34-15 |  |  | 1510 R7 |  | 延平健康線 74A |  |  | B2/D25_A1 | [8 empty] | 延平DS.1510_74A | 健康線(1510) 74RY | LINE161 | [5 empty] | 578 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Water1 | 第一段警報 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | 1511 | ON/OFF | 延平健康線 1511 ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1511_DS | 1511(健康線) DS | LINE161 | [5 empty] | 579 |  |  |  |  | DI | [29 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | Water2 | 第二段警報 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0849 |  |  | 1-35-01 |  |  | 1511 | ON/OFF | 延平健康線 1511 ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1511_DS | 1511(健康線) DS | LINE161 | [5 empty] | 580 |  |  |  |  | DI | [29 empty] | Normal/Alarm |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0850 |  |  | 1-35-02 |  |  | 1512 | ON/OFF | 延平健康線 1512 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1512_DS | 1512(健康線) DS | LINE161 | [5 empty] | 581 |  |  |  |  | DI | [29 empty] | Normal/Test | Test | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝～延平線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | 1513 | ON/OFF | 延平健康線 1513 ABS |  |  | B2/D25_A1 | [8 empty] | 延平DS.1513_DS | 1513(健康線) DS | LINE161 | [5 empty] | 582 |  |  |  |  | DI | [29 empty] | Normal/Fault |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 | 161 | 161KV | 1510 | 延平健康線 | 1513E | ES3 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | 1513E | ON/OFF | 延平健康線 1513E ABS |  |  | B3/D25_A1 | [8 empty] | 延平DS.1513E_ES | 1513E(健康線) ES | LINE161 | [5 empty] | 583 |  |  |  |  | DI | [29 empty] | Normal/Alarm | Alarm | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | 1513E | ON/OFF | 延平健康線 1513E ABS |  |  | ELEM/D25_A1 | [8 empty] | 延平DS.1513E_ES | 1513E(健康線) ES | LINE161 | [5 empty] | 584 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 585
D25 | 延平DS | 161 | 161kV | ComPoint |  |  | 87CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 586
D25 | 延平DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | Locate Empty |  |  |  |  | B3/D25_A1 | [8 empty] | Point Empty | [7 empty] | 587
D25 | 延平DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | Locate Empty |  |  |  |  | B1/D25_A1 | [8 empty] | 延平DS.161#1DTR_86A | 161KV #1DTR 86RY | OTHER | [5 empty] | 588 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 2-32-02 |  |  | 平73線 | U/L | 平73線 F19 KA73 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA73_LCO_TAP | 23KV平七三線(KA73) LCO TAP | FEEDER | [5 empty] | 589 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | Locate Empty |  |  |  |  | B1/D25_A1 | [8 empty] | 延平DS.161#2DTR_86A | 161KV #2DTR 86RY | OTHER | [5 empty] | 590 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0773 |  |  | 2-32-05 |  |  | 平76線 | U/L | 平76線 F22 KA76 LCO分流器 |  |  | B1/D25_A1 | [8 empty] | 延平DS.KA76_LCO_TAP | 23KV平七六線(KA76) LCO TAP | FEEDER | [5 empty] | 591 |  |  |  |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | USE/LOCK | LOCK
D25 | 延平DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | Locate Empty |  |  |  |  | B1/D25_A1 | [8 empty] | 延平DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER | [5 empty] | 592 |  |  |  |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0776 |  |  | 2-32-08 |  |  | Locate Empty | A/N | 23KV LOA 79RY復閉失敗 |  |  | B1/D25_A1 | [8 empty] | Point Empty | [7 empty] | 593
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-00 |  | 2-26 | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 594 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 161 | 161kV | 1BUS | #1BUS |  | VUA |  | Insert | [15 empty] | 2-33-09 | [7 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 595 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 2BUS | #2BUS |  | VUA |  | Insert | [15 empty] | 2-33-10 | [7 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 596 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV |  |  |  | CBA |  | Insert | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-34-00 | [16 empty] | 延平DS.161KV_CBA | 161KV斷路器重故障 | OTHER |  |  |  |  | CDC | 597 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV |  |  |  | CBF |  | Insert | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [9 empty] | 2-34-01 | [16 empty] | 延平DS.161KV_CBF | 161KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 598 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | ComPoint |  |  | 60A |  | Insert | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [9 empty] | 2-34-06 | [7 empty] | B3/D25_A1 | [8 empty] | 延平DS.23KV_SC_60A | 23KV電容器組 60RY | OTHER |  |  |  |  | CDC | 599 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | OPA |  | DEL | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [9 empty] | 2-33-05 | [23 empty] | CDC | 600 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | PSF |  | DEL | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [9 empty] | 2-34-05 | [23 empty] | CDC | 601 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | STUV |  | DEL | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [9 empty] | 2-33-08 | [23 empty] | CDC | 602 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | CommACF |  | DEL | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-34-07 | [23 empty] | CDC | 603 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | Door2 |  | DEL | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [9 empty] | 2-33-01 | [23 empty] | CDC | 604 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | Door3 |  | DEL | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [9 empty] | 2-33-02 | [23 empty] | CDC | 605 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | Lights1 |  | DEL | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [9 empty] | 2-33-03 |  | 2-1E | [21 empty] | CDC | 606 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | 空調機跳脫警報 |  | DEL | [15 empty] | 2-32-09 | [23 empty] | CDC | 607 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-11 |  | 2-31 | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 608 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-14 |  | 2-34 | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 609 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-04 |  | 2-2A | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 610 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-06 |  | 2-2C | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 611 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-07 |  | 2-2D | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 612 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | ADJ |  | DEL | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [9 empty] | 2-31-15 |  | 2-35 | [5 empty] | B2/D25_D1 | [15 empty] | CDC | 613 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | CHG1 |  | DEL | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-33-12 | [23 empty] | CDC | 614 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 0 |  |  |  |  | CHG2 |  | DEL | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-33-13 | [23 empty] | CDC | 615 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI
D25 | 延平DS | 22 | 22kV | 200 | TIE(200) |  | 51A |  | Insert | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [9 empty] | 1-18-03 | [7 empty] | B3/D25_A1 | [8 empty] | 延平DS.200_51A | 23KV TIE(200) 51RY | TIE |  |  |  |  | CDC | 616 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [29 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 200 | TIE(200) |  | 51NA |  | DEL | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [9 empty] | 1-18-04 | [7 empty] | B1/D25_A1 | [15 empty] | CDC | 617 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI
D25 | 延平DS |  |  | 1DTR | #1DTR |  | Tap Chan |  | Insert | TapPos |  | Rise/Low | Y | 3 | DI-SP | [9 empty] | 1-32-12 |  | 1-60 | [5 empty] | B1/D25_A1 | [8 empty] | 延平DS.#1DTR_A/M | #1DTR OLTC A/M | MTR |  |  |  |  | CDC | 618 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [29 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D25 | 延平DS |  |  | 2DTR | #2DTR |  | Tap Chan |  | Insert | TapPos |  | Rise/Low | Y | 3 | DI-SP | [9 empty] | 1-33-01 |  | 1-62 | [5 empty] | B1/D25_A1 | [8 empty] | 延平DS.#2DTR_A/M | #2DTR OLTC A/M | MTR |  |  |  |  | CDC | 619 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [29 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D25 | 延平DS |  |  | 3DTR | #3DTR |  | Tap Chan |  | Insert | TapPos |  | Rise/Low | Y | 3 | DI-SP | [9 empty] | 1-33-06 |  | 1-64 | [5 empty] | B1/D25_A1 | [8 empty] | 延平DS.#3DTR_A/M | #3DTR OLTC A/M | MTR |  |  |  |  | CDC | 620 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [29 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 287UL |  | Insert | [15 empty] | 2-30-00 |  | 1-67 | [5 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER |  |  |  |  | CDC | 621 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 51Z_UL |  | Insert | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [9 empty] | 2-30-01 |  | 1-68 | [5 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 622 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | RYFA |  | Insert | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-30-02 | [7 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER |  |  |  |  | CDC | 623 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 287UL |  | Insert | [15 empty] | 2-30-03 |  | 1-6A | [5 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER |  |  |  |  | CDC | 624 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 51Z_UL |  | Insert | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [9 empty] | 2-30-04 |  | 1-6B | [5 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 625 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | RYFA |  | Insert | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-30-05 | [7 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER |  |  |  |  | CDC | 626 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | 287UL |  | Insert | [15 empty] | 2-30-06 |  | 1-6D | [5 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER |  |  |  |  | CDC | 627 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | 51Z_UL |  | Insert | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [9 empty] | 2-30-07 |  | 1-6E | [5 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 628 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | RYFA |  | Insert | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [9 empty] | 2-30-08 | [7 empty] | B2/D25_A1 | [8 empty] | 延平DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER |  |  |  |  | CDC | 629 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [29 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 1BUS | 1BUS |  | PTE | (非取樣點) | Insert | [23 empty] | B3/D25_A1 | [8 empty] | 延平DS.1BUS_PTE | #1BUS_PTE(非取樣點) | OTHER | [5 empty] | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 2ABUS | 2ABUS |  | PTE | (非取樣點) | Insert | [23 empty] | B3/D25_A1 | [8 empty] | 延平DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 2BBUS | 2BBUS |  | PTE | (非取樣點) | Insert | [23 empty] | B3/D25_A1 | [8 empty] | 延平DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 22 | 22kV | 3BUS | 3BUS |  | PTE | (非取樣點) | Insert | [23 empty] | B3/D25_A1 | [8 empty] | 延平DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D25 | 延平DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D25/161/1BUS/V; OPRD2: D25/161/2BUS/V
D25 | 延平DS |  |  | 2DTR | #2DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/D25_A1 | [12 empty] | 延平DS.#2DTR_MVAR | #2DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: D25/22/330/MVAR; OPRD2: D25/22/340/MVAR
D25 | 延平DS |  |  | 2DTR | #2DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/D25_A1 | [12 empty] | 延平DS.#2DTR_MW | #2DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: D25/22/330/MW; OPRD2: D25/22/340/MW
D25 | 延平DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D25_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D25/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D25 | 延平DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D25_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: D25/161/1510/MW; OPRD2: D25/161/1550/MW; OPRD3: D25/161/1560/MW; OPRD4: D25/22/310/MW
D25 | 延平DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D25_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D25/0/CalcPoint/OPRN2_MW
D25 | 延平DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D25_A1 | [17 empty] | none
D25 | 延平DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D25_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D25/0/CalcPoint/OPRN1; OPRD2: D25/0/CalcPoint/OPRN2; OPRD3: D25/0/CalcPoint/PRFL_UL
D25 | 延平DS |  |  | 2DTR | #2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D25_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D25/22/330/I_R; OPRD2: D25/22/340/I_R
D25 | 延平DS |  |  | 2DTR | #2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D25_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D25/22/330/I_S; OPRD2: D25/22/340/I_S
D25 | 延平DS |  |  | 2DTR | #2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D25_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D25/22/330/I_T; OPRD2: D25/22/340/I_T
D25 | 延平DS | 161 | 161kV | 1510 | 延平健康線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D25_A1 | [12 empty] | 延平DS.1510_AMP | 健康線 AMP | LINE161 | AMP_CAL | C20R1600 | amp_cal | OPRD1: D25/161/1510/MW; OPRD2: D25/161/1510/MVAR; OPRD3: D25/0/CalcPoint/Vbs4
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D25_A1 | [12 empty] | 延平DS.1550_AMP | 台南延平線 AMP | LINE161 | AMP_CAL | C20R1200 | amp_cal | OPRD1: D25/161/1550/MW; OPRD2: D25/161/1550/MVAR; OPRD3: D25/0/CalcPoint/Vbs4
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D25_A1 | [12 empty] | 延平DS.1560_AMP | 忠孝延平線 AMP | LINE161 | AMP_CAL | C20R1001 | amp_cal | OPRD1: D25/161/1560/MW; OPRD2: D25/161/1560/MVAR; OPRD3: D25/0/CalcPoint/Vbs4
D25 | 延平DS | 22 | 22kV | 1BUS | #1BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D25_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D25/22/1BUS/V
D25 | 延平DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D25_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D25/22/2ABUS/V
D25 | 延平DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D25_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D25/22/2BBUS/V
D25 | 延平DS | 22 | 22kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D25_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D25/22/3BUS/V
D25 | 延平DS |  |  | 1DTR | #1DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D25_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 延平DS.#1DTR_MVA | #1DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: D25/22/310/MW; OPRD2: D25/22/310/MVAR
D25 | 延平DS |  |  | 2DTR | #2DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D25_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 延平DS.#2DTR_MVA | #2DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: D25//2DTR/MW; OPRD2: D25//2DTR/MVAR
D25 | 延平DS |  |  | 1DTR | #1DTR |  | LOAD | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#1DTR_LOAD | #1DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_LOAD | OPRD1: D25//1DTR/MVA; OPRD2: 0
D25 | 延平DS |  |  | 2DTR | #2DTR |  | LOAD | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#2DTR_LOAD | #2DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_LOAD | OPRD1: D25//2DTR/MVA; OPRD2: 0
D25 | 延平DS |  |  | 1DTR | #1DTR |  | PF | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#1DTR_PF | #1DTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D25/22/310/MW; OPRD2: D25/22/310/MVAR
D25 | 延平DS |  |  | 2DTR | #2DTR |  | PF | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#2DTR_PF | #2DTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D25//2DTR/MW; OPRD2: D25//2DTR/MVAR
D25 | 延平DS |  |  | 1DTR | #1DTR |  | TR_PERM | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#1DTR_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D25//1DTR/SupLocal; OPRD2: D25//1DTR/Tap Chan
D25 | 延平DS |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D25//2DTR/SupLocal; OPRD2: D25//2DTR/Tap Chan
D25 | 延平DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D25_A1 | [12 empty] | 延平DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D25//3DTR/SupLocal; OPRD2: D25//3DTR/Tap Chan
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA51/I_R; OPRD3: D25/22/KA51/I_S; OPRD4: D25/22/KA51/I_T
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA52/I_R; OPRD3: D25/22/KA52/I_S; OPRD4: D25/22/KA52/I_T
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA53/I_R; OPRD3: D25/22/KA53/I_S; OPRD4: D25/22/KA53/I_T
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA54/I_R; OPRD3: D25/22/KA54/I_S; OPRD4: D25/22/KA54/I_T
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA55/I_R; OPRD3: D25/22/KA55/I_S; OPRD4: D25/22/KA55/I_T
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA56/I_R; OPRD3: D25/22/KA56/I_S; OPRD4: D25/22/KA56/I_T
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA57/I_R; OPRD3: D25/22/KA57/I_S; OPRD4: D25/22/KA57/I_T
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/1BUS/V; OPRD2: D25/22/KA58/I_R; OPRD3: D25/22/KA58/I_S; OPRD4: D25/22/KA58/I_T
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2ABUS/V; OPRD2: D25/22/KA61/I_R; OPRD3: D25/22/KA61/I_S; OPRD4: D25/22/KA61/I_T
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2ABUS/V; OPRD2: D25/22/KA62/I_R; OPRD3: D25/22/KA62/I_S; OPRD4: D25/22/KA62/I_T
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2ABUS/V; OPRD2: D25/22/KA63/I_R; OPRD3: D25/22/KA63/I_S; OPRD4: D25/22/KA63/I_T
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2ABUS/V; OPRD2: D25/22/KA64/I_R; OPRD3: D25/22/KA64/I_S; OPRD4: D25/22/KA64/I_T
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2BBUS/V; OPRD2: D25/22/KA65/I_R; OPRD3: D25/22/KA65/I_S; OPRD4: D25/22/KA65/I_T
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2BBUS/V; OPRD2: D25/22/KA66/I_R; OPRD3: D25/22/KA66/I_S; OPRD4: D25/22/KA66/I_T
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2BBUS/V; OPRD2: D25/22/KA67/I_R; OPRD3: D25/22/KA67/I_S; OPRD4: D25/22/KA67/I_T
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/2BBUS/V; OPRD2: D25/22/KA68/I_R; OPRD3: D25/22/KA68/I_S; OPRD4: D25/22/KA68/I_T
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA71/I_R; OPRD3: D25/22/KA71/I_S; OPRD4: D25/22/KA71/I_T
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA72/I_R; OPRD3: D25/22/KA72/I_S; OPRD4: D25/22/KA72/I_T
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA73/I_R; OPRD3: D25/22/KA73/I_S; OPRD4: D25/22/KA73/I_T
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA74/I_R; OPRD3: D25/22/KA74/I_S; OPRD4: D25/22/KA74/I_T
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA75/I_R; OPRD3: D25/22/KA75/I_S; OPRD4: D25/22/KA75/I_T
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA76/I_R; OPRD3: D25/22/KA76/I_S; OPRD4: D25/22/KA76/I_T
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA77/I_R; OPRD3: D25/22/KA77/I_S; OPRD4: D25/22/KA77/I_T
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D25/22/3BUS/V; OPRD2: D25/22/KA78/I_R; OPRD3: D25/22/KA78/I_S; OPRD4: D25/22/KA78/I_T
D25 | 延平DS | 22 | 22kV | KA51 | 平51線(KA51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA51/kVA; OPRD2: D25/22/KA51/KVAR
D25 | 延平DS | 22 | 22kV | KA52 | 平52線(KA52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA52/kVA; OPRD2: D25/22/KA52/KVAR
D25 | 延平DS | 22 | 22kV | KA53 | 平53線(KA53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA53/kVA; OPRD2: D25/22/KA53/KVAR
D25 | 延平DS | 22 | 22kV | KA54 | 平54線(KA54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA54/kVA; OPRD2: D25/22/KA54/KVAR
D25 | 延平DS | 22 | 22kV | KA55 | 平55線(KA55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA55/kVA; OPRD2: D25/22/KA55/KVAR
D25 | 延平DS | 22 | 22kV | KA56 | 平56線(KA56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA56/kVA; OPRD2: D25/22/KA56/KVAR
D25 | 延平DS | 22 | 22kV | KA57 | 平57線(KA57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA57/kVA; OPRD2: D25/22/KA57/KVAR
D25 | 延平DS | 22 | 22kV | KA58 | 平58線(KA58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA58/kVA; OPRD2: D25/22/KA58/KVAR
D25 | 延平DS | 22 | 22kV | KA61 | 平61線(KA61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA61/kVA; OPRD2: D25/22/KA61/KVAR
D25 | 延平DS | 22 | 22kV | KA62 | 平62線(KA62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA62/kVA; OPRD2: D25/22/KA62/KVAR
D25 | 延平DS | 22 | 22kV | KA63 | 平63線(KA63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA63/kVA; OPRD2: D25/22/KA63/KVAR
D25 | 延平DS | 22 | 22kV | KA64 | 平64線(KA64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA64/kVA; OPRD2: D25/22/KA64/KVAR
D25 | 延平DS | 22 | 22kV | KA65 | 平65線(KA65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA65/kVA; OPRD2: D25/22/KA65/KVAR
D25 | 延平DS | 22 | 22kV | KA66 | 平66線(KA66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA66/kVA; OPRD2: D25/22/KA66/KVAR
D25 | 延平DS | 22 | 22kV | KA67 | 平67線(KA67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA67/kVA; OPRD2: D25/22/KA67/KVAR
D25 | 延平DS | 22 | 22kV | KA68 | 平68線(KA68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA68/kVA; OPRD2: D25/22/KA68/KVAR
D25 | 延平DS | 22 | 22kV | KA71 | 平71線(KA71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA71/kVA; OPRD2: D25/22/KA71/KVAR
D25 | 延平DS | 22 | 22kV | KA72 | 平72線(KA72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA72/kVA; OPRD2: D25/22/KA72/KVAR
D25 | 延平DS | 22 | 22kV | KA73 | 平73線(KA73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA73/kVA; OPRD2: D25/22/KA73/KVAR
D25 | 延平DS | 22 | 22kV | KA74 | 平74線(KA74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA74/kVA; OPRD2: D25/22/KA74/KVAR
D25 | 延平DS | 22 | 22kV | KA75 | 平75線(KA75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA75/kVA; OPRD2: D25/22/KA75/KVAR
D25 | 延平DS | 22 | 22kV | KA76 | 平76線(KA76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA76/kVA; OPRD2: D25/22/KA76/KVAR
D25 | 延平DS | 22 | 22kV | KA77 | 平77線(KA77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA77/kVA; OPRD2: D25/22/KA77/KVAR
D25 | 延平DS | 22 | 22kV | KA78 | 平78線(KA78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D25_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D25/22/KA78/kVA; OPRD2: D25/22/KA78/KVAR
D25 | 延平DS | 0 |  | CalcPoint |  |  | DTR_MW | [9 empty] | B1/D25_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: D25//2DTR/MW; OPRD2: D25/22/310/MW
D25 | 延平DS | 0 |  | CalcPoint |  |  | DTR_MVAR | [9 empty] | B1/D25_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: D25//2DTR/MVAR; OPRD2: D25/22/310/MVAR
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D25_A1 | [12 empty] | 延平DS.210_SC_MVAR | 23KV#1SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D25/22/210/CB; OPRD2: 13.8; OPRD3: 0
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D25_A1 | [12 empty] | 延平DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D25/22/220/CB; OPRD2: 13.8; OPRD3: 0
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D25_A1 | [12 empty] | 延平DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D25/22/230/CB; OPRD2: 13.8; OPRD3: 0
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D25_A1 | [12 empty] | 延平DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D25/22/240/CB; OPRD2: 13.8; OPRD3: 0
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D25_A1 | [12 empty] | 延平DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D25/22/250/CB; OPRD2: 13.8; OPRD3: 0
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D25_A1 | [12 empty] | 延平DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D25/22/260/CB; OPRD2: 13.8; OPRD3: 0
D25 | 延平DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D25_A1 | [12 empty] | 延平DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_14 |  | com_alarm_40 | D25//1DTR/96D | D25//1DTR/51ZA | D25//1DTR/TRA | D25//1DTR/96B2 | D25//1DTR/63Q | D25//1DTR/96B1 | D25//1DTR/96PA | D25//1DTR/87A | D25//2DTR/TRA | D25//2DTR/96B1 | D25//2DTR/96B2 | D25//2DTR/63Q | D25//2DTR/87A | D25//2DTR/96D | D25//2DTR/51ZA | D25//2DTR/96PA | D25//3DTR/TRA | D25//3DTR/51ZA | D25//3DTR/96B2 | D25//3DTR/96B1 | D25//3DTR/63Q | D25//3DTR/96PA | D25//3DTR/87A | D25//3DTR/96D | D25/161/1750/PHA | D25/161/1750/GDA | D25/161/1760/GDA | D25/161/1760/PHA | D25/161/1770/GDA | D25/161/1770/PHA | D25/161/1BUS/87A | D25/161/2BUS/87A | D25/22/310/PHA | D25/22/310/GDA | D25/22/330/PHA | D25/22/330/GDA | D25/22/340/GDA | D25/22/340/PHA | D25/22/350/PHA | D25/22/350/GDA
D25 | 延平DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D25_A1 | [12 empty] | 延平DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D25//1DTR/TRF; OPRD2: D25//2DTR/TRF; OPRD3: D25//3DTR/TRF
D25 | 延平DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/22/350/CB
D25 | 延平DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/161/1750/CB
D25 | 延平DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/161/1760/CB
D25 | 延平DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/161/1770/CB
D25 | 延平DS | 22 | 22kV | 310_D1 | #1DTR(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/22/310/CB
D25 | 延平DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/22/330/CB
D25 | 延平DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/22/340/CB
D25 | 延平DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/0/RTU/RTU_R_L
D25 | 延平DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/0/StaDev/STUV
D25 | 延平DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/0/StaDev/DCA
D25 | 延平DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/0/StaDev/DCE
D25 | 延平DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/22/ComPoint/CBA
D25 | 延平DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/22/ComPoint/CBF
D25 | 延平DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D25_D1 | [17 empty] | lamp2CC | OPRD1: D25/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D25 | 延平DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 延平DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D25/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 延平DS.1510_AMP | 健康線 AMP | LINE161 | D25/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 延平DS.1550_AMP | 台南延平線 AMP | LINE161 | D25/161/1550/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 延平DS.1560_AMP | 忠孝延平線 AMP | LINE161 | D25/161/1560/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1001 | 900.000000 | 900.000000 | 1001.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D25 | 延平DS | 0 |  | TRTOT | 延平主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 延平DS.TRTOT_MW | 延平主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 6 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  | TRTOT | 延平主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 延平DS.TRTOT_MVAR | 延平主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 7 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七一線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七一線KVA | 23KV平七一線KVA | FEEDER |  |  | KVA_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七一線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七一線KW | 23KV平七一線KW | FEEDER |  |  | KW_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七七線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七七線KVA | 23KV平七七線KVA | FEEDER |  |  | KVA_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七七線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七七線KW | 23KV平七七線KW | FEEDER |  |  | KW_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七二線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七二線KVA | 23KV平七二線KVA | FEEDER |  |  | KVA_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七二線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七二線KW | 23KV平七二線KW | FEEDER |  |  | KW_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七八線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七八線KVA | 23KV平七八線KVA | FEEDER |  |  | KVA_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七八線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七八線KW | 23KV平七八線KW | FEEDER |  |  | KW_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七三線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七三線KVA | 23KV平七三線KVA | FEEDER |  |  | KVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七三線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七三線KW | 23KV平七三線KW | FEEDER |  |  | KW_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七五線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七五線KVA | 23KV平七五線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七五線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七五線KW | 23KV平七五線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七六線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七六線KVA | 23KV平七六線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七六線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七六線KW | 23KV平七六線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七四線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七四線KVA | 23KV平七四線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平七四線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平七四線KW | 23KV平七四線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五一線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五一線KVA | 23KV平五一線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五一線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五一線KW | 23KV平五一線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五七線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五七線KVA | 23KV平五七線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五七線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五七線KW | 23KV平五七線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五二線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五二線KVA | 23KV平五二線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五二線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五二線KW | 23KV平五二線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五八線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五八線KVA | 23KV平五八線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五八線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五八線KW | 23KV平五八線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五三線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五三線KVA | 23KV平五三線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五三線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五三線KW | 23KV平五三線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五六線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五六線KVA | 23KV平五六線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五六線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五六線KW | 23KV平五六線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五四線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五四線KVA | 23KV平五四線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五四線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五四線KW | 23KV平五四線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六一線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六一線KVA | 23KV平六一線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六一線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六一線KW | 23KV平六一線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六七線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六七線KVA | 23KV平六七線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六七線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六七線KW | 23KV平六七線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六二線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六二線KVA | 23KV平六二線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六二線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六二線KW | 23KV平六二線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六八線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六八線KVA | 23KV平六八線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六八線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六八線KW | 23KV平六八線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六三線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六三線KVA | 23KV平六三線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六三線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六三線KW | 23KV平六三線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六五線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六五線KVA | 23KV平六五線KVA | FEEDER |  |  | KVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六五線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六五線KW | 23KV平六五線KW | FEEDER |  |  | KW_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六六線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六六線KVA | 23KV平六六線KVA | FEEDER |  |  | KVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六六線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六六線KW | 23KV平六六線KW | FEEDER |  |  | KW_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六四線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六四線KVA | 23KV平六四線KVA | FEEDER |  |  | KVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平六四線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平六四線KW | 23KV平六四線KW | FEEDER |  |  | KW_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五五線KVA | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五五線KVA | 23KV平五五線KVA | FEEDER |  |  | KVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  |  |  |  | 平五五線KW | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.平五五線KW | 23KV平五五線KW | FEEDER |  |  | KW_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_MVA | #1DTR二次側 MVA | MTR | D25//1DTR/MVA |  | MVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_LOAD | #1DTR 負載率 | MTR | D25//1DTR/Loading |  | TR_LOAD_60 |  |  | 57 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_PF | #1DTR 功率因素 | MTR | D25//1DTR/PF |  | RPDC_PF_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D25 | 延平DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 62 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_MW | #2DTR MW | MTR | D25//2DTR/MW |  | MTR_PQ_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_MVAR | #2DTR MVAR | MTR | D25//2DTR/MVAR |  | MTR_PQ_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_MVA | #2DTR二次側 MVA | MTR | D25//2DTR/MVA |  | MVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_LOAD | #2DTR 負載率 | MTR | D25//2DTR/Loading |  | TR_LOAD_60 |  |  | 67 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_PF | #2DTR 功率因素 | MTR | D25//2DTR/PF |  | RPDC_PF_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D25 | 延平DS | 22 | 22kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.210_SC_MVAR | 23KV#1SC MVAR | SC | D25/22/210/MVAR |  | SC_CAL_23 |  |  | 69 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D25/22/220/MVAR |  | SC_CAL_23 |  |  | 70 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D25/22/230/MVAR |  | SC_CAL_23 |  |  | 71 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D25/22/240/MVAR |  | SC_CAL_23 |  |  | 72 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D25/22/250/MVAR |  | SC_CAL_23 |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 延平DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D25/22/260/MVAR |  | SC_CAL_23 |  |  | 74 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 延平DS.23KV#2BUS_KV | 23KV #2BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 75 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | _CBA | 斷路器重故障(_CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.23KV_CBA_4 | 23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 82 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | _CBF | 斷路器輕故障(_CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.23KV_CBF_4 | 23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 83 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 84 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D25 | 延平DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 延平DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D25/0/CalcPoint/SUBA |  | STATION_FAULT_14 |  |  | 85 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 延平DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D25/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 86 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 87 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 88 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510_AMP | 健康線 | [27 empty] | ADCS_S | [8 empty] | 延平DS.1510_AMP_A | 健康線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 161 | 161kV | 1550_AMP | 台南延平線 | [27 empty] | ADCS_S | [8 empty] | 延平DS.1550_AMP_A | 台南延平線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 161 | 161kV | 1560_AMP | 忠孝延平線 | [27 empty] | ADCS_S | [8 empty] | 延平DS.1560_AMP_A | 忠孝延平線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 延平DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 93 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 94 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 95 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.210_CB_4 | 210(23KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 96 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.220_CB_4 | 220(23KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 97 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.230_CB_4 | 230(23KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 98 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.240_CB_4 | 240(23KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 99 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 101 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_PERM | #1DTR TAP PERMISSION POINT | MTR | D25//1DTR/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | D25//2DTR/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D25//3DTR/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 1DTR_MVA | #1DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.#1DTR_MVA_4 | #1DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 2DTR_MVA | #2DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.#2DTR_MVA_4 | #2DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 2DTR_MVA | #2DTR |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.#2DTR_MVA_5 | #2DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 3DTR_MVA | #3DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 延平DS.#3DTR_MVA_4 | #3DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 1BUS | #1BUS |  | 23KV#1BUSC | [25 empty] | CDCS | [8 empty] | 延平DS.23KV#1BUSC | #1BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 延平DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 延平DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 延平DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 延平DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T3 |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 延平DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D25 | 延平DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 延平DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 延平DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 119 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D25/0/RTU/ADCH1 |  |  |  | CDC | 120 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D25/0/RTU/ADCH2 |  |  |  | CDC | 121 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D25/0/RTU/ADCH3 |  |  |  | CDC | 122 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D25/0/RTU/ADCL1 |  |  |  | CDC | 123 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D25/0/RTU/ADCL2 |  |  |  | CDC | 124 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D25/0/RTU/ADCL3 |  |  |  | CDC | 125 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D25/161/1BUS/V |  |  |  | CDC | 126 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D25 | 延平DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D25/161/2BUS/V |  |  |  | CDC | 127 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D25 | 延平DS | 22 | 22kV | 1BUS | #1BUS |  | V | [17 empty] | 1-AD | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV#1BUS_KV | 23KV #1BUS KV | BUS | D25/22/1BUS/V |  |  |  | CDC | 128 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-D8 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D25/22/2ABUS/V |  |  |  | CDC | 129 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-EE | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D25/22/2BBUS/V |  |  |  | CDC | 130 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-89 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D25/22/3BUS/V |  |  |  | CDC | 131 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1510_MW | 健康線 MW | LINE161 | D25/161/1510/MW |  |  |  | CDC | 132 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1510_MVAR | 健康線 MVAR | LINE161 | D25/161/1510/MVAR |  |  |  | CDC | 133 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1550_MW | 台南延平線 MW | LINE161 | D25/161/1550/MW |  |  |  | CDC | 134 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1550_MVAR | 台南延平線 MVAR | LINE161 | D25/161/1550/MVAR |  |  |  | CDC | 135 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1560_MW | 忠孝延平線 MW | LINE161 | D25/161/1560/MW |  |  |  | CDC | 136 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1560_MVAR | 忠孝延平線 MVAR | LINE161 | D25/161/1560/MVAR |  |  |  | CDC | 137 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D25 | 延平DS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-94 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1500TIE_AMP | 1500TIE AMP | TIE | D25/161/1500/I_R |  |  |  | CDC | 138 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-91 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D25/0/StaDev/DCV_N |  |  |  | CDC | 139 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D25 | 延平DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-90 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D25/0/StaDev/DCV_P |  |  |  | CDC | 140 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七一線 | 平七一線 |  | 平七一線KVAR | [17 empty] | 2-8A | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七一線KVAR | 23KV平七一線 KVAR | FEEDER | D25/22/KA71/KVAR |  |  |  | CDC | 141 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七一線 | 平七一線 |  | 平七一線A1 | [17 empty] | 2-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七一線A1 | 23KV平七一線 R相AMP | FEEDER | D25/22/KA71/I_R |  |  |  | CDC | 142 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七一線 | 平七一線 |  | 平七一線A2 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七一線A2 | 23KV平七一線 S相AMP | FEEDER | D25/22/KA71/I_S |  |  |  | CDC | 143 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七一線 | 平七一線 |  | 平七一線A3 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七一線A3 | 23KV平七一線 T相AMP | FEEDER | D25/22/KA71/I_T |  |  |  | CDC | 144 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七七線 | 平七七線 |  | 平七七線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七七線KVAR | 23KV平七七線 KVAR | FEEDER | D25/22/KA77/KVAR |  |  |  | CDC | 145 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七七線 | 平七七線 |  | 平七七線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七七線A1 | 23KV平七七線 R相AMP | FEEDER | D25/22/KA77/I_R |  |  |  | CDC | 146 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七七線 | 平七七線 |  | 平七七線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七七線A2 | 23KV平七七線 S相AMP | FEEDER | D25/22/KA77/I_S |  |  |  | CDC | 147 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七七線 | 平七七線 |  | 平七七線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七七線A3 | 23KV平七七線 T相AMP | FEEDER | D25/22/KA77/I_T |  |  |  | CDC | 148 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七二線 | 平七二線 |  | 平七二線KVAR | [17 empty] | 2-8E | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七二線KVAR | 23KV平七二線 KVAR | FEEDER | D25/22/KA72/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七二線 | 平七二線 |  | 平七二線A1 | [17 empty] | 2-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七二線A1 | 23KV平七二線 R相AMP | FEEDER | D25/22/KA72/I_R |  |  |  | CDC | 150 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七二線 | 平七二線 |  | 平七二線A2 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七二線A2 | 23KV平七二線 S相AMP | FEEDER | D25/22/KA72/I_S |  |  |  | CDC | 151 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七二線 | 平七二線 |  | 平七二線A3 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七二線A3 | 23KV平七二線 T相AMP | FEEDER | D25/22/KA72/I_T |  |  |  | CDC | 152 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七八線 | 平七八線 |  | 平七八線KVAR | [17 empty] | 2-A6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七八線KVAR | 23KV平七八線 KVAR | FEEDER | D25/22/KA78/KVAR |  |  |  | CDC | 153 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七八線 | 平七八線 |  | 平七八線A1 | [17 empty] | 2-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七八線A1 | 23KV平七八線 R相AMP | FEEDER | D25/22/KA78/I_R |  |  |  | CDC | 154 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七八線 | 平七八線 |  | 平七八線A2 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七八線A2 | 23KV平七八線 S相AMP | FEEDER | D25/22/KA78/I_S |  |  |  | CDC | 155 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七八線 | 平七八線 |  | 平七八線A3 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七八線A3 | 23KV平七八線 T相AMP | FEEDER | D25/22/KA78/I_T |  |  |  | CDC | 156 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七三線 | 平七三線 |  | 平七三線KVAR | [17 empty] | 2-92 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七三線KVAR | 23KV平七三線 KVAR | FEEDER | D25/22/KA73/KVAR |  |  |  | CDC | 157 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七三線 | 平七三線 |  | 平七三線A1 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七三線A1 | 23KV平七三線 R相AMP | FEEDER | D25/22/KA73/I_R |  |  |  | CDC | 158 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七三線 | 平七三線 |  | 平七三線A2 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七三線A2 | 23KV平七三線 S相AMP | FEEDER | D25/22/KA73/I_S |  |  |  | CDC | 159 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七三線 | 平七三線 |  | 平七三線A3 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七三線A3 | 23KV平七三線 T相AMP | FEEDER | D25/22/KA73/I_T |  |  |  | CDC | 160 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七五線 | 平七五線 |  | 平七五線KVAR | [17 empty] | 2-9A | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七五線KVAR | 23KV平七五線 KVAR | FEEDER | D25/22/KA75/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七五線 | 平七五線 |  | 平七五線A1 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七五線A1 | 23KV平七五線 R相AMP | FEEDER | D25/22/KA75/I_R |  |  |  | CDC | 162 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七五線 | 平七五線 |  | 平七五線A2 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七五線A2 | 23KV平七五線 S相AMP | FEEDER | D25/22/KA75/I_S |  |  |  | CDC | 163 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七五線 | 平七五線 |  | 平七五線A3 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七五線A3 | 23KV平七五線 T相AMP | FEEDER | D25/22/KA75/I_T |  |  |  | CDC | 164 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七六線 | 平七六線 |  | 平七六線KVAR | [17 empty] | 2-9E | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七六線KVAR | 23KV平七六線 KVAR | FEEDER | D25/22/KA76/KVAR |  |  |  | CDC | 165 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七六線 | 平七六線 |  | 平七六線A1 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七六線A1 | 23KV平七六線 R相AMP | FEEDER | D25/22/KA76/I_R |  |  |  | CDC | 166 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七六線 | 平七六線 |  | 平七六線A2 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七六線A2 | 23KV平七六線 S相AMP | FEEDER | D25/22/KA76/I_S |  |  |  | CDC | 167 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七六線 | 平七六線 |  | 平七六線A3 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七六線A3 | 23KV平七六線 T相AMP | FEEDER | D25/22/KA76/I_T |  |  |  | CDC | 168 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七四線 | 平七四線 |  | 平七四線KVAR | [17 empty] | 2-96 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七四線KVAR | 23KV平七四線 KVAR | FEEDER | D25/22/KA74/KVAR |  |  |  | CDC | 169 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七四線 | 平七四線 |  | 平七四線A1 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七四線A1 | 23KV平七四線 R相AMP | FEEDER | D25/22/KA74/I_R |  |  |  | CDC | 170 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七四線 | 平七四線 |  | 平七四線A2 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七四線A2 | 23KV平七四線 S相AMP | FEEDER | D25/22/KA74/I_S |  |  |  | CDC | 171 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七四線 | 平七四線 |  | 平七四線A3 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七四線A3 | 23KV平七四線 T相AMP | FEEDER | D25/22/KA74/I_T |  |  |  | CDC | 172 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五一線 | 平五一線 |  | 平五一線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五一線KVAR | 23KV平五一線 KVAR | FEEDER | D25/22/KA51/KVAR |  |  |  | CDC | 173 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五一線 | 平五一線 |  | 平五一線A1 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五一線A1 | 23KV平五一線 R相AMP | FEEDER | D25/22/KA51/I_R |  |  |  | CDC | 174 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五一線 | 平五一線 |  | 平五一線A2 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五一線A2 | 23KV平五一線 S相AMP | FEEDER | D25/22/KA51/I_S |  |  |  | CDC | 175 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五一線 | 平五一線 |  | 平五一線A3 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五一線A3 | 23KV平五一線 T相AMP | FEEDER | D25/22/KA51/I_T |  |  |  | CDC | 176 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五七線 | 平五七線 |  | 平五七線KVAR | [17 empty] | 1-C8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五七線KVAR | 23KV平五七線 KVAR | FEEDER | D25/22/KA57/KVAR |  |  |  | CDC | 177 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五七線 | 平五七線 |  | 平五七線A1 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五七線A1 | 23KV平五七線 R相AMP | FEEDER | D25/22/KA57/I_R |  |  |  | CDC | 178 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五七線 | 平五七線 |  | 平五七線A2 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五七線A2 | 23KV平五七線 S相AMP | FEEDER | D25/22/KA57/I_S |  |  |  | CDC | 179 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五七線 | 平五七線 |  | 平五七線A3 | [17 empty] | 1-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五七線A3 | 23KV平五七線 T相AMP | FEEDER | D25/22/KA57/I_T |  |  |  | CDC | 180 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五二線 | 平五二線 |  | 平五二線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五二線KVAR | 23KV平五二線 KVAR | FEEDER | D25/22/KA52/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五二線 | 平五二線 |  | 平五二線A1 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五二線A1 | 23KV平五二線 R相AMP | FEEDER | D25/22/KA52/I_R |  |  |  | CDC | 182 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五二線 | 平五二線 |  | 平五二線A2 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五二線A2 | 23KV平五二線 S相AMP | FEEDER | D25/22/KA52/I_S |  |  |  | CDC | 183 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五二線 | 平五二線 |  | 平五二線A3 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五二線A3 | 23KV平五二線 T相AMP | FEEDER | D25/22/KA52/I_T |  |  |  | CDC | 184 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五八線 | 平五八線 |  | 平五八線KVAR | [17 empty] | 1-CC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五八線KVAR | 23KV平五八線 KVAR | FEEDER | D25/22/KA58/KVAR |  |  |  | CDC | 185 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五八線 | 平五八線 |  | 平五八線A1 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五八線A1 | 23KV平五八線 R相AMP | FEEDER | D25/22/KA58/I_R |  |  |  | CDC | 186 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五八線 | 平五八線 |  | 平五八線A2 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五八線A2 | 23KV平五八線 S相AMP | FEEDER | D25/22/KA58/I_S |  |  |  | CDC | 187 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五八線 | 平五八線 |  | 平五八線A3 | [17 empty] | 1-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五八線A3 | 23KV平五八線 T相AMP | FEEDER | D25/22/KA58/I_T |  |  |  | CDC | 188 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五三線 | 平五三線 |  | 平五三線KVAR | [17 empty] | 1-B6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五三線KVAR | 23KV平五三線 KVAR | FEEDER | D25/22/KA53/KVAR |  |  |  | CDC | 189 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五三線 | 平五三線 |  | 平五三線A1 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五三線A1 | 23KV平五三線 R相AMP | FEEDER | D25/22/KA53/I_R |  |  |  | CDC | 190 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五三線 | 平五三線 |  | 平五三線A2 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五三線A2 | 23KV平五三線 S相AMP | FEEDER | D25/22/KA53/I_S |  |  |  | CDC | 191 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五三線 | 平五三線 |  | 平五三線A3 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五三線A3 | 23KV平五三線 T相AMP | FEEDER | D25/22/KA53/I_T |  |  |  | CDC | 192 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五六線 | 平五六線 |  | 平五六線KVAR | [17 empty] | 1-C4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五六線KVAR | 23KV平五六線 KVAR | FEEDER | D25/22/KA56/KVAR |  |  |  | CDC | 193 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五六線 | 平五六線 |  | 平五六線A1 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五六線A1 | 23KV平五六線 R相AMP | FEEDER | D25/22/KA56/I_R |  |  |  | CDC | 194 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五六線 | 平五六線 |  | 平五六線A2 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五六線A2 | 23KV平五六線 S相AMP | FEEDER | D25/22/KA56/I_S |  |  |  | CDC | 195 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五六線 | 平五六線 |  | 平五六線A3 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五六線A3 | 23KV平五六線 T相AMP | FEEDER | D25/22/KA56/I_T |  |  |  | CDC | 196 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五四線 | 平五四線 |  | 平五四線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五四線KVAR | 23KV平五四線 KVAR | FEEDER | D25/22/KA54/KVAR |  |  |  | CDC | 197 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五四線 | 平五四線 |  | 平五四線A1 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五四線A1 | 23KV平五四線 R相AMP | FEEDER | D25/22/KA54/I_R |  |  |  | CDC | 198 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五四線 | 平五四線 |  | 平五四線A2 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五四線A2 | 23KV平五四線 S相AMP | FEEDER | D25/22/KA54/I_S |  |  |  | CDC | 199 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五四線 | 平五四線 |  | 平五四線A3 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五四線A3 | 23KV平五四線 T相AMP | FEEDER | D25/22/KA54/I_T |  |  |  | CDC | 200 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六一線 | 平六一線 |  | 平六一線KVAR | [17 empty] | 1-D9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六一線KVAR | 23KV平六一線 KVAR | FEEDER | D25/22/KA61/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六一線 | 平六一線 |  | 平六一線A1 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六一線A1 | 23KV平六一線 R相AMP | FEEDER | D25/22/KA61/I_R |  |  |  | CDC | 202 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六一線 | 平六一線 |  | 平六一線A2 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六一線A2 | 23KV平六一線 S相AMP | FEEDER | D25/22/KA61/I_S |  |  |  | CDC | 203 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六一線 | 平六一線 |  | 平六一線A3 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六一線A3 | 23KV平六一線 T相AMP | FEEDER | D25/22/KA61/I_T |  |  |  | CDC | 204 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六七線 | 平六七線 |  | 平六七線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六七線KVAR | 23KV平六七線 KVAR | FEEDER | D25/22/KA67/KVAR |  |  |  | CDC | 205 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六七線 | 平六七線 |  | 平六七線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六七線A1 | 23KV平六七線 R相AMP | FEEDER | D25/22/KA67/I_R |  |  |  | CDC | 206 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六七線 | 平六七線 |  | 平六七線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六七線A2 | 23KV平六七線 S相AMP | FEEDER | D25/22/KA67/I_S |  |  |  | CDC | 207 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六七線 | 平六七線 |  | 平六七線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六七線A3 | 23KV平六七線 T相AMP | FEEDER | D25/22/KA67/I_T |  |  |  | CDC | 208 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六二線 | 平六二線 |  | 平六二線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六二線KVAR | 23KV平六二線 KVAR | FEEDER | D25/22/KA62/KVAR |  |  |  | CDC | 209 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六二線 | 平六二線 |  | 平六二線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六二線A1 | 23KV平六二線 R相AMP | FEEDER | D25/22/KA62/I_R |  |  |  | CDC | 210 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六二線 | 平六二線 |  | 平六二線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六二線A2 | 23KV平六二線 S相AMP | FEEDER | D25/22/KA62/I_S |  |  |  | CDC | 211 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六二線 | 平六二線 |  | 平六二線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六二線A3 | 23KV平六二線 T相AMP | FEEDER | D25/22/KA62/I_T |  |  |  | CDC | 212 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六八線 | 平六八線 |  | 平六八線KVAR | [17 empty] | 1-FB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六八線KVAR | 23KV平六八線 KVAR | FEEDER | D25/22/KA68/KVAR |  |  |  | CDC | 213 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六八線 | 平六八線 |  | 平六八線A1 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六八線A1 | 23KV平六八線 R相AMP | FEEDER | D25/22/KA68/I_R |  |  |  | CDC | 214 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六八線 | 平六八線 |  | 平六八線A2 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六八線A2 | 23KV平六八線 S相AMP | FEEDER | D25/22/KA68/I_S |  |  |  | CDC | 215 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六八線 | 平六八線 |  | 平六八線A3 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六八線A3 | 23KV平六八線 T相AMP | FEEDER | D25/22/KA68/I_T |  |  |  | CDC | 216 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六三線 | 平六三線 |  | 平六三線KVAR | [17 empty] | 1-E1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六三線KVAR | 23KV平六三線 KVAR | FEEDER | D25/22/KA63/KVAR |  |  |  | CDC | 217 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六三線 | 平六三線 |  | 平六三線A1 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六三線A1 | 23KV平六三線 R相AMP | FEEDER | D25/22/KA63/I_R |  |  |  | CDC | 218 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六三線 | 平六三線 |  | 平六三線A2 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六三線A2 | 23KV平六三線 S相AMP | FEEDER | D25/22/KA63/I_S |  |  |  | CDC | 219 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六三線 | 平六三線 |  | 平六三線A3 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六三線A3 | 23KV平六三線 T相AMP | FEEDER | D25/22/KA63/I_T |  |  |  | CDC | 220 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六五線 | 平六五線 |  | 平六五線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六五線KVAR | 23KV平六五線 KVAR | FEEDER | D25/22/KA65/KVAR |  |  |  | CDC | 221 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六五線 | 平六五線 |  | 平六五線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六五線A1 | 23KV平六五線 R相AMP | FEEDER | D25/22/KA65/I_R |  |  |  | CDC | 222 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六五線 | 平六五線 |  | 平六五線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六五線A2 | 23KV平六五線 S相AMP | FEEDER | D25/22/KA65/I_S |  |  |  | CDC | 223 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六五線 | 平六五線 |  | 平六五線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六五線A3 | 23KV平六五線 T相AMP | FEEDER | D25/22/KA65/I_T |  |  |  | CDC | 224 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六六線 | 平六六線 |  | 平六六線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六六線KVAR | 23KV平六六線 KVAR | FEEDER | D25/22/KA66/KVAR |  |  |  | CDC | 225 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六六線 | 平六六線 |  | 平六六線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六六線A1 | 23KV平六六線 R相AMP | FEEDER | D25/22/KA66/I_R |  |  |  | CDC | 226 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六六線 | 平六六線 |  | 平六六線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六六線A2 | 23KV平六六線 S相AMP | FEEDER | D25/22/KA66/I_S |  |  |  | CDC | 227 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六六線 | 平六六線 |  | 平六六線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六六線A3 | 23KV平六六線 T相AMP | FEEDER | D25/22/KA66/I_T |  |  |  | CDC | 228 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六四線 | 平六四線 |  | 平六四線KVAR | [17 empty] | 1-E5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六四線KVAR | 23KV平六四線 KVAR | FEEDER | D25/22/KA64/KVAR |  |  |  | CDC | 229 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六四線 | 平六四線 |  | 平六四線A1 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六四線A1 | 23KV平六四線 R相AMP | FEEDER | D25/22/KA64/I_R |  |  |  | CDC | 230 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六四線 | 平六四線 |  | 平六四線A2 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六四線A2 | 23KV平六四線 S相AMP | FEEDER | D25/22/KA64/I_S |  |  |  | CDC | 231 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六四線 | 平六四線 |  | 平六四線A3 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六四線A3 | 23KV平六四線 T相AMP | FEEDER | D25/22/KA64/I_T |  |  |  | CDC | 232 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五五線 | 平五五線 |  | 平五五線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五五線KVAR | 23KV平五五線 KVAR | FEEDER | D25/22/KA55/KVAR |  |  |  | CDC | 233 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五五線 | 平五五線 |  | 平五五線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五五線A1 | 23KV平五五線 R相AMP | FEEDER | D25/22/KA55/I_R |  |  |  | CDC | 234 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五五線 | 平五五線 |  | 平五五線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五五線A2 | 23KV平五五線 S相AMP | FEEDER | D25/22/KA55/I_S |  |  |  | CDC | 235 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五五線 | 平五五線 |  | 平五五線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五五線A3 | 23KV平五五線 T相AMP | FEEDER | D25/22/KA55/I_T |  |  |  | CDC | 236 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | _100 | 100 |  | I_R | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | D25/22/100/I_R |  |  |  | CDC | 237 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | _100 | 100 |  | I_S | [17 empty] | 1-D1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | D25/22/100/I_S |  |  |  | CDC | 238 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | _100 | 100 |  | I_T | [17 empty] | 1-D2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | D25/22/100/I_T |  |  |  | CDC | 239 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 1-FF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D25/22/200/I_R |  |  |  | CDC | 240 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 2-82 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D25/22/200/I_S |  |  |  | CDC | 241 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 2-83 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D25/22/200/I_T |  |  |  | CDC | 242 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1DTR | #1DTR二次側 |  | MW | [17 empty] | 1-A8 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_MW | #1DTR二次側 MW | MTR | D25/22/310/MW |  |  |  | CDC | 243 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 1DTR | #1DTR二次側 |  | MVAR | [17 empty] | 1-A9 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_MVAR | #1DTR二次側 MVAR | MTR | D25/22/310/MVAR |  |  |  | CDC | 244 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 1DTR | #1DTR二次側 |  | I_R | [17 empty] | 1-AA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_A1 | #1DTR二次側 R相AMP | MTR | D25/22/310/I_R |  |  |  | CDC | 245 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1DTR | #1DTR二次側 |  | I_S | [17 empty] | 1-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_A2 | #1DTR二次側 S相AMP | MTR | D25/22/310/I_S |  |  |  | CDC | 246 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1DTR | #1DTR二次側 |  | I_T | [17 empty] | 1-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_A3 | #1DTR二次側 T相AMP | MTR | D25/22/310/I_T |  |  |  | CDC | 247 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-95 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_OIL | #1DTR 油溫 | MTR | D25//1DTR/OilTemp |  |  |  | CDC | 248 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | CoilTemp | [17 empty] | 1-96 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_COIL | #1DTR 線溫 | MTR | D25//1DTR/CoilTemp |  |  |  | CDC | 249 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | TapPosMv | [17 empty] | 1-97 |  | 1-61 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 延平DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | D25//1DTR/Tap Chan |  |  |  | CDC | 250 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-98 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR_OIL | #2DTR 油溫 | MTR | D25//2DTR/OilTemp |  |  |  | CDC | 251 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR_COIL | #2DTR 線溫 | MTR | D25//2DTR/CoilTemp |  |  |  | CDC | 252 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | TapPosMv | [17 empty] | 1-9A |  | 1-63 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | D25//2DTR/Tap Chan |  |  |  | CDC | 253 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-D3 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D25/22/330/MW |  |  |  | CDC | 254 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-D4 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D25/22/330/MVAR |  |  |  | CDC | 255 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-D5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D25/22/330/I_R |  |  |  | CDC | 256 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-D6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D25/22/330/I_S |  |  |  | CDC | 257 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-D7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D25/22/330/I_T |  |  |  | CDC | 258 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 1-E9 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D25/22/340/MW |  |  |  | CDC | 259 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 1-EA | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D25/22/340/MVAR |  |  |  | CDC | 260 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 1-EB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D25/22/340/I_R |  |  |  | CDC | 261 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 1-EC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D25/22/340/I_S |  |  |  | CDC | 262 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 1-ED | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D25/22/340/I_T |  |  |  | CDC | 263 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 2-84 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_MW | #3DTR二次側 MW | MTR | D25/22/350/KW |  |  |  | CDC | 264 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 2-85 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D25/22/350/KVAR |  |  |  | CDC | 265 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D25 | 延平DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 2-86 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D25/22/350/I_R |  |  |  | CDC | 266 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 2-87 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D25/22/350/I_S |  |  |  | CDC | 267 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 2-88 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D25/22/350/I_T |  |  |  | CDC | 268 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-9B | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_OIL | #3DTR 油溫 | MTR | D25//3DTR/OilTemp |  |  |  | CDC | 269 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_COIL | #3DTR 線溫 | MTR | D25//3DTR/CoilTemp |  |  |  | CDC | 270 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-9D |  | 1-65 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 延平DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D25//3DTR/Tap Chan |  |  |  | CDC | 271 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D25 | 延平DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D25/0/RTU/ADCL4 |  |  |  | CDC | 272 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D25/0/RTU/ADCH4 |  |  |  | CDC | 273 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五一線 | 平五一線 |  | 平五一線A0 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五一線A0 | 23KV平五一線 N相AMP | FEEDER | D25/22/KA51/I_N |  |  |  | CDC | 274 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五二線 | 平五二線 |  | 平五二線A0 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五二線A0 | 23KV平五二線 N相AMP | FEEDER | D25/22/KA52/I_N |  |  |  | CDC | 275 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五三線 | 平五三線 |  | 平五三線A0 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五三線A0 | 23KV平五三線 N相AMP | FEEDER | D25/22/KA53/I_N |  |  |  | CDC | 276 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五四線 | 平五四線 |  | 平五四線A0 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五四線A0 | 23KV平五四線 N相AMP | FEEDER | D25/22/KA54/I_N |  |  |  | CDC | 277 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五五線 | 平五五線 |  | 平五五線A0 | [17 empty] | 2-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五五線A0 | 23KV平五五線 N相AMP | FEEDER | D25/22/KA55/I_N |  |  |  | CDC | 278 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五六線 | 平五六線 |  | 平五六線A0 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五六線A0 | 23KV平五六線 N相AMP | FEEDER | D25/22/KA56/I_N |  |  |  | CDC | 279 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五七線 | 平五七線 |  | 平五七線A0 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五七線A0 | 23KV平五七線 N相AMP | FEEDER | D25/22/KA57/I_N |  |  |  | CDC | 280 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平五八線 | 平五八線 |  | 平五八線A0 | [17 empty] | 2-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平五八線A0 | 23KV平五八線 N相AMP | FEEDER | D25/22/KA58/I_N |  |  |  | CDC | 281 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六一線 | 平六一線 |  | 平六一線A0 | [17 empty] | 2-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六一線A0 | 23KV平六一線 N相AMP | FEEDER | D25/22/KA61/I_N |  |  |  | CDC | 282 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六二線 | 平六二線 |  | 平六二線A0 | [17 empty] | 2-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六二線A0 | 23KV平六二線 N相AMP | FEEDER | D25/22/KA62/I_N |  |  |  | CDC | 283 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六三線 | 平六三線 |  | 平六三線A0 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六三線A0 | 23KV平六三線 N相AMP | FEEDER | D25/22/KA63/I_N |  |  |  | CDC | 284 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六四線 | 平六四線 |  | 平六四線A0 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六四線A0 | 23KV平六四線 N相AMP | FEEDER | D25/22/KA64/I_N |  |  |  | CDC | 285 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六五線 | 平六五線 |  | 平六五線A0 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六五線A0 | 23KV平六五線 N相AMP | FEEDER | D25/22/KA65/I_N |  |  |  | CDC | 286 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六六線 | 平六六線 |  | 平六六線A0 | [17 empty] | 2-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六六線A0 | 23KV平六六線 N相AMP | FEEDER | D25/22/KA66/I_N |  |  |  | CDC | 287 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六七線 | 平六七線 |  | 平六七線A0 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六七線A0 | 23KV平六七線 N相AMP | FEEDER | D25/22/KA67/I_N |  |  |  | CDC | 288 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平六八線 | 平六八線 |  | 平六八線A0 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平六八線A0 | 23KV平六八線 N相AMP | FEEDER | D25/22/KA68/I_N |  |  |  | CDC | 289 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七一線 | 平七一線 |  | 平七一線A0 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七一線A0 | 23KV平七一線 N相AMP | FEEDER | D25/22/KA71/I_N |  |  |  | CDC | 290 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七二線 | 平七二線 |  | 平七二線A0 | [17 empty] | 2-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七二線A0 | 23KV平七二線 N相AMP | FEEDER | D25/22/KA72/I_N |  |  |  | CDC | 291 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七三線 | 平七三線 |  | 平七三線A0 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七三線A0 | 23KV平七三線 N相AMP | FEEDER | D25/22/KA73/I_N |  |  |  | CDC | 292 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七四線 | 平七四線 |  | 平七四線A0 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七四線A0 | 23KV平七四線 N相AMP | FEEDER | D25/22/KA74/I_N |  |  |  | CDC | 293 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七五線 | 平七五線 |  | 平七五線A0 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七五線A0 | 23KV平七五線 N相AMP | FEEDER | D25/22/KA75/I_N |  |  |  | CDC | 294 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七六線 | 平七六線 |  | 平七六線A0 | [17 empty] | 2-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七六線A0 | 23KV平七六線 N相AMP | FEEDER | D25/22/KA76/I_N |  |  |  | CDC | 295 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七七線 | 平七七線 |  | 平七七線A0 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七七線A0 | 23KV平七七線 N相AMP | FEEDER | D25/22/KA77/I_N |  |  |  | CDC | 296 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 22 | 22kV | 平七八線 | 平七八線 |  | 平七八線A0 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 延平DS.平七八線A0 | 23KV平七八線 N相AMP | FEEDER | D25/22/KA78/I_N |  |  |  | CDC | 297 | GENERICAIPoint | DS033_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1550_OF | 台南延平線 |  | R | [17 empty] | 1-8A | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1550_OF_R | 台南延平線 R相 油壓 | OTHER | D25/161/1550/OilPreR |  |  |  | CDC | 298 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1550_OF | 台南延平線 |  | S | [17 empty] | 1-8B | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1550_OF_S | 台南延平線 S相 油壓 | OTHER | D25/161/1550/OilPreS |  |  |  | CDC | 299 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1550_OF | 台南延平線 |  | T | [17 empty] | 1-8C | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1550_OF_T | 台南延平線 T相 油壓 | OTHER | D25/161/1550/OilPreT |  |  |  | CDC | 300 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1560_OF | 忠孝延平線 |  | R | [17 empty] | 1-8D | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1560_OF_R | 忠孝延平線 R相 油壓 | OTHER | D25/161/1560/OilPreR |  |  |  | CDC | 301 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1560_OF | 忠孝延平線 |  | S | [17 empty] | 1-8E | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1560_OF_S | 忠孝延平線 S相 油壓 | OTHER | D25/161/1560/OilPreS |  |  |  | CDC | 302 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 0 |  | 1560_OF | 忠孝延平線 |  | T | [17 empty] | 1-8F | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 延平DS.1560_OF_T | 忠孝延平線 T相 油壓 | OTHER | D25/161/1560/OilPreT |  |  |  | CDC | 303 | GENERICAIPoint | DS033_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1510_PHA | 健康線(1510) 相間RY | LINE161 | D25/161/1510/PHA |  |  |  | CDC | 304 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1510_GDA | 健康線(1510) 接地RY | LINE161 | D25/161/1510/GDA |  |  |  | CDC | 305 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | 85A | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1510_85A | 健康線(1510) 85RY | LINE161 | D25/161/1510/85A |  |  |  | CDC | 306 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | 74A | [17 empty] | 2-34-15 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1510_74A | 健康線(1510) 74RY | LINE161 | D25/0/ComPoint/IRFA |  |  |  | CDC | 307 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | 85UL | [17 empty] | 1-30-06 |  | 1-44 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1510_85UL | 健康線(1510) 85RY U/L | LINE161 | D25/161/1510/85UL |  |  |  | CDC | 308 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 延平DS.1510_CB | 1510(健康線) CB | LINE161 | D25/161/1510/CB |  |  |  | CDC | 309 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | DS1 | 1511 | [16 empty] | 1-35-00 | 1-35-01 | 1-78 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1511_DS | 1511(健康線) DS | LINE161 | D25/161/1510/DS1 |  |  |  | CDC | 310 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | DS2 | 1512 | [16 empty] | 1-35-02 | 1-35-03 | 1-79 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1512_DS | 1512(健康線) DS | LINE161 | D25/161/1510/DS2 |  |  |  | CDC | 311 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | DS3 | 1513 | [16 empty] | 1-35-04 | 1-35-05 | 1-7A | [5 empty] | ADCS_S | [8 empty] | 延平DS.1513_DS | 1513(健康線) DS | LINE161 | D25/161/1510/DS3 |  |  |  | CDC | 312 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | E3 | 1513E | [16 empty] | 1-35-06 | 1-35-07 | 1-7B | [5 empty] | ADCS_S | [8 empty] | 延平DS.1513E_ES | 1513E(健康線) ES | LINE161 | D25/161/1510/ES3 |  |  |  | CDC | 313 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1550_PHA | 台南延平線(1550) 相間RY | LINE161 | D25/161/1550/PHA |  |  |  | CDC | 314 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1550_GDA | 台南延平線(1550) 接地RY | LINE161 | D25/161/1550/GDA |  |  |  | CDC | 315 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 延平DS.1550_CB | 1550(台南延平線) CB | LINE161 | D25/161/1550/CB |  |  |  | CDC | 316 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | DS1 | 1551 | [16 empty] | 1-34-08 | 1-34-09 | 1-74 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1551_DS | 1551(台南延平線) DS | LINE161 | D25/161/1550/DS1 |  |  |  | CDC | 317 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | DS2 | 1552 | [16 empty] | 1-34-10 | 1-34-11 | 1-75 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1552_DS | 1552(台南延平線) DS | LINE161 | D25/161/1550/DS2 |  |  |  | CDC | 318 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | DS3 | 1553 | [16 empty] | 1-34-12 | 1-34-13 | 1-76 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1553_DS | 1553(台南延平線) DS | LINE161 | D25/161/1550/DS3 |  |  |  | CDC | 319 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | E3 | 1553E | [16 empty] | 1-34-14 | 1-34-15 | 1-77 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1553E_ES | 1553E(台南延平線) ES | LINE161 | D25/161/1550/ES3 |  |  |  | CDC | 320 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1560_PHA | 忠孝延平線(1560) 相間RY | LINE161 | D25/161/1560/PHA |  |  |  | CDC | 321 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1560_GDA | 忠孝延平線(1560) 接地RY | LINE161 | D25/161/1560/GDA |  |  |  | CDC | 322 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 延平DS.1560_CB | 1560(忠孝延平線) CB | LINE161 | D25/161/1560/CB |  |  |  | CDC | 323 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | DS1 | 1561 | [16 empty] | 1-34-00 | 1-34-01 | 1-70 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1561_DS | 1561(忠孝延平線) DS | LINE161 | D25/161/1560/DS1 |  |  |  | CDC | 324 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | DS2 | 1562 | [16 empty] | 1-34-02 | 1-34-03 | 1-71 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1562_DS | 1562(忠孝延平線) DS | LINE161 | D25/161/1560/DS2 |  |  |  | CDC | 325 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | DS3 | 1563 | [16 empty] | 1-34-04 | 1-34-05 | 1-72 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1563_DS | 1563(忠孝延平線) DS | LINE161 | D25/161/1560/DS3 |  |  |  | CDC | 326 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | E3 | 1563E | [16 empty] | 1-34-06 | 1-34-07 | 1-73 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1563E_ES | 1563E(忠孝延平線) ES | LINE161 | D25/161/1560/ES3 |  |  |  | CDC | 327 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 22 | 22kV | KA51 | 平五一線(KA51) |  | PHA | [17 empty] | 1-10-07 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA51_PHA | 23KV平五一線(KA51) 相間RY | FEEDER | D25/22/KA51/PHA |  |  |  | CDC | 328 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA51 | 平五一線(KA51) |  | GDA | [17 empty] | 1-11-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA51_GDA | 23KV平五一線(KA51) 接地RY | FEEDER | D25/22/KA51/GDA |  |  |  | CDC | 329 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA51_LCO | 平五一線(KA51) LCO |  | TapPosMv | [17 empty] | 2-31-00 |  | 2-26 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA51_LCO_TAP | 23KV平五一線(KA51) LCO TAP | FEEDER |  |  |  |  | CDC | 330 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA51 | KA51(23KV平五一線) |  | CB | [17 empty] | 1-10-06 |  | 1-12 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA51_CB | KA51(23KV平五一線) CB | FEEDER | D25/22/KA51/CB |  |  |  | CDC | 331 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA52 | 平五二線(KA52) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA52_PHA | 23KV平五二線(KA52) 相間RY | FEEDER | D25/22/KA52/PHA |  |  |  | CDC | 332 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA52 | 平五二線(KA52) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA52_GDA | 23KV平五二線(KA52) 接地RY | FEEDER | D25/22/KA52/GDA |  |  |  | CDC | 333 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA52_LCO | 平五二線(KA52) LCO |  | TapPosMv | [17 empty] | 2-31-01 |  | 2-27 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA52_LCO_TAP | 23KV平五二線(KA52) LCO TAP | FEEDER | D25/22/KA52/ADJ |  |  |  | CDC | 334 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA52 | KA52(23KV平五二線) |  | CB | [17 empty] | 1-11-01 |  | 1-13 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA52_CB | KA52(23KV平五二線) CB | FEEDER | D25/22/KA52/CB |  |  |  | CDC | 335 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA53 | 平五三線(KA53) |  | PHA | [17 empty] | 1-11-05 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA53_PHA | 23KV平五三線(KA53) 相間RY | FEEDER | D25/22/KA64/CB |  |  |  | CDC | 336 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA53 | 平五三線(KA53) |  | GDA | [17 empty] | 1-11-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA53_GDA | 23KV平五三線(KA53) 接地RY | FEEDER | D25/22/KA64/PHA |  |  |  | CDC | 337 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA53_LCO | 平五三線(KA53) LCO |  | TapPosMv | [17 empty] | 2-31-02 |  | 2-28 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA53_LCO_TAP | 23KV平五三線(KA53) LCO TAP | FEEDER | D25/22/KA53/ADJ |  |  |  | CDC | 338 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA53 | KA53(23KV平五三線) |  | CB | [17 empty] | 1-11-04 |  | 1-14 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA53_CB | KA53(23KV平五三線) CB | FEEDER | D25/22/KA53/CB |  |  |  | CDC | 339 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA54 | 平五四線(KA54) |  | PHA | [17 empty] | 1-12-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA54_PHA | 23KV平五四線(KA54) 相間RY | FEEDER | D25/22/230/CB |  |  |  | CDC | 340 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA54 | 平五四線(KA54) |  | GDA | [17 empty] | 1-12-01 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA54_GDA | 23KV平五四線(KA54) 接地RY | FEEDER | D25/22/230/SCA |  |  |  | CDC | 341 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA54_LCO | 平五四線(KA54) LCO |  | TapPosMv | [17 empty] | 2-31-03 |  | 2-29 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA54_LCO_TAP | 23KV平五四線(KA54) LCO TAP | FEEDER | D25/22/KA54/ADJ |  |  |  | CDC | 342 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA54 | KA54(23KV平五四線) |  | CB | [17 empty] | 1-11-07 |  | 1-15 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA54_CB | KA54(23KV平五四線) CB | FEEDER | D25/22/KA54/CB |  |  |  | CDC | 343 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA56 | 平五六線(KA56) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA56_PHA | 23KV平五六線(KA56) 相間RY | FEEDER | D25/22/KA56/PHA |  |  |  | CDC | 344 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA56 | 平五六線(KA56) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA56_GDA | 23KV平五六線(KA56) 接地RY | FEEDER | D25/22/KA56/GDA |  |  |  | CDC | 345 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA56_LCO | 平五六線(KA56) LCO |  | TapPosMv | [17 empty] | 2-31-05 |  | 2-2B | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA56_LCO_TAP | 23KV平五六線(KA56) LCO TAP | FEEDER | D25/22/KA56/ADJ |  |  |  | CDC | 346 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA56 | KA56(23KV平五六線) |  | CB | [17 empty] | 1-12-05 |  | 1-17 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA56_CB | KA56(23KV平五六線) CB | FEEDER | D25/22/KA56/CB |  |  |  | CDC | 347 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA61 | 平六一線(KA61) |  | PHA | [17 empty] | 1-14-05 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA61_PHA | 23KV平六一線(KA61) 相間RY | FEEDER | D25/22/260/CB |  |  |  | CDC | 348 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA61 | 平六一線(KA61) |  | GDA | [17 empty] | 1-14-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA61_GDA | 23KV平六一線(KA61) 接地RY | FEEDER | D25/22/KA61/GDA |  |  |  | CDC | 349 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA61_LCO | 平六一線(KA61) LCO |  | TapPosMv | [17 empty] | 2-31-08 |  | 2-2E | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA61_LCO_TAP | 23KV平六一線(KA61) LCO TAP | FEEDER | D25/22/KA61/ADJ |  |  |  | CDC | 350 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA61 | KA61(23KV平六一線) |  | CB | [17 empty] | 1-14-04 |  | 1-1C | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA61_CB | KA61(23KV平六一線) CB | FEEDER | D25/22/KA61/CB |  |  |  | CDC | 351 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA62 | 平六二線(KA62) |  | PHA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA62_PHA | 23KV平六二線(KA62) 相間RY | FEEDER | D25/22/KA62/PHA |  |  |  | CDC | 352 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA62 | 平六二線(KA62) |  | GDA | [17 empty] | 1-15-01 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA62_GDA | 23KV平六二線(KA62) 接地RY | FEEDER | D25/22/KA62/GDA |  |  |  | CDC | 353 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA62_LCO | 平六二線(KA62) LCO |  | TapPosMv | [17 empty] | 2-31-09 |  | 2-2F | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA62_LCO_TAP | 23KV平六二線(KA62) LCO TAP | FEEDER | D25/22/KA62/ADJ |  |  |  | CDC | 354 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA62 | KA62(23KV平六二線) |  | CB | [17 empty] | 1-14-07 |  | 1-1D | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA62_CB | KA62(23KV平六二線) CB | FEEDER | D25/22/KA62/CB |  |  |  | CDC | 355 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA63 | 平六三線(KA63) |  | PHA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA63_PHA | 23KV平六三線(KA63) 相間RY | FEEDER | D25/22/KA63/PHA |  |  |  | CDC | 356 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA63 | 平六三線(KA63) |  | GDA | [17 empty] | 1-15-04 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA63_GDA | 23KV平六三線(KA63) 接地RY | FEEDER | D25/22/KA63/GDA |  |  |  | CDC | 357 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA63_LCO | 平六三線(KA63) LCO |  | TapPosMv | [17 empty] | 2-31-10 |  | 2-30 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA63_LCO_TAP | 23KV平六三線(KA63) LCO TAP | FEEDER | D25/22/KA63/ADJ |  |  |  | CDC | 358 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA63 | KA63(23KV平六三線) |  | CB | [17 empty] | 1-15-02 |  | 1-1E | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA63_CB | KA63(23KV平六三線) CB | FEEDER | D25/22/KA63/CB |  |  |  | CDC | 359 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA65 | 平六五線(KA65) |  | PHA | [17 empty] | 1-16-07 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA65_PHA | 23KV平六五線(KA65) 相間RY | FEEDER | D25/22/KA65/PHA |  |  |  | CDC | 360 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA65 | 平六五線(KA65) |  | GDA | [17 empty] | 1-17-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA65_GDA | 23KV平六五線(KA65) 接地RY | FEEDER | D25/22/KA65/GDA |  |  |  | CDC | 361 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA65_LCO | 平六五線(KA65) LCO |  | TapPosMv | [17 empty] | 2-31-12 |  | 2-32 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA65_LCO_TAP | 23KV平六五線(KA65) LCO TAP | FEEDER | D25/22/KA65/ADJ |  |  |  | CDC | 362 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA65 | KA65(23KV平六五線) |  | CB | [17 empty] | 1-16-06 |  | 1-24 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA65_CB | KA65(23KV平六五線) CB | FEEDER | D25/22/KA65/CB |  |  |  | CDC | 363 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA66 | 平六六線(KA66) |  | PHA | [17 empty] | 1-17-02 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA66_PHA | 23KV平六六線(KA66) 相間RY | FEEDER | D25/22/KA66/PHA |  |  |  | CDC | 364 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA66 | 平六六線(KA66) |  | GDA | [17 empty] | 1-17-03 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA66_GDA | 23KV平六六線(KA66) 接地RY | FEEDER | D25/22/KA66/GDA |  |  |  | CDC | 365 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA66_LCO | 平六六線(KA66) LCO |  | TapPosMv | [17 empty] | 2-31-13 |  | 2-33 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA66_LCO_TAP | 23KV平六六線(KA66) LCO TAP | FEEDER | D25/22/KA66/ADJ |  |  |  | CDC | 366 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA66 | KA66(23KV平六六線) |  | CB | [17 empty] | 1-17-01 |  | 1-25 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA66_CB | KA66(23KV平六六線) CB | FEEDER | D25/22/KA66/CB |  |  |  | CDC | 367 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA71 | 平七一線(KA71) |  | PHA | [17 empty] | 1-19-01 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA71_PHA | 23KV平七一線(KA71) 相間RY | FEEDER | D25/22/KA71/PHA |  |  |  | CDC | 368 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA71 | 平七一線(KA71) |  | GDA | [17 empty] | 1-19-02 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA71_GDA | 23KV平七一線(KA71) 接地RY | FEEDER | D25/22/KA71/GDA |  |  |  | CDC | 369 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA71_LCO | 平七一線(KA71) LCO |  | TapPosMv | [17 empty] | 2-32-00 |  | 2-36 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA71_LCO_TAP | 23KV平七一線(KA71) LCO TAP | FEEDER | D25//1DTR/87UL2 |  |  |  | CDC | 370 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA71 | KA71(23KV平七一線) |  | CB | [17 empty] | 1-19-00 |  | 1-2A | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA71_CB | KA71(23KV平七一線) CB | FEEDER | D25/22/KA71/CB |  |  |  | CDC | 371 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA72 | 平七二線(KA72) |  | PHA | [17 empty] | 1-19-04 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA72_PHA | 23KV平七二線(KA72) 相間RY | FEEDER | D25/22/KA72/PHA |  |  |  | CDC | 372 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA72 | 平七二線(KA72) |  | GDA | [17 empty] | 1-19-05 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA72_GDA | 23KV平七二線(KA72) 接地RY | FEEDER | D25/22/KA72/GDA |  |  |  | CDC | 373 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA72_LCO | 平七二線(KA72) LCO |  | TapPosMv | [17 empty] | 2-32-01 |  | 2-37 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA72_LCO_TAP | 23KV平七二線(KA72) LCO TAP | FEEDER | D25//1DTR/51Z_UL |  |  |  | CDC | 374 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA72 | KA72(23KV平七二線) |  | CB | [17 empty] | 1-19-03 |  | 1-2B | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA72_CB | KA72(23KV平七二線) CB | FEEDER | D25/22/KA72/CB |  |  |  | CDC | 375 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA76 | 平七六線(KA76) |  | PHA | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA76_PHA | 23KV平七六線(KA76) 相間RY | FEEDER | D25/22/KA76/PHA |  |  |  | CDC | 376 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA76 | 平七六線(KA76) |  | GDA | [17 empty] | 1-1B-01 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA76_GDA | 23KV平七六線(KA76) 接地RY | FEEDER | D25/22/KA76/GDA |  |  |  | CDC | 377 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA76_LCO | 平七六線(KA76) LCO |  | TapPosMv | [17 empty] | 2-32-05 |  | 2-3B | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA76_LCO_TAP | 23KV平七六線(KA76) LCO TAP | FEEDER | D25/22/KA76/ADJ |  |  |  | CDC | 378 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA76 | KA76(23KV平七六線) |  | CB | [17 empty] | 1-1A-07 |  | 1-2F | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA76_CB | KA76(23KV平七六線) CB | FEEDER | D25/22/KA76/CB |  |  |  | CDC | 379 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA77 | 平七七線(KA77) |  | PHA | [17 empty] | 1-1B-03 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA77_PHA | 23KV平七七線(KA77) 相間RY | FEEDER |  |  |  |  | CDC | 380 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA77 | 平七七線(KA77) |  | GDA | [17 empty] | 1-1B-04 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA77_GDA | 23KV平七七線(KA77) 接地RY | FEEDER |  |  |  |  | CDC | 381 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA77_LCO | 平七七線(KA77) LCO |  | TapPosMv | [17 empty] | 2-32-06 |  | 2-3C | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA77_LCO_TAP | 23KV平七七線(KA77) LCO TAP | FEEDER | D25//3DTR/87UL2 |  |  |  | CDC | 382 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA77 | KA77(23KV平七七線) |  | CB | [17 empty] | 1-1B-02 |  | 1-30 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA77_CB | KA77(23KV平七七線) CB | FEEDER | D25/22/KA77/CB |  |  |  | CDC | 383 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA78 | 平七八線(KA78) |  | PHA | [17 empty] | 1-1B-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA78_PHA | 23KV平七八線(KA78) 相間RY | FEEDER | D25/22/KA78/PHA |  |  |  | CDC | 384 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA78 | 平七八線(KA78) |  | GDA | [17 empty] | 1-1B-07 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA78_GDA | 23KV平七八線(KA78) 接地RY | FEEDER | D25/22/KA78/GDA |  |  |  | CDC | 385 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA78_LCO | 平七八線(KA78) LCO |  | TapPosMv | [17 empty] | 2-32-07 |  | 2-3D | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA78_LCO_TAP | 23KV平七八線(KA78) LCO TAP | FEEDER | D25//3DTR/51Z_UL |  |  |  | CDC | 386 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA78 | KA78(23KV平七八線) |  | CB | [17 empty] | 1-1B-05 |  | 1-31 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA78_CB | KA78(23KV平七八線) CB | FEEDER | D25/22/KA78/CB |  |  |  | CDC | 387 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-05-00 |  | 1-09 | [5 empty] | 161KV_S | [8 empty] | 延平DS.1500_CB | 1500(TIE) CB | TIE | D25/161/1500/CB |  |  |  | CDC | 388 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-05-01 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D25/161/1500/50A |  |  |  | CDC | 389 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 2-38-00 | 2-38-01 | 2-10 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1501_DS | 1501(TIE) DS | TIE | D25/161/1500/DS1 |  |  |  | CDC | 390 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 2-38-02 | 2-38-03 | 2-11 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1502_DS | 1502(TIE) DS | TIE | D25/161/1500/DS2 |  |  |  | CDC | 391 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-10-00 |  | 1-0F | [5 empty] | 161KV_S | [8 empty] | 延平DS.390_CB | 390(#1SSTR) CB | OTHER | D25/22/390/CB |  |  |  | CDC | 392 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-10-01 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D25/22/100/CB |  |  |  | CDC | 393 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-10-02 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D25/22/100/PHA |  |  |  | CDC | 394 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-1C-03 |  | 1-34 | [5 empty] | 161KV_S | [8 empty] | 延平DS.490_CB | 490(#2SSTR) CB | OTHER | D25/22/490/CB |  |  |  | CDC | 395 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-1C-04 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D25/22/490/PHA |  |  |  | CDC | 396 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-1C-05 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D25/22/490/GDA |  |  |  | CDC | 397 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-05-05 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 延平DS.1750_CB | 1750(#1DTR) CB | MTR | D25/161/1750/CB |  |  |  | CDC | 398 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-06-03 |  | 1-10 | [5 empty] | ADCS_S | [8 empty] | 延平DS.310_CB | 310(#1DTR) CB | MTR | D25/22/310/CB |  |  |  | CDC | 399 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.310_51A | #1DTR二次側(310) 51RY | MTR | D25/22/310/PHA |  |  |  | CDC | 400 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-38-04 | 2-38-05 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1751_DS | 1751(#1DTR) DS | MTR | D25/161/1750/DS1 |  |  |  | CDC | 401 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 2-38-06 | 2-38-07 | 2-13 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1752_DS | 1752(#1DTR) DS | MTR | D25/161/1750/DS2 |  |  |  | CDC | 402 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-06-05 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 延平DS.1760_CB | 1760(#2DTR) CB | MTR | D25/161/1760/CB |  |  |  | CDC | 403 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-07-03 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 延平DS.330_CB | 330(#2DTR) CB | MTR | D25/22/330/CB |  |  |  | CDC | 404 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-07-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.330_51A | #2DTR二次側(330) 51RY | MTR | D25/22/330/PHA |  |  |  | CDC | 405 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-38-08 | 2-38-09 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1761_DS | 1761(#2DTR) DS | MTR | D25/161/1760/DS1 |  |  |  | CDC | 406 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 2-38-10 | 2-38-11 | 2-15 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1762_DS | 1762(#2DTR) DS | MTR | D25/161/1760/DS2 |  |  |  | CDC | 407 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-07-07 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 延平DS.1770_CB | 1770(#3DTR) CB | MTR | D25/161/1770/CB |  |  |  | CDC | 408 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-07-05 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 延平DS.340_CB | 340(#2DTR) CB | MTR | D25/22/340/CB |  |  |  | CDC | 409 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-07-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.340_51A | #2DTR二次側(340) 51RY | MTR | D25/22/340/PHA |  |  |  | CDC | 410 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 2-38-12 | 2-38-13 | 2-16 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1771_DS | 1771(#3DTR) DS | MTR | D25/161/1770/DS1 |  |  |  | CDC | 411 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 2-38-14 | 2-38-15 | 2-17 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1772_DS | 1772(#3DTR) DS | MTR | D25/161/1770/DS2 |  |  |  | CDC | 412 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D25 | 延平DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D25/161/1BUS/VUA |  |  |  | CDC | 413 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-05-02 | [7 empty] | 161KV_S | [8 empty] | 延平DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D25/161/1BUS/87A |  |  |  | CDC | 414 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-46 | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D25/161/1BUS/87UL |  |  |  | CDC | 415 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D25/161/2BUS/VUA |  |  |  | CDC | 416 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_S | [8 empty] | 延平DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D25/161/2BUS/87A |  |  |  | CDC | 417 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-32-09 |  | 1-47 | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D25/161/2BUS/87UL |  |  |  | CDC | 418 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-34-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D25/161//CBA |  |  |  | CDC | 419 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-34-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D25/161//CBF |  |  |  | CDC | 420 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV |  |  |  | CBA | [17 empty] | 2-34-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.23KV_CBA | 23KV斷路器重故障 | OTHER | D25/22/KA73/ADJ |  |  |  | CDC | 421 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV |  |  |  | CBF | [17 empty] | 2-34-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.23KV_CBF | 23KV斷路器輕故障 | OTHER | D25/22/KA74/ADJ |  |  |  | CDC | 422 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | _SC | 電容器組 |  | 60A | [17 empty] | 2-34-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.23KV_SC_60A | 23KV電容器組 60RY | OTHER | D25/22/ComPoint/60A |  |  |  | CDC | 423 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | OSCA | [17 empty] | 1-08-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.OSC啟動 | 示波器啟動警報 | OTHER | D25/161/ComPoint/OSCA |  |  |  | CDC | 424 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D25/0/RTU/RTU_R_L |  |  |  | CDC | 425 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D25 | 延平DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 延平DS.TEST_CB | TEST CB | OTHER | D25/0/RTU/Test_CB |  |  |  | CDC | 426 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-32-10 | [7 empty] | ADCS_S | [8 empty] | 延平DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D25/22/210/SC_A_M |  |  |  | CDC | 427 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | Fire2 | [17 empty] | 2-32-11 | [7 empty] | ADCS_S | [8 empty] | 延平DS.火災警報(2) | 火災警報(2) | OTHER | D25/22/220/SC_A_M |  |  |  | CDC | 428 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | Fire3 | [17 empty] | 2-32-12 | [7 empty] | ADCS_S | [8 empty] | 延平DS.火災警報(3) | 火災警報(3) | OTHER | D25/22/230/SC_A_M |  |  |  | CDC | 429 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | OPA | [17 empty] | 2-33-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 430 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | SUBA | [17 empty] | 2-34-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.其他重故障 | 變電所內其他重故障 | OTHER | D25/22/KA75/ADJ |  |  |  | CDC | 431 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | SUBF | [17 empty] | 2-34-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 432 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-33-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D25/22/KA57/ADJ |  |  |  | CDC | 433 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D25 | 延平DS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-33-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D25/22/KA58/ADJ |  |  |  | CDC | 434 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D25 | 延平DS | 0 |  |  |  |  | STUV | [17 empty] | 2-33-08 | [7 empty] | ADCS_S | [8 empty] | 延平DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 435 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-11 | [7 empty] | ADCS_S | [8 empty] | 延平DS.直流電源DCA | 直流電源故障警報 | OTHER | D25/22/KA64/ADJ |  |  |  | CDC | 436 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | DCE | [17 empty] | 2-33-14 | [7 empty] | ADCS_S | [8 empty] | 延平DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D25/22/KA67/ADJ |  |  |  | CDC | 437 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | COMT | [17 empty] | 2-33-15 | [7 empty] | ADCS_S | [8 empty] | 延平DS.空壓機COMT | 空壓機運轉超時警報 | OTHER | D25/22/KA68/ADJ |  |  |  | CDC | 438 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | OilLeak1 | [17 empty] | 2-34-11 | [7 empty] | ADCS_S | [8 empty] | 延平DS.洩油池警報(1) | 洩油池水位警報(1) | OTHER | D25/0/StaDev/Fire2 |  |  |  | CDC | 439 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | OilLeak2 | [17 empty] | 2-34-12 | [7 empty] | ADCS_S | [8 empty] | 延平DS.洩油池警報(2) | 洩油池水位警報(2) | OTHER | D25/0/StaDev/Fire3 |  |  |  | CDC | 440 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | CommACF | [17 empty] | 2-34-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 441 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-13 | [7 empty] | ADCS_S | [8 empty] | 延平DS.無人化防盜(1) | 無人化防盜(1)保全 | OTHER | D25/22/240/SC_A_M |  |  |  | CDC | 442 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | Burglar2 | [17 empty] | 2-32-14 | [7 empty] | ADCS_S | [8 empty] | 延平DS.無人化防盜(2) | 無人化防盜(2) | OTHER | D25/22/260/SC_A_M |  |  |  | CDC | 443 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | Door1 | [17 empty] | 2-33-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.無人化門禁(1) | 無人化門禁(1)圍牆小門 | OTHER | D25/22/KA51/ADJ |  |  |  | CDC | 444 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | Door2 | [17 empty] | 2-33-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.無人化門禁(2) | 無人化門禁(2)大樓鐵捲門 | OTHER |  |  |  |  | CDC | 445 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | Door3 | [17 empty] | 2-33-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.無人化門禁(3) | 無人化門禁(3)控制室大門 | OTHER |  |  |  |  | CDC | 446 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-33-03 |  | 2-1E | [5 empty] | ADCS_S | [8 empty] | 延平DS.開關場照明(A) | 開關場照明(A) | OTHER |  |  |  |  | CDC | 447 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D25 | 延平DS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-33-04 |  | 2-1F | [5 empty] | ADCS_S | [8 empty] | 延平DS.開關場照明(B) | 開關場照明(B) | OTHER | D25/22/KA55/ADJ |  |  |  | CDC | 448 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D25 | 延平DS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 2-32-09 | [7 empty] | ADCS_S | [8 empty] | 延平DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER |  |  |  |  | CDC | 449 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D25 | 延平DS | 22 | 22kV | KA64 | 平六四線(KA64) |  | PHA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA64_PHA | 23KV平六四線(KA64) 相間RY | FEEDER | D25/22/KA73/CB |  |  |  | CDC | 450 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA64 | 平六四線(KA64) |  | GDA | [17 empty] | 1-15-07 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA64_GDA | 23KV平六四線(KA64) 接地RY | FEEDER | D25/22/KA73/PHA |  |  |  | CDC | 451 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA64_LCO | 平六四線(KA64) LCO |  | TapPosMv | [17 empty] | 2-31-11 |  | 2-31 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA64_LCO_TAP | 23KV平六四線(KA64) LCO TAP | FEEDER |  |  |  |  | CDC | 452 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA64 | KA64(23KV平六四線) |  | CB | [17 empty] | 1-15-05 |  | 1-1F | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA64_CB | KA64(23KV平六四線) CB | FEEDER |  |  |  |  | CDC | 453 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-35-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.水位警報(1) | 地下室水位警報(1) | OTHER | D25/0/StaDev/Door1 |  |  |  | CDC | 454 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-35-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.水位警報(2) | 地下室水位警報(2) | OTHER | D25/0/StaDev/Door2 |  |  |  | CDC | 455 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA67 | 平六七線(KA67) |  | PHA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA67_PHA | 23KV平六七線(KA67) 相間RY | FEEDER |  |  |  |  | CDC | 456 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA67 | 平六七線(KA67) |  | GDA | [17 empty] | 1-17-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA67_GDA | 23KV平六七線(KA67) 接地RY | FEEDER |  |  |  |  | CDC | 457 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA67_LCO | 平六七線(KA67) LCO |  | TapPosMv | [17 empty] | 2-31-14 |  | 2-34 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA67_LCO_TAP | 23KV平六七線(KA67) LCO TAP | FEEDER |  |  |  |  | CDC | 458 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA67 | KA67(23KV平六七線) |  | CB | [17 empty] | 1-17-04 |  | 1-26 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA67_CB | KA67(23KV平六七線) CB | FEEDER | D25/22/KA77/GDA |  |  |  | CDC | 459 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA74 | 平七四線(KA74) |  | PHA | [17 empty] | 1-1A-02 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA74_PHA | 23KV平七四線(KA74) 相間RY | FEEDER |  |  |  |  | CDC | 460 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA74 | 平七四線(KA74) |  | GDA | [17 empty] | 1-1A-03 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA74_GDA | 23KV平七四線(KA74) 接地RY | FEEDER |  |  |  |  | CDC | 461 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA74_LCO | 平七四線(KA74) LCO |  | TapPosMv | [17 empty] | 2-32-03 |  | 2-39 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA74_LCO_TAP | 23KV平七四線(KA74) LCO TAP | FEEDER | D25//2DTR/87UL2 |  |  |  | CDC | 462 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA74 | KA74(23KV平七四線) |  | CB | [17 empty] | 1-1A-01 |  | 1-2D | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA74_CB | KA74(23KV平七四線) CB | FEEDER |  |  |  |  | CDC | 463 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA55 | 平五五線(KA55) |  | PHA | [17 empty] | 1-12-03 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA55_PHA | 23KV平五五線(KA55) 相間RY | FEEDER | D25/22/240/CB |  |  |  | CDC | 464 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA55 | 平五五線(KA55) |  | GDA | [17 empty] | 1-12-04 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA55_GDA | 23KV平五五線(KA55) 接地RY | FEEDER | D25/22/240/SCA |  |  |  | CDC | 465 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA55_LCO | 平五五線(KA55) LCO |  | TapPosMv | [17 empty] | 2-31-04 |  | 2-2A | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA55_LCO_TAP | 23KV平五五線(KA55) LCO TAP | FEEDER |  |  |  |  | CDC | 466 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA55 | KA55(23KV平五五線) |  | CB | [17 empty] | 1-12-02 |  | 1-16 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA55_CB | KA55(23KV平五五線) CB | FEEDER | D25/22/KA55/CB |  |  |  | CDC | 467 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA57 | 平五七線(KA57) |  | PHA | [17 empty] | 1-13-01 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA57_PHA | 23KV平五七線(KA57) 相間RY | FEEDER | D25/22/KA57/PHA |  |  |  | CDC | 468 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA57 | 平五七線(KA57) |  | GDA | [17 empty] | 1-13-02 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA57_GDA | 23KV平五七線(KA57) 接地RY | FEEDER | D25/22/KA57/GDA |  |  |  | CDC | 469 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA57_LCO | 平五七線(KA57) LCO |  | TapPosMv | [17 empty] | 2-31-06 |  | 2-2C | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA57_LCO_TAP | 23KV平五七線(KA57) LCO TAP | FEEDER |  |  |  |  | CDC | 470 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA57 | KA57(23KV平五七線) |  | CB | [17 empty] | 1-13-00 |  | 1-18 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA57_CB | KA57(23KV平五七線) CB | FEEDER | D25/22/KA57/CB |  |  |  | CDC | 471 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA58 | 平五八線(KA58) |  | PHA | [17 empty] | 1-13-04 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA58_PHA | 23KV平五八線(KA58) 相間RY | FEEDER | D25/22/KA67/CB |  |  |  | CDC | 472 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA58 | 平五八線(KA58) |  | GDA | [17 empty] | 1-13-05 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA58_GDA | 23KV平五八線(KA58) 接地RY | FEEDER | D25/22/KA67/PHA |  |  |  | CDC | 473 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA58_LCO | 平五八線(KA58) LCO |  | TapPosMv | [17 empty] | 2-31-07 |  | 2-2D | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA58_LCO_TAP | 23KV平五八線(KA58) LCO TAP | FEEDER |  |  |  |  | CDC | 474 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA58 | KA58(23KV平五八線) |  | CB | [17 empty] | 1-13-03 |  | 1-19 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA58_CB | KA58(23KV平五八線) CB | FEEDER | D25/22/KA58/CB |  |  |  | CDC | 475 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA68 | 平六八線(KA68) |  | PHA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA68_PHA | 23KV平六八線(KA68) 相間RY | FEEDER | D25/22/250/CB |  |  |  | CDC | 476 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA68 | 平六八線(KA68) |  | GDA | [17 empty] | 1-18-01 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA68_GDA | 23KV平六八線(KA68) 接地RY | FEEDER | D25/22/250/SCA |  |  |  | CDC | 477 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA68_LCO | 平六八線(KA68) LCO |  | TapPosMv | [17 empty] | 2-31-15 |  | 2-35 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA68_LCO_TAP | 23KV平六八線(KA68) LCO TAP | FEEDER |  |  |  |  | CDC | 478 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA68 | KA68(23KV平六八線) |  | CB | [17 empty] | 1-17-07 |  | 1-27 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA68_CB | KA68(23KV平六八線) CB | FEEDER |  |  |  |  | CDC | 479 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA73 | 平七三線(KA73) |  | PHA | [17 empty] | 1-19-07 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA73_PHA | 23KV平七三線(KA73) 相間RY | FEEDER |  |  |  |  | CDC | 480 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA73 | 平七三線(KA73) |  | GDA | [17 empty] | 1-1A-00 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA73_GDA | 23KV平七三線(KA73) 接地RY | FEEDER |  |  |  |  | CDC | 481 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA73_LCO | 平七三線(KA73) LCO |  | TapPosMv | [17 empty] | 2-32-02 |  | 2-38 | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA73_LCO_TAP | 23KV平七三線(KA73) LCO TAP | FEEDER | D25//1DTR/RYFA |  |  |  | CDC | 482 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA73 | KA73(23KV平七三線) |  | CB | [17 empty] | 1-19-06 |  | 1-2C | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA73_CB | KA73(23KV平七三線) CB | FEEDER |  |  |  |  | CDC | 483 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | KA75 | 平七五線(KA75) |  | PHA | [17 empty] | 1-1A-05 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA75_PHA | 23KV平七五線(KA75) 相間RY | FEEDER |  |  |  |  | CDC | 484 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA75 | 平七五線(KA75) |  | GDA | [17 empty] | 1-1A-06 | [7 empty] | DDCS4_1 | [8 empty] | 延平DS.KA75_GDA | 23KV平七五線(KA75) 接地RY | FEEDER |  |  |  |  | CDC | 485 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | KA75_LCO | 平七五線(KA75) LCO |  | TapPosMv | [17 empty] | 2-32-04 |  | 2-3A | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA75_LCO_TAP | 23KV平七五線(KA75) LCO TAP | FEEDER | D25//2DTR/51Z_UL |  |  |  | CDC | 486 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D25 | 延平DS | 22 | 22kV | KA75 | KA75(23KV平七五線) |  | CB | [17 empty] | 1-1A-04 |  | 1-2E | [5 empty] | DDCS4_1 | [8 empty] | 延平DS.KA75_CB | KA75(23KV平七五線) CB | FEEDER |  |  |  |  | CDC | 487 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-33-12 | [7 empty] | ADCS_S | [8 empty] | 延平DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER |  |  |  |  | CDC | 488 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-33-13 | [7 empty] | ADCS_S | [8 empty] | 延平DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 489 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-35-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | D25/0/StaDev/Door3 |  |  |  | CDC | 490 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-14-01 |  | 1-1B | [5 empty] | ADCS_S | [8 empty] | 延平DS.100_CB | 100(TIE) CB | TIE | D25/22/KA68/GDA |  |  |  | CDC | 491 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-14-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.100_51A | 23KV TIE(100) 51RY | TIE | D25/22/200/CB |  |  |  | CDC | 492 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-14-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.100_51NA | 23KV TIE(100) 51N RY | TIE | D25/22/200/PHA |  |  |  | CDC | 493 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-18-02 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 延平DS.200_CB | 200(TIE) CB | TIE | D25/22/250/UVA |  |  |  | CDC | 494 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-18-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.200_51A | 23KV TIE(200) 51RY | TIE | D25/22/200/51A |  |  |  | CDC | 495 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-18-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.200_51NA | 23KV TIE(200) 51N RY | TIE |  |  |  |  | CDC | 496 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1DTR_51A | #1DTR 51RY | MTR | D25/161/1750/PHA |  |  |  | CDC | 497 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-06-02 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1DTR_51NA | #1DTR 51N RY | MTR | D25/161/1750/GDA |  |  |  | CDC | 498 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-06-00 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D25//1DTR/51ZA |  |  |  | CDC | 499 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-05-06 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1DTR_87A | #1DTR 87RY | MTR | D25//1DTR/87A |  |  |  | CDC | 500 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-05-07 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D25//1DTR/96PA |  |  |  | CDC | 501 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_96D | #1DTR 96D RY | MTR | D25//1DTR/96D |  |  |  | CDC | 502 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_96P | #1DTR 96P RY | MTR | D25//1DTR/96P |  |  |  | CDC | 503 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-32-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D25//1DTR/63Q |  |  |  | CDC | 504 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-32-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D25//1DTR/96B1 |  |  |  | CDC | 505 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D25//1DTR/96B2 |  |  |  | CDC | 506 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_TRA | #1DTR 重故障 | MTR | D25//1DTR/TRA |  |  |  | CDC | 507 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D25//1DTR/TRF |  |  |  | CDC | 508 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_S/L | #1DTR OLTC S/L | MTR | D25//1DTR/SupLocal |  |  |  | CDC | 509 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D25 | 延平DS | 0 |  | 1DTR | #1DTR |  | A_M | [17 empty] | 1-32-12 |  | 1-60 | [5 empty] | ADCS_S | [8 empty] | 延平DS.#1DTR_A/M | #1DTR OLTC A/M | MTR | D25//1DTR/Tap Chan |  |  |  | CDC | 510 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-07-01 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2DTR_51A | #2DTR 51RY | MTR | D25/161/1760/PHA |  |  |  | CDC | 511 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-07-02 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2DTR_51NA | #2DTR 51N RY | MTR | D25/161/1760/GDA |  |  |  | CDC | 512 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-07-00 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D25//2DTR/51ZA |  |  |  | CDC | 513 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-06-06 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2DTR_87A | #2DTR 87RY | MTR | D25//2DTR/87A |  |  |  | CDC | 514 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-06-07 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D25//2DTR/96PA |  |  |  | CDC | 515 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_96D | #2DTR 96D RY | MTR | D25//2DTR/96D |  |  |  | CDC | 516 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-32-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_96P | #2DTR 96P RY | MTR | D25//2DTR/96P |  |  |  | CDC | 517 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D25//2DTR/63Q |  |  |  | CDC | 518 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-33-09 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D25//2DTR/96B1 |  |  |  | CDC | 519 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-33-10 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D25//2DTR/96B2 |  |  |  | CDC | 520 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_TRA | #2DTR 重故障 | MTR | D25//2DTR/TRA |  |  |  | CDC | 521 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D25//2DTR/TRF |  |  |  | CDC | 522 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | SupLocal | [17 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | D25//2DTR/SupLocal |  |  |  | CDC | 523 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D25 | 延平DS | 0 |  | 2DTR | #2DTR |  | A_M | [17 empty] | 1-33-01 |  | 1-62 | [5 empty] | ADCS_S | [8 empty] | 延平DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | D25//2DTR/Tap Chan |  |  |  | CDC | 524 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D25 | 延平DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-08-05 |  | 1-33 | [5 empty] | ADCS_S | [8 empty] | 延平DS.350_CB | 350(#3DTR) CB | MTR | D25/22/350/CB |  |  |  | CDC | 525 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-08-03 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#3DTR_51A | #3DTR 51RY | MTR | D25/161/1770/PHA |  |  |  | CDC | 526 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-08-04 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#3DTR_51NA | #3DTR 51N RY | MTR | D25/161/1770/GDA |  |  |  | CDC | 527 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-08-02 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D25//3DTR/51ZA |  |  |  | CDC | 528 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-08-00 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#3DTR_87A | #3DTR 87RY | MTR | D25//3DTR/87A |  |  |  | CDC | 529 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-08-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.350_51A | #3DTR二次側(350) 51RY | MTR | D25/22/350/PHA |  |  |  | CDC | 530 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-08-01 | [7 empty] | 161KV_S | [8 empty] | 延平DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D25//3DTR/96PA |  |  |  | CDC | 531 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_96D | #3DTR 96D RY | MTR | D25//3DTR/96D |  |  |  | CDC | 532 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-33-12 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_96P | #3DTR 96P RY | MTR | D25//3DTR/96P |  |  |  | CDC | 533 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-33-13 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D25//3DTR/63Q |  |  |  | CDC | 534 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-33-14 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D25//3DTR/96B1 |  |  |  | CDC | 535 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-33-15 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D25//3DTR/96B2 |  |  |  | CDC | 536 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-33-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_TRA | #3DTR 重故障 | MTR | D25//3DTR/TRA |  |  |  | CDC | 537 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-33-08 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D25//3DTR/TRF |  |  |  | CDC | 538 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D25//3DTR/SupLocal |  |  |  | CDC | 539 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D25 | 延平DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-33-06 |  | 1-64 | [5 empty] | ADCS_S | [8 empty] | 延平DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D25//3DTR/Tap Chan |  |  |  | CDC | 540 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-10-03 |  | 1-11 | [5 empty] | ADCS_S | [8 empty] | 延平DS.210_CB | 210(23KV #1SC) CB | SC | D25/22/210/CB |  |  |  | CDC | 541 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-30-10 |  | 2-20 | [5 empty] | ADCS_S | [8 empty] | 延平DS.210_A/M | 23KV #1SC 乏控器 A/M | SC |  |  |  |  | CDC | 542 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-10-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.210_SCA | 23KV #1SC 51,51N RY | SC | D25/22/210/SCA |  |  |  | CDC | 543 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-10-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.210_UVA | 23KV #1SC 27RY(欠壓) | SC | D25/22/210/UVA |  |  |  | CDC | 544 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-13-06 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 延平DS.220_CB | 220(23KV #2SC) CB | SC | D25/22/220/CB |  |  |  | CDC | 545 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-30-11 |  | 2-21 | [5 empty] | ADCS_S | [8 empty] | 延平DS.220_A/M | 23KV #2SC 乏控器 A/M | SC |  |  |  |  | CDC | 546 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-13-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.220_SCA | 23KV #2SC 51,51N RY | SC | D25/22/KA68/CB |  |  |  | CDC | 547 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-14-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.220_UVA | 23KV #2SC 27RY(欠壓) | SC | D25/22/KA68/PHA |  |  |  | CDC | 548 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-16-00 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 延平DS.230_CB | 230(23KV #3SC) CB | SC | D25/22/KA73/GDA |  |  |  | CDC | 549 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-30-12 |  | 2-22 | [5 empty] | ADCS_S | [8 empty] | 延平DS.230_A/M | 23KV #3SC 乏控器 A/M | SC |  |  |  |  | CDC | 550 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-16-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.230_SCA | 23KV #3SC 51,51N RY | SC | D25/22/KA74/CB |  |  |  | CDC | 551 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-16-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | D25/22/KA74/PHA |  |  |  | CDC | 552 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-16-03 |  | 1-23 | [5 empty] | ADCS_S | [8 empty] | 延平DS.240_CB | 240(23KV #4SC) CB | SC | D25/22/KA74/GDA |  |  |  | CDC | 553 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-30-13 |  | 2-23 | [5 empty] | ADCS_S | [8 empty] | 延平DS.240_A/M | 23KV #4SC 乏控器 A/M | SC |  |  |  |  | CDC | 554 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-16-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.240_SCA | 23KV #4SC 51,51N RY | SC | D25/22/KA75/CB |  |  |  | CDC | 555 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-16-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | D25/22/KA75/PHA |  |  |  | CDC | 556 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-1C-00 |  | 1-32 | [5 empty] | ADCS_S | [8 empty] | 延平DS.250_CB | 250(23KV #5SC) CB | SC |  |  |  |  | CDC | 557 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-30-15 |  | 2-25 | [5 empty] | ADCS_S | [8 empty] | 延平DS.250_A/M | 23KV #5SC 乏控器 A/M | SC |  |  |  |  | CDC | 558 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-1C-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.250_SCA | 23KV #5SC 51,51N RY | SC |  |  |  |  | CDC | 559 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-1C-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC |  |  |  |  | CDC | 560 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-18-05 |  | 1-29 | [5 empty] | ADCS_S | [8 empty] | 延平DS.260_CB | 260(23KV #6SC) CB | SC |  |  |  |  | CDC | 561 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-30-14 |  | 2-24 | [5 empty] | ADCS_S | [8 empty] | 延平DS.260_A/M | 23KV #6SC 乏控器 A/M | SC |  |  |  |  | CDC | 562 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-18-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.260_SCA | 23KV #6SC 51,51N RY | SC |  |  |  |  | CDC | 563 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-18-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC |  |  |  |  | CDC | 564 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-34-10 | [7 empty] | ADCS_S | [8 empty] | 延平DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D25/0/StaDev/Fire1 |  |  |  | CDC | 565 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-35-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D25/0/StaDev/Lights1 |  |  |  | CDC | 566 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 延平DS.1550_87A | 台南延平線(1550) 87RY | LINE161 | D25/161/1550/87A |  |  |  | CDC | 567 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | 87UL | [17 empty] | 1-30-04 |  | 1-42 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1550_87UL | 台南延平線(1550) 87RY U/L | LINE161 | D25/161/1550/87UL |  |  |  | CDC | 568 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 0 |  | 1550 | 台南延平線(1550) |  | 87CFA | [17 empty] | 2-34-14 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1550_87CFA | 台南延平線(1550)87RY通訊故障 | OTHER | D25/0/StaDev/Burglar2 |  |  |  | CDC | 569 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1550 | 台南延平線(1550) |  | RYFA | [17 empty] | 2-35-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1550_RYFA | 台南延平線(1550)數位電驛故障 | OTHER | D25/0/StaDev/Lights2 |  |  |  | CDC | 570 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | 79UL | [17 empty] | 1-30-05 |  | 1-43 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1550_79UL | 台南延平線(1550) 79RY U/L | LINE161 | D25/161/1550/79UL |  |  |  | CDC | 571 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-05-04 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D25/161/ComPoint/RCA |  |  |  | CDC | 572 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | 79UL | [17 empty] | 1-30-03 |  | 1-41 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1560_79UL | 忠孝延平線(1560) 79RY U/L | LINE161 | D25/161/1560/79UL |  |  |  | CDC | 573 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 0 |  | 1560 | 忠孝延平線(1560) |  | 87CFA | [17 empty] | 2-34-13 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1560_87CFA | 忠孝延平線(1560)87RY通訊故障 | OTHER | D25/0/StaDev/Burglar1 |  |  |  | CDC | 574 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1560 | 忠孝延平線(1560) |  | RYFA | [17 empty] | 2-35-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1560_RYFA | 忠孝延平線(1560)數位電驛故障 | OTHER | D25/0/ComPoint/OPA |  |  |  | CDC | 575 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | IEDA | [17 empty] | 2-32-15 | [7 empty] | ADCS_S | [8 empty] | 延平DS.IEDA | 變壓器資產管理監視IED故障 | OTHER | D25/22/250/SC_A_M |  |  |  | CDC | 576 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-09-00 | [7 empty] | ADCS_S | [8 empty] | 延平DS.310_GDA | 310開關箱IED RY GDA | OTHER | D25/22/310/GDA |  |  |  | CDC | 577 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.330_GDA | 330開關箱IED RY GDA | OTHER | D25/22/330/GDA |  |  |  | CDC | 578 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-09-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.340_GDA | 340開關箱IED RY GDA | OTHER | D25/22/340/GDA |  |  |  | CDC | 579 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-09-03 | [7 empty] | ADCS_S | [8 empty] | 延平DS.350_GDA | 350開關箱IED RY GDA | OTHER | D25/22/350/GDA |  |  |  | CDC | 580 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  |  |  |  | GEN | [17 empty] | 2-35-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.GEN | 緊急發電機運轉 | OTHER | D25/0/StaDev/ACB1 |  |  |  | CDC | 581 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D25 | 延平DS | 0 |  |  |  |  | PMA | [17 empty] | 2-35-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.PMA | 電力量測表計故障 | OTHER | D25/0/StaDev/ACB2 |  |  |  | CDC | 582 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1560 | 忠孝延平線(1560) |  | 87A1 | [17 empty] | 1-00-01 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1560_87A1 | 忠孝延平線(1560)第一套87RY | OTHER | D25/161/1560/87A1 |  |  |  | CDC | 583 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1560 | 忠孝延平線(1560) |  | 87A2 | [17 empty] | 1-00-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.1560_87A2 | 忠孝延平線(1560)第二套87RY | OTHER | D25/161/1560/87A2 |  |  |  | CDC | 584 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 0 |  | 1560 | 忠孝延平線(1560) |  | 1_87UL1 | [17 empty] | 1-30-02 |  | 1-40 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1560_87UL1 | 忠孝延平線(1560)#1 87RY U/L | OTHER | D25/161/1560/87UL1 |  |  |  | CDC | 585 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 0 |  | 1560 | 忠孝延平線(1560) |  | 1_87UL2 | [17 empty] | 1-30-07 |  | 1-45 | [5 empty] | ADCS_S | [8 empty] | 延平DS.1560_87UL2 | 忠孝延平線(1560)#2 87RY U/L | OTHER | D25/161/1560/87UL2 |  |  |  | CDC | 586 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-35-09 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161KV_BUS_CTFA | 161KV BUS 87RY CT回路故障 | OTHER | D25/161/1BUS/BUS_VUA |  |  |  | CDC | 587 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 2-35-08 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D25/0/StaDev/STUV |  |  |  | CDC | 588 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D25 | 延平DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 2-35-10 | [7 empty] | ADCS_S | [8 empty] | 延平DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D25/161/2BUS/BUS_VUA |  |  |  | CDC | 589 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1611DTR | #1DTR |  | DTR_86A | [17 empty] | 1-09-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#1DTR_86A | 161KV #1DTR 86RY | OTHER | D25//1DTR/DTR_86A |  |  |  | CDC | 590 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1611DTR | #1DTR |  | 187UL | [17 empty] | 1-32-10 |  | 1-66 | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | D25//1DTR/87UL |  |  |  | CDC | 591 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1611DTR | #1DTR |  | 287UL | [17 empty] | 2-30-00 |  | 1-67 | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER | D25/161/1750/287UL |  |  |  | CDC | 592 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1611DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-30-01 |  | 1-68 | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER | D25/161/1750/51Z_UL |  |  |  | CDC | 593 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1611DTR | #1DTR |  | RYFA | [17 empty] | 2-30-02 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER | D25/161/1750/RYFA |  |  |  | CDC | 594 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1612DTR | #2DTR |  | DTR_86A | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#2DTR_86A | 161KV #2DTR 86RY | OTHER | D25//2DTR/DTR_86A |  |  |  | CDC | 595 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1612DTR | #2DTR |  | 187UL | [17 empty] | 1-32-15 |  | 1-69 | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | D25//2DTR/87UL |  |  |  | CDC | 596 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1612DTR | #2DTR |  | 287UL | [17 empty] | 2-30-03 |  | 1-6A | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER | D25/161/1760/287UL |  |  |  | CDC | 597 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1612DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-30-04 |  | 1-6B | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER | D25/161/1760/51Z_UL |  |  |  | CDC | 598 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1612DTR | #2DTR |  | RYFA | [17 empty] | 2-30-05 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER | D25/161/1760/RYFA |  |  |  | CDC | 599 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1613DTR | #3DTR |  | DTR_86A | [17 empty] | 1-09-07 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER | D25//3DTR/DTR_86A |  |  |  | CDC | 600 | GENERICDIPoint | DS033_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D25 | 延平DS | 161 | 161kV | 1613DTR | #3DTR |  | 187UL | [17 empty] | 1-33-04 |  | 1-6C | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | D25//3DTR/87UL |  |  |  | CDC | 601 | GENERICDIPoint | DS033_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1613DTR | #3DTR |  | 287UL | [17 empty] | 2-30-06 |  | 1-6D | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | D25/161/1770/287UL |  |  |  | CDC | 602 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1613DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-30-07 |  | 1-6E | [5 empty] | ADCS_S | [8 empty] | 延平DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | D25/161/1770/51Z_UL |  |  |  | CDC | 603 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D25 | 延平DS | 161 | 161kV | 1613DTR | #3DTR |  | RYFA | [17 empty] | 2-30-08 | [7 empty] | ADCS_S | [8 empty] | 延平DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | D25/161/1770/RYFA |  |  |  | CDC | 604 | GENERICDIPoint | DS033_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D25 | 延平DS | 0 |  | TRD | 延平DS |  | 073 | [25 empty] | TRAIN_AD | [8 empty] | 延平DS.TRD_073 | 延平DS NT #3DTR 23KV_Hi_Limit | [6 empty] | 605 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 0 |  | TRD | 延平DS |  | 074 | [25 empty] | TRAIN_AD | [8 empty] | 延平DS.TRD_074 | 延平DS NT #3DTR 23KV_Lo_Limit | [6 empty] | 606 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 0 |  | TRD | 延平DS |  | 075 | [25 empty] | TRAIN_AD | [8 empty] | 延平DS.TRD_075 | 延平DS NT #2DTR 23KV_Hi_Limit | [6 empty] | 607 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 0 |  | TRD | 延平DS |  | 076 | [25 empty] | TRAIN_AD | [8 empty] | 延平DS.TRD_076 | 延平DS NT #2DTR 23KV_Lo_Limit | [6 empty] | 608 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 0 |  | TRD | 延平DS |  | 077 | [25 empty] | TRAIN_AD | [8 empty] | 延平DS.TRD_077 | 延平DS NT #1DTR 23KV_Hi_Limit | [6 empty] | 609 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 0 |  | TRD | 延平DS |  | 078 | [25 empty] | TRAIN_AD | [8 empty] | 延平DS.TRD_078 | 延平DS NT #1DTR 23KV_Lo_Limit | [6 empty] | 610 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D25 | 延平DS | 22 | 22kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 延平DS.210_SC_CAP | 23KV#1SC 容量 | SC | [5 empty] | 611 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 延平DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 612 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 延平DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 613 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 延平DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 614 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 延平DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 615 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 22 | 22kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 延平DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 616 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1510LE | 1510LE (非取樣點) | LINE161 | D25/161/1510/LE0 |  |  |  |  | 617 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1510 | 健康線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1510BE | 1510BE (非取樣點) | LINE161 | D25/161/1510/BE0 |  |  |  |  | 618 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1550LE | 1550LE (非取樣點) | LINE161 | D25/161/1550/LE0 |  |  |  |  | 619 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1550 | 台南延平線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1550BE | 1550BE (非取樣點) | LINE161 | D25/161/1550/BE0 |  |  |  |  | 620 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1560LE | 1560LE (非取樣點) | LINE161 | D25/161/1560/LE0 |  |  |  |  | 621 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1560 | 忠孝延平線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1560BE | 1560BE (非取樣點) | LINE161 | D25/161/1560/BE0 |  |  |  |  | 622 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA51 | KA51_DS |  | DS1 | KA51_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA51_DS | KA51_DS (非取樣點) | FEEDER | D25/22/KA51/DS1 |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA51 | KA51_ES |  | LE0 | KA51_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA51_ES | KA51_ES (非取樣點) | FEEDER | D25/22/KA51/ES |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA52 | KA52_DS |  | DS1 | KA52_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA52_DS | KA52_DS (非取樣點) | FEEDER | D25/22/KA52/DS1 |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA52 | KA52_ES |  | LE0 | KA52_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA52_ES | KA52_ES (非取樣點) | FEEDER | D25/22/KA52/ES |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA53 | KA53_DS |  | DS1 | KA53_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA53_DS | KA53_DS (非取樣點) | FEEDER | D25/22/KA53/DS1 |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA53 | KA53_ES |  | LE0 | KA53_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA53_ES | KA53_ES (非取樣點) | FEEDER | D25/22/KA53/ES |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA54 | KA54_DS |  | DS1 | KA54_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA54_DS | KA54_DS (非取樣點) | FEEDER | D25/22/KA54/DS1 |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA54 | KA54_ES |  | LE0 | KA54_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA54_ES | KA54_ES (非取樣點) | FEEDER | D25/22/KA54/ES |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA56 | KA56_DS |  | DS1 | KA56_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA56_DS | KA56_DS (非取樣點) | FEEDER | D25/22/KA56/DS1 |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA56 | KA56_ES |  | LE0 | KA56_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA56_ES | KA56_ES (非取樣點) | FEEDER | D25/22/KA56/ES |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA61 | KA61_DS |  | DS1 | KA61_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA61_DS | KA61_DS (非取樣點) | FEEDER | D25/22/KA61/DS |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA61 | KA61_ES |  | LE0 | KA61_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA61_ES | KA61_ES (非取樣點) | FEEDER | D25/22/KA61/ES |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA62 | KA62_DS |  | DS1 | KA62_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA62_DS | KA62_DS (非取樣點) | FEEDER | D25/22/KA62/DS |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA62 | KA62_ES |  | LE0 | KA62_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA62_ES | KA62_ES (非取樣點) | FEEDER | D25/22/KA62/ES |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA63 | KA63_DS |  | DS1 | KA63_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA63_DS | KA63_DS (非取樣點) | FEEDER | D25/22/KA63/DS |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA63 | KA63_ES |  | LE0 | KA63_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA63_ES | KA63_ES (非取樣點) | FEEDER | D25/22/KA63/ES |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA65 | KA65_DS |  | DS1 | KA65_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA65_DS | KA65_DS (非取樣點) | FEEDER | D25/22/KA65/DS |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA65 | KA65_ES |  | LE0 | KA65_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA65_ES | KA65_ES (非取樣點) | FEEDER | D25/22/KA65/ES |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA66 | KA66_DS |  | DS1 | KA66_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA66_DS | KA66_DS (非取樣點) | FEEDER | D25/22/KA66/DS |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA66 | KA66_ES |  | LE0 | KA66_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA66_ES | KA66_ES (非取樣點) | FEEDER | D25/22/KA66/ES |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA71 | KA71_DS |  | DS1 | KA71_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA71_DS | KA71_DS (非取樣點) | FEEDER | D25/22/KA71/DS |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA71 | KA71_ES |  | LE0 | KA71_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA71_ES | KA71_ES (非取樣點) | FEEDER | D25/22/KA71/ES |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA72 | KA72_DS |  | DS1 | KA72_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA72_DS | KA72_DS (非取樣點) | FEEDER | D25/22/KA72/DS |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA72 | KA72_ES |  | LE0 | KA72_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA72_ES | KA72_ES (非取樣點) | FEEDER | D25/22/KA72/ES |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA76 | KA76_DS |  | DS1 | KA76_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA76_DS | KA76_DS (非取樣點) | FEEDER | D25/22/KA76/DS |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA76 | KA76_ES |  | LE0 | KA76_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA76_ES | KA76_ES (非取樣點) | FEEDER | D25/22/KA76/ES |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA77 | KA77_DS |  | DS1 | KA77_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA77_DS | KA77_DS (非取樣點) | FEEDER | D25/22/KA77/DS |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA77 | KA77_ES |  | LE0 | KA77_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA77_ES | KA77_ES (非取樣點) | FEEDER | D25/22/KA77/ES |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA78 | KA78_DS |  | DS1 | KA78_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA78_DS | KA78_DS (非取樣點) | FEEDER | D25/22/KA78/DS |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA78 | KA78_ES |  | LE0 | KA78_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA78_ES | KA78_ES (非取樣點) | FEEDER | D25/22/KA78/ES |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 延平DS.1501E | 1501E (非取樣點) | TIE | D25/161/1500/E1 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 延平DS.1502E | 1502E (非取樣點) | TIE | D25/161/1500/E2 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 延平DS.391 | 391 (非取樣點) | OTHER | D25/22/390/DS1 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 延平DS.491 | 491 (非取樣點) | OTHER | D25/22/490/D1 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1750TE | 1750TE (非取樣點) | MTR | D25/161/1750/TE0 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1750BE | 1750BE (非取樣點) | MTR | D25/161/1750/BE0 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 延平DS.311 | 311 (非取樣點) | MTR | D25/22/310/DS1 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 延平DS.311E | 311E (非取樣點) | MTR | D25/22/310/E1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1760TE | 1760TE (非取樣點) | MTR | D25/161/1760/TE0 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1760BE | 1760BE (非取樣點) | MTR | D25/161/1760/BE0 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 延平DS.331 | 331 (非取樣點) | MTR | D25/22/330/DS1 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 延平DS.331E | 331E (非取樣點) | MTR | D25/22/330/E1 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1770TE | 1770TE (非取樣點) | MTR | D25/161/1770/TE0 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1770BE | 1770BE (非取樣點) | MTR | D25/161/1770/BE0 |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 延平DS.341 | 341 (非取樣點) | MTR | D25/22/340/DS1 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 延平DS.341E | 341E (非取樣點) | MTR | D25/22/340/E1 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 延平DS.15B1E | 15B1E (非取樣點) | BUS | D25/161/161B1E/BE1 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 延平DS.15B2E | 15B2E (非取樣點) | BUS | D25/161/161B2E/BE2 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 延平DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 671 | NotelDIPoint | [38 empty] | START/STOP | STOP
D25 | 延平DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 延平DS.391E | 391E (非取樣點) | OTHER | D25/22/390/E1 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 延平DS.491E | 491E (非取樣點) | OTHER | D25/22/490/E1 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA64 | KA64_DS |  | DS1 | KA64_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA64_DS | KA64_DS (非取樣點) | FEEDER | D25/22/KA64/DS |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA64 | KA64_ES |  | LE0 | KA64_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA64_ES | KA64_ES (非取樣點) | FEEDER | D25/22/KA64/ES |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 69 | 69kV | 1550 | 台南延平線(1550) |  | PW1UL | 1550_PW1UL | [24 empty] | ADCS_S | [8 empty] | 延平DS.1550_PW1UL | 台南紅線(1550)PW1_UL(非取樣點) | LINE69 | [5 empty] | 676 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D25 | 延平DS | 69 | 69kV | 1550 | 台南延平線(1550) |  | PW2UL | 1550_PW2UL | [24 empty] | ADCS_S | [8 empty] | 延平DS.1550_PW2UL | 台南紅線(1550)PW2_UL(非取樣點) | LINE69 | [5 empty] | 677 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
D25 | 延平DS | 69 | 69kV | 1550 | 台南延平線(1550) |  | HCBUL | 1550_HCBUL | [24 empty] | ADCS_S | [8 empty] | 延平DS.1550_HCBUL | 台南紅線(1550)HCB_UL(非取樣點) | LINE69 | [5 empty] | 678 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D25 | 延平DS | 69 | 69kV | 1560 | 忠孝延平線(1560) |  | PW1UL | 1560_PW1UL | [24 empty] | ADCS_S | [8 empty] | 延平DS.1560_PW1UL | 台南白線(1560)PW1_UL(非取樣點) | LINE69 | [5 empty] | 679 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D25 | 延平DS | 69 | 69kV | 1560 | 忠孝延平線(1560) |  | PW2UL | 1560_PW2UL | [24 empty] | ADCS_S | [8 empty] | 延平DS.1560_PW2UL | 台南白線(1560)PW2_UL(非取樣點) | LINE69 | [5 empty] | 680 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
D25 | 延平DS | 69 | 69kV | 1560 | 忠孝延平線(1560) |  | HCBUL | 1560_HCBUL | [24 empty] | ADCS_S | [8 empty] | 延平DS.1560_HCBUL | 台南白線(1560)HCB_UL(非取樣點) | LINE69 | [5 empty] | 681 | NotelDIPoint | [38 empty] | USE/LOCK | USE
D25 | 延平DS | 0 |  | KA67 | KA67_DS |  | DS1 | KA67_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA67_DS | KA67_DS (非取樣點) | FEEDER | D25/22/KA67/DS |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA67 | KA67_ES |  | LE0 | KA67_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA67_ES | KA67_ES (非取樣點) | FEEDER | D25/22/KA67/ES |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA74 | KA74_DS |  | DS1 | KA74_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA74_DS | KA74_DS (非取樣點) | FEEDER | D25/22/KA74/DS |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA74 | KA74_ES |  | LE0 | KA74_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA74_ES | KA74_ES (非取樣點) | FEEDER | D25/22/KA74/ES |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA55 | KA55_DS |  | DS1 | KA55_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA55_DS | KA55_DS (非取樣點) | FEEDER | D25/22/KA55/DS1 |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA55 | KA55_ES |  | LE0 | KA55_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA55_ES | KA55_ES (非取樣點) | FEEDER | D25/22/KA55/ES |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA57 | KA57_DS |  | DS1 | KA57_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA57_DS | KA57_DS (非取樣點) | FEEDER | D25/22/KA57/DS1 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA57 | KA57_ES |  | LE0 | KA57_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA57_ES | KA57_ES (非取樣點) | FEEDER | D25/22/KA57/ES |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA58 | KA58_DS |  | DS1 | KA58_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA58_DS | KA58_DS (非取樣點) | FEEDER | D25/22/KA58/DS1 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA58 | KA58_ES |  | LE0 | KA58_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA58_ES | KA58_ES (非取樣點) | FEEDER | D25/22/KA58/ES |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA68 | KA68_DS |  | DS1 | KA68_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA68_DS | KA68_DS (非取樣點) | FEEDER | D25/22/KA68/DS |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA68 | KA68_ES |  | LE0 | KA68_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA68_ES | KA68_ES (非取樣點) | FEEDER | D25/22/KA68/ES |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA73 | KA73_DS |  | DS1 | KA73_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA73_DS | KA73_DS (非取樣點) | FEEDER | D25/22/KA73/DS |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA73 | KA73_ES |  | LE0 | KA73_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA73_ES | KA73_ES (非取樣點) | FEEDER | D25/22/KA73/ES |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | KA75 | KA75_DS |  | DS1 | KA75_DS | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA75_DS | KA75_DS (非取樣點) | FEEDER | D25/22/KA75/DS |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | KA75 | KA75_ES |  | LE0 | KA75_ES | [24 empty] | DDCS4_1 | [8 empty] | 延平DS.KA75_ES | KA75_ES (非取樣點) | FEEDER | D25/22/KA75/ES |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 延平DS.101 | 101 (非取樣點) | TIE | D25/22/100/DS1 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 延平DS.102 | 102 (非取樣點) | TIE | D25/22/100/DS2 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 延平DS.201 | 201 (非取樣點) | TIE | D25/22/200/D1 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 延平DS.202 | 202 (非取樣點) | TIE | D25/22/200/D2 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 延平DS.351 | 351 (非取樣點) | MTR | D25/22/350/DS1 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 延平DS.351E | 351E (非取樣點) | MTR | D25/22/350/E1 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 延平DS.211E | 211E (非取樣點) | SC | D25/22/210/E1 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 210 | #1SC(210) |  | SC0 | 210SC | [24 empty] | ADCS_S | [8 empty] | 延平DS.210SC_ES | 210SC_ES (非取樣點) | SC | D25/22/210/ES |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 延平DS.211 | 211 (非取樣點) | SC | D25/22/210/DS1 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 延平DS.221E | 221E (非取樣點) | SC | D25/22/220/E1 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 220 | #2SC(220) |  | SC0 | 220SC | [24 empty] | ADCS_S | [8 empty] | 延平DS.220SC_ES | 220SC_ES (非取樣點) | SC | D25/22/220/ES |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 延平DS.221 | 221 (非取樣點) | SC | D25/22/220/DS1 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 延平DS.231E | 231E (非取樣點) | SC | D25/22/230/E1 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 230 | #3SC(230) |  | SC0 | 230SC | [24 empty] | ADCS_S | [8 empty] | 延平DS.230SC_ES | 230SC_ES (非取樣點) | SC | D25/22/230/ES |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 延平DS.231 | 231 (非取樣點) | SC | D25/22/230/D1 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 延平DS.241E | 241E (非取樣點) | SC | D25/22/240/E1 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 240 | #4SC(240) |  | SC0 | 240SC | [24 empty] | ADCS_S | [8 empty] | 延平DS.240SC_ES | 240SC_ES (非取樣點) | SC | D25/22/240/ES |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 延平DS.241 | 241 (非取樣點) | SC | D25/22/240/D1 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 延平DS.251E | 251E (非取樣點) | SC | D25/22/250/E1 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_S | [8 empty] | 延平DS.250SC_ES | 250SC_ES (非取樣點) | SC | D25/22/250/ES |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 延平DS.251 | 251 (非取樣點) | SC | D25/22/250/D1 |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 延平DS.261E | 261E (非取樣點) | SC | D25/22/260/E1 |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_S | [8 empty] | 延平DS.260SC_ES | 260SC_ES (非取樣點) | SC | D25/22/260/ES |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 延平DS.261 | 261 (非取樣點) | SC | D25/22/260/D1 |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D25 | 延平DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_S | [8 empty] | 延平DS.101E | 101E(非取樣點) | OTHER | D25/22/100/E1 |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_S | [8 empty] | 延平DS.102E | 102E(非取樣點) | OTHER | D25/22/100/E2 |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_S | [8 empty] | 延平DS.201E | 201E(非取樣點) | OTHER | D25/22/200/E1 |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_S | [8 empty] | 延平DS.202E | 202E(非取樣點) | OTHER | D25/22/200/E2 |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 1BUS | 1BUS |  | PTE | 1BUS_PTE | [24 empty] | ADCS_S | [8 empty] | 延平DS.1BUS_PTE | #1BUS_PTE(非取樣點) | OTHER | D25/22/1BUS/PTE |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 延平DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | D25/22/2ABUS/PTE |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 延平DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | D25/22/2BBUS/PTE |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D25 | 延平DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_S | [8 empty] | 延平DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | D25/22/3BUS/PTE |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo