## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 0.1 | TEST | 10% TEST | ADCL_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 2 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | TEST CB |  |  | ELEM/ALL | [8 empty] | 小北DS.TEST_CB | TEST CB | OTHER | [5 empty] | 3 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 0.9 | TEST | 90% TEST | ADCH_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 4 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1510 | 87A | 安南小北一路 1510 87 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_87A | 安南小北一路(1510) 87RY | LINE161 | [5 empty] | 5 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | #1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | Locate Empty | KV | 161KV #1BUS電壓 | kV_-210_210(-2000_2000) | aaa | B2/D26_A1 | [8 empty] | 小北DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 6 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D26 | 小北DS | 161 | 161kV | #2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | Locate Empty | KV | 161KV #2BUS電壓 | kV_-210_210(-2000_2000) | aba | B2/D26_A1 | [8 empty] | 小北DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 7 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1510 | PHA | 安南小北一路 1510 PHA相間 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_PHA | 安南小北一路(1510) 相間RY | LINE161 | [5 empty] | 8 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1510 | MW | 安南小北一路 1510 瓦 | MW_-224_224(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1510_MW | 安南小北一路 MW | LINE161 | [5 empty] | 9 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.448 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1510 | GDA | 安南小北一路 1510 GDA接地 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_GDA | 安南小北一路(1510) 接地RY | LINE161 | [5 empty] | 10 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1510 | MVAR | 安南小北一路 1510 乏 | MVAR_-224_224(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1510_MVAR | 安南小北一路 MVAR | LINE161 | [5 empty] | 11 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.448 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/1Bus | L/P02D261/T2 |  |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1510 | ON/OFF | 安南小北一路 1510 CB |  | aaba | B2/D26_A1 | [8 empty] | 小北DS.1510_CB | 1510(安南小北一路) CB | LINE161 | [5 empty] | 12 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1520 | MW | 安南小北二路 1520 瓦 | MW_-224_224(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1520_MW | 安南小北二路 MW | LINE161 | [5 empty] | 13 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.448 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1520 | 87A | 安南小北二路 1520 87 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_87A | 安南小北二路(1520) 87RY | LINE161 | [5 empty] | 14 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1520 | MVAR | 安南小北二路 1520 乏 | MVAR_-224_224(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1520_MVAR | 安南小北二路 MVAR | LINE161 | [5 empty] | 15 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.448 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1520 | PHA | 安南小北二路 1520 PHA相間 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_PHA | 安南小北二路(1520) 相間RY | LINE161 | [5 empty] | 16 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1520 | GDA | 安南小北二路 1520 GDA接地 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_GDA | 安南小北二路(1520) 接地RY | LINE161 | [5 empty] | 17 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1510 | KG | 安南小北一路 1510 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1510_OF_R | 安南小北一路 R相 油壓 | OTHER | [5 empty] | 18 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1510 | KG | 安南小北一路 1510 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1510_OF_S | 安南小北一路 S相 油壓 | OTHER | [5 empty] | 19 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1510 | KG | 安南小北一路 1510 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1510_OF_T | 安南小北一路 T相 油壓 | OTHER | [5 empty] | 20 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1520 | KG | 安南小北二路 1520 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1520_OF_R | 安南小北二路 R相 油壓 | OTHER | [5 empty] | 21 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1520 | KG | 安南小北二路 1520 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1520_OF_S | 安南小北二路 S相 油壓 | OTHER | [5 empty] | 22 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1520 | KG | 安南小北二路 1520 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/D26_A1 | [8 empty] | 小北DS.1520_OF_T | 安南小北二路 T相 油壓 | OTHER | [5 empty] | 23 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | RTU第二箱 | V | DCP 電壓 | kV_-150_150(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 24 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | RTU第二箱 | V | DCN 電壓 | kV_-150_150(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 25 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D26 | 小北DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 26 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | #1ADTR | ℃ | #1ADTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 27 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | #1BDTR | ℃ | #1BDTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 28 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/1Bus | L/P02D261/T2 |  |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1520 | ON/OFF | 安南小北二路 1520 CB |  | abba | B2/D26_A1 | [8 empty] | 小北DS.1520_CB | 1520(安南小北二路) CB | LINE161 | [5 empty] | 29 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/1Bus | T/1DTR |  |  | 0045 |  | 0010 | 1-05-05 |  | 1-0A | #1DTR | ON/OFF | #1DTR 1750 CB |  | aacb | ELEM/D26_A1 | [8 empty] | 小北DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 30 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 31 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #2ADTR | ℃ | #2ADTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 32 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #2BDTR | ℃ | #2BDTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 33 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/2Bus | T/2DTR |  |  | 0055 |  | 0011 | 1-06-07 |  | 1-0B | #2DTR | ON/OFF | #2DTR 1760 CB |  | abcb | ELEM/D26_A1 | [8 empty] | 小北DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 34 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/2Bus | T/3DTR |  |  | 0065 |  | 0012 | 1-08-01 |  | 1-0C | #3DTR | ON/OFF | #3DTR 1770 CB |  | abeb | ELEM/D26_A1 | [8 empty] | 小北DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 35 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #3DTR | ℃ | #3DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 36 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #3DTR | ℃ | #3DTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_COIL | #3DTR 線溫 | MTR | [5 empty] | 37 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | T/1DTR(A) |  |  | 0051 |  | 0016 | 1-06-03 |  | 1-10 | 310 | ON/OFF | #D1A 310 CB |  | aaca | ELEM/D26_A1 | [8 empty] | 小北DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 38 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 310 | MW | 310 瓦 | MW_-36_36(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 39 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D26 | 小北DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D26_A1 | [16 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 310 | MVAR | 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 41 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D26 | 小北DS | 161 | 161kV | ComPoint | BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 161KV BUS | 87BA | 161KV BUS 87BA |  |  | B2/D26_A1 | [8 empty] | 小北DS.161BUS_87A | 161KV BUS 87RY | BUS | [5 empty] | 42 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 310R | A | 310 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 43 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 310S | A | 310 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 44 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | C/1SC |  |  | 0178 |  | 0018 | 1-16-02 |  | 1-12 | #1SC | ON/OFF | #1SC 210 CB |  | aadb | B3/D26_A1 | [8 empty] | 小北DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 45 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 310T | A | 310 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 46 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #1DTR | 87A | #1DTR 87 RY |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 47 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 備用線 | MVAR | 北21線F1 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北21線KVAR | 11KV北21線 KVAR | FEEDER | [5 empty] | 48 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 49 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 備用線 | A | 北21線F1 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北21線A1 | 11KV北21線 R相AMP | FEEDER | [5 empty] | 50 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #1DTR | 51ZA | #1DTR 51Z RY |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 51 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 備用線 | A | 北21線F1 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北21線A2 | 11KV北21線 S相AMP | FEEDER | [5 empty] | 52 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #1DTR | 51A | #1DTR 1750 51 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 53 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 備用線 | A | 北21線F1 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北21線A3 | 11KV北21線 T相AMP | FEEDER | [5 empty] | 54 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #1DTR | 51NA | #1DTR 1750 51N RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 55 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 協進線 | MVAR | 北22線 KG22 F2乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北22線KVAR | 11KV北22線 KVAR | FEEDER | [5 empty] | 56 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KG21/T1 |  |  | 0160 |  | 0019 | 1-14-00 |  | 1-13 | 備用線 | ON/OFF | 北21線 CB |  | aaeb | B2/D26_D1 | [8 empty] | 小北DS.KG21_CB | KG21(11KV北21線) CB | FEEDER | [5 empty] | 57 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 協進線 | A | 北22線KG22 F2 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北22線A1 | 11KV北22線 R相AMP | FEEDER | [5 empty] | 58 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 310 | 51A | 310 51RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.310_51A | #1DTR二次側(310) 51RY | MTR | [5 empty] | 59 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 協進線 | A | 北22線KG22 F2 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北22線A2 | 11KV北22線 S相AMP | FEEDER | [5 empty] | 60 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 協進線 | A | 北22線KG22 F2 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北22線A3 | 11KV北22線 T相AMP | FEEDER | [5 empty] | 61 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 臨安線 | MVAR | 北23線KG23 F3 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北23線KVAR | 11KV北23線 KVAR | FEEDER | [5 empty] | 62 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KG22/T1 |  |  | 0163 |  | 0020 | 1-14-03 |  | 1-14 | 協進線 | ON/OFF | 北22線 KG22 F2 CB |  | aafb | B2/D26_D1 | [8 empty] | 小北DS.KG22_CB | KG22(11KV北22線) CB | FEEDER | [5 empty] | 63 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 臨安線 | A | 北23線KG23 F3 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北23線A1 | 11KV北23線 R相AMP | FEEDER | [5 empty] | 64 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #2DTR | 87A | #2DTR 87 RY |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 65 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 臨安線 | A | 北23線KG23 F3 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北23線A2 | 11KV北23線 S相AMP | FEEDER | [5 empty] | 66 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 67 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 臨安線 | A | 北23線KG23 F3 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北23線A3 | 11KV北23線 T相AMP | FEEDER | [5 empty] | 68 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #2DTR | 51ZA | #2DTR 51Z RY |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 69 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 民族線 | MVAR | 北24線KG24 F4 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北24線KVAR | 11KV北24線 KVAR | FEEDER | [5 empty] | 70 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #2DTR | 51A | #2DTR 1760 51 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 71 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 民族線 | A | 北24線KG24 F4 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北24線A1 | 11KV北24線 R相AMP | FEEDER | [5 empty] | 72 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #2DTR | 51NA | #2DTR 1760 51N RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 73 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 民族線 | A | 北24線KG24 F4 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北24線A2 | 11KV北24線 S相AMP | FEEDER | [5 empty] | 74 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KG23/T1 |  |  | 0166 |  | 0021 | 1-14-06 |  | 1-15 | 臨安線 | ON/OFF | 北23線KG23 F3 CB |  | aagb | B2/D26_D1 | [8 empty] | 小北DS.KG23_CB | KG23(11KV北23線) CB | FEEDER | [5 empty] | 75 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 民族線 | A | 北24線KG24 F4 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北24線A3 | 11KV北24線 T相AMP | FEEDER | [5 empty] | 76 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 330 | 51A | 330 51RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 77 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 備用線 | MVAR | 北25線F5 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北25線KVAR | 11KV北25線 KVAR | FEEDER | [5 empty] | 78 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KG24/T1 |  |  | 0169 |  | 0022 | 1-15-01 |  | 1-16 | 民族線 | ON/OFF | 北24線KG24 F4 CB |  | aahb | B2/D26_D1 | [8 empty] | 小北DS.KG24_CB | KG24(11KV北24線) CB | FEEDER | [5 empty] | 79 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 備用線 | A | 北25線F5 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北25線A1 | 11KV北25線 R相AMP | FEEDER | [5 empty] | 80 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 320 | 51A | 320 51RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.320_51A | #1DTR二次側(320) 51RY | MTR | [5 empty] | 81 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% | TEST | 10% TEST | ADCL_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 82 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KG25/T1 |  |  | 0172 |  | 0023 | 1-15-04 |  | 1-17 | 備用線 | ON/OFF | 北25線 F5 CB |  | aaib | B2/D26_D1 | [8 empty] | 小北DS.KG25_CB | KG25(11KV北25線) CB | FEEDER | [5 empty] | 83 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% | TEST | 90% TEST | ADCH_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #3DTR | 87A | #3DTR 87 RY |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 85 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 備用線 | A | 北25線F5 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北25線A2 | 11KV北25線 S相AMP | FEEDER | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #3DTR | 96PA | #3DTR 機械保護動作(96PA) |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 87 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 備用線 | A | 北25線F5 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北25線A3 | 11KV北25線 T相AMP | FEEDER | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #3DTR | 51ZA | #3DTR 51Z RY |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 89 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 長榮線 | MVAR | 北26線KG26 F6 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北26線KVAR | 11KV北26線 KVAR | FEEDER | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | #3DTR | 51A | #3DTR 1770 51 RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 91 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 長榮線 | A | 北26線KG26 F6 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北26線A1 | 11KV北26線 R相AMP | FEEDER | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | #3DTR | 51NA | #3DTR 1770 51N RY |  |  | B2/D26_A1 | [8 empty] | 小北DS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 93 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 長榮線 | A | 北26線KG26 F6 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北26線A2 | 11KV北26線 S相AMP | FEEDER | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KG26/T1 |  |  | 0175 |  | 0024 | 1-15-07 |  | 1-18 | 長榮線 | ON/OFF | 北26線KG26 F6 CB |  | aajb | B2/D26_D1 | [8 empty] | 小北DS.KG26_CB | KG26(11KV北26線) CB | FEEDER | [5 empty] | 95 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 長榮線 | A | 北26線KG26 F6 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北26線A3 | 11KV北26線 T相AMP | FEEDER | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0072 |  |  | 1-C8 |  |  | #D1ABUS | KV | #D1ABUS 310 電壓 #1A PT | kV_-9_9(-2000_2000) | aaa | B3/D26_A1 | [8 empty] | 小北DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 340 | 51A | 340 51RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 98 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | #TIE 100 | A | #TIE 100 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | #TIE 100 | A | #TIE 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | #TIE 100 | A | #TIE 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D26_A1 | [8 empty] | 小北DS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 102 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 320 | MW | 320 瓦 | MW_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 電驛盤 | RCA | 線路復閉電驛監視 |  |  | B3/D26_A1 | [8 empty] | 小北DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 320 | MVAR | 320 乏 | MVAR_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | C/2SC |  |  | 0181 |  | 0025 | 1-16-05 |  | 1-19 | #2SC | ON/OFF | #2SC 220 CB |  | aakb | B3/D26_A1 | [8 empty] | 小北DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 106 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 320 | A | 320 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 350 | 51A | 350 51RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | [5 empty] | 108 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 320 | A | 320 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 350 | 51A | 350 51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.350_GDA2 | 350開關箱IED RY GDA | OTHER | [5 empty] | 110 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 310 | 81A | #1DTR 1A 310 CB 81A/S |  |  | B3/D26_A1 | [8 empty] | 小北DS.310_81A/S | (310)81RY 動作/Reset | OTHER | [5 empty] | 111 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 320 | A | 320 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 320 | 81A | #1DTR 1B 320 CB 81A/S |  |  | B3/D26_A1 | [8 empty] | 小北DS.320_81A/S | (320)81RY 動作/Reset | OTHER | [5 empty] | 113 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 延平線 | MVAR | 北60線KG60 F7 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北60線KVAR | 23KV北60線 KVAR | FEEDER | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 330 | 81A | #2DTR 2A 330 CB 81A/S |  |  | B3/D26_A1 | [8 empty] | 小北DS.330_81A/S | (330)81RY 動作/Reset | OTHER | [5 empty] | 115 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 延平線 | A | 北60線KG60 F7 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北60線A1 | 23KV北60線 R相AMP | FEEDER | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 340 | 81A | #2DTR 2B 340 CB 81A/S |  |  | B3/D26_A1 | [8 empty] | 小北DS.340_81A/S | (340)81RY 動作/Reset | OTHER | [5 empty] | 117 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 延平線 | A | 北60線KG60 F7 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北60線A2 | 23KV北60線 S相AMP | FEEDER | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 350 | #3DDTR(350) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 350 | 81A | #3DTR 350 CB 81A/S |  |  | B3/D26_A1 | [8 empty] | 小北DS.350_81A/S | (350)81RY 動作/Reset | OTHER | [5 empty] | 119 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 延平線 | A | 北60線KG60 F7 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北60線A3 | 23KV北60線 T相AMP | FEEDER | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 310 | GDA | #1DTR 1A 310 GDA |  |  | B3/D26_A1 | [8 empty] | 小北DS.310_GDA | #1A DTR(310) 接地RY | OTHER | [5 empty] | 121 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 農民線 | MVAR | 北61線KG61 F8 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北61線KVAR | 23KV北61線 KVAR | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | 320 | GDA | #1DTR 1B 320 GDA |  |  | B3/D26_A1 | [8 empty] | 小北DS.320_GDA | #1B DTR(320) 接地RY | OTHER | [5 empty] | 123 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 農民線 | A | 北61線KG61 F8 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北61線A1 | 23KV北61線 R相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 330 | GDA | #2DTR 2A 330 GDA |  |  | B3/D26_A1 | [8 empty] | 小北DS.330_GDA | #2A DTR(330) 接地RY | OTHER | [5 empty] | 125 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 農民線 | A | 北61線KG61 F8 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北61線A2 | 23KV北61線 S相AMP | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 340 | GDA | #2DTR 2B 340 GDA |  |  | B3/D26_A1 | [8 empty] | 小北DS.340_GDA | #2B DTR(340) 接地RY | OTHER | [5 empty] | 127 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 農民線 | A | 北61線KG61 F8 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北61線A3 | 23KV北61線 T相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 | [10 empty] | B1/D26_A1 | [16 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 立人線 | MVAR | 北62線KG62 F9 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北62線KVAR | 23KV北62線 KVAR | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 | [10 empty] | B1/D26_A1 | [16 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 立人線 | A | 北62線KG62 F9 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北62線A1 | 23KV北62線 R相AMP | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 | [10 empty] | B1/D26_A1 | [16 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 立人線 | A | 北62線KG62 F9 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北62線A2 | 23KV北62線 S相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 立人線 | A | 北62線KG62 F9 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北62線A3 | 23KV北62線 T相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 公北線 | MVAR | 北63線KG63 F10 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北63線KVAR | 23KV北63線 KVAR | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 公北線 | A | 北63線KG63 F10 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北63線A1 | 23KV北63線 R相AMP | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 公北線 | A | 北63線KG63 F10 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北63線A2 | 23KV北63線 S相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 公北線 | A | 北63線KG63 F10 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北63線A3 | 23KV北63線 T相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0097 |  |  | 1-E1 |  |  | #D1BBUS | KV | #D1BBUS 320 電壓 #1B PT | kV_-18_18(-2000_2000) | baa | B3/D26_A1 | [8 empty] | 小北DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 330 | MW | 330 瓦 | MW_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 330 | MVAR | 330 乏 | MVAR_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 330 | A | 330 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 330 | A | 330 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 330 | A | 330 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 成醫線 | MVAR | 北54線KG54 F11 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北54線KVAR | 23KV北54線 KVAR | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 成醫線 | A | 北54線KG54 F11 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北54線A1 | 23KV北54線 R相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 成醫線 | A | 北54線KG54 F11 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北54線A2 | 23KV北54線 S相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 成醫線 | A | 北54線KG54 F11 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北54線A3 | 23KV北54線 T相AMP | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 站前線 | MVAR | 北55線KG55 F12乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北55線KVAR | 23KV北55線 KVAR | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 站前線 | A | 北55線KG55 F12 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北55線A1 | 23KV北55線 R相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 站前線 | A | 北55線KG55 F12 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北55線A2 | 23KV北55線 S相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 站前線 | A | 北55線KG55 F12 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北55線A3 | 23KV北55線 T相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 東雲線 | MVAR | 北56線KG56 F13 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北56線KVAR | 23KV北56線 KVAR | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 東雲線 | A | 北56線KG56 F13 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北56線A1 | 23KV北56線 R相AMP | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 東雲線 | A | 北56線KG56 F13 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北56線A2 | 23KV北56線 S相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 東雲線 | A | 北56線KG56 F13 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北56線A3 | 23KV北56線 T相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 永樂線 | MVAR | 北57線KG57 F14 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北57線KVAR | 23KV北57線 KVAR | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 永樂線 | A | 北57線KG57 F14 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北57線A1 | 23KV北57線 R相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 永樂線 | A | 北57線KG57 F14 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北57線A2 | 23KV北57線 S相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 永樂線 | A | 北57線KG57 F14 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北57線A3 | 23KV北57線 T相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0119 |  |  | 1-F7 |  |  | #D2ABUS | KV | #D2ABUS 330 電壓 #2A PT | kV_-18_18(-2000_2000) | aba | B3/D26_A1 | [8 empty] | 小北DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | #TIE 200 | A | #TIE 200 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | #TIE 200 | A | #TIE 200 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | #TIE 200 | A | #TIE 200 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 340 | MW | 340 瓦 | MW_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 340 | MVAR | 340 乏 | MVAR_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 340 | A | 340 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 340 | A | 340 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 340 | A | 340 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% | TEST | 10% TEST | ADCL_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% | TEST | 90% TEST | ADCH_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 正覺線 | MVAR | 北64線KG64 F15 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北64線KVAR | 23KV北64線 KVAR | FEEDER | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 正覺線 | A | 北64線KG64 F15 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北64線A1 | 23KV北64線 R相AMP | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 正覺線 | A | 北64線KG64 F15 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北64線A2 | 23KV北64線 S相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 正覺線 | A | 北64線KG64 F15 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北64線A3 | 23KV北64線 T相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 東榮線 | MVAR | 北65線KG65 F16 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北65線KVAR | 23KV北65線 KVAR | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 東榮線 | A | 北65線KG65 F16 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北65線A1 | 23KV北65線 R相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 東榮線 | A | 北65線KG65 F16 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北65線A2 | 23KV北65線 S相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 東榮線 | A | 北65線KG65 F16 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北65線A3 | 23KV北65線 T相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 站后線 | MVAR | 北66線KG66 F17 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北66線KVAR | 23KV北66線 KVAR | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 站后線 | A | 北66線KG66 F17 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北66線A1 | 23KV北66線 R相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 站后線 | A | 北66線KG66 F17 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北66線A2 | 23KV北66線 S相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 站后線 | A | 北66線KG66 F17 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北66線A3 | 23KV北66線 T相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 文和線 | MVAR | 北67線KG67 F18 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北67線KVAR | 23KV北67線 KVAR | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 文和線 | A | 北67線KG67 F18 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北67線A1 | 23KV北67線 R相AMP | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 文和線 | A | 北67線KG67 F18 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北67線A2 | 23KV北67線 S相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 文和線 | A | 北67線KG67 F18 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北67線A3 | 23KV北67線 T相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0155 |  |  | 2-9B |  |  | #D2BBUS | KV | #D2BBUS 340 電壓#2B PT | kV_-18_18(-2000_2000) | bba | B3/D26_A1 | [8 empty] | 小北DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0156 |  |  | 2-9C |  |  | #3 BUS PT | KV | #3 BUS 350 電壓#3 PT | kV_-18_18(-2000_2000) | aca | B3/D26_A1 | [8 empty] | 小北DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 350 | MW | 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 350 | MVAR | 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 350 | A | 350 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 350 | A | 350 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrG | B/2ABus | A/300 |  |  | 0184 |  | 0026 | 1-17-00 |  | 1-1A | #TIE 100 | ON/OFF | #TIE 100 CB |  | abab | B3/D26_A1 | [8 empty] | 小北DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 195 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 350 | A | 350 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 備用線 | 51A | 北21線 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG21_PHA | 11KV北21線(KG21) 相間RY | FEEDER | [5 empty] | 197 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 備用線 | 51NA | 北21線1 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG21_GDA | 11KV北21線(KG21) 接地RY | FEEDER | [5 empty] | 198 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | F21 | MVAR | 北71線KG71 F21 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北71線KVAR | 23KV北71線 KVAR | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KG60/T1 |  |  | 0187 |  | 0027 | 1-17-03 |  | 1-1B | 延平線 | ON/OFF | 北60線KG60 F7 CB |  | abbb | B2/D26_D1 | [8 empty] | 小北DS.KG60_CB | KG60(23KV北60線) CB | FEEDER | [5 empty] | 200 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | F21 | A | 北71線KG71 F21 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北71線A1 | 23KV北71線 R相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | 協進線 | 51A | 北22線KG22 F2 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG22_PHA | 11KV北22線(KG22) 相間RY | FEEDER | [5 empty] | 202 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | F21 | A | 北71線KG71 F21 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北71線A2 | 23KV北71線 S相AMP | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | 協進線 | 51NA | 北22線KG22 F2 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG22_GDA | 11KV北22線(KG22) 接地RY | FEEDER | [5 empty] | 204 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | F21 | A | 北71線KG71 F21 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北71線A3 | 23KV北71線 T相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KG61/T1 |  |  | 0190 |  | 0028 | 1-17-06 |  | 1-1C | 農民線 | ON/OFF | 北61線KG61 F8 CB |  | abcb | B2/D26_D1 | [8 empty] | 小北DS.KG61_CB | KG61(23KV北61線) CB | FEEDER | [5 empty] | 206 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | F21 | A | 北71線KG71 F21 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北71線A0 | 23KV北71線 N相AMP | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | 臨安線 | 51A | 北23線KG23 F3 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG23_PHA | 11KV北23線(KG23) 相間RY | FEEDER | [5 empty] | 208 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | F22 | MVAR | 北72線KG72 F22 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北72線KVAR | 23KV北72線 KVAR | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 臨安線 | 51NA | 北23線KG23 F3 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG23_GDA | 11KV北23線(KG23) 接地RY | FEEDER | [5 empty] | 210 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | F22 | A | 北72線KG72 F22 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北72線A1 | 23KV北72線 R相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KG62/T1 |  |  | 0193 |  | 0029 | 1-18-01 |  | 1-1D | 立人線 | ON/OFF | 北62線KG62 F9 CB |  | abdb | B2/D26_D1 | [8 empty] | 小北DS.KG62_CB | KG62(23KV北62線) CB | FEEDER | [5 empty] | 212 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | F22 | A | 北72線KG72 F22 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北72線A2 | 23KV北72線 S相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 民族線 | 51A | 北24線KG24 F4 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG24_PHA | 11KV北24線(KG24) 相間RY | FEEDER | [5 empty] | 214 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | F22 | A | 北72線KG72 F22 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北72線A3 | 23KV北72線 T相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 民族線 | 51NA | 北24線KG24 F4 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG24_GDA | 11KV北24線(KG24) 接地RY | FEEDER | [5 empty] | 216 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | F22 | A | 北72線KG72 F22 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北72線A0 | 23KV北72線 N相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KG63/T1 |  |  | 0196 |  | 0030 | 1-18-04 |  | 1-1E | 公北線 | ON/OFF | 北63線KG63 F10 CB |  | abeb | B2/D26_D1 | [8 empty] | 小北DS.KG63_CB | KG63(23KV北63線) CB | FEEDER | [5 empty] | 218 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | F23 | MVAR | 北73線KG73 F23 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北73線KVAR | 23KV北73線 KVAR | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | 備用線 | 51A | 北25線 F5 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG25_PHA | 11KV北25線(KG25) 相間RY | FEEDER | [5 empty] | 220 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | F23 | A | 北73線KG73 F23 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北73線A1 | 23KV北73線 R相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | 備用線 | 51NA | 北25線 F5 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG25_GDA | 11KV北25線(KG25) 接地RY | FEEDER | [5 empty] | 222 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | F23 | A | 北73線KG73 F23 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北73線A2 | 23KV北73線 S相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | C/4SC |  |  | 0199 |  | 0031 | 1-18-07 |  | 1-1F | #4SC | ON/OFF | #4SC 240 CB |  | abfb | B3/D26_A1 | [8 empty] | 小北DS.240_CB | 240(23KV #4SC) CB | SC | [5 empty] | 224 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | F23 | A | 北73線KG73 F23 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北73線A3 | 23KV北73線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | 長榮線 | 51A | 北26線KG26 F6 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG26_PHA | 11KV北26線(KG26) 相間RY | FEEDER | [5 empty] | 226 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | F23 | A | 北73線KG73 F23 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北73線A0 | 23KV北73線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | 長榮線 | 51NA | 北26線KG26 F6 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG26_GDA | 11KV北26線(KG26) 接地RY | FEEDER | [5 empty] | 228 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | F24 | MVAR | 北74線KG74 F24 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北74線KVAR | 23KV北74線 KVAR | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | T/2DTR(A) |  |  | 0061 |  | 0032 | 1-07-05 |  | 1-20 | 330 | ON/OFF | #D2A 330 CB |  | abga | ELEM/D26_A1 | [8 empty] | 小北DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 230 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | F24 | A | 北74線KG74 F24 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北74線A1 | 23KV北74線 R相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | #1SC | 51/51A | #1SC 210 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 232 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | F24 | A | 北74線KG74 F24 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北74線A2 | 23KV北74線 S相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | #1SC | 27/59 A | #1SC 210 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 234 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | F24 | A | 北74線KG74 F24 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北74線A3 | 23KV北74線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | T/1DTR(B) |  |  | 0063 |  | 0033 | 1-07-07 |  | 1-21 | 320 | ON/OFF | #D1B 320 CB |  | baba | ELEM/D26_A1 | [8 empty] | 小北DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 236 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | F24 | A | 北74線KG74 F24 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北74線A0 | 23KV北74線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | #2SC | 51/51A | #2SC 220 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 238 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | F25 | MVAR | 北75線KG75 F25 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北75線KVAR | 23KV北75線 KVAR | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | #2SC | 27/59 A | #2SC 220 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 240 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | F25 | A | 北75線KG75 F25 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北75線A1 | 23KV北75線 R相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | C/3SC |  |  | 0202 |  | 0034 | 1-19-02 |  | 1-22 | #3SC | ON/OFF | #3SC 230 CB |  | bacb | B3/D26_A1 | [8 empty] | 小北DS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | F25 | A | 北75線KG75 F25 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北75線A2 | 23KV北75線 S相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | #TIE 100 | 51A | #TIE 100 51 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | F25 | A | 北75線KG75 F25 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北75線A3 | 23KV北75線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | #TIE 100 | 51NA | #TIE 100 51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | F25 | A | 北75線KG75 F25 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北75線A0 | 23KV北75線 N相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KG54/T1 |  |  | 0205 |  | 0035 | 1-19-05 |  | 1-23 | 成醫線 | ON/OFF | 北54線KG54 F11 CB |  | badb | B2/D26_D1 | [8 empty] | 小北DS.KG54_CB | KG54(23KV北54線) CB | FEEDER | [5 empty] | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | F26 | MVAR | 北76線KG76 F26 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北76線KVAR | 23KV北76線 KVAR | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | 延平線 | 51A | 北60線KG60 F7 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG60_PHA | 23KV北60線(KG60) 相間RY | FEEDER | [5 empty] | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | F26 | A | 北76線KG76 F26 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北76線A1 | 23KV北76線 R相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | 延平線 | 51NA | 北60線KG60 F7 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG60_GDA | 23KV北60線(KG60) 接地RY | FEEDER | [5 empty] | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | F26 | A | 北76線KG76 F26 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北76線A2 | 23KV北76線 S相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KG55/T1 |  |  | 0208 |  | 0036 | 1-1A-00 |  | 1-24 | 站前線 | ON/OFF | 北55線KG55F12 CB |  | baeb | B2/D26_D1 | [8 empty] | 小北DS.KG55_CB | KG55(23KV北55線) CB | FEEDER | [5 empty] | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | F26 | A | 北76線KG76 F26 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北76線A3 | 23KV北76線 T相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | 農民線 | 51A | 北61線KG61 F8 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG61_PHA | 23KV北61線(KG61) 相間RY | FEEDER | [5 empty] | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | F26 | A | 北76線KG76 F26 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北76線A0 | 23KV北76線 N相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% | TEST | 10% TEST | ADCL_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | 農民線 | 51NA | 北61線KG61 F8 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG61_GDA | 23KV北61線(KG61) 接地RY | FEEDER | [5 empty] | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% | TEST | 90% TEST | ADCH_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KG56/T1 |  |  | 0211 |  | 0037 | 1-1A-03 |  | 1-25 | 東雲線 | ON/OFF | 北56線KG56 F13 CB |  | bafb | B2/D26_D1 | [8 empty] | 小北DS.KG56_CB | KG56(23KV北56線) CB | FEEDER | [5 empty] | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 立人線 | 51A | 北62線KG62 F9 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG62_PHA | 23KV北62線(KG62) 相間RY | FEEDER | [5 empty] | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | F27 | MVAR | 北77線KG77 F27 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北77線KVAR | 23KV北77線 KVAR | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 立人線 | 51NA | 北62線KG62 F9 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG62_GDA | 23KV北62線(KG62) 接地RY | FEEDER | [5 empty] | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | F27 | A | 北77線KG77 F27 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北77線A1 | 23KV北77線 R相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KG57/T1 |  |  | 0214 |  | 0038 | 1-1A-06 |  | 1-26 | 永樂線 | ON/OFF | 北57線KG57 F14 CB |  | bagb | B2/D26_D1 | [8 empty] | 小北DS.KG57_CB | KG57(23KV北57線) CB | FEEDER | [5 empty] | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | F27 | A | 北77線KG77 F27 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北77線A2 | 23KV北77線 S相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 公北線 | 51A | 北63線KG63 F10 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG63_PHA | 23KV北63線(KG63) 相間RY | FEEDER | [5 empty] | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | F27 | A | 北77線KG77 F27 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北77線A3 | 23KV北77線 T相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 公北線 | 51NA | 北63線KG63 F10 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG63_GDA | 23KV北63線(KG63) 接地RY | FEEDER | [5 empty] | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | F27 | A | 北77線KG77 F27 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北77線A0 | 23KV北77線 N相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/1BBus | B/2BBus |  |  | 0217 |  | 0039 | 1-1B-01 |  | 1-27 | #TIE 200 | ON/OFF | #TIE 200 CB |  | bahb | B3/D26_A1 | [8 empty] | 小北DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | F28 | MVAR | 北78線KG78 F28 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北78線KVAR | 23KV北78線 KVAR | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | #4SC | 51/51A | #4SC 240 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.240_SCA | 23KV #4SC 51,51N RY | SC | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | F28 | A | 北78線KG78 F28 R相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北78線A1 | 23KV北78線 R相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | #4SC | 27/59 A | #4SC 240 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | F28 | A | 北78線KG78 F28 S相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北78線A2 | 23KV北78線 S相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | C/6SC |  |  | 0238 |  | 0040 | 1-1D-06 |  | 1-28 | #6SC | ON/OFF | #6SC 260 CB |  | bbab | B3/D26_A1 | [8 empty] | 小北DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | F28 | A | 北78線KG78 F28 T相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北78線A3 | 23KV北78線 T相AMP | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | #3SC | 51/51A | #3SC 230 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | F28 | A | 北78線KG78 F28 N相電流 | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北78線A0 | 23KV北78線 N相AMP | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | #3SC | 27/59 A | #3SC 230 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | #TIE 300 | A | #TIE 300 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | #TIE 300 | A | #TIE 300 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KG64/T1 |  |  | 0220 |  | 0041 | 1-1B-04 |  | 1-29 | 正覺線 | ON/OFF | 北64線KG64 F15 CB |  | bbbb | B2/D26_D1 | [8 empty] | 小北DS.KG64_CB | KG64(23KV北64線) CB | FEEDER | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | #TIE 300 | A | #TIE 300 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D26_A1 | [8 empty] | 小北DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 成醫線 | 51A | 北54線KG54 F11 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG54_PHA | 23KV北54線(KG54) 相間RY | FEEDER | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | 成醫線 | 51NA | 北54線KG54 F11 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG54_GDA | 23KV北54線(KG54) 接地RY | FEEDER | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 北21線 | A | 北21線F1 KG21 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北21線A0 | 11KV北21線 N相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KG65/T1 |  |  | 0223 |  | 0042 | 1-1B-07 |  | 1-2A | 東榮線 | ON/OFF | 北65線KG65 F16 CB |  | bbcb | B2/D26_D1 | [8 empty] | 小北DS.KG65_CB | KG65(23KV北65線) CB | FEEDER | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 北22線 | A | 北22線F2 KG22 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北22線A0 | 11KV北22線 N相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | 站前線 | 51A | 北55線KG55 F12 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG55_PHA | 23KV北55線(KG55) 相間RY | FEEDER | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 北23線 | A | 北23線F3 KG23 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北23線A0 | 11KV北23線 N相AMP | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | 站前線 | 51NA | 北55線KG55 F12 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG55_GDA | 23KV北55線(KG55) 接地RY | FEEDER | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 北24線 | A | 北24線F4 KG24 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北24線A0 | 11KV北24線 N相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KG66/T1 |  |  | 0226 |  | 0043 | 1-1C-02 |  | 1-2B | 站后線 | ON/OFF | 北66線KG66 F17 CB |  | bbdb | B2/D26_D1 | [8 empty] | 小北DS.KG66_CB | KG66(23KV北66線) CB | FEEDER | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 北25線 | A | 北25線F5 KG25 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北25線A0 | 11KV北25線 N相AMP | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | 東雲線 | 51A | 北56線KG56 F13 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG56_PHA | 23KV北56線(KG56) 相間RY | FEEDER | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 北26線 | A | 北26線F6 KG26 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北26線A0 | 11KV北26線 N相AMP | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 東雲線 | 51NA | 北56線KG56 F13 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG56_GDA | 23KV北56線(KG56) 接地RY | FEEDER | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KG67/T1 |  |  | 0229 |  | 0044 | 1-1C-05 |  | 1-2C | 文和線 | ON/OFF | 北67線KG67 F18 CB |  | bbeb | B2/D26_D1 | [8 empty] | 小北DS.KG67_CB | KG67(23KV北67線) CB | FEEDER | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 北64線 | A | 北64線F15 KG64 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北64線A0 | 23KV北64線 N相AMP | FEEDER | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 永樂線 | 51A | 北57線KG57 F14 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG57_PHA | 23KV北57線(KG57) 相間RY | FEEDER | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 北65線 | A | 北65線F16 KG65 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北65線A0 | 23KV北65線 N相AMP | FEEDER | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 永樂線 | 51NA | 北57線KG57 F14 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG57_GDA | 23KV北57線(KG57) 接地RY | FEEDER | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 北66線 | A | 北66線F17 KG66 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北66線A0 | 23KV北66線 N相AMP | FEEDER | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KG68/T1 |  |  | 0232 |  | 0045 | [7 empty] | bbfb | B2/D26_D1 | [16 empty] | 307 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 北67線 | A | 北67線F18 KG67 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北67線A0 | 23KV北67線 N相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | #TIE 200 | 51A | #TIE 200 51 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 北68線 | A | 北68線F19 KG68 A (N) |  |  | B2/D26_D1 | [16 empty] | 310 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | #TIE 200 | 51NA | #TIE 200 51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 北69線 | A | 北69線F20 KG69 A (N) |  |  | B2/D26_D1 | [16 empty] | 312 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 北60線 | A | 北60線F7 KG60 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北60線A0 | 23KV北60線 N相AMP | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KG69/T1 |  |  | 0235 |  | 0046 | [7 empty] | bbgb | B2/D26_D1 | [16 empty] | 314 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 北61線 | A | 北61線F8 KG61 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北61線A0 | 23KV北61線 N相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 正覺線 | 51A | 北64線KG64 F15 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG64_PHA | 23KV北64線(KG64) 相間RY | FEEDER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 北62線 | A | 北62線F9 KG62 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北62線A0 | 23KV北62線 N相AMP | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 正覺線 | 51NA | 北64線KG64 F15 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG64_GDA | 23KV北64線(KG64) 接地RY | FEEDER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 北63線 | A | 北63線F10 KG63 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北63線A0 | 23KV北63線 N相AMP | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | C/5SC |  |  | 0241 |  | 0047 | 1-1E-01 |  | 1-2F | #5SC | ON/OFF | #5SC 250 CB |  | bbhb | B3/D26_A1 | [8 empty] | 小北DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 北54線 | A | 北54線F11 KG54 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北54線A0 | 23KV北54線 N相AMP | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | 東榮線 | 51A | 北65線KG65 F16 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG65_PHA | 23KV北65線(KG65) 相間RY | FEEDER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 北55線 | A | 北55線F12 KG55 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北55線A0 | 23KV北55線 N相AMP | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 東榮線 | 51NA | 北65線KG65 F16 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG65_GDA | 23KV北65線(KG65) 接地RY | FEEDER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 北56線 | A | 北56線F13 KG56 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北56線A0 | 23KV北56線 N相AMP | FEEDER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | T/2DTR(B) |  |  | 0071 |  | 0048 | 1-08-07 |  | 1-30 | 340 | ON/OFF | #D2B 340 CB |  | bbia | ELEM/D26_A1 | [8 empty] | 小北DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 北57線 | A | 北57線F14 KG57 A (N) | A_-600_600(-2000_2000) |  | B2/D26_D1 | [8 empty] | 小北DS.北57線A0 | 23KV北57線 N相AMP | FEEDER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 站后線 | 51A | 北66線KG66 F17 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG66_PHA | 23KV北66線(KG66) 相間RY | FEEDER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 站后線 | 51NA | 北66線KG66 F17 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG66_GDA | 23KV北66線(KG66) 接地RY | FEEDER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | C/7SC |  |  | 0249 |  | 0049 | 1-1F-01 |  | 1-31 | #7SC | ON/OFF | #7SC 270 CB |  | accb | B3/D26_A1 | [8 empty] | 小北DS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | 文和線 | 51A | 北67線KG67 F18 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG67_PHA | 23KV北67線(KG67) 相間RY | FEEDER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 文和線 | 51NA | 北67線KG67 F18 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG67_GDA | 23KV北67線(KG67) 接地RY | FEEDER | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | T/3DTR |  |  | 0077 |  | 0050 | 1-09-05 |  | 1-32 | 350 | ON/OFF | #D3 350 CB |  | acba | ELEM/D26_A1 | [8 empty] | 小北DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 | [10 empty] | B2/D26_D1 | [16 empty] | 334 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 | [10 empty] | B2/D26_D1 | [16 empty] | 335 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG71/T1 |  |  | 0252 |  | 0051 | 1-1F-04 |  | 1-33 | F21 | ON/OFF | 北71線KG71 F21 CB |  | acdb | B2/D26_D1 | [8 empty] | 小北DS.KG71_CB | KG71(23KV北71線) CB | FEEDER | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 | [10 empty] | B2/D26_D1 | [16 empty] | 337 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 | [10 empty] | B2/D26_D1 | [16 empty] | 338 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG72/T1 |  |  | 0255 |  | 0052 | 1-1F-07 |  | 1-34 | F22 | ON/OFF | 北72線KG72 F22 CB |  | aceb | B2/D26_D1 | [8 empty] | 小北DS.KG72_CB | KG72(23KV北72線) CB | FEEDER | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | #6SC | 51/51A | #6SC 260 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | #6SC | 27/59 A | #6SC 260 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG73/T1 |  |  | 0258 |  | 0053 | 2-00-02 |  | 1-35 | F23 | ON/OFF | 北73線KG73 F23 CB |  | acfb | B2/D26_D1 | [8 empty] | 小北DS.KG73_CB | KG73(23KV北73線) CB | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | #5SC | 51/51NA | #5SC 250 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | #5SC | 27/59 A | #5SC 250 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG74/T1 |  |  | 0261 |  | 0054 | 2-00-05 |  | 1-36 | F24 | ON/OFF | 北74線KG74 F24 CB |  | acgb | B2/D26_D1 | [8 empty] | 小北DS.KG74_CB | KG74(23KV北74線) CB | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | #7SC | 51/51NA | #7SC 270 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | #7SC | 27/59 A | #7SC 270 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG75/T1 |  |  | 0264 |  | 0055 | 2-01-00 |  | 1-37 | F25 | ON/OFF | 北75線KG75 F25 CB |  | achb | B2/D26_D1 | [8 empty] | 小北DS.KG75_CB | KG75(23KV北75線) CB | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0253 |  |  | 1-1F-05 |  |  | F21 | 51A | 北71線KG71 F21 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG71_PHA | 23KV北71線(KG71) 相間RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0254 |  |  | 1-1F-06 |  |  | F21 | 51NA | 北71線KG71 F21 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG71_GDA | 23KV北71線(KG71) 接地RY | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG76/T1 |  |  | 0267 |  | 0056 | 2-01-03 |  | 1-38 | F26 | ON/OFF | 北76線KG76 F26 CB |  | acib | B2/D26_D1 | [8 empty] | 小北DS.KG76_CB | KG76(23KV北76線) CB | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 |  |  | 2-00-00 |  |  | F22 | 51A | 北72線KG72 F22 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG72_PHA | 23KV北72線(KG72) 相間RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | F22 | 51NA | 北72線KG72 F22 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG72_GDA | 23KV北72線(KG72) 接地RY | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG77/T1 |  |  | 0270 |  | 0057 | 2-01-06 |  | 1-39 | F27 | ON/OFF | 北77線KG77 F27 CB |  | acjb | B2/D26_D1 | [8 empty] | 小北DS.KG77_CB | KG77(23KV北77線) CB | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | F23 | 51A | 北73線KG73 F23 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG73_PHA | 23KV北73線(KG73) 相間RY | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | F23 | 51NA | 北73線KG73 F23 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG73_GDA | 23KV北73線(KG73) 接地RY | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KG78/T1 |  |  | 0273 |  | 0058 | 2-02-01 |  | 1-3A | F28 | ON/OFF | 北78線KG78 F28 CB |  | ackb | B2/D26_D1 | [8 empty] | 小北DS.KG78_CB | KG78(23KV北78線) CB | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | F24 | 51A | 北74線KG74 F24 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG74_PHA | 23KV北74線(KG74) 相間RY | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | F24 | 51NA | 北74線KG74 F24 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG74_GDA | 23KV北74線(KG74) 接地RY | FEEDER | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | C/8SC |  |  | 0276 |  | 0059 | 2-02-04 |  | 1-3B | #8SC | ON/OFF | #8SC 280 CB |  | aclb | B3/D26_A1 | [8 empty] | 小北DS.280_CB | 280(23KV #8SC) CB | SC | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | F25 | 51A | 北75線KG75 F25 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG75_PHA | 23KV北75線(KG75) 相間RY | FEEDER | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | F25 | 51NA | 北75線KG75 F25 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG75_GDA | 23KV北75線(KG75) 接地RY | FEEDER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3Bus | B/2ABus |  |  | 0279 |  | 0060 | 2-02-07 |  | 1-3C | #TIE 300 | ON/OFF | #TIE 300 CB |  | acmb | B3/D26_A1 | [8 empty] | 小北DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | F26 | 51A | 北76線KG76 F26 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG76_PHA | 23KV北76線(KG76) 相間RY | FEEDER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | F26 | 51NA | 北76線KG76 F26 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG76_GDA | 23KV北76線(KG76) 接地RY | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0064 | 1-30-02 |  | 1-40 | 1510 | U/L | 安南小北一路 1510 87 RY U/L |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_87UL | 安南小北一路(1510) 87RY U/L | LINE161 | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 |  |  | 2-01-07 |  |  | F27 | 51A | 北77線KG77 F27 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG77_PHA | 23KV北77線(KG77) 相間RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | F27 | 51NA | 北77線KG77 F27 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG77_GDA | 23KV北77線(KG77) 接地RY | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0065 | 1-30-03 |  | 1-41 | 1510 | U/L | 安南小北一路 1510 79 RY U/L |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_79UL | 安南小北一路(1510) 79RY U/L | LINE161 | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 |  |  | 2-02-02 |  |  | F28 | 51A | 北78線KG78 F28 51 RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG78_PHA | 23KV北78線(KG78) 相間RY | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | F28 | 51NA | 北78線KG78 F28 51N RY |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG78_GDA | 23KV北78線(KG78) 接地RY | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0066 | 1-30-04 |  | 1-42 | 1520 | U/L | 安南小北二路 1520 87 RY U/L |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_87UL | 安南小北二路(1520) 87RY U/L | LINE161 | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 2-02-05 |  |  | #8SC | 51/51NA | #8SC 280 51/51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | #8SC | 27/59 A | #8SC 280 27/59 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  | 0067 | 1-30-05 |  | 1-43 | 1520 | U/L | 安南小北二路 1520 79 RY U/L |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_79UL | 安南小北二路(1520) 79RY U/L | LINE161 | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0280 |  |  | 2-03-00 |  |  | #TIE 300 | 51A | #TIE 300 51 RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | #TIE 300 | 51NA | #TIE 300 51N RY |  |  | B3/D26_A1 | [8 empty] | 小北DS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0597 |  | 0072 | 2-31-05 |  | 1-48 | 公北線 | U/L | 北63線KG63 F10 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG63_79UL | 23KV北63線(KG63) 79RY U/L | FEEDER | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU | L/S | L/R STATUS |  |  | ELEM/D26_A1 | [8 empty] | 小北DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0598 |  | 0073 | 2-31-06 |  | 1-49 | #4SC | A/M | #4SC Q-CTL A/M |  |  | B2/D26_D1 | [8 empty] | 小北DS.240_A/M | 23KV #4SC 乏控器 A/M | SC | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | AUTO/MANUAL | MANUAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0599 |  | 0074 | 2-31-07 |  | 1-4A | #3SC | A/M | #3SC Q-CTL A/M |  |  | B2/D26_D1 | [8 empty] | 小北DS.230_A/M | 23KV #3SC 乏控器 A/M | SC | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | AUTO/MANUAL | MANUAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0600 |  | 0075 | 2-31-08 |  | 1-4B | 成醫線 | U/L | 北54線KG54 F11 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG54_79UL | 23KV北54線(KG54) 79RY U/L | FEEDER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0601 |  | 0076 | 2-31-09 |  | 1-4C | 站前線 | U/L | 北55線KG55 F12 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG55_79UL | 23KV北55線(KG55) 79RY U/L | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | 1510 | A/N | 安南小北一路 1510 RYFA(電驛故障) |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_RYFA | 安南小北一路(1510)數位電驛故障 | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | 1510 | A/N | 安南小北一路 1510 87CFA (87L通訊故障) |  |  | B2/D26_A1 | [8 empty] | 小北DS.1510_87CFA | 安南小北一路(1510)87RY通訊故障 | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | 1520 | A/N | 安南小北二路 1520 RYFA(電驛故障) |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_RYFA | 安南小北二路(1520)數位電驛故障 | OTHER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | 1520 | A/N | 安南小北二路 1520 87CFA (87L通訊故障) |  |  | B2/D26_A1 | [8 empty] | 小北DS.1520_87CFA | 安南小北二路(1520)87RY通訊故障 | OTHER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0602 |  | 0077 | 2-31-10 |  | 1-4D | 東雲線 | U/L | 北56線KG56 F13 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG56_79UL | 23KV北56線(KG56) 79RY U/L | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0603 |  | 0078 | 2-31-11 |  | 1-4E | 永樂線 | U/L | 北57線KG57 F14 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG57_79UL | 23KV北57線(KG57) 79RY U/L | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0604 |  | 0079 | 2-31-12 |  | 1-4F | 正覺線 | U/L | 北64線KG64 F15 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG64_79UL | 23KV北64線(KG64) 79RY U/L | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0605 |  | 0080 | 2-31-13 |  | 1-50 | 東榮線 | U/L | 北65線KG65 F16 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG65_79UL | 23KV北65線(KG65) 79RY U/L | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0606 |  | 0081 | 2-31-14 |  | 1-51 | 站后線 | U/L | 北66線KG66 F17 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG66_79UL | 23KV北66線(KG66) 79RY U/L | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0864 |  | 0082 | 2-36-00 |  | 1-52 | F26 | ON/OFF | 北76線KG76 F26 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG76_79UL | 23KV北76線(KG76) 79RY U/L | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0865 |  | 0083 | 2-36-01 |  | 1-53 | F26 | ON/OFF | 北76線KG76 F26 51N U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG76_ADJ | 23KV北76線(KG76) LCO分流器 U/L | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0866 |  | 0084 | 2-36-02 |  | 1-54 | F27 | ON/OFF | 北77線KG77 F27 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG77_79UL | 23KV北77線(KG77) 79RY U/L | FEEDER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0085 | 2-36-03 |  | 1-55 | F27 | ON/OFF | 北77線KG77 F27 51N U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG77_ADJ | 23KV北77線(KG77) LCO分流器 U/L | FEEDER | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0868 |  | 0086 | 2-36-04 |  | 1-56 | F28 | ON/OFF | 北78線KG78 F28 79RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG78_79UL | 23KV北78線(KG78) 79RY U/L | FEEDER | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | 51_51NUL |  |  | Status | 51/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0869 |  | 0087 | 2-36-05 |  | 1-57 | F28 | ON/OFF | 北78線KG78 F28 51N U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG78_ADJ | 23KV北78線(KG78) LCO分流器 U/L | FEEDER | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0088 | 1-34-14 |  | 1-58 | 通訊室 | A/N | 通訊設備 光纖次故障(備用) |  |  | B3/D26_A1 | [16 empty] | 399 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0815 |  | 0089 | 1-34-15 |  | 1-59 | 通訊室 | A/N | 通信室溫控警報 |  |  | B3/D26_A1 | [8 empty] | 小北DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0817 |  | 0090 | 1-35-01 |  | 1-5A | #3DTR | A/N | #3DTR 96P |  |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0818 |  | 0091 | 1-35-02 |  | 1-5B | #3DTR | A/N | #3DTR 63Q |  |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0812 |  | 0092 | 1-34-12 |  | 1-5C | 通訊室 | A/N | 通訊設備 AC故障 |  |  | B3/D26_A1 | [8 empty] | 小北DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0096 | 1-32-12 |  | 1-60 | #1ADTR | A/M | #1ATR OLTC A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D26 | 小北DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0024 |  | 0097 | 1-98 |  | 1-61 | #1ADTR | 升/降 | #1ADTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 405 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0560 |  | 0098 | 1-33-00 |  | 1-62 | #1BDTR | A/M | #1BTR OLTC A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D26 | 小北DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0025 |  | 0099 | 1-99 |  | 1-63 | #1BDTR | 升/降 | #1BDTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 407 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 161 | 161kV | ComPoint | BUS |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | 161kV BUS | RYFA | 161KV BUS數位電驛故障 |  |  | B3/D26_A1 | [8 empty] | 小北DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | ComPoint | BUS |  | 87CTFA | 161KV BUS 87RY CT 迴路故障 |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | 161kV BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D26_A1 | [8 empty] | 小北DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0563 |  | 0100 | 1-33-03 |  | 1-64 | #2ADTR | A/M | #2ATR OLTC A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D26 | 小北DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0551 | [10 empty] | B1/D26_A1 | [16 empty] | 411 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  | 0101 | 1-9D |  | 1-65 | #2ADTR | 升/降 | #2ADTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 412 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D26_A1 | [8 empty] | 小北DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0567 |  | 0102 | 1-33-07 |  | 1-66 | #2BDTR | A/M | #2BTR OLTC A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D26 | 小北DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | #1ADTR | R/L | #1ATR OLTC R/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0030 |  | 0103 | 1-9E |  | 1-67 | #2BDTR | 升/降 | #2BDTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 416 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0557 |  |  | 1-32-13 |  |  | #1DTR | A/N | #1DTR TRA |  | a | B1/D26_A1 | [8 empty] | 小北DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | #1DTR | A/N | #1DTR TRF |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | #1BDTR | R/L | #1BTR OLTC R/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS |  |  | 3DTR | #3DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0570 |  | 0104 | 1-33-10 |  | 1-68 | #3DTR | A/M | #3DTR OLTC A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D26 | 小北DS |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0034 |  | 0105 | 1-A2 |  | 1-69 | #3DTR | ℃ | #3DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | [5 empty] | 421 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | #2ADTR | R/L | #2ATR OLTC R/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 161 | 161kV | ComPoint | BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0106 | 1-32-08 |  | 1-6A | 161kV BUS | U/L | 161KV BUS╴87UL |  |  | B2/D26_A1 | [8 empty] | 小北DS.161BUS_87UL | 161KV BUS 87RY U/L | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0564 |  |  | 1-33-04 |  |  | #2DTR | A/N | #2DTR TRA |  | a | B1/D26_A1 | [8 empty] | 小北DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #2DTR | A/N | #2DTR TRF |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | #2BDTR | R/L | #2BTR OLTC R/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0528 |  | 0108 | 1-31-00 |  | 1-6C | 備用線 | U/L | 北21線 F1 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG21_ADJ | 11KV北21線(KG21) LCO分流器 U/L | FEEDER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0529 |  | 0109 | 1-31-01 |  | 1-6D | 協進線 | U/L | 北22線KG22 F2 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG22_ADJ | 11KV北22線(KG22) LCO分流器 U/L | FEEDER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | #3DTR | R/L | #3DTR OLTC R/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0530 |  | 0110 | 1-31-02 |  | 1-6E | 臨安線 | U/L | 北23線KG23 F3 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG23_ADJ | 11KV北23線(KG23) LCO分流器 U/L | FEEDER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0571 |  |  | 1-33-11 |  |  | #3DTR | A/N | #3DTR TRA |  | a | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | #3DTR | A/N | #3DTR TRF |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0531 |  | 0111 | 1-31-03 |  | 1-6F | 民族線 | U/L | 北24線KG24 F4 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG24_ADJ | 11KV北24線(KG24) LCO分流器 U/L | FEEDER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0532 |  | 0112 | 1-31-04 |  | 1-70 | 備用線 | U/L | 北25線 F5 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG25_ADJ | 11KV北25線(KG25) LCO分流器 U/L | FEEDER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0575 | [10 empty] | B1/D26_A1 | [16 empty] | 435 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0576 |  |  | 2-30-00 |  |  | #1DTR | A/N | #1DTR 96D |  |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0577 |  |  | 2-30-01 |  |  | #1DTR | A/N | #1DTR 96P |  |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | ComPoint |  |  | CBA | 11或22kV |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0578 |  |  | 2-30-02 |  |  | #1DTR | A/N | #1DTR 63Q |  |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | ComPoint |  |  | CBF | 11或22kV |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0579 |  |  | 2-30-03 |  |  | #1DTR | A/N | #1DTR 96B1 |  |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0580 |  |  | 2-30-04 |  |  | #1DTR | A/N | #1DTR 96B2 |  |  | B3/D26_A1 | [8 empty] | 小北DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 2-30-06 |  |  | #2DTR | A/N | #2DTR 96P |  |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0583 |  |  | 2-30-07 |  |  | #2DTR | A/N | #2DTR 63Q |  |  | B3/D26_A1 | [8 empty] | 小北DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 2-30-08 |  |  | #2DTR | A/N | #2DTR 96B1 |  |  | ELEM/D26_A1 | [8 empty] | 小北DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 2-30-09 |  |  | #2DTR | A/N | #2DTR 96B2 |  |  | ELEM/D26_A1 | [8 empty] | 小北DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0586 |  |  | 2-30-10 |  |  | 備用線 | U/L | 北21線 F1 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG21_79UL | 11KV北21線(KG21) 79RY U/L | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0587 |  |  | 2-30-11 |  |  | 協進線 | U/L | 北22線KG22 F2 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG22_79UL | 11KV北22線(KG22) 79RY U/L | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0588 |  |  | 2-30-12 |  |  | 臨安線 | U/L | 北23線KG23 F3 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG23_79UL | 11KV北23線(KG23) 79RY U/L | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0591 |  |  | 2-30-15 |  |  | 長榮線 | U/L | 北26線KG26 F6 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG26_79UL | 11KV北26線(KG26) 79RY U/L | FEEDER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0592 |  |  | 2-31-00 |  |  | #1SC | A/M | #1SC Q-CTL A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | AUTO/MANUAL | MANUAL
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0593 |  |  | 2-31-01 |  |  | #2SC | A/M | #2SC Q-CTL A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | AUTO/MANUAL | MANUAL
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0594 |  |  | 2-31-02 |  |  | 延平線 | U/L | 北60線KG60 F7 79RY U/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.KG60_79UL | 23KV北60線(KG60) 79RY U/L | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0595 |  |  | 2-31-03 |  |  | 農民線 | U/L | 北61線KG61 F8 79RY U/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.KG61_79UL | 23KV北61線(KG61) 79RY U/L | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0596 |  |  | 2-31-04 |  |  | 立人線 | U/L | 北62線KG62 F9 79RY U/L |  |  | B1/D26_A1 | [8 empty] | 小北DS.KG62_79UL | 23KV北62線(KG62) 79RY U/L | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0533 |  | 0113 | 1-31-05 |  | 1-71 | 長榮線 | U/L | 北26線KG26 F6 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG26_ADJ | 11KV北26線(KG26) LCO分流器 U/L | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0534 |  | 0114 | 1-31-06 |  | 1-72 | 延平線 | U/L | 北60線KG60 F7 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG60_ADJ | 23KV北60線(KG60) LCO分流器 U/L | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0535 |  | 0115 | 1-31-07 |  | 1-73 | 農民線 | U/L | 北61線KG61 F8 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG61_ADJ | 23KV北61線(KG61) LCO分流器 U/L | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0536 |  | 0116 | 1-31-08 |  | 1-74 | 立人線 | U/L | 北62線KG62 F9 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG62_ADJ | 23KV北62線(KG62) LCO分流器 U/L | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0537 |  | 0117 | 1-31-09 |  | 1-75 | 公北線 | U/L | 北63線KG63 F10 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG63_ADJ | 23KV北63線(KG63) LCO分流器 U/L | FEEDER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0538 |  | 0118 | 1-31-10 |  | 1-76 | 成醫線 | U/L | 北54線KG54 F11 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG54_ADJ | 23KV北54線(KG54) LCO分流器 U/L | FEEDER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0539 |  | 0119 | 1-31-11 |  | 1-77 | 站前線 | U/L | 北55線KG55 F12 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG55_ADJ | 23KV北55線(KG55) LCO分流器 U/L | FEEDER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0540 |  | 0120 | 1-31-12 |  | 1-78 | 東雲線 | U/L | 北56線KG56 F13 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG56_ADJ | 23KV北56線(KG56) LCO分流器 U/L | FEEDER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0541 |  | 0121 | 1-31-13 |  | 1-79 | 永樂線 | U/L | 北57線KG57 F14 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG57_ADJ | 23KV北57線(KG57) LCO分流器 U/L | FEEDER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0542 |  | 0122 | 1-31-14 |  | 1-7A | 正覺線 | U/L | 北64線KG64 F15 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG64_ADJ | 23KV北64線(KG64) LCO分流器 U/L | FEEDER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0768 |  |  | 2-32-00 |  |  | 備用線 | U/L | 備用線 F19 79RY U/L |  |  | B1/D26_A1 | [16 empty] | 464 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0769 |  |  | 2-32-01 |  |  | 備用線 | U/L | 備用線 F20 79RY U/L |  |  | B1/D26_A1 | [16 empty] | 465 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0770 |  |  | 2-32-02 |  |  | #6SC | A/M | #6SC Q-CTL A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.260_A/M | 23KV #6SC 乏控器 A/M | SC | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | AUTO/MANUAL | MANUAL
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0771 |  |  | 2-32-03 |  |  | #5SC | A/M | #5SC Q-CTL A/M |  |  | B1/D26_A1 | [8 empty] | 小北DS.250_A/M | 23KV #5SC 乏控器 A/M | SC | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | AUTO/MANUAL | MANUAL
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0772 |  |  | 2-32-04 |  |  | 60Ry | A/N | 11,23kV SC 60A |  |  | B1/D26_A1 | [8 empty] | 小北DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0773 |  |  | 2-32-05 |  |  | Locate Empty |  |  |  |  | B1/D26_A1 | [16 empty] | 469 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0774 |  |  | 2-32-06 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B1/D26_A1 | [8 empty] | 小北DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0775 |  |  | 2-32-07 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B1/D26_A1 | [8 empty] | 小北DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0776 |  |  | 2-32-08 |  |  | 1530 | A/N | 1530 MDAR 故障(備用位置) |  |  | B1/D26_A1 | [16 empty] | 472 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0777 |  |  | 2-32-09 |  |  | 1540 | A/N | 1540 MDAR 故障(備用位置) |  |  | B1/D26_A1 | [16 empty] | 473 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0543 |  | 0123 | 1-31-15 |  | 1-7B | 東榮線 | U/L | 北65線KG65 F16 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG65_ADJ | 23KV北65線(KG65) LCO分流器 U/L | FEEDER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0544 |  | 0124 | 1-32-00 |  | 1-7C | 站后線 | U/L | 北66線KG66 F17 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG66_ADJ | 23KV北66線(KG66) LCO分流器 U/L | FEEDER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0545 |  | 0125 | 1-32-01 |  | 1-7D | 文和線 | U/L | 北67線KG67 F18 LCO 分流器 |  |  | B2/D26_D1 | [8 empty] | 小北DS.KG67_ADJ | 23KV北67線(KG67) LCO分流器 U/L | FEEDER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0546 |  | 0126 | 1-32-02 |  | 1-7E | 備用線 | U/L | 備用線KG68 F19 LCO 分流器 |  |  | B2/D26_D1 | [16 empty] | 477 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | ABS1 | 1511 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0832 | 833 | 0128 | 2-34-00 | 2-34-01 | 2-00 | 1511 | ON/OFF | 安南小北一路 1511 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1511_DS | 1511(安南小北一路) DS | LINE161 | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | ABS2 | 1512 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0834 | 835 | 0129 | 2-34-02 | 2-34-03 | 2-01 | 1512 | ON/OFF | 安南小北一路 1512 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1512_DS | 1512(安南小北一路) DS | LINE161 | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | ES2 | 1512E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0836 | 837 | 0130 | 2-34-04 | 2-34-05 | 2-02 | 1512E | ON/OFF | 安南小北一路 1512E ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1512E_ES | 1512E(安南小北一路) ES | LINE161 | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | ABS1 | 1521 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0842 | 843 | 0132 | 2-34-10 | 2-34-11 | 2-04 | 1521 | ON/OFF | 安南小北二路 1521 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1521_DS | 1521(安南小北二路) DS | LINE161 | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | ABS2 | 1522 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0844 | 845 | 0133 | 2-34-12 | 2-34-13 | 2-05 | 1522 | ON/OFF | 安南小北二路 1522 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1522_DS | 1522(安南小北二路) DS | LINE161 | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | ES2 | 1522E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0846 | 847 | 0134 | 2-34-14 | 2-34-15 | 2-06 | 1522E | ON/OFF | 安南小北二路 1522E ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1522E_ES | 1522E(安南小北二路) ES | LINE161 | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D26 | 小北DS | 161 | 161kV | 1500 | TIE(1500) |  | ABS1 | 1501 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Sect1C | B/1Bus | B/2Bus |  |  | 0896 | 897 | 0144 | 2-38-00 | 2-38-01 | 2-10 | 161KV | ON/OFF | 161KV TIE 1501 ABS |  | no rule | B2/D26_A1 | [8 empty] | 小北DS.1501_DS | 1501 DS | BUS | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | ABS1 | 1751 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0902 | 903 | 0146 | 2-38-06 | 2-38-07 | 2-12 | #1DTR | ON/OFF | #1DTR 1751 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | ABS1 | 1761 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0908 | 909 | 0148 | 2-38-12 | 2-38-13 | 2-14 | #2DTR | ON/OFF | #2DTR 1761 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | ABS1 | 1771 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 | 0150 | 2-39-02 | 2-39-03 | 2-16 | #3DTR | ON/OFF | #3DTR 1771 ABS |  |  | B2/D26_A1 | [8 empty] | 小北DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0822 |  | 0152 | 1-35-06 |  | 2-18 | F21 | ON/OFF | 北71線KG71 F21 51N U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG71_ADJ | 23KV北71線(KG71) LCO分流器 U/L | FEEDER | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0823 |  | 0153 | 1-35-07 |  | 2-19 | F22 | ON/OFF | 北72線KG72 F22 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG72_79UL | 23KV北72線(KG72) 79RY U/L | FEEDER | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0154 | 1-32-10 |  |  | #1DTR | ON/OFF | #1DTR 87 L.S. |  |  | B1/D26_A1 | [8 empty] | 小北DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0547 |  | 0155 | 1-32-03 |  | 1-7F | 備用線 | U/L | 備用線KG69 F20 LCO 分流器 |  |  | B1/D26_A1 | [8 empty] | 小北DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0550 |  | 0156 | [8 empty] | B1/D26_A1 | [16 empty] | 492 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0561 |  | 0157 | 1-33-01 |  |  | #2DTR | ON/OFF | #2DTR 87 L.S. |  |  | B1/D26_A1 | [8 empty] | 小北DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0573 |  | 0158 | [8 empty] | B1/D26_A1 | [16 empty] | 494 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  | 0159 | [8 empty] | B1/D26_A1 | [16 empty] | 495 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 | [10 empty] | B2/D26_D1 | [16 empty] | 496 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 | [10 empty] | B2/D26_D1 | [16 empty] | 497 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0160 | 2-32-10 |  | 2-20 | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B2/D26_D1 | [8 empty] | 小北DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0161 | 2-32-11 |  | 2-21 | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B2/D26_D1 | [8 empty] | 小北DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ON/OFF | OFF
D26 | 小北DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 1-34-04 |  |  | ACBA | A/N | ACBA |  |  | B3/D26_A1 | [8 empty] | 小北DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0806 |  |  | 1-34-06 |  |  | CHG2 | A/N | 通訊充電機故障 |  |  | B3/D26_A1 | [8 empty] | 小北DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0807 |  |  | 1-34-07 |  |  | 集油池 | A/N | 集油池警報 OWA |  |  | B3/D26_A1 | [8 empty] | 小北DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 1-34-10 |  |  | 冷氣機 | A/N | 冷氣機警報 |  |  | B3/D26_A1 | [8 empty] | 小北DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D26 | 小北DS | 0 | 161 | 161KV | 所內設施 |  | OSCF | 示波器故障 |  | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0811 |  |  | 1-34-11 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D26_A1 | [8 empty] | 小北DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  | 0162 | 2-32-12 |  | 2-22 | 350 | USE/LOCK | #3DTR 350 CB 81RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.350_81UL | (350)81RY USE/LOCK | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全系統 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0813 |  |  | 1-34-13 |  |  | 通訊室 | A/N | 通訊設備 光纖主故障(備用) |  |  | B3/D26_A1 | [16 empty] | 506 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0163 | 2-32-13 |  | 2-23 | 保全主機 | A/N | 無人化防盜(1)保金系統 |  |  | B2/D26_D1 | [8 empty] | 小北DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0164 | 2-32-14 |  | 2-24 | 310 | USE/LOCK | #1DTR 1A 310 CB 81RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.310_81UL | (310)81RY USE/LOCK | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | Door1 | 小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0816 |  |  | 1-35-00 |  |  | #3DTR | A/N | #3DTR 96D |  |  | B3/D26_A1 | [8 empty] | 小北DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  | 0165 | 2-32-15 |  | 2-25 | 320 | USE/LOCK | #1DTR 1B 320 CB 81RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.320_81UL | (320)81RY USE/LOCK | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0784 |  | 0166 | 2-33-00 |  | 2-26 | 小門 | A/N | 無人化門禁(1)小門 |  |  | B3/D26_A1 | [8 empty] | 小北DS.無人化門禁(1) | 無人化門禁(1)電動大門及小門 | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Auto | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0785 |  | 0167 | 2-33-01 |  | 2-27 | 330 | USE/LOCK | #2DTR 2A 330 CB 81RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.330_81UL | (330)81RY USE/LOCK | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Auto | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0168 | 2-33-02 |  | 2-28 | 340 | USE/LOCK | #2DTR 2B 340 CB 81RY U/L |  |  | B2/D26_D1 | [8 empty] | 小北DS.340_81UL | (340)81RY USE/LOCK | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 1-35-05 |  |  | F21 | ON/OFF | 北71線KG71 F21 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG71_79UL | 23KV北71線(KG71) 79RY U/L | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  | 0169 | 2-33-03 |  | 2-29 | Locate Empty |  | 開關場照明(A)未接 |  |  | B2/D26_D1 | [8 empty] | 小北DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  | 0170 | 2-33-04 |  | 2-2A | Locate Empty |  | 開關場照明(B)未接 |  |  | B2/D26_D1 | [8 empty] | 小北DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0824 | [10 empty] | B1/D26_A1 | [16 empty] | 517 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 1-35-09 |  |  | F23 | ON/OFF | 北73線KG73 F23 79RY U/L |  |  | B2/D26_A1 | [8 empty] | 小北DS.KG73_79UL | 23KV北73線(KG73) 79RY U/L | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 1-35-10 |  |  | F23 | ON/OFF | 北73線KG73 F23 51N U/L |  |  | B2/D26_A1 | [8 empty] | 小北DS.KG73_ADJ | 23KV北73線(KG73) LCO分流器 U/L | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 1-35-11 |  |  | F24 | ON/OFF | 北74線KG74 F24 79RY U/L |  |  | ELEM/D26_A1 | [8 empty] | 小北DS.KG74_79UL | 23KV北74線(KG74) 79RY U/L | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 1-35-12 |  |  | F24 | ON/OFF | 北74線KG74 F24 51N U/L |  |  | ELEM/D26_A1 | [8 empty] | 小北DS.KG74_ADJ | 23KV北74線(KG74) LCO分流器 U/L | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 1-35-13 |  |  | F25 | ON/OFF | 北75線KG75 F25 79RY U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG75_79UL | 23KV北75線(KG75) 79RY U/L | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Normal | 0 |  |  | USE/LOCK | USE
D26 | 小北DS | 0 |  | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 1-35-14 |  |  | F25 | ON/OFF | 北75線KG75 F25 51N U/L |  |  | B3/D26_A1 | [8 empty] | 小北DS.KG75_ADJ | 23KV北75線(KG75) LCO分流器 U/L | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | USE/LOCK | LOCK
D26 | 小北DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 1-35-15 |  |  | Locate Empty |  |  |  |  | B3/D26_A1 | [16 empty] | 524 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  | 0171 | 2-33-05 |  | 2-2B | OPA |  | OPA |  |  | B2/D26_D1 | [8 empty] | 小北DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0790 |  | 0172 | 2-33-06 |  | 2-2C | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/D26_A1 | [8 empty] | 小北DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Auto | 0 |  |  | ON/OFF | ON
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0791 |  | 0173 | 2-33-07 |  | 2-2D | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/D26_A1 | [8 empty] | 小北DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Auto | 0 |  |  | ON/OFF | ON
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0174 | 2-33-08 |  | 2-2E | Locate Empty |  |  |  |  | B2/D26_D1 | [8 empty] | 小北DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0175 | 2-33-09 |  | 2-2F | 電驛盤 | A/N | VUA#1 BUS三相平衡電驛監視 |  |  | B2/D26_D1 | [8 empty] | 小北DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0176 | 2-33-10 |  | 2-30 | 電驛盤 | A/N | VUA#2 BUS三相平衡電驛監視 |  |  | B2/D26_D1 | [8 empty] | 小北DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0795 |  | 0177 | 2-33-11 |  | 2-31 | 充電機 | A/N | 直流電源接地故障 DCE |  |  | B2/D26_D1 | [8 empty] | 小北DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0796 |  | 0178 | 2-33-12 |  | 2-32 | 直流電源箱 | A/N | 直流電源故障 DCA |  |  | B2/D26_D1 | [8 empty] | 小北DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0797 |  | 0179 | 2-33-13 |  | 2-33 | 直流電源箱 | A/N | CHG1 |  |  | B2/D26_D1 | [8 empty] | 小北DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0180 | 2-33-14 |  | 2-34 | 空壓機 | A/N | COMT |  |  | B2/D26_D1 | [8 empty] | 小北DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  | 0181 | 2-33-15 |  | 2-35 | GIS | A/N | 161KV CBA |  |  | B2/D26_D1 | [8 empty] | 小北DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0802 |  | 0184 | 1-34-02 |  | 2-38 | 11KV 22KV | A/N | 11KV 22KV CBA |  |  | B3/D26_A1 | [8 empty] | 小北DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0803 |  | 0185 | 1-34-03 |  | 2-39 | 11KV 22KV | A/N | 11KV 22KV CBF |  |  | B3/D26_A1 | [8 empty] | 小北DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP |  | Bb2EthA | B/1Bus |  |  |  | 0898 | 899 |  | 2-38-02 | 2-38-03 |  | 161KV | ON/OFF | 161KV TIE 15B1 EABS |  | aadz | B2/D26_A1 | [8 empty] | 小北DS.161KV_15B1E | #1BUS 15B1E | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP |  | Bb2EthA | B/2Bus |  |  |  | 0900 | 901 |  | 2-38-04 | 2-38-05 |  | 161KV | ON/OFF | 161KV TIE 15B2 EABS |  | aadz | B2/D26_A1 | [8 empty] | 小北DS.161KV_15B2E | #2BUS 15B2E | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | CLOSE/OPEN | OPEN
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0568 |  | 0187 | 1-33-08 |  |  | #3DTR | ON/OFF | #3DTR 87 L.S. |  |  | B1/D26_A1 | [8 empty] | 小北DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0819 |  | 0188 | 1-35-03 |  | 2-3E | #3DTR | A/N | #3DTR 96B1 |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0820 |  | 0189 | 1-35-04 |  | 2-3F | #3DTR | A/N | #3DTR 96B2 |  |  | B1/D26_A1 | [8 empty] | 小北DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 1APT | #1APT |  | D1 | #1ABUS_PTD(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbC | B/1ABus | T/1APT | [12 empty] | aabb | B3/D26_A1 | [8 empty] | 小北DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 543 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 1BPT | #1BPT |  | D1 | #1BBUS_PTD(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbC | B/1BBus | T/1BPT | [12 empty] | baab | B3/D26_A1 | [8 empty] | 小北DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 544 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 545 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 546 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | DS | (非取樣點) | [24 empty] | B3/D26_A1 | [16 empty] | 547 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.310_ES | 310_ES (非取樣點) | MTR | [5 empty] | 548 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.320_DS | 320_DS (非取樣點) | MTR | [5 empty] | 549 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.320_ES | 320_ES (非取樣點) | MTR | [5 empty] | 550 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 551 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 552 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 1SSTR | #1SSTR(1SSTR) |  | LBS | (非取樣點) |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | B/1ABus | T/1SSTR | [12 empty] | aaab | B3/D26_A1 | [8 empty] | 小北DS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 553 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 2APT | #2APT |  | D1 | #2ABUS_PTD(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbC | B/2ABus | T/2APT | [12 empty] | abhb | B3/D26_A1 | [8 empty] | 小北DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 554 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 2BPT | #2BPT |  | D1 | #2BBUS_PTD(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbC | B/2BBus | T/2BPT | [12 empty] | bbjb | B3/D26_A1 | [8 empty] | 小北DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 555 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 556 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 557 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.330_DS | 330_DS (非取樣點) | MTR | [5 empty] | 558 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.330_ES | 330_ES (非取樣點) | MTR | [5 empty] | 559 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.340_DS | 340_DS (非取樣點) | MTR | [5 empty] | 560 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.340_ES | 340_ES (非取樣點) | MTR | [5 empty] | 561 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 562 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 563 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 2SSTR | #2SSTR(2SSTR) |  | LBS | (非取樣點) |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | B/2BBus | T/2SSTR | [12 empty] | bbkb | B3/D26_A1 | [8 empty] | 小北DS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 564 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 3BE | #3BE |  | BE1 | #3 BE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2EthA | B/3Bus | [13 empty] | acab | B3/D26_A1 | [16 empty] | 565 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 3PT | #3PT |  | D1 | #3BUS_PTD(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbE | B/3Bus | T/3PT | [12 empty] | acab | B3/D26_A1 | [8 empty] | 小北DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 566 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 3PT | #3PT |  | E1 | #3BUS_PTE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 567 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 568 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 569 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | DS | 351 (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 570 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 571 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 572 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 573 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 574 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 575 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 576 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 577 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 578 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 579 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 580 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | DS | 271 (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 581 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | E1 | 281E (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 582 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | DS | 281 (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 583 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 100 | TIE(100) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.100_DS | 100_DS (非取樣點) | TIE | [5 empty] | 584 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 200 | TIE(200) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.200_DS | 200_DS (非取樣點) | TIE | [5 empty] | 585 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | D1 | 301 (非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 586 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | D2 | 302 (非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [16 empty] | 587 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 588 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D26_A1 | [8 empty] | 小北DS.302E | 302E(非取樣點) | OTHER | [5 empty] | 589 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG21_DS | KG21_DS (非取樣點) | FEEDER | [5 empty] | 590 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG21_ES | KG21_ES (非取樣點) | FEEDER | [5 empty] | 591 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG22_DS | KG22_DS (非取樣點) | FEEDER | [5 empty] | 592 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG22_ES | KG22_ES (非取樣點) | FEEDER | [5 empty] | 593 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG23_DS | KG23_DS (非取樣點) | FEEDER | [5 empty] | 594 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG23_ES | KG23_ES (非取樣點) | FEEDER | [5 empty] | 595 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | KG26 | 北23線(KG23) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG26_DS | KG26_DS (非取樣點) | FEEDER | [5 empty] | 596 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG26 | 北23線(KG23) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG26_ES | KG26_ES (非取樣點) | FEEDER | [5 empty] | 597 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG24_DS | KG24_DS (非取樣點) | FEEDER | [5 empty] | 598 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG24_ES | KG24_ES (非取樣點) | FEEDER | [5 empty] | 599 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG25_DS | KG25_DS (非取樣點) | FEEDER | [5 empty] | 600 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG25_ES | KG25_ES (非取樣點) | FEEDER | [5 empty] | 601 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG54_DS | KG54_DS (非取樣點) | FEEDER | [5 empty] | 602 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG54_ES | KG54_ES (非取樣點) | FEEDER | [5 empty] | 603 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG55_DS | KG55_DS (非取樣點) | FEEDER | [5 empty] | 604 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG55_ES | KG55_ES (非取樣點) | FEEDER | [5 empty] | 605 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG56_DS | KG56_DS (非取樣點) | FEEDER | [5 empty] | 606 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG56_ES | KG56_ES (非取樣點) | FEEDER | [5 empty] | 607 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG57_DS | KG57_DS (非取樣點) | FEEDER | [5 empty] | 608 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG57_ES | KG57_ES (非取樣點) | FEEDER | [5 empty] | 609 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG60_DS | KG60_DS (非取樣點) | FEEDER | [5 empty] | 610 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG60_ES | KG60_ES (非取樣點) | FEEDER | [5 empty] | 611 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG61_DS | KG61_DS (非取樣點) | FEEDER | [5 empty] | 612 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG61_ES | KG61_ES (非取樣點) | FEEDER | [5 empty] | 613 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG62_DS | KG62_DS (非取樣點) | FEEDER | [5 empty] | 614 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG62_ES | KG62_ES (非取樣點) | FEEDER | [5 empty] | 615 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG63_DS | KG63_DS (非取樣點) | FEEDER | [5 empty] | 616 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG63_ES | KG63_ES (非取樣點) | FEEDER | [5 empty] | 617 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG64_DS | KG64_DS (非取樣點) | FEEDER | [5 empty] | 618 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG64_ES | KG64_ES (非取樣點) | FEEDER | [5 empty] | 619 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | DS | (非取樣點) | f | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG65_DS | KG65_DS (非取樣點) | FEEDER | [5 empty] | 620 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG65_ES | KG65_ES (非取樣點) | FEEDER | [5 empty] | 621 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG66_DS | KG66_DS (非取樣點) | FEEDER | [5 empty] | 622 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG66_ES | KG66_ES (非取樣點) | FEEDER | [5 empty] | 623 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG67_DS | KG67_DS (非取樣點) | FEEDER | [5 empty] | 624 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG67_ES | KG67_ES (非取樣點) | FEEDER | [5 empty] | 625 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [16 empty] | 626 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG68 | 北68線(KG68) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [16 empty] | 627 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [16 empty] | 628 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG69 | 北69線(KG69) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [16 empty] | 629 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG71_DS | KG71_DS (非取樣點) | FEEDER | [5 empty] | 630 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG71_ES | KG71_ES (非取樣點) | FEEDER | [5 empty] | 631 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG72_DS | KG72_DS (非取樣點) | FEEDER | [5 empty] | 632 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG72_ES | KG72_ES (非取樣點) | FEEDER | [5 empty] | 633 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG73_DS | KG73_DS (非取樣點) | FEEDER | [5 empty] | 634 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG73_ES | KG73_ES (非取樣點) | FEEDER | [5 empty] | 635 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG74_DS | KG74_DS (非取樣點) | FEEDER | [5 empty] | 636 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG74_ES | KG74_ES (非取樣點) | FEEDER | [5 empty] | 637 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG75_DS | KG75_DS (非取樣點) | FEEDER | [5 empty] | 638 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG75_ES | KG75_ES (非取樣點) | FEEDER | [5 empty] | 639 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG76 | 北75線(KG75) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG76_DS | KG76_DS (非取樣點) | FEEDER | [5 empty] | 640 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG76 | 北75線(KG75) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG76_ES | KG76_ES (非取樣點) | FEEDER | [5 empty] | 641 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG77_DS | KG77_DS (非取樣點) | FEEDER | [5 empty] | 642 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG77_ES | KG77_ES (非取樣點) | FEEDER | [5 empty] | 643 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG78_DS | KG78_DS (非取樣點) | FEEDER | [5 empty] | 644 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D26_D1 | [8 empty] | 小北DS.KG78_ES | KG78_ES (非取樣點) | FEEDER | [5 empty] | 645 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 646 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 647 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 648 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 649 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1530 | 備用線路(1530) |  | LE0 | 1530LE (非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 650 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1530 | 備用線路(1530) |  | BE0 | 1530BE (非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 651 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1540 | 備用線路(1540) |  | LE0 | 1540LE (非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 652 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1540 | 備用線路(1540) |  | BE0 | 1540BE (非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D26_A1 | [8 empty] | 小北DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 653 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D26 | 小北DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D26_A1 | [12 empty] | 小北DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D26/161/1BUS/V; OPRD2: D26/161/2BUS/V
D26 | 小北DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D26_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D26/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D26 | 小北DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D26_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: D26/161/1510/MW; OPRD2: D26/161/1520/MW
D26 | 小北DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D26_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D26/0/CalcPoint/OPRN2_MW
D26 | 小北DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D26_A1 | [17 empty] | none
D26 | 小北DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D26_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D26/0/CalcPoint/OPRN1; OPRD2: D26/0/CalcPoint/OPRN2; OPRD3: D26/0/CalcPoint/PRFL_UL
D26 | 小北DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D26_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D26/11/310/I_R; OPRD2: D26/22/320/I_R
D26 | 小北DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D26_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D26/11/310/I_S; OPRD2: D26/22/320/I_S
D26 | 小北DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D26_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D26/11/310/I_T; OPRD2: D26/22/320/I_T
D26 | 小北DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D26_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D26/22/330/I_R; OPRD2: D26/22/340/I_R
D26 | 小北DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D26_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D26/22/330/I_S; OPRD2: D26/22/340/I_S
D26 | 小北DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D26_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D26/22/330/I_T; OPRD2: D26/22/340/I_T
D26 | 小北DS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D26_A1 | [12 empty] | 小北DS.1510_AMP | 安南小北一路 AMP | LINE161 | AMP_CAL | C08R0800 | amp_cal | OPRD1: D26/161/1510/MW; OPRD2: D26/161/1510/MVAR; OPRD3: NULL
D26 | 小北DS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D26_A1 | [12 empty] | 小北DS.1520_AMP | 安南小北二路 AMP | LINE161 | AMP_CAL | C08R0800 | amp_cal | OPRD1: D26/161/1520/MW; OPRD2: D26/161/1520/MVAR; OPRD3: NULL
D26 | 小北DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D26_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D26/11/1ABUS/V
D26 | 小北DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D26_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D26/22/1BBUS/V
D26 | 小北DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D26_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D26/22/2ABUS/V
D26 | 小北DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D26_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D26/22/2BBUS/V
D26 | 小北DS | 22 | 22kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D26_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D26/22/3BUS/V
D26 | 小北DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D26_A1 | [12 empty] | 小北DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D26//1DTR(A)/SupLocal; OPRD2: D26//1DTR(A)/Tap Chan
D26 | 小北DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D26_A1 | [12 empty] | 小北DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D26//1DTR(B)/SupLocal; OPRD2: D26//1DTR(B)/Tap Chan
D26 | 小北DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D26_A1 | [12 empty] | 小北DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D26//2DTR(A)/SupLocal; OPRD2: D26//2DTR(A)/Tap Chan
D26 | 小北DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D26_A1 | [12 empty] | 小北DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D26//2DTR(B)/SupLocal; OPRD2: D26//2DTR(B)/Tap Chan
D26 | 小北DS |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B1/D26_A1 | [12 empty] | 小北DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D26//3DTR/SupLocal; OPRD2: D26//3DTR/Tap Chan
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/11/KG21/I_R; OPRD3: D26/11/KG21/I_S; OPRD4: D26/11/KG21/I_T
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/11/KG22/I_R; OPRD3: D26/11/KG22/I_S; OPRD4: D26/11/KG22/I_T
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/11/KG23/I_R; OPRD3: D26/11/KG23/I_S; OPRD4: D26/11/KG23/I_T
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/11/KG24/I_R; OPRD3: D26/11/KG24/I_S; OPRD4: D26/11/KG24/I_T
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/11/KG25/I_R; OPRD3: D26/11/KG25/I_S; OPRD4: D26/11/KG25/I_T
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/11/KG26/I_R; OPRD3: D26/11/KG26/I_S; OPRD4: D26/11/KG26/I_T
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG54/I_R; OPRD3: D26/22/KG54/I_S; OPRD4: D26/22/KG54/I_T
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG55/I_R; OPRD3: D26/22/KG55/I_S; OPRD4: D26/22/KG55/I_T
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG56/I_R; OPRD3: D26/22/KG56/I_S; OPRD4: D26/22/KG56/I_T
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG57/I_R; OPRD3: D26/22/KG57/I_S; OPRD4: D26/22/KG57/I_T
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG60/I_R; OPRD3: D26/22/KG60/I_S; OPRD4: D26/22/KG60/I_T
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG61/I_R; OPRD3: D26/22/KG61/I_S; OPRD4: D26/22/KG61/I_T
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG62/I_R; OPRD3: D26/22/KG62/I_S; OPRD4: D26/22/KG62/I_T
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG63/I_R; OPRD3: D26/22/KG63/I_S; OPRD4: D26/22/KG63/I_T
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG64/I_R; OPRD3: D26/22/KG64/I_S; OPRD4: D26/22/KG64/I_T
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG65/I_R; OPRD3: D26/22/KG65/I_S; OPRD4: D26/22/KG65/I_T
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG66/I_R; OPRD3: D26/22/KG66/I_S; OPRD4: D26/22/KG66/I_T
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG67/I_R; OPRD3: D26/22/KG67/I_S; OPRD4: D26/22/KG67/I_T
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG71/I_R; OPRD3: D26/22/KG71/I_S; OPRD4: D26/22/KG71/I_T
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG72/I_R; OPRD3: D26/22/KG72/I_S; OPRD4: D26/22/KG72/I_T
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG73/I_R; OPRD3: D26/22/KG73/I_S; OPRD4: D26/22/KG73/I_T
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG74/I_R; OPRD3: D26/22/KG74/I_S; OPRD4: D26/22/KG74/I_T
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG75/I_R; OPRD3: D26/22/KG75/I_S; OPRD4: D26/22/KG75/I_T
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG76/I_R; OPRD3: D26/22/KG76/I_S; OPRD4: D26/22/KG76/I_T
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG77/I_R; OPRD3: D26/22/KG77/I_S; OPRD4: D26/22/KG77/I_T
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: D26/22/KG78/I_R; OPRD3: D26/22/KG78/I_S; OPRD4: D26/22/KG78/I_T
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/11/KG21/kVA; OPRD2: D26/11/KG21/KVAR
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/11/KG22/kVA; OPRD2: D26/11/KG22/KVAR
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/11/KG23/kVA; OPRD2: D26/11/KG23/KVAR
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/11/KG24/kVA; OPRD2: D26/11/KG24/KVAR
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/11/KG25/kVA; OPRD2: D26/11/KG25/KVAR
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/11/KG26/kVA; OPRD2: D26/11/KG26/KVAR
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG54/kVA; OPRD2: D26/22/KG54/KVAR
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG55/kVA; OPRD2: D26/22/KG55/KVAR
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG56/kVA; OPRD2: D26/22/KG56/KVAR
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG57/kVA; OPRD2: D26/22/KG57/KVAR
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG60/kVA; OPRD2: D26/22/KG60/KVAR
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG61/kVA; OPRD2: D26/22/KG61/KVAR
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG62/kVA; OPRD2: D26/22/KG62/KVAR
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG63/kVA; OPRD2: D26/22/KG63/KVAR
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG64/kVA; OPRD2: D26/22/KG64/KVAR
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG65/kVA; OPRD2: D26/22/KG65/KVAR
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG66/kVA; OPRD2: D26/22/KG66/KVAR
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG67/kVA; OPRD2: D26/22/KG67/KVAR
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG71/kVA; OPRD2: D26/22/KG71/KVAR
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG72/kVA; OPRD2: D26/22/KG72/KVAR
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG73/kVA; OPRD2: D26/22/KG73/KVAR
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG74/kVA; OPRD2: D26/22/KG74/KVAR
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG75/kVA; OPRD2: D26/22/KG75/KVAR
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG76/kVA; OPRD2: D26/22/KG76/KVAR
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG77/kVA; OPRD2: D26/22/KG77/KVAR
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D26_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D26/22/KG78/kVA; OPRD2: D26/22/KG78/KVAR
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D26/11/210/CB; OPRD2: 6.9; OPRD3: 0
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D26/11/220/CB; OPRD2: 6.9; OPRD3: 0
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D26/22/230/CB; OPRD2: 13.8; OPRD3: 0
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D26/22/240/CB; OPRD2: 13.8; OPRD3: 0
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D26/22/250/CB; OPRD2: 13.8; OPRD3: 0
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D26/22/260/CB; OPRD2: 13.8; OPRD3: 0
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D26/22/270/CB; OPRD2: 13.8; OPRD3: 0
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D26_A1 | [12 empty] | 小北DS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D26/22/280/CB; OPRD2: 13.8; OPRD3: 0
D26 | 小北DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D26_A1 | [12 empty] | 小北DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_13 |  | com_alarm_29 | OPRD1: D26//1DTR/96D; OPRD2: D26//1DTR/TRA; OPRD3: D26//1DTR/63Q; OPRD4: D26//1DTR/96B2; OPRD5: D26//1DTR/96B1; OPRD6: D26//1DTR/87A; OPRD7: D26//1DTR/96PA; OPRD8: D26//1DTR/51ZA; OPRD9: D26//2DTR/96PA; OPRD10: D26//2DTR/51ZA; OPRD11: D26//2DTR/TRA; OPRD12: D26//2DTR/87A; OPRD13: D26//2DTR/63Q; OPRD14: D26//2DTR/96B1; OPRD15: D26//2DTR/96B2; OPRD16: D26//2DTR/96D; OPRD17: D26//3DTR/96B1; OPRD18: D26//3DTR/96B2; OPRD19: D26//3DTR/63Q; OPRD20: D26//3DTR/96PA; OPRD21: D26//3DTR/51ZA; OPRD22: D26//3DTR/87A; OPRD23: D26//3DTR/96D; OPRD24: D26//3DTR/TRA; OPRD25: D26/11/310/GDA; OPRD26: D26/161/BUS/87A; OPRD27: D26/22/320/GDA; OPRD28: D26/22/330/GDA; OPRD29: D26/22/340/GDA
D26 | 小北DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D26_A1 | [12 empty] | 小北DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D26//1DTR/TRF; OPRD2: D26//2DTR/TRF; OPRD3: D26//3DTR/TRF
D26 | 小北DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/161/1750/CB
D26 | 小北DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/161/1760/CB
D26 | 小北DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/161/1770/CB
D26 | 小北DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/11/310/CB
D26 | 小北DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/22/330/CB
D26 | 小北DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/22/320/CB
D26 | 小北DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/22/340/CB
D26 | 小北DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/22/350/CB
D26 | 小北DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/0/RTU/RTU_R_L
D26 | 小北DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/0/StaDev/PMA
D26 | 小北DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/0/StaDev/STUV
D26 | 小北DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/0/StaDev/DCE
D26 | 小北DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D26_D1 | [17 empty] | lamp2CC | OPRD1: D26/0/StaDev/DCA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D26 | 小北DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 小北DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D26/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 小北DS.1510_AMP | 安南小北一路 AMP | LINE161 | D26/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 小北DS.1520_AMP | 安南小北二路 AMP | LINE161 | D26/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D26 | 小北DS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D26/11/210/MVAR |  | SC_CAL_11 |  |  | 5 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D26/11/220/MVAR |  | SC_CAL_11 |  |  | 6 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 230_SC | #3SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D26/22/230/MVAR |  | SC_CAL_23 |  |  | 7 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D26/22/240/MVAR |  | SC_CAL_23 |  |  | 8 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D26/22/250/MVAR |  | SC_CAL_23 |  |  | 9 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D26/22/260/MVAR |  | SC_CAL_23 |  |  | 10 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | TRTOT | 小北主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 小北DS.TRTOT_MW | 小北主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 11 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | TRTOT | 小北主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 小北DS.TRTOT_MVAR | 小北主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 12 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北21線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北21線KVA | 11KV北21線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北21線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北21線KW | 11KV北21線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北22線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北22線KVA | 11KV北22線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北22線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北22線KW | 11KV北22線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北23線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北23線KVA | 11KV北23線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北23線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北23線KW | 11KV北23線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北24線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北24線KVA | 11KV北24線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北24線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北24線KW | 11KV北24線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北25線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北25線KVA | 11KV北25線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北25線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北25線KW | 11KV北25線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北26線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北26線KVA | 11KV北26線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北26線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北26線KW | 11KV北26線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北54線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北54線KVA | 23KV北54線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北54線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北54線KW | 23KV北54線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北55線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北55線KVA | 23KV北55線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北55線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北55線KW | 23KV北55線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北56線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北56線KVA | 23KV北56線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北56線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北56線KW | 23KV北56線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北57線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北57線KVA | 23KV北57線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北57線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北57線KW | 23KV北57線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北64線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北64線KVA | 23KV北64線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北64線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北64線KW | 23KV北64線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北65線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北65線KVA | 23KV北65線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北65線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北65線KW | 23KV北65線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北66線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北66線KVA | 23KV北66線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北66線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北66線KW | 23KV北66線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北67線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北67線KVA | 23KV北67線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北67線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北67線KW | 23KV北67線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北60線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北60線KVA | 23KV北60線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北60線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北60線KW | 23KV北60線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北61線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北61線KVA | 23KV北61線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北61線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北61線KW | 23KV北61線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北62線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北62線KVA | 23KV北62線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北62線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北62線KW | 23KV北62線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北63線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北63線KVA | 23KV北63線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北63線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北63線KW | 23KV北63線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 53 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 56 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 59 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 68 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  |  |  |  | 北71線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北71線KVA | 23KV北71線KVA | FEEDER |  |  | KVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北71線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北71線KW | 23KV北71線KW | FEEDER |  |  | KW_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北72線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北72線KVA | 23KV北72線KVA | FEEDER |  |  | KVA_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北72線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北72線KW | 23KV北72線KW | FEEDER |  |  | KW_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北73線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北73線KVA | 23KV北73線KVA | FEEDER |  |  | KVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北73線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北73線KW | 23KV北73線KW | FEEDER |  |  | KW_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北74線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北74線KVA | 23KV北74線KVA | FEEDER |  |  | KVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北74線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北74線KW | 23KV北74線KW | FEEDER |  |  | KW_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北75線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北75線KVA | 23KV北75線KVA | FEEDER |  |  | KVA_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北75線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北75線KW | 23KV北75線KW | FEEDER |  |  | KW_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北76線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北76線KVA | 23KV北76線KVA | FEEDER |  |  | KVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北76線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北76線KW | 23KV北76線KW | FEEDER |  |  | KW_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北77線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北77線KVA | 23KV北77線KVA | FEEDER |  |  | KVA_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北77線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北77線KW | 23KV北77線KW | FEEDER |  |  | KW_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北78線KVA | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北78線KVA | 23KV北78線KVA | FEEDER |  |  | KVA_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  |  |  |  | 北78線KW | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.北78線KW | 23KV北78線KW | FEEDER |  |  | KW_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 86 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D26 | 小北DS | 22 | 22kV | 270_SC | #7SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.270_SC_MVAR | 23KV#7SC MVAR | SC | D26/22/270/MVAR |  | SC_CAL_23 |  |  | 88 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 280_SC | #8SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 小北DS.280_SC_MVAR | 23KV#8SC MVAR | SC | D26/22/280/MVAR |  | SC_CAL_23 |  |  | 89 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 90 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 91 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 320_CB | #1DTR(320_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.320_CB_4 | 320(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 92 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 93 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 94 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 95 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 96 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 97 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.230_CB_4 | 230(23KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 98 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.240_CB_4 | 240(23KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 99 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 101 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 102 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 103 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 104 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D26 | 小北DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 小北DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D26/0/CalcPoint/SUBA |  | STATION_FAULT_13 |  |  | 105 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 小北DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D26/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 106 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 107 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 108 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510_AMP | 安南小北一路 | [27 empty] | ADCS_S | [8 empty] | 小北DS.1510_AMP_A | 安南小北一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 161 | 161kV | 1520_AMP | 安南小北二路 | [27 empty] | ADCS_S | [8 empty] | 小北DS.1520_AMP_A | 安南小北二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 111 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 112 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D26//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D26//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D26//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D26//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.#1DTR_MVA_4 | #1DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.#1DTR_MVA_5 | #1DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 119 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 120 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.#2DTR_MVA_4 | #2DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 121 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.#2DTR_MVA_5 | #2DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 122 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 小北DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 123 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 124 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 125 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 126 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR | D26//3DTR/TR_PERM |  | DTR_PERM |  |  | 127 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 128 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 3DTR_MVA | #3DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 小北DS.#3DTR_MVA_4 | #3DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 129 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 小北DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 130 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 小北DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 131 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 小北DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 132 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 小北DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 133 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 小北DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 134 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 小北DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T5 |  |  | 135 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 小北DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B5 |  |  | 136 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D26 | 小北DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 小北DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 137 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 小北DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 138 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D26/0/RTU/ADCH1 |  |  |  | CDC | 139 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D26/0/RTU/ADCH2 |  |  |  | CDC | 140 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D26/0/RTU/ADCH3 |  |  |  | CDC | 141 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D26/0/RTU/ADCH4 |  |  |  | CDC | 142 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D26/0/RTU/ADCL1 |  |  |  | CDC | 143 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D26/0/RTU/ADCL2 |  |  |  | CDC | 144 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D26/0/RTU/ADCL3 |  |  |  | CDC | 145 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D26/0/RTU/ADCL4 |  |  |  | CDC | 146 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D26/161/1BUS/V |  |  |  | CDC | 147 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D26 | 小北DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D26/161/2BUS/V |  |  |  | CDC | 148 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D26 | 小北DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-C8 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D26/11/1ABUS/V |  |  |  | CDC | 149 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D26 | 小北DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-E1 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D26/22/1BBUS/V |  |  |  | CDC | 150 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-9B | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D26/22/2BBUS/V |  |  |  | CDC | 151 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-224_224(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1510_MW | 安南小北一路 MW | LINE161 | D26/161/1510/MW |  |  |  | CDC | 152 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-224_224(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1510_MVAR | 安南小北一路 MVAR | LINE161 | D26/161/1510/MVAR |  |  |  | CDC | 153 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-224_224(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1520_MW | 安南小北二路 MW | LINE161 | D26/161/1520/MW |  |  |  | CDC | 154 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-224_224(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1520_MVAR | 安南小北二路 MVAR | LINE161 | D26/161/1520/MVAR |  |  |  | CDC | 155 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D26 | 小北DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-93 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D26/0/StaDev/DCV_N |  |  |  | CDC | 156 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D26 | 小北DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-92 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D26/0/StaDev/DCV_P |  |  |  | CDC | 157 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北21線 | 北21線 |  | 北21線KVAR | [17 empty] | 1-AE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北21線KVAR | 11KV北21線 KVAR | FEEDER | D26/11/KG21/KVAR |  |  |  | CDC | 158 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北21線 | 北21線 |  | 北21線A1 | [17 empty] | 1-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北21線A1 | 11KV北21線 R相AMP | FEEDER | D26/11/KG21/I_R |  |  |  | CDC | 159 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北21線 | 北21線 |  | 北21線A2 | [17 empty] | 1-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北21線A2 | 11KV北21線 S相AMP | FEEDER | D26/11/KG21/I_S |  |  |  | CDC | 160 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北21線 | 北21線 |  | 北21線A3 | [17 empty] | 1-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北21線A3 | 11KV北21線 T相AMP | FEEDER | D26/11/KG21/I_T |  |  |  | CDC | 161 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北22線 | 北22線 |  | 北22線KVAR | [17 empty] | 1-B2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北22線KVAR | 11KV北22線 KVAR | FEEDER | D26/11/KG22/KVAR |  |  |  | CDC | 162 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北22線 | 北22線 |  | 北22線A1 | [17 empty] | 1-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北22線A1 | 11KV北22線 R相AMP | FEEDER | D26/11/KG22/I_R |  |  |  | CDC | 163 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北22線 | 北22線 |  | 北22線A2 | [17 empty] | 1-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北22線A2 | 11KV北22線 S相AMP | FEEDER | D26/11/KG22/I_S |  |  |  | CDC | 164 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北22線 | 北22線 |  | 北22線A3 | [17 empty] | 1-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北22線A3 | 11KV北22線 T相AMP | FEEDER | D26/11/KG22/I_T |  |  |  | CDC | 165 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北23線 | 北23線 |  | 北23線KVAR | [17 empty] | 1-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北23線KVAR | 11KV北23線 KVAR | FEEDER | D26/11/KG23/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北23線 | 北23線 |  | 北23線A1 | [17 empty] | 1-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北23線A1 | 11KV北23線 R相AMP | FEEDER | D26/11/KG23/I_R |  |  |  | CDC | 167 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北23線 | 北23線 |  | 北23線A2 | [17 empty] | 1-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北23線A2 | 11KV北23線 S相AMP | FEEDER | D26/11/KG23/I_S |  |  |  | CDC | 168 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北23線 | 北23線 |  | 北23線A3 | [17 empty] | 1-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北23線A3 | 11KV北23線 T相AMP | FEEDER | D26/11/KG23/I_T |  |  |  | CDC | 169 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北24線 | 北24線 |  | 北24線KVAR | [17 empty] | 1-BA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北24線KVAR | 11KV北24線 KVAR | FEEDER | D26/11/KG24/KVAR |  |  |  | CDC | 170 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北24線 | 北24線 |  | 北24線A1 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北24線A1 | 11KV北24線 R相AMP | FEEDER | D26/11/KG24/I_R |  |  |  | CDC | 171 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北24線 | 北24線 |  | 北24線A2 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北24線A2 | 11KV北24線 S相AMP | FEEDER | D26/11/KG24/I_S |  |  |  | CDC | 172 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北24線 | 北24線 |  | 北24線A3 | [17 empty] | 1-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北24線A3 | 11KV北24線 T相AMP | FEEDER | D26/11/KG24/I_T |  |  |  | CDC | 173 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北25線 | 北25線 |  | 北25線KVAR | [17 empty] | 1-BE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北25線KVAR | 11KV北25線 KVAR | FEEDER | D26/11/KG25/KVAR |  |  |  | CDC | 174 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北25線 | 北25線 |  | 北25線A1 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北25線A1 | 11KV北25線 R相AMP | FEEDER | D26/11/KG25/I_R |  |  |  | CDC | 175 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北25線 | 北25線 |  | 北25線A2 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北25線A2 | 11KV北25線 S相AMP | FEEDER | D26/11/KG25/I_S |  |  |  | CDC | 176 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北25線 | 北25線 |  | 北25線A3 | [17 empty] | 1-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北25線A3 | 11KV北25線 T相AMP | FEEDER | D26/11/KG25/I_T |  |  |  | CDC | 177 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北26線 | 北26線 |  | 北26線KVAR | [17 empty] | 1-C4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北26線KVAR | 11KV北26線 KVAR | FEEDER | D26/11/KG26/KVAR |  |  |  | CDC | 178 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北26線 | 北26線 |  | 北26線A1 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北26線A1 | 11KV北26線 R相AMP | FEEDER | D26/11/KG26/I_R |  |  |  | CDC | 179 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北26線 | 北26線 |  | 北26線A2 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北26線A2 | 11KV北26線 S相AMP | FEEDER | D26/11/KG26/I_S |  |  |  | CDC | 180 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北26線 | 北26線 |  | 北26線A3 | [17 empty] | 1-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北26線A3 | 11KV北26線 T相AMP | FEEDER | D26/11/KG26/I_T |  |  |  | CDC | 181 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北54線 | 北54線 |  | 北54線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北54線KVAR | 23KV北54線 KVAR | FEEDER | D26/22/KG54/KVAR |  |  |  | CDC | 182 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北54線 | 北54線 |  | 北54線A1 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北54線A1 | 23KV北54線 R相AMP | FEEDER | D26/22/KG54/I_R |  |  |  | CDC | 183 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北54線 | 北54線 |  | 北54線A2 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北54線A2 | 23KV北54線 S相AMP | FEEDER | D26/22/KG54/I_S |  |  |  | CDC | 184 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北54線 | 北54線 |  | 北54線A3 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北54線A3 | 23KV北54線 T相AMP | FEEDER | D26/22/KG54/I_T |  |  |  | CDC | 185 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北55線 | 北55線 |  | 北55線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北55線KVAR | 23KV北55線 KVAR | FEEDER | D26/22/KG55/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北55線 | 北55線 |  | 北55線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北55線A1 | 23KV北55線 R相AMP | FEEDER | D26/22/KG55/I_R |  |  |  | CDC | 187 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北55線 | 北55線 |  | 北55線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北55線A2 | 23KV北55線 S相AMP | FEEDER | D26/22/KG55/I_S |  |  |  | CDC | 188 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北55線 | 北55線 |  | 北55線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北55線A3 | 23KV北55線 T相AMP | FEEDER | D26/22/KG55/I_T |  |  |  | CDC | 189 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北56線 | 北56線 |  | 北56線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北56線KVAR | 23KV北56線 KVAR | FEEDER | D26/22/KG56/KVAR |  |  |  | CDC | 190 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北56線 | 北56線 |  | 北56線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北56線A1 | 23KV北56線 R相AMP | FEEDER | D26/22/KG56/I_R |  |  |  | CDC | 191 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北56線 | 北56線 |  | 北56線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北56線A2 | 23KV北56線 S相AMP | FEEDER | D26/22/KG56/I_S |  |  |  | CDC | 192 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北56線 | 北56線 |  | 北56線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北56線A3 | 23KV北56線 T相AMP | FEEDER | D26/22/KG56/I_T |  |  |  | CDC | 193 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北57線 | 北57線 |  | 北57線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北57線KVAR | 23KV北57線 KVAR | FEEDER | D26/22/KG57/KVAR |  |  |  | CDC | 194 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北57線 | 北57線 |  | 北57線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北57線A1 | 23KV北57線 R相AMP | FEEDER | D26/22/KG57/I_R |  |  |  | CDC | 195 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北57線 | 北57線 |  | 北57線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北57線A2 | 23KV北57線 S相AMP | FEEDER | D26/22/KG57/I_S |  |  |  | CDC | 196 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北57線 | 北57線 |  | 北57線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北57線A3 | 23KV北57線 T相AMP | FEEDER | D26/22/KG57/I_T |  |  |  | CDC | 197 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北64線 | 北64線 |  | 北64線KVAR | [17 empty] | 2-83 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北64線KVAR | 23KV北64線 KVAR | FEEDER | D26/22/KG64/KVAR |  |  |  | CDC | 198 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北64線 | 北64線 |  | 北64線A1 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北64線A1 | 23KV北64線 R相AMP | FEEDER | D26/22/KG64/I_R |  |  |  | CDC | 199 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北64線 | 北64線 |  | 北64線A2 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北64線A2 | 23KV北64線 S相AMP | FEEDER | D26/22/KG64/I_S |  |  |  | CDC | 200 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北64線 | 北64線 |  | 北64線A3 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北64線A3 | 23KV北64線 T相AMP | FEEDER | D26/22/KG64/I_T |  |  |  | CDC | 201 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北65線 | 北65線 |  | 北65線KVAR | [17 empty] | 2-87 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北65線KVAR | 23KV北65線 KVAR | FEEDER | D26/22/KG65/KVAR |  |  |  | CDC | 202 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北65線 | 北65線 |  | 北65線A1 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北65線A1 | 23KV北65線 R相AMP | FEEDER | D26/22/KG65/I_R |  |  |  | CDC | 203 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北65線 | 北65線 |  | 北65線A2 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北65線A2 | 23KV北65線 S相AMP | FEEDER | D26/22/KG65/I_S |  |  |  | CDC | 204 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北65線 | 北65線 |  | 北65線A3 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北65線A3 | 23KV北65線 T相AMP | FEEDER | D26/22/KG65/I_T |  |  |  | CDC | 205 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北66線 | 北66線 |  | 北66線KVAR | [17 empty] | 2-8B | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北66線KVAR | 23KV北66線 KVAR | FEEDER | D26/22/KG66/KVAR |  |  |  | CDC | 206 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北66線 | 北66線 |  | 北66線A1 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北66線A1 | 23KV北66線 R相AMP | FEEDER | D26/22/KG66/I_R |  |  |  | CDC | 207 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北66線 | 北66線 |  | 北66線A2 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北66線A2 | 23KV北66線 S相AMP | FEEDER | D26/22/KG66/I_S |  |  |  | CDC | 208 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北66線 | 北66線 |  | 北66線A3 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北66線A3 | 23KV北66線 T相AMP | FEEDER | D26/22/KG66/I_T |  |  |  | CDC | 209 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北67線 | 北67線 |  | 北67線KVAR | [17 empty] | 2-8F | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北67線KVAR | 23KV北67線 KVAR | FEEDER | D26/22/KG67/KVAR |  |  |  | CDC | 210 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北67線 | 北67線 |  | 北67線A1 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北67線A1 | 23KV北67線 R相AMP | FEEDER | D26/22/KG67/I_R |  |  |  | CDC | 211 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北67線 | 北67線 |  | 北67線A2 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北67線A2 | 23KV北67線 S相AMP | FEEDER | D26/22/KG67/I_S |  |  |  | CDC | 212 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北67線 | 北67線 |  | 北67線A3 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北67線A3 | 23KV北67線 T相AMP | FEEDER | D26/22/KG67/I_T |  |  |  | CDC | 213 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-F7 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D26/22/2ABUS/V |  |  |  | CDC | 214 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 北60線 | 北60線 |  | 北60線KVAR | [17 empty] | 1-D1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北60線KVAR | 23KV北60線 KVAR | FEEDER | D26/22/KG60/KVAR |  |  |  | CDC | 215 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北60線 | 北60線 |  | 北60線A1 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北60線A1 | 23KV北60線 R相AMP | FEEDER | D26/22/KG60/I_R |  |  |  | CDC | 216 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北60線 | 北60線 |  | 北60線A2 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北60線A2 | 23KV北60線 S相AMP | FEEDER | D26/22/KG60/I_S |  |  |  | CDC | 217 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北60線 | 北60線 |  | 北60線A3 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北60線A3 | 23KV北60線 T相AMP | FEEDER | D26/22/KG60/I_T |  |  |  | CDC | 218 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北61線 | 北61線 |  | 北61線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北61線KVAR | 23KV北61線 KVAR | FEEDER | D26/22/KG61/KVAR |  |  |  | CDC | 219 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北61線 | 北61線 |  | 北61線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北61線A1 | 23KV北61線 R相AMP | FEEDER | D26/22/KG61/I_R |  |  |  | CDC | 220 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北61線 | 北61線 |  | 北61線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北61線A2 | 23KV北61線 S相AMP | FEEDER | D26/22/KG61/I_S |  |  |  | CDC | 221 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北61線 | 北61線 |  | 北61線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北61線A3 | 23KV北61線 T相AMP | FEEDER | D26/22/KG61/I_T |  |  |  | CDC | 222 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北62線 | 北62線 |  | 北62線KVAR | [17 empty] | 1-D9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北62線KVAR | 23KV北62線 KVAR | FEEDER | D26/22/KG62/KVAR |  |  |  | CDC | 223 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北62線 | 北62線 |  | 北62線A1 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北62線A1 | 23KV北62線 R相AMP | FEEDER | D26/22/KG62/I_R |  |  |  | CDC | 224 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北62線 | 北62線 |  | 北62線A2 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北62線A2 | 23KV北62線 S相AMP | FEEDER | D26/22/KG62/I_S |  |  |  | CDC | 225 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北62線 | 北62線 |  | 北62線A3 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北62線A3 | 23KV北62線 T相AMP | FEEDER | D26/22/KG62/I_T |  |  |  | CDC | 226 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北63線 | 北63線 |  | 北63線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北63線KVAR | 23KV北63線 KVAR | FEEDER | D26/22/KG63/KVAR |  |  |  | CDC | 227 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北63線 | 北63線 |  | 北63線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北63線A1 | 23KV北63線 R相AMP | FEEDER | D26/22/KG63/I_R |  |  |  | CDC | 228 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北63線 | 北63線 |  | 北63線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北63線A2 | 23KV北63線 S相AMP | FEEDER | D26/22/KG63/I_S |  |  |  | CDC | 229 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北63線 | 北63線 |  | 北63線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北63線A3 | 23KV北63線 T相AMP | FEEDER | D26/22/KG63/I_T |  |  |  | CDC | 230 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D26/22/100/I_R |  |  |  | CDC | 231 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D26/22/100/I_S |  |  |  | CDC | 232 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D26/22/100/I_T |  |  |  | CDC | 233 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 1-F8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D26/22/200/I_R |  |  |  | CDC | 234 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 1-F9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D26/22/200/I_S |  |  |  | CDC | 235 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 1-FA | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D26/22/200/I_T |  |  |  | CDC | 236 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D26/11/310/KW |  |  |  | CDC | 237 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D26/11/310/KVAR |  |  |  | CDC | 238 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D26/11/310/I_R |  |  |  | CDC | 239 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D26/11/310/I_S |  |  |  | CDC | 240 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D26/11/310/I_T |  |  |  | CDC | 241 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-95 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR_OIL | #1DTR 油溫 | MTR | D26//1DTR/OilTemp |  |  |  | CDC | 242 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-96 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D26//1DTR(A)/CoilTemp |  |  |  | CDC | 243 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-98 |  | 1-61 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D26//1DTR(A)/TapPosMv |  |  |  | CDC | 244 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D26/22/320/KW |  |  |  | CDC | 245 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D26/22/320/KVAR |  |  |  | CDC | 246 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D26/22/320/I_R |  |  |  | CDC | 247 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D26/22/320/I_S |  |  |  | CDC | 248 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D26/22/320/I_T |  |  |  | CDC | 249 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-97 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D26//1DTR(B)/CoilTemp |  |  |  | CDC | 250 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-99 |  | 1-63 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D26//1DTR(B)/TapPosMv |  |  |  | CDC | 251 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-E2 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D26/22/330/KW |  |  |  | CDC | 252 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-E3 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D26/22/330/KVAR |  |  |  | CDC | 253 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-E4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D26/22/330/I_R |  |  |  | CDC | 254 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-E5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D26/22/330/I_S |  |  |  | CDC | 255 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-E6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D26/22/330/I_T |  |  |  | CDC | 256 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-9A | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR_OIL | #2DTR 油溫 | MTR | D26//2DTR/OilTemp |  |  |  | CDC | 257 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-9B | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D26//2DTR(A)/CoilTemp |  |  |  | CDC | 258 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-9D |  | 1-65 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D26//2DTR(A)/TapPosMv |  |  |  | CDC | 259 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 1-FB | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D26/22/340/KW |  |  |  | CDC | 260 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 1-FC | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D26/22/340/KVAR |  |  |  | CDC | 261 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 1-FD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D26/22/340/I_R |  |  |  | CDC | 262 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 1-FE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D26/22/340/I_S |  |  |  | CDC | 263 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 1-FF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D26/22/340/I_T |  |  |  | CDC | 264 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D26//2DTR(B)/CoilTemp |  |  |  | CDC | 265 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-9E |  | 1-67 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D26//2DTR(B)/TapPosMv |  |  |  | CDC | 266 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-9C | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D26/22/3BUS/V |  |  |  | CDC | 267 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D26 | 小北DS | 22 | 22kV | 北71線 | 北71線 |  | 北71線KVAR | [17 empty] | 2-A2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北71線KVAR | 23KV北71線 KVAR | FEEDER | D26/22/KG71/KVAR |  |  |  | CDC | 268 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北71線 | 北71線 |  | 北71線A1 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北71線A1 | 23KV北71線 R相AMP | FEEDER | D26/22/KG71/I_R |  |  |  | CDC | 269 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北71線 | 北71線 |  | 北71線A2 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北71線A2 | 23KV北71線 S相AMP | FEEDER | D26/22/KG71/I_S |  |  |  | CDC | 270 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北71線 | 北71線 |  | 北71線A3 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北71線A3 | 23KV北71線 T相AMP | FEEDER | D26/22/KG71/I_T |  |  |  | CDC | 271 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北71線 | 北71線 |  | 北71線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北71線A0 | 23KV北71線 N相AMP | FEEDER | D26/22/KG71/I_N |  |  |  | CDC | 272 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北72線 | 北72線 |  | 北72線KVAR | [17 empty] | 2-A7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北72線KVAR | 23KV北72線 KVAR | FEEDER | D26/22/KG72/KVAR |  |  |  | CDC | 273 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北72線 | 北72線 |  | 北72線A1 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北72線A1 | 23KV北72線 R相AMP | FEEDER | D26/22/KG72/I_R |  |  |  | CDC | 274 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北72線 | 北72線 |  | 北72線A2 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北72線A2 | 23KV北72線 S相AMP | FEEDER | D26/22/KG72/I_S |  |  |  | CDC | 275 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北72線 | 北72線 |  | 北72線A3 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北72線A3 | 23KV北72線 T相AMP | FEEDER | D26/22/KG72/I_T |  |  |  | CDC | 276 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北72線 | 北72線 |  | 北72線A0 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北72線A0 | 23KV北72線 N相AMP | FEEDER | D26/22/KG72/I_N |  |  |  | CDC | 277 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北73線 | 北73線 |  | 北73線KVAR | [17 empty] | 2-AC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北73線KVAR | 23KV北73線 KVAR | FEEDER | D26/22/KG73/KVAR |  |  |  | CDC | 278 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北73線 | 北73線 |  | 北73線A1 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北73線A1 | 23KV北73線 R相AMP | FEEDER | D26/22/KG73/I_R |  |  |  | CDC | 279 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北73線 | 北73線 |  | 北73線A2 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北73線A2 | 23KV北73線 S相AMP | FEEDER | D26/22/KG73/I_S |  |  |  | CDC | 280 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北73線 | 北73線 |  | 北73線A3 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北73線A3 | 23KV北73線 T相AMP | FEEDER | D26/22/KG73/I_T |  |  |  | CDC | 281 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北73線 | 北73線 |  | 北73線A0 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北73線A0 | 23KV北73線 N相AMP | FEEDER | D26/22/KG73/I_N |  |  |  | CDC | 282 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北74線 | 北74線 |  | 北74線KVAR | [17 empty] | 2-B1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北74線KVAR | 23KV北74線 KVAR | FEEDER | D26/22/KG74/KVAR |  |  |  | CDC | 283 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北74線 | 北74線 |  | 北74線A1 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北74線A1 | 23KV北74線 R相AMP | FEEDER | D26/22/KG74/I_R |  |  |  | CDC | 284 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北74線 | 北74線 |  | 北74線A2 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北74線A2 | 23KV北74線 S相AMP | FEEDER | D26/22/KG74/I_S |  |  |  | CDC | 285 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北74線 | 北74線 |  | 北74線A3 | [17 empty] | 2-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北74線A3 | 23KV北74線 T相AMP | FEEDER | D26/22/KG74/I_T |  |  |  | CDC | 286 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北74線 | 北74線 |  | 北74線A0 | [17 empty] | 2-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北74線A0 | 23KV北74線 N相AMP | FEEDER | D26/22/KG74/I_N |  |  |  | CDC | 287 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北75線 | 北75線 |  | 北75線KVAR | [17 empty] | 2-B6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北75線KVAR | 23KV北75線 KVAR | FEEDER | D26/22/KG75/KVAR |  |  |  | CDC | 288 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北75線 | 北75線 |  | 北75線A1 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北75線A1 | 23KV北75線 R相AMP | FEEDER | D26/22/KG75/I_R |  |  |  | CDC | 289 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北75線 | 北75線 |  | 北75線A2 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北75線A2 | 23KV北75線 S相AMP | FEEDER | D26/22/KG75/I_S |  |  |  | CDC | 290 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北75線 | 北75線 |  | 北75線A3 | [17 empty] | 2-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北75線A3 | 23KV北75線 T相AMP | FEEDER | D26/22/KG75/I_T |  |  |  | CDC | 291 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北75線 | 北75線 |  | 北75線A0 | [17 empty] | 2-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北75線A0 | 23KV北75線 N相AMP | FEEDER | D26/22/KG75/I_N |  |  |  | CDC | 292 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北76線 | 北76線 |  | 北76線KVAR | [17 empty] | 2-BB | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北76線KVAR | 23KV北76線 KVAR | FEEDER | D26/22/KG76/KVAR |  |  |  | CDC | 293 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北76線 | 北76線 |  | 北76線A1 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北76線A1 | 23KV北76線 R相AMP | FEEDER | D26/22/KG76/I_R |  |  |  | CDC | 294 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北76線 | 北76線 |  | 北76線A2 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北76線A2 | 23KV北76線 S相AMP | FEEDER | D26/22/KG76/I_S |  |  |  | CDC | 295 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北76線 | 北76線 |  | 北76線A3 | [17 empty] | 2-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北76線A3 | 23KV北76線 T相AMP | FEEDER | D26/22/KG76/I_T |  |  |  | CDC | 296 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北76線 | 北76線 |  | 北76線A0 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北76線A0 | 23KV北76線 N相AMP | FEEDER | D26/22/KG76/I_N |  |  |  | CDC | 297 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北77線 | 北77線 |  | 北77線KVAR | [17 empty] | 2-C2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北77線KVAR | 23KV北77線 KVAR | FEEDER | D26/22/KG77/KVAR |  |  |  | CDC | 298 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北77線 | 北77線 |  | 北77線A1 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北77線A1 | 23KV北77線 R相AMP | FEEDER | D26/22/KG77/I_R |  |  |  | CDC | 299 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北77線 | 北77線 |  | 北77線A2 | [17 empty] | 2-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北77線A2 | 23KV北77線 S相AMP | FEEDER | D26/22/KG77/I_S |  |  |  | CDC | 300 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北77線 | 北77線 |  | 北77線A3 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北77線A3 | 23KV北77線 T相AMP | FEEDER | D26/22/KG77/I_T |  |  |  | CDC | 301 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北77線 | 北77線 |  | 北77線A0 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北77線A0 | 23KV北77線 N相AMP | FEEDER | D26/22/KG77/I_N |  |  |  | CDC | 302 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北78線 | 北78線 |  | 北78線KVAR | [17 empty] | 2-C7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北78線KVAR | 23KV北78線 KVAR | FEEDER | D26/22/KG78/KVAR |  |  |  | CDC | 303 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北78線 | 北78線 |  | 北78線A1 | [17 empty] | 2-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北78線A1 | 23KV北78線 R相AMP | FEEDER | D26/22/KG78/I_R |  |  |  | CDC | 304 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北78線 | 北78線 |  | 北78線A2 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北78線A2 | 23KV北78線 S相AMP | FEEDER | D26/22/KG78/I_S |  |  |  | CDC | 305 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北78線 | 北78線 |  | 北78線A3 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北78線A3 | 23KV北78線 T相AMP | FEEDER | D26/22/KG78/I_T |  |  |  | CDC | 306 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北78線 | 北78線 |  | 北78線A0 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北78線A0 | 23KV北78線 N相AMP | FEEDER | D26/22/KG78/I_N |  |  |  | CDC | 307 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 2-CC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV_300_A1 | 23KV 300 R相AMP | TIE | D26/22/300/I_R |  |  |  | CDC | 308 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 2-CD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV_300_A2 | 23KV 300 S相AMP | TIE | D26/22/300/I_S |  |  |  | CDC | 309 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 2-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.23KV_300_A3 | 23KV 300 T相AMP | TIE | D26/22/300/I_T |  |  |  | CDC | 310 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 2-9D | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_MW | #3DTR二次側 MW | MTR | D26/22/350/KW |  |  |  | CDC | 311 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D26 | 小北DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 2-9E | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D26/22/350/KVAR |  |  |  | CDC | 312 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D26 | 小北DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 2-9F | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D26/22/350/I_R |  |  |  | CDC | 313 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 2-A0 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D26/22/350/I_S |  |  |  | CDC | 314 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 2-A1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D26/22/350/I_T |  |  |  | CDC | 315 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-9F | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_OIL | #3DTR 油溫 | MTR | D26//3DTR/OilTemp |  |  |  | CDC | 316 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-A0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_COIL | #3DTR 線溫 | MTR | D26//3DTR/CoilTemp |  |  |  | CDC | 317 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-A2 |  | 1-69 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 小北DS.#3DTR_TAP | #3DTR OLTC TAP | MTR | D26//3DTR/TapPosMv |  |  |  | CDC | 318 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D26 | 小北DS | 11 | 11kV | 北21線 | 北21線 |  | 北21線A0 | [17 empty] | 2-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北21線A0 | 11KV北21線 N相AMP | FEEDER | D26/11/KG21/I_N |  |  |  | CDC | 319 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北22線 | 北22線 |  | 北22線A0 | [17 empty] | 2-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北22線A0 | 11KV北22線 N相AMP | FEEDER | D26/11/KG22/I_N |  |  |  | CDC | 320 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北23線 | 北23線 |  | 北23線A0 | [17 empty] | 2-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北23線A0 | 11KV北23線 N相AMP | FEEDER | D26/11/KG23/I_N |  |  |  | CDC | 321 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北24線 | 北24線 |  | 北24線A0 | [17 empty] | 2-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北24線A0 | 11KV北24線 N相AMP | FEEDER | D26/11/KG24/I_N |  |  |  | CDC | 322 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北25線 | 北25線 |  | 北25線A0 | [17 empty] | 2-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北25線A0 | 11KV北25線 N相AMP | FEEDER | D26/11/KG25/I_N |  |  |  | CDC | 323 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 11 | 11kV | 北26線 | 北26線 |  | 北26線A0 | [17 empty] | 2-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北26線A0 | 11KV北26線 N相AMP | FEEDER | D26/11/KG26/I_N |  |  |  | CDC | 324 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北54線 | 北54線 |  | 北54線A0 | [17 empty] | 2-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北54線A0 | 23KV北54線 N相AMP | FEEDER | D26/22/KG54/I_N |  |  |  | CDC | 325 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北55線 | 北55線 |  | 北55線A0 | [17 empty] | 2-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北55線A0 | 23KV北55線 N相AMP | FEEDER | D26/22/KG55/I_N |  |  |  | CDC | 326 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北56線 | 北56線 |  | 北56線A0 | [17 empty] | 2-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北56線A0 | 23KV北56線 N相AMP | FEEDER | D26/22/KG56/I_N |  |  |  | CDC | 327 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北57線 | 北57線 |  | 北57線A0 | [17 empty] | 2-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北57線A0 | 23KV北57線 N相AMP | FEEDER | D26/22/KG57/I_N |  |  |  | CDC | 328 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北60線 | 北60線 |  | 北60線A0 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北60線A0 | 23KV北60線 N相AMP | FEEDER | D26/22/KG60/I_N |  |  |  | CDC | 329 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北61線 | 北61線 |  | 北61線A0 | [17 empty] | 2-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北61線A0 | 23KV北61線 N相AMP | FEEDER | D26/22/KG61/I_N |  |  |  | CDC | 330 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北62線 | 北62線 |  | 北62線A0 | [17 empty] | 2-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北62線A0 | 23KV北62線 N相AMP | FEEDER | D26/22/KG62/I_N |  |  |  | CDC | 331 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北63線 | 北63線 |  | 北63線A0 | [17 empty] | 2-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北63線A0 | 23KV北63線 N相AMP | FEEDER | D26/22/KG63/I_N |  |  |  | CDC | 332 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北64線 | 北64線 |  | 北64線A0 | [17 empty] | 2-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北64線A0 | 23KV北64線 N相AMP | FEEDER | D26/22/KG64/I_N |  |  |  | CDC | 333 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北65線 | 北65線 |  | 北65線A0 | [17 empty] | 2-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北65線A0 | 23KV北65線 N相AMP | FEEDER | D26/22/KG65/I_N |  |  |  | CDC | 334 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北66線 | 北66線 |  | 北66線A0 | [17 empty] | 2-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北66線A0 | 23KV北66線 N相AMP | FEEDER | D26/22/KG66/I_N |  |  |  | CDC | 335 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 22 | 22kV | 北67線 | 北67線 |  | 北67線A0 | [17 empty] | 2-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 小北DS.北67線A0 | 23KV北67線 N相AMP | FEEDER | D26/22/KG67/I_N |  |  |  | CDC | 336 | GENERICAIPoint | DS031_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1510_OF | 安南小北一路 |  | R | [17 empty] | 1-8C | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1510_OF_R | 安南小北一路 R相 油壓 | OTHER | D26/161/1510/OilPreR |  |  |  | CDC | 337 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1510_OF | 安南小北一路 |  | S | [17 empty] | 1-8D | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1510_OF_S | 安南小北一路 S相 油壓 | OTHER | D26/161/1510/OilPreS |  |  |  | CDC | 338 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1510_OF | 安南小北一路 |  | T | [17 empty] | 1-8E | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1510_OF_T | 安南小北一路 T相 油壓 | OTHER | D26/161/1510/OilPreT |  |  |  | CDC | 339 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1520_OF | 安南小北二路 |  | R | [17 empty] | 1-8F | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1520_OF_R | 安南小北二路 R相 油壓 | OTHER | D26/161/1520/OilPreR |  |  |  | CDC | 340 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1520_OF | 安南小北二路 |  | S | [17 empty] | 1-90 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1520_OF_S | 安南小北二路 S相 油壓 | OTHER | D26/161/1520/OilPreS |  |  |  | CDC | 341 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 0 |  | 1520_OF | 安南小北二路 |  | T | [17 empty] | 1-91 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 小北DS.1520_OF_T | 安南小北二路 T相 油壓 | OTHER | D26/161/1520/OilPreT |  |  |  | CDC | 342 | GENERICAIPoint | DS031_L1 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_S | [8 empty] | 小北DS.1510_GDA | 安南小北一路(1510) 接地RY | LINE161 | D26/161/1510/GDA |  |  |  | CDC | 343 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 小北DS.1510_CB | 1510(安南小北一路) CB | LINE161 | D26/161/1510/CB |  |  |  | CDC | 344 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | 79UL | [17 empty] | 1-30-03 |  | 1-41 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1510_79UL | 安南小北一路(1510) 79RY U/L | LINE161 | D26/161/1510/79UL |  |  |  | CDC | 345 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | DS1 | 1511 | [16 empty] | 2-34-00 | 2-34-01 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1511_DS | 1511(安南小北一路) DS | LINE161 | D26/161/1510/ABS1 |  |  |  | CDC | 346 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | DS2 | 1512 | [16 empty] | 2-34-02 | 2-34-03 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1512_DS | 1512(安南小北一路) DS | LINE161 | D26/161/1510/ABS2 |  |  |  | CDC | 347 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | E2 | 1512E | [16 empty] | 2-34-04 | 2-34-05 | 2-02 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1512E_ES | 1512E(安南小北一路) ES | LINE161 | D26/161/1510/ES2 |  |  |  | CDC | 348 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 小北DS.1520_GDA | 安南小北二路(1520) 接地RY | LINE161 | D26/161/1520/GDA |  |  |  | CDC | 349 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 小北DS.1520_CB | 1520(安南小北二路) CB | LINE161 | D26/161/1520/CB |  |  |  | CDC | 350 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | 79UL | [17 empty] | 1-30-05 |  | 1-43 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1520_79UL | 安南小北二路(1520) 79RY U/L | LINE161 | D26/161/1520/79UL |  |  |  | CDC | 351 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | DS1 | 1521 | [16 empty] | 2-34-10 | 2-34-11 | 2-04 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1521_DS | 1521(安南小北二路) DS | LINE161 | D26/161/1520/ABS1 |  |  |  | CDC | 352 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | DS2 | 1522 | [16 empty] | 2-34-12 | 2-34-13 | 2-05 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1522_DS | 1522(安南小北二路) DS | LINE161 | D26/161/1520/ABS2 |  |  |  | CDC | 353 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | E2 | 1522E | [16 empty] | 2-34-14 | 2-34-15 | 2-06 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1522E_ES | 1522E(安南小北二路) ES | LINE161 | D26/161/1520/ES2 |  |  |  | CDC | 354 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | PHA | [17 empty] | 1-14-04 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_PHA | 11KV北22線(KG22) 相間RY | FEEDER | D26/11/KG22/51A |  |  |  | CDC | 355 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) |  | GDA | [17 empty] | 1-14-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_GDA | 11KV北22線(KG22) 接地RY | FEEDER | D26/11/KG22/51NA |  |  |  | CDC | 356 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-21 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_79UL | 11KV北22線(KG22) 79RY U/L | FEEDER | D26/161/ComPoint/OSCF |  |  |  | CDC | 357 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG22 | 北22線(KG22) LCO分流器 |  | ADJ | [17 empty] | 1-31-01 |  | 1-6D | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_ADJ | 11KV北22線(KG22) LCO分流器 U/L | FEEDER | D26/11/KG22/ADJ |  |  |  | CDC | 358 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG22 | KG22(11KV北22線) |  | CB | [17 empty] | 1-14-03 |  | 1-14 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_CB | KG22(11KV北22線) CB | FEEDER | D26/11/KG22/CB |  |  |  | CDC | 359 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_PHA | 11KV北23線(KG23) 相間RY | FEEDER | D26/11/KG23/51A |  |  |  | CDC | 360 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_GDA | 11KV北23線(KG23) 接地RY | FEEDER | D26/11/KG23/51NA |  |  |  | CDC | 361 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-22 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_79UL | 11KV北23線(KG23) 79RY U/L | FEEDER | D26/0/StaDev/CommACF |  |  |  | CDC | 362 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG23 | 北23線(KG23) LCO分流器 |  | ADJ | [17 empty] | 1-31-02 |  | 1-6E | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_ADJ | 11KV北23線(KG23) LCO分流器 U/L | FEEDER | D26/11/KG23/ADJ |  |  |  | CDC | 363 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG23 | KG23(11KV北23線) |  | CB | [17 empty] | 1-14-06 |  | 1-15 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_CB | KG23(11KV北23線) CB | FEEDER | D26/11/KG23/CB |  |  |  | CDC | 364 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_PHA | 11KV北24線(KG24) 相間RY | FEEDER | D26/11/KG24/51A |  |  |  | CDC | 365 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_GDA | 11KV北24線(KG24) 接地RY | FEEDER | D26/11/KG24/51NA |  |  |  | CDC | 366 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) 79RY |  | 79UL | [17 empty] | 2-30-13 |  | 2-23 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_79UL | 11KV北24線(KG24) 79RY U/L | FEEDER |  |  |  |  | CDC | 367 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG24 | 北24線(KG24) LCO分流器 |  | ADJ | [17 empty] | 1-31-03 |  | 1-6F | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_ADJ | 11KV北24線(KG24) LCO分流器 U/L | FEEDER | D26/11/KG24/ADJ |  |  |  | CDC | 368 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG24 | KG24(11KV北24線) |  | CB | [17 empty] | 1-15-01 |  | 1-16 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_CB | KG24(11KV北24線) CB | FEEDER | D26/11/KG24/CB |  |  |  | CDC | 369 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_PHA | 11KV北26線(KG26) 相間RY | FEEDER | D26/11/KG26/51A |  |  |  | CDC | 370 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_GDA | 11KV北26線(KG26) 接地RY | FEEDER | D26/11/KG26/51NA |  |  |  | CDC | 371 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) 79RY |  | 79UL | [17 empty] | 2-30-15 |  | 2-25 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_79UL | 11KV北26線(KG26) 79RY U/L | FEEDER | D26/0/StaDev/R_Temp |  |  |  | CDC | 372 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG26 | 北26線(KG26) LCO分流器 |  | ADJ | [17 empty] | 1-31-05 |  | 1-71 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_ADJ | 11KV北26線(KG26) LCO分流器 U/L | FEEDER | D26/11/KG26/ADJ |  |  |  | CDC | 373 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG26 | KG26(11KV北26線) |  | CB | [17 empty] | 1-15-07 |  | 1-18 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_CB | KG26(11KV北26線) CB | FEEDER | D26/11/KG26/CB |  |  |  | CDC | 374 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | PHA | [17 empty] | 1-19-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_PHA | 23KV北54線(KG54) 相間RY | FEEDER | D26/22/KG54/51A |  |  |  | CDC | 375 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) |  | GDA | [17 empty] | 1-19-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_GDA | 23KV北54線(KG54) 接地RY | FEEDER | D26/22/KG54/51NA |  |  |  | CDC | 376 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-2E | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_79UL | 23KV北54線(KG54) 79RY U/L | FEEDER | D26/22/KG72/51_51NUL |  |  |  | CDC | 377 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG54 | 北54線(KG54) LCO分流器 |  | ADJ | [17 empty] | 1-31-10 |  | 1-76 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_ADJ | 23KV北54線(KG54) LCO分流器 U/L | FEEDER | D26/22/KG54/ADJ |  |  |  | CDC | 378 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG54 | KG54(23KV北54線) |  | CB | [17 empty] | 1-19-05 |  | 1-23 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_CB | KG54(23KV北54線) CB | FEEDER | D26/22/KG54/CB |  |  |  | CDC | 379 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | PHA | [17 empty] | 1-1A-01 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_PHA | 23KV北55線(KG55) 相間RY | FEEDER | D26/22/KG55/51A |  |  |  | CDC | 380 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) |  | GDA | [17 empty] | 1-1A-02 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_GDA | 23KV北55線(KG55) 接地RY | FEEDER | D26/22/KG55/51NA |  |  |  | CDC | 381 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 2-2F | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_79UL | 23KV北55線(KG55) 79RY U/L | FEEDER | D26/22/KG73/79UL |  |  |  | CDC | 382 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG55 | 北55線(KG55) LCO分流器 |  | ADJ | [17 empty] | 1-31-11 |  | 1-77 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_ADJ | 23KV北55線(KG55) LCO分流器 U/L | FEEDER | D26/22/KG55/ADJ |  |  |  | CDC | 383 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG55 | KG55(23KV北55線) |  | CB | [17 empty] | 1-1A-00 |  | 1-24 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_CB | KG55(23KV北55線) CB | FEEDER | D26/22/KG55/CB |  |  |  | CDC | 384 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | PHA | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_PHA | 23KV北56線(KG56) 相間RY | FEEDER | D26/22/KG56/51A |  |  |  | CDC | 385 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) |  | GDA | [17 empty] | 1-1A-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_GDA | 23KV北56線(KG56) 接地RY | FEEDER | D26/22/KG56/51NA |  |  |  | CDC | 386 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-30 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_79UL | 23KV北56線(KG56) 79RY U/L | FEEDER | D26/22/KG73/51_51NUL |  |  |  | CDC | 387 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG56 | 北56線(KG56) LCO分流器 |  | ADJ | [17 empty] | 1-31-12 |  | 1-78 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_ADJ | 23KV北56線(KG56) LCO分流器 U/L | FEEDER | D26/22/KG56/ADJ |  |  |  | CDC | 388 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG56 | KG56(23KV北56線) |  | CB | [17 empty] | 1-1A-03 |  | 1-25 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_CB | KG56(23KV北56線) CB | FEEDER | D26/22/KG56/CB |  |  |  | CDC | 389 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | PHA | [17 empty] | 1-1A-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_PHA | 23KV北57線(KG57) 相間RY | FEEDER | D26/22/KG57/51A |  |  |  | CDC | 390 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) |  | GDA | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_GDA | 23KV北57線(KG57) 接地RY | FEEDER | D26/22/KG57/51NA |  |  |  | CDC | 391 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) 79RY |  | 79UL | [17 empty] | 2-31-11 |  | 2-31 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_79UL | 23KV北57線(KG57) 79RY U/L | FEEDER | D26/22/KG74/79UL |  |  |  | CDC | 392 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG57 | 北57線(KG57) LCO分流器 |  | ADJ | [17 empty] | 1-31-13 |  | 1-79 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_ADJ | 23KV北57線(KG57) LCO分流器 U/L | FEEDER | D26/22/KG57/ADJ |  |  |  | CDC | 393 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG57 | KG57(23KV北57線) |  | CB | [17 empty] | 1-1A-06 |  | 1-26 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_CB | KG57(23KV北57線) CB | FEEDER | D26/22/KG57/CB |  |  |  | CDC | 394 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | PHA | [17 empty] | 1-1B-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_PHA | 23KV北64線(KG64) 相間RY | FEEDER | D26/22/KG64/51A |  |  |  | CDC | 395 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) |  | GDA | [17 empty] | 1-1B-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_GDA | 23KV北64線(KG64) 接地RY | FEEDER | D26/22/KG64/51NA |  |  |  | CDC | 396 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-32 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_79UL | 23KV北64線(KG64) 79RY U/L | FEEDER | D26/22/KG74/51_51NUL |  |  |  | CDC | 397 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG64 | 北64線(KG64) LCO分流器 |  | ADJ | [17 empty] | 1-31-14 |  | 1-7A | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_ADJ | 23KV北64線(KG64) LCO分流器 U/L | FEEDER | D26/22/KG64/ADJ |  |  |  | CDC | 398 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG64 | KG64(23KV北64線) |  | CB | [17 empty] | 1-1B-04 |  | 1-29 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_CB | KG64(23KV北64線) CB | FEEDER | D26/22/KG64/CB |  |  |  | CDC | 399 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | PHA | [17 empty] | 1-1C-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_PHA | 23KV北65線(KG65) 相間RY | FEEDER | D26/22/KG65/51A |  |  |  | CDC | 400 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) |  | GDA | [17 empty] | 1-1C-01 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_GDA | 23KV北65線(KG65) 接地RY | FEEDER | D26/22/KG65/51NA |  |  |  | CDC | 401 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) 79RY |  | 79UL | [17 empty] | 2-31-13 |  | 2-33 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_79UL | 23KV北65線(KG65) 79RY U/L | FEEDER | D26/22/KG75/79UL |  |  |  | CDC | 402 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG65 | 北65線(KG65) LCO分流器 |  | ADJ | [17 empty] | 1-31-15 |  | 1-7B | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_ADJ | 23KV北65線(KG65) LCO分流器 U/L | FEEDER | D26/22/KG65/ADJ |  |  |  | CDC | 403 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG65 | KG65(23KV北65線) |  | CB | [17 empty] | 1-1B-07 |  | 1-2A | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_CB | KG65(23KV北65線) CB | FEEDER | D26/22/KG65/CB |  |  |  | CDC | 404 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | PHA | [17 empty] | 1-1C-03 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_PHA | 23KV北66線(KG66) 相間RY | FEEDER | D26/22/KG66/51A |  |  |  | CDC | 405 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) |  | GDA | [17 empty] | 1-1C-04 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_GDA | 23KV北66線(KG66) 接地RY | FEEDER | D26/22/KG66/51NA |  |  |  | CDC | 406 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) 79RY |  | 79UL | [17 empty] | 2-31-14 |  | 2-34 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_79UL | 23KV北66線(KG66) 79RY U/L | FEEDER | D26/22/KG75/51_51NUL |  |  |  | CDC | 407 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG66 | 北66線(KG66) LCO分流器 |  | ADJ | [17 empty] | 1-32-00 |  | 1-7C | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_ADJ | 23KV北66線(KG66) LCO分流器 U/L | FEEDER | D26/22/KG66/ADJ |  |  |  | CDC | 408 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG66 | KG66(23KV北66線) |  | CB | [17 empty] | 1-1C-02 |  | 1-2B | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_CB | KG66(23KV北66線) CB | FEEDER | D26/22/KG66/CB |  |  |  | CDC | 409 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | PHA | [17 empty] | 1-1C-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_PHA | 23KV北67線(KG67) 相間RY | FEEDER | D26/22/KG67/51A |  |  |  | CDC | 410 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) |  | GDA | [17 empty] | 1-1C-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_GDA | 23KV北67線(KG67) 接地RY | FEEDER | D26/22/KG67/51NA |  |  |  | CDC | 411 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) 79RY |  | 79UL | [17 empty] | 2-31-15 |  | 2-35 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_79UL | 23KV北67線(KG67) 79RY U/L | FEEDER |  |  |  |  | CDC | 412 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG67 | 北67線(KG67) LCO分流器 |  | ADJ | [17 empty] | 1-32-01 |  | 1-7D | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_ADJ | 23KV北67線(KG67) LCO分流器 U/L | FEEDER | D26/22/KG67/ADJ |  |  |  | CDC | 413 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG67 | KG67(23KV北67線) |  | CB | [17 empty] | 1-1C-05 |  | 1-2C | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_CB | KG67(23KV北67線) CB | FEEDER | D26/22/KG67/CB |  |  |  | CDC | 414 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-05-05 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 小北DS.1750_CB | 1750(#1DTR) CB | MTR | D26/161/1750/CB |  |  |  | CDC | 415 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-06-03 |  | 1-10 | [5 empty] | ADCS_S | [8 empty] | 小北DS.310_CB | 310(#1DTR) CB | MTR | D26/11/310/CB |  |  |  | CDC | 416 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-07-07 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 小北DS.320_CB | 320(#1DTR) CB | MTR | D26/22/320/CB |  |  |  | CDC | 417 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-06-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.310_51A | #1DTR二次側(310) 51RY | MTR | D26/11/310/51A |  |  |  | CDC | 418 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.320_51A | #1DTR二次側(320) 51RY | MTR | D26/22/320/51A |  |  |  | CDC | 419 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-38-06 | 2-38-07 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1751_DS | 1751(#1DTR) DS | MTR | D26/161/1750/ABS1 |  |  |  | CDC | 420 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-06-07 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 小北DS.1760_CB | 1760(#2DTR) CB | MTR | D26/161/1760/CB |  |  |  | CDC | 421 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-07-05 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 小北DS.330_CB | 330(#2DTR) CB | MTR | D26/22/330/CB |  |  |  | CDC | 422 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-08-07 |  | 1-30 | [5 empty] | ADCS_S | [8 empty] | 小北DS.340_CB | 340(#2DTR) CB | MTR | D26/22/340/CB |  |  |  | CDC | 423 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-07-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.330_51A | #2DTR二次側(330) 51RY | MTR | D26/22/330/51A |  |  |  | CDC | 424 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-09-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.340_51A | #2DTR二次側(340) 51RY | MTR | D26/22/340/51A |  |  |  | CDC | 425 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-38-12 | 2-38-13 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1761_DS | 1761(#2DTR) DS | MTR | D26/161/1760/ABS1 |  |  |  | CDC | 426 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-16-02 |  | 1-12 | [5 empty] | ADCS_S | [8 empty] | 小北DS.210_CB | 210(11KV #1SC) CB | SC | D26/11/210/CB |  |  |  | CDC | 427 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-31-00 |  | 2-26 | [5 empty] | ADCS_S | [8 empty] | 小北DS.210_A/M | 11KV #1SC 乏控器 A/M | SC | D26//3DTR/96D |  |  |  | CDC | 428 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-16-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.210_SCA | 11KV #1SC 51,51N RY | SC | D26/11/210/SCA |  |  |  | CDC | 429 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-16-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D26/11/210/UVA |  |  |  | CDC | 430 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-16-05 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 小北DS.220_CB | 220(11KV #2SC) CB | SC | D26/11/220/CB |  |  |  | CDC | 431 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-31-01 |  | 2-27 | [5 empty] | ADCS_S | [8 empty] | 小北DS.220_A/M | 11KV #2SC 乏控器 A/M | SC | D26//3DTR/96P |  |  |  | CDC | 432 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-16-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.220_SCA | 11KV #2SC 51,51N RY | SC | D26/11/220/SCA |  |  |  | CDC | 433 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-16-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D26/11/220/UVA |  |  |  | CDC | 434 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-19-02 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 小北DS.230_CB | 230(23KV #3SC) CB | SC | D26/22/230/CB |  |  |  | CDC | 435 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-31-07 |  | 2-2D | [5 empty] | ADCS_S | [8 empty] | 小北DS.230_A/M | 23KV #3SC 乏控器 A/M | SC | D26/22/KG72/79UL |  |  |  | CDC | 436 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-19-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.230_SCA | 23KV #3SC 51,51N RY | SC | D26/22/230/SCA |  |  |  | CDC | 437 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-19-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | D26/22/230/UVA |  |  |  | CDC | 438 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-18-07 |  | 1-1F | [5 empty] | ADCS_S | [8 empty] | 小北DS.240_CB | 240(23KV #4SC) CB | SC | D26/22/240/CB |  |  |  | CDC | 439 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-31-06 |  | 2-2C | [5 empty] | ADCS_S | [8 empty] | 小北DS.240_A/M | 23KV #4SC 乏控器 A/M | SC | D26/22/KG71/51_51NUL |  |  |  | CDC | 440 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-19-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.240_SCA | 23KV #4SC 51,51N RY | SC | D26/22/240/SCA |  |  |  | CDC | 441 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-19-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.240_UVA | 23KV #4SC 27RY(欠壓) | SC | D26/22/240/UVA |  |  |  | CDC | 442 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-1E-01 |  | 1-2F | [5 empty] | ADCS_S | [8 empty] | 小北DS.250_CB | 250(23KV #5SC) CB | SC | D26/22/250/CB |  |  |  | CDC | 443 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-32-03 |  | 2-39 | [5 empty] | ADCS_S | [8 empty] | 小北DS.250_A/M | 23KV #5SC 乏控器 A/M | SC | D26//1DTR/96B1 |  |  |  | CDC | 444 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-1E-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.250_SCA | 23KV #5SC 51,51N RY | SC | D26/22/250/SCA |  |  |  | CDC | 445 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-1E-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D26/22/250/UVA |  |  |  | CDC | 446 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-1D-06 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 小北DS.260_CB | 260(23KV #6SC) CB | SC | D26/22/260/CB |  |  |  | CDC | 447 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-32-02 |  | 2-38 | [5 empty] | ADCS_S | [8 empty] | 小北DS.260_A/M | 23KV #6SC 乏控器 A/M | SC | D26//1DTR/63Q |  |  |  | CDC | 448 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-1D-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.260_SCA | 23KV #6SC 51,51N RY | SC | D26/22/260/SCA |  |  |  | CDC | 449 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-1E-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D26/22/260/UVA |  |  |  | CDC | 450 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D26/22/KG55/79UL |  |  |  | CDC | 451 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1500 | 1501(1500) |  | DS1 | 1501 | [16 empty] | 2-38-00 | 2-38-01 | 2-10 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1501_DS | 1501 DS | BUS | D26/161/1500/ABS1 |  |  |  | CDC | 452 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D26/22/KG56/79UL |  |  |  | CDC | 453 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-34-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D26/22/260/SC_A_M |  |  |  | CDC | 454 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-34-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D26/22/250/SC_A_M |  |  |  | CDC | 455 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-33-15 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D26/22/KG67/79UL |  |  |  | CDC | 456 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-34-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_CBF | 161KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 457 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-09-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D26/0/ComPoint/RCA |  |  |  | CDC | 458 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV |  |  |  | COMT | [17 empty] | 2-33-14 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | D26/22/KG66/79UL |  |  |  | CDC | 459 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | OSCA | [17 empty] | 1-09-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.OSC啟動 | 示波器啟動警報 | OTHER | D26/161/ComPoint/OSCA |  |  |  | CDC | 460 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D26/0/RTU/RTU_R_L |  |  |  | CDC | 461 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D26 | 小北DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 小北DS.TEST_CB | TEST CB | OTHER | D26/0/RTU/Test_CB |  |  |  | CDC | 462 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-32-10 | [7 empty] | ADCS_S | [8 empty] | 小北DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D26/11/KG21/79UL |  |  |  | CDC | 463 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | OPA | [17 empty] | 2-33-05 | [7 empty] | ADCS_S | [8 empty] | 小北DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D26/22/KG63/79UL |  |  |  | CDC | 464 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-33-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D26/22/240/SC_A_M |  |  |  | CDC | 465 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D26 | 小北DS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-33-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D26/22/230/SC_A_M |  |  |  | CDC | 466 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D26 | 小北DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-34-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.所內電源ACBA | 所內電源故障警報 | OTHER | D26/0/ComPoint/60A |  |  |  | CDC | 467 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | STUV | [17 empty] | 1-34-09 | [7 empty] | ADCS_S | [8 empty] | 小北DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 468 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-12 | [7 empty] | ADCS_S | [8 empty] | 小北DS.直流電源DCA | 直流電源故障警報 | OTHER | D26/22/KG64/79UL |  |  |  | CDC | 469 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-34-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D26/0/StaDev/Water2 |  |  |  | CDC | 470 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-34-12 | [7 empty] | ADCS_S | [8 empty] | 小北DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D26/22/350/81UL |  |  |  | CDC | 471 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-13 | [7 empty] | ADCS_S | [8 empty] | 小北DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D26/11/KG24/79UL |  |  |  | CDC | 472 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | Door1 | [17 empty] | 2-33-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.無人化門禁(1) | 無人化門禁(1)電動大門及小門 | OTHER | D26/11/210/SC_A_M |  |  |  | CDC | 473 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 小北DS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | D26/0/StaDev/Fire1 |  |  |  | CDC | 474 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D26 | 小北DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-32-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.水位警報(1) | 地下室水位警報(1) | OTHER | D26//2DTR/96P |  |  |  | CDC | 475 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-32-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.水位警報(2) | 地下室水位警報(2) | OTHER | D26//2DTR/63Q |  |  |  | CDC | 476 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1530 | 備用一(1530) |  | CB | [17 empty] | 1-01-02 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 小北DS.1530_CB | 1530(備用一) CB | LINE161 |  |  |  |  | CDC | 477 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1530 | 備用一(1530) |  | DS1 | 1531 | [16 empty] | 2-35-00 | 2-35-01 | 2-08 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1531_DS | 1531(備用一) DS | LINE161 |  |  |  |  | CDC | 478 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1530 | 備用一(1530) |  | DS2 | 1532 | [16 empty] | 2-35-02 | 2-35-03 | 2-09 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1532_DS | 1532(備用一) DS | LINE161 |  |  |  |  | CDC | 479 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1530 | 備用一(1530) |  | E2 | 1532E | [16 empty] | 2-35-04 | 2-35-05 | 2-0A | [5 empty] | ADCS_S | [8 empty] | 小北DS.1532E_ES | 1532E(備用一) ES | LINE161 |  |  |  |  | CDC | 480 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D26 | 小北DS | 161 | 161kV | 1540 | 備用二(1540) |  | CB | [17 empty] | 1-01-07 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 小北DS.1540_CB | 1540(備用二) CB | LINE161 |  |  |  |  | CDC | 481 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1540 | 備用二(1540) |  | DS1 | 1541 | [16 empty] | 2-35-08 | 2-35-09 | 2-0C | [5 empty] | ADCS_S | [8 empty] | 小北DS.1541_DS | 1541(備用二) DS | LINE161 |  |  |  |  | CDC | 482 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1540 | 備用二(1540) |  | DS2 | 1542 | [16 empty] | 2-35-10 | 2-35-11 | 2-0D | [5 empty] | ADCS_S | [8 empty] | 小北DS.1542_DS | 1542(備用二) DS | LINE161 |  |  |  |  | CDC | 483 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 161 | 161kV | 1540 | 備用二(1540) |  | E2 | 1542E | [16 empty] | 2-35-12 | 2-35-13 | 2-0E | [5 empty] | ADCS_S | [8 empty] | 小北DS.1542E_ES | 1542E(備用二) ES | LINE161 |  |  |  |  | CDC | 484 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-08-01 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 小北DS.1770_CB | 1770(#3DTR) CB | MTR | D26/161/1770/CB |  |  |  | CDC | 485 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 2-39-02 | 2-39-03 | 2-16 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1771_DS | 1771(#3DTR) DS | MTR | D26/161/1770/ABS1 |  |  |  | CDC | 486 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | PHA | [17 empty] | 1-14-01 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_PHA | 11KV北21線(KG21) 相間RY | FEEDER | D26/11/KG21/51A |  |  |  | CDC | 487 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) |  | GDA | [17 empty] | 1-14-02 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_GDA | 11KV北21線(KG21) 接地RY | FEEDER | D26/11/KG21/51NA |  |  |  | CDC | 488 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-20 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_79UL | 11KV北21線(KG21) 79RY U/L | FEEDER | D26/0/StaDev/AIRCON |  |  |  | CDC | 489 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG21 | 北21線(KG21) LCO分流器 |  | ADJ | [17 empty] | 1-31-00 |  | 1-6C | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_ADJ | 11KV北21線(KG21) LCO分流器 U/L | FEEDER | D26/11/KG21/ADJ |  |  |  | CDC | 490 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG21 | KG21(11KV北21線) |  | CB | [17 empty] | 1-14-00 |  | 1-13 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_CB | KG21(11KV北21線) CB | FEEDER | D26/11/KG21/CB |  |  |  | CDC | 491 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_PHA | 11KV北25線(KG25) 相間RY | FEEDER | D26/11/KG25/51A |  |  |  | CDC | 492 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_GDA | 11KV北25線(KG25) 接地RY | FEEDER | D26/11/KG25/51NA |  |  |  | CDC | 493 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-24 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_79UL | 11KV北25線(KG25) 79RY U/L | FEEDER |  |  |  |  | CDC | 494 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 11 | 11kV | KG25 | 北25線(KG25) LCO分流器 |  | ADJ | [17 empty] | 1-31-04 |  | 1-70 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_ADJ | 11KV北25線(KG25) LCO分流器 U/L | FEEDER | D26/11/KG25/ADJ |  |  |  | CDC | 495 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 11 | 11kV | KG25 | KG25(11KV北25線) |  | CB | [17 empty] | 1-15-04 |  | 1-17 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_CB | KG25(11KV北25線) CB | FEEDER | D26/11/KG25/CB |  |  |  | CDC | 496 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | PHA | [17 empty] | 1-17-04 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_PHA | 23KV北60線(KG60) 相間RY | FEEDER | D26/22/KG60/51A |  |  |  | CDC | 497 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_GDA | 23KV北60線(KG60) 接地RY | FEEDER | D26/22/KG60/51NA |  |  |  | CDC | 498 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-28 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_79UL | 23KV北60線(KG60) 79RY U/L | FEEDER | D26//3DTR/63Q |  |  |  | CDC | 499 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG60 | 北60線(KG60) LCO分流器 |  | ADJ | [17 empty] | 1-31-06 |  | 1-72 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_ADJ | 23KV北60線(KG60) LCO分流器 U/L | FEEDER | D26/22/KG60/ADJ |  |  |  | CDC | 500 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG60 | KG60(23KV北60線) |  | CB | [17 empty] | 1-17-03 |  | 1-1B | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_CB | KG60(23KV北60線) CB | FEEDER | D26/22/KG60/CB |  |  |  | CDC | 501 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_PHA | 23KV北61線(KG61) 相間RY | FEEDER | D26/22/KG61/51A |  |  |  | CDC | 502 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_GDA | 23KV北61線(KG61) 接地RY | FEEDER | D26/22/KG61/51NA |  |  |  | CDC | 503 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) 79RY |  | 79UL | [17 empty] | 2-31-03 |  | 2-29 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_79UL | 23KV北61線(KG61) 79RY U/L | FEEDER | D26//3DTR/96B1 |  |  |  | CDC | 504 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG61 | 北61線(KG61) LCO分流器 |  | ADJ | [17 empty] | 1-31-07 |  | 1-73 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_ADJ | 23KV北61線(KG61) LCO分流器 U/L | FEEDER | D26/22/KG61/ADJ |  |  |  | CDC | 505 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG61 | KG61(23KV北61線) |  | CB | [17 empty] | 1-17-06 |  | 1-1C | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_CB | KG61(23KV北61線) CB | FEEDER | D26/22/KG61/CB |  |  |  | CDC | 506 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_PHA | 23KV北62線(KG62) 相間RY | FEEDER | D26/22/KG62/51A |  |  |  | CDC | 507 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_GDA | 23KV北62線(KG62) 接地RY | FEEDER | D26/22/KG62/51NA |  |  |  | CDC | 508 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-2A | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_79UL | 23KV北62線(KG62) 79RY U/L | FEEDER | D26//3DTR/96B2 |  |  |  | CDC | 509 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG62 | 北62線(KG62) LCO分流器 |  | ADJ | [17 empty] | 1-31-08 |  | 1-74 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_ADJ | 23KV北62線(KG62) LCO分流器 U/L | FEEDER | D26/22/KG62/ADJ |  |  |  | CDC | 510 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG62 | KG62(23KV北62線) |  | CB | [17 empty] | 1-18-01 |  | 1-1D | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_CB | KG62(23KV北62線) CB | FEEDER | D26/22/KG62/CB |  |  |  | CDC | 511 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_PHA | 23KV北63線(KG63) 相間RY | FEEDER | D26/22/KG63/51A |  |  |  | CDC | 512 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_GDA | 23KV北63線(KG63) 接地RY | FEEDER | D26/22/KG63/51NA |  |  |  | CDC | 513 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) 79RY |  | 79UL | [17 empty] | 2-31-05 |  | 2-2B | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_79UL | 23KV北63線(KG63) 79RY U/L | FEEDER | D26/22/KG71/79UL |  |  |  | CDC | 514 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG63 | 北63線(KG63) LCO分流器 |  | ADJ | [17 empty] | 1-31-09 |  | 1-75 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_ADJ | 23KV北63線(KG63) LCO分流器 U/L | FEEDER | D26/22/KG63/ADJ |  |  |  | CDC | 515 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG63 | KG63(23KV北63線) |  | CB | [17 empty] | 1-18-04 |  | 1-1E | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_CB | KG63(23KV北63線) CB | FEEDER | D26/22/KG63/CB |  |  |  | CDC | 516 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-33-13 | [7 empty] | ADCS_S | [8 empty] | 小北DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D26/22/KG65/79UL |  |  |  | CDC | 517 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-34-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D26/0/StaDev/Water1 |  |  |  | CDC | 518 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-06-01 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#1DTR_51A | #1DTR 51RY | MTR | D26/161/1750/51A |  |  |  | CDC | 519 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-06-02 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#1DTR_51NA | #1DTR 51N RY | MTR | D26/161/1750/51NA |  |  |  | CDC | 520 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-06-00 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D26//1DTR/51ZA |  |  |  | CDC | 521 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-05-06 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#1DTR_87A | #1DTR 87RY | MTR | D26//1DTR/87A |  |  |  | CDC | 522 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-05-07 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D26//1DTR/96PA |  |  |  | CDC | 523 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 2-30-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_96D | #1DTR 96D RY | MTR | D26/161/ComPoint/CBF |  |  |  | CDC | 524 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 2-30-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_96P | #1DTR 96P RY | MTR | D26/0/ComPoint/LOA |  |  |  | CDC | 525 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 2-30-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D26/0/ComPoint/CBA |  |  |  | CDC | 526 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 2-30-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D26/0/ComPoint/CBF |  |  |  | CDC | 527 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 2-30-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D26/0/StaDev/ACBA |  |  |  | CDC | 528 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_TRA | #1DTR 重故障 | MTR | D26//1DTR/TRA |  |  |  | CDC | 529 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D26//1DTR/TRF |  |  |  | CDC | 530 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D26//1DTR(A)/SupLocal |  |  |  | CDC | 531 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-32-12 |  | 1-60 | [5 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D26//1DTR(A)/Tap Chan |  |  |  | CDC | 532 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D26//1DTR(B)/SupLocal |  |  |  | CDC | 533 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-33-00 |  | 1-62 | [5 empty] | ADCS_S | [8 empty] | 小北DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D26//1DTR(B)/Tap Chan |  |  |  | CDC | 534 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#2DTR_51A | #2DTR 51RY | MTR | D26/161/1760/51A |  |  |  | CDC | 535 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#2DTR_51NA | #2DTR 51N RY | MTR | D26/161/1760/51NA |  |  |  | CDC | 536 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-07-02 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D26//2DTR/51ZA |  |  |  | CDC | 537 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-07-00 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#2DTR_87A | #2DTR 87RY | MTR | D26//2DTR/87A |  |  |  | CDC | 538 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-07-01 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D26//2DTR/96PA |  |  |  | CDC | 539 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-30-05 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_96D | #2DTR 96D RY | MTR |  |  |  |  | CDC | 540 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-30-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_96P | #2DTR 96P RY | MTR | D26/0/StaDev/CHG2 |  |  |  | CDC | 541 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-30-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D26/0/StaDev/OilLeak1 |  |  |  | CDC | 542 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-30-08 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D26/0/StaDev/PMA |  |  |  | CDC | 543 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-30-09 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D26/0/StaDev/STUV |  |  |  | CDC | 544 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_TRA | #2DTR 重故障 | MTR | D26//2DTR/TRA |  |  |  | CDC | 545 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D26//2DTR/TRF |  |  |  | CDC | 546 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D26//2DTR(A)/SupLocal |  |  |  | CDC | 547 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-33-03 |  | 1-64 | [5 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D26//2DTR(A)/Tap Chan |  |  |  | CDC | 548 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D26//2DTR(B)/SupLocal |  |  |  | CDC | 549 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-33-07 |  | 1-66 | [5 empty] | ADCS_S | [8 empty] | 小北DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D26//2DTR(B)/Tap Chan |  |  |  | CDC | 550 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D26 | 小北DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-17-00 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 小北DS.100_CB | 100(TIE) CB | TIE | D26/22/100/CB |  |  |  | CDC | 551 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-17-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.100_51A | 11KV TIE(100) 51RY | TIE | D26/22/100/51A |  |  |  | CDC | 552 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-17-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D26/22/100/51NA |  |  |  | CDC | 553 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-1B-01 |  | 1-27 | [5 empty] | ADCS_S | [8 empty] | 小北DS.200_CB | 200(TIE) CB | TIE | D26/22/200/CB |  |  |  | CDC | 554 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-1B-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.200_51A | 23KV TIE(200) 51RY | TIE | D26/22/200/51A |  |  |  | CDC | 555 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-1B-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D26/22/200/51NA |  |  |  | CDC | 556 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-34-15 | [7 empty] | ADCS_S | [8 empty] | 小北DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D26/22/320/81UL |  |  |  | CDC | 557 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | PHA | [17 empty] | 1-1F-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_PHA | 23KV北71線(KG71) 相間RY | FEEDER | D26/22/KG71/51A |  |  |  | CDC | 558 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) |  | GDA | [17 empty] | 1-1F-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_GDA | 23KV北71線(KG71) 接地RY | FEEDER | D26/22/KG71/51NA |  |  |  | CDC | 559 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) 79RY |  | 79UL | [17 empty] | 1-35-05 |  | 1-48 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_79UL | 23KV北71線(KG71) 79RY U/L | FEEDER | D26/0/ComPoint/OPA |  |  |  | CDC | 560 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG71 | 北71線(KG71) LCO分流器 |  | ADJ | [17 empty] | 1-35-06 |  | 1-49 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_ADJ | 23KV北71線(KG71) LCO分流器 U/L | FEEDER | D26/0/StaDev/ACB1 |  |  |  | CDC | 561 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG71 | KG71(23KV北71線) |  | CB | [17 empty] | 1-1F-04 |  | 1-33 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_CB | KG71(23KV北71線) CB | FEEDER | D26/22/KG71/CB |  |  |  | CDC | 562 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | PHA | [17 empty] | 2-00-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_PHA | 23KV北72線(KG72) 相間RY | FEEDER | D26/22/KG72/51A |  |  |  | CDC | 563 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) |  | GDA | [17 empty] | 2-00-01 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_GDA | 23KV北72線(KG72) 接地RY | FEEDER | D26/22/KG72/51NA |  |  |  | CDC | 564 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) 79RY |  | 79UL | [17 empty] | 1-35-07 |  | 1-4A | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_79UL | 23KV北72線(KG72) 79RY U/L | FEEDER | D26/0/StaDev/ACB2 |  |  |  | CDC | 565 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG72 | 北72線(KG72) LCO分流器 |  | ADJ | [17 empty] | 1-35-08 |  | 1-4B | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_ADJ | 23KV北72線(KG72) LCO分流器 U/L | FEEDER |  |  |  |  | CDC | 566 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG72 | KG72(23KV北72線) |  | CB | [17 empty] | 1-1F-07 |  | 1-34 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_CB | KG72(23KV北72線) CB | FEEDER | D26/22/KG72/CB |  |  |  | CDC | 567 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | PHA | [17 empty] | 2-00-03 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_PHA | 23KV北73線(KG73) 相間RY | FEEDER | D26/22/KG73/51A |  |  |  | CDC | 568 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) |  | GDA | [17 empty] | 2-00-04 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_GDA | 23KV北73線(KG73) 接地RY | FEEDER | D26/22/KG73/51NA |  |  |  | CDC | 569 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) 79RY |  | 79UL | [17 empty] | 1-35-09 |  | 1-4C | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_79UL | 23KV北73線(KG73) 79RY U/L | FEEDER | D26/161/1BUS/BUS_VUA |  |  |  | CDC | 570 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG73 | 北73線(KG73) LCO分流器 |  | ADJ | [17 empty] | 1-35-10 |  | 1-4D | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_ADJ | 23KV北73線(KG73) LCO分流器 U/L | FEEDER | D26/161/2BUS/BUS_VUA |  |  |  | CDC | 571 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG73 | KG73(23KV北73線) |  | CB | [17 empty] | 2-00-02 |  | 1-35 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_CB | KG73(23KV北73線) CB | FEEDER | D26/22/KG73/CB |  |  |  | CDC | 572 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | PHA | [17 empty] | 2-00-06 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_PHA | 23KV北74線(KG74) 相間RY | FEEDER | D26/22/KG74/51A |  |  |  | CDC | 573 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) |  | GDA | [17 empty] | 2-00-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_GDA | 23KV北74線(KG74) 接地RY | FEEDER | D26/22/KG74/51NA |  |  |  | CDC | 574 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) 79RY |  | 79UL | [17 empty] | 1-35-11 |  | 1-4E | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_79UL | 23KV北74線(KG74) 79RY U/L | FEEDER | D26/0/StaDev/DCE |  |  |  | CDC | 575 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG74 | 北74線(KG74) LCO分流器 |  | ADJ | [17 empty] | 1-35-12 |  | 1-4F | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_ADJ | 23KV北74線(KG74) LCO分流器 U/L | FEEDER | D26/0/StaDev/DCA |  |  |  | CDC | 576 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG74 | KG74(23KV北74線) |  | CB | [17 empty] | 2-00-05 |  | 1-36 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_CB | KG74(23KV北74線) CB | FEEDER | D26/22/KG74/CB |  |  |  | CDC | 577 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | PHA | [17 empty] | 2-01-01 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_PHA | 23KV北75線(KG75) 相間RY | FEEDER | D26/22/KG75/51A |  |  |  | CDC | 578 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) |  | GDA | [17 empty] | 2-01-02 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_GDA | 23KV北75線(KG75) 接地RY | FEEDER | D26/22/KG75/51NA |  |  |  | CDC | 579 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) 79RY |  | 79UL | [17 empty] | 1-35-13 |  | 1-50 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_79UL | 23KV北75線(KG75) 79RY U/L | FEEDER | D26/0/StaDev/CHG1 |  |  |  | CDC | 580 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG75 | 北75線(KG75) LCO分流器 |  | ADJ | [17 empty] | 1-35-14 |  | 1-51 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_ADJ | 23KV北75線(KG75) LCO分流器 U/L | FEEDER | D26/0/ComPoint/COMT |  |  |  | CDC | 581 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG75 | KG75(23KV北75線) |  | CB | [17 empty] | 2-01-00 |  | 1-37 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_CB | KG75(23KV北75線) CB | FEEDER | D26/22/KG75/CB |  |  |  | CDC | 582 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | PHA | [17 empty] | 2-01-04 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_PHA | 23KV北76線(KG76) 相間RY | FEEDER | D26/22/KG76/51A |  |  |  | CDC | 583 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) |  | GDA | [17 empty] | 2-01-05 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_GDA | 23KV北76線(KG76) 接地RY | FEEDER | D26/22/KG76/51NA |  |  |  | CDC | 584 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) 79RY |  | 79UL | [17 empty] | 2-36-00 |  | 1-52 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_79UL | 23KV北76線(KG76) 79RY U/L | FEEDER | D26/22/KG76/79UL |  |  |  | CDC | 585 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG76 | 北76線(KG76) LCO分流器 |  | ADJ | [17 empty] | 2-36-01 |  | 1-53 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_ADJ | 23KV北76線(KG76) LCO分流器 U/L | FEEDER | D26/22/KG76/51_51NUL |  |  |  | CDC | 586 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG76 | KG76(23KV北76線) |  | CB | [17 empty] | 2-01-03 |  | 1-38 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_CB | KG76(23KV北76線) CB | FEEDER | D26/22/KG76/CB |  |  |  | CDC | 587 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | PHA | [17 empty] | 2-01-07 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_PHA | 23KV北77線(KG77) 相間RY | FEEDER | D26/22/KG77/51A |  |  |  | CDC | 588 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) |  | GDA | [17 empty] | 2-02-00 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_GDA | 23KV北77線(KG77) 接地RY | FEEDER | D26/22/KG77/51NA |  |  |  | CDC | 589 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) 79RY |  | 79UL | [17 empty] | 2-36-02 |  | 1-54 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_79UL | 23KV北77線(KG77) 79RY U/L | FEEDER | D26/22/KG77/79UL |  |  |  | CDC | 590 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG77 | 北77線(KG77) LCO分流器 |  | ADJ | [17 empty] | 2-36-03 |  | 1-55 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_ADJ | 23KV北77線(KG77) LCO分流器 U/L | FEEDER | D26/22/KG77/51_51NUL |  |  |  | CDC | 591 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG77 | KG77(23KV北77線) |  | CB | [17 empty] | 2-01-06 |  | 1-39 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_CB | KG77(23KV北77線) CB | FEEDER | D26/22/KG77/CB |  |  |  | CDC | 592 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | PHA | [17 empty] | 2-02-02 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_PHA | 23KV北78線(KG78) 相間RY | FEEDER | D26/22/KG78/51A |  |  |  | CDC | 593 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) |  | GDA | [17 empty] | 2-02-03 | [7 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_GDA | 23KV北78線(KG78) 接地RY | FEEDER | D26/22/KG78/51NA |  |  |  | CDC | 594 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) 79RY |  | 79UL | [17 empty] | 2-36-04 |  | 1-56 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_79UL | 23KV北78線(KG78) 79RY U/L | FEEDER | D26/22/KG78/79UL |  |  |  | CDC | 595 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 22 | 22kV | KG78 | 北78線(KG78) LCO分流器 |  | ADJ | [17 empty] | 2-36-05 |  | 1-57 | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_ADJ | 23KV北78線(KG78) LCO分流器 U/L | FEEDER | D26/22/KG78/51_51NUL |  |  |  | CDC | 596 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D26 | 小北DS | 22 | 22kV | KG78 | KG78(23KV北78線) |  | CB | [17 empty] | 2-02-01 |  | 1-3A | [5 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_CB | KG78(23KV北78線) CB | FEEDER | D26/22/KG78/CB |  |  |  | CDC | 597 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 2-02-07 |  | 1-3C | [5 empty] | ADCS_S | [8 empty] | 小北DS.300_CB | 300(TIE) CB | TIE | D26/22/300/CB |  |  |  | CDC | 598 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 2-03-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.300_51A | 23KV TIE(300) 51RY | TIE | D26/22/300/51A |  |  |  | CDC | 599 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 2-03-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.300_51NA | 23KV TIE(300) 51N RY | TIE | D26/22/300/51NA |  |  |  | CDC | 600 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-09-05 |  | 1-32 | [5 empty] | ADCS_S | [8 empty] | 小北DS.350_CB | 350(#3DTR) CB | MTR | D26/22/350/CB |  |  |  | CDC | 601 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-08-05 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#3DTR_51A | #3DTR 51RY | MTR | D26/161/1770/51A |  |  |  | CDC | 602 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-08-06 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#3DTR_51NA | #3DTR 51N RY | MTR | D26/161/1770/51NA |  |  |  | CDC | 603 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-08-04 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D26//3DTR/51ZA |  |  |  | CDC | 604 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-08-02 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#3DTR_87A | #3DTR 87RY | MTR | D26//3DTR/87A |  |  |  | CDC | 605 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-09-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.350_51A | #3DTR二次側(350) 51RY | MTR |  |  |  |  | CDC | 606 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-08-03 | [7 empty] | 161KV_S | [8 empty] | 小北DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D26//3DTR/96PA |  |  |  | CDC | 607 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-35-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_96D | #3DTR 96D RY | MTR | D26/0/StaDev/Door1 |  |  |  | CDC | 608 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-35-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_96P | #3DTR 96P RY | MTR | D26/22/330/81UL |  |  |  | CDC | 609 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-35-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D26/22/340/81UL |  |  |  | CDC | 610 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-35-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D26//3DTR/87UL2 |  |  |  | CDC | 611 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-35-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D26//3DTR/51Z_UL |  |  |  | CDC | 612 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_TRA | #3DTR 重故障 | MTR | D26//3DTR/TRA |  |  |  | CDC | 613 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-33-12 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D26//3DTR/TRF |  |  |  | CDC | 614 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-33-09 | [7 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_S/L | #3DTR OLTC S/L | MTR | D26//3DTR/SupLocal |  |  |  | CDC | 615 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D26 | 小北DS | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-33-10 |  | 1-68 | [5 empty] | ADCS_S | [8 empty] | 小北DS.#3DTR_A/M | #3DTR OLTC A/M | MTR | D26//3DTR/Tap Chan |  |  |  | CDC | 616 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 1-1F-01 |  | 1-31 | [5 empty] | ADCS_S | [8 empty] | 小北DS.270_CB | 270(23KV #7SC) CB | SC | D26/22/270/CB |  |  |  | CDC | 617 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 1-1F-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.270_SCA | 23KV #7SC 51,51N RY | SC | D26/22/270/SCA |  |  |  | CDC | 618 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 1-1F-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | D26/22/270/UVA |  |  |  | CDC | 619 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | CB | [17 empty] | 2-02-04 |  | 1-3B | [5 empty] | ADCS_S | [8 empty] | 小北DS.280_CB | 280(23KV #8SC) CB | SC | D26/22/280/CB |  |  |  | CDC | 620 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [17 empty] | 2-02-05 | [7 empty] | ADCS_S | [8 empty] | 小北DS.280_SCA | 23KV #8SC 51,51N RY | SC | D26/22/280/SCA |  |  |  | CDC | 621 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [17 empty] | 2-02-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | D26/22/280/UVA |  |  |  | CDC | 622 | GENERICDIPoint | DS031_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | GDA2 | [17 empty] | 1-09-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.350_GDA2 | 350開關箱IED RY GDA | OTHER | D26/22/350/51NA |  |  |  | CDC | 623 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.350_PHA2 | 350開關箱IED RY PHA | OTHER | D26/22/350/51A |  |  |  | CDC | 624 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-34-11 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D26/0/StaDev/1A5Other |  |  |  | CDC | 625 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_S | [8 empty] | 小北DS.1510_87A | 安南小北一路(1510) 87RY | LINE161 | D26/161/1510/87A |  |  |  | CDC | 626 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | 87UL | [17 empty] | 1-30-02 |  | 1-40 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1510_87UL | 安南小北一路(1510) 87RY U/L | LINE161 | D26/161/1510/87UL |  |  |  | CDC | 627 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 1510 | 安南小北一路(1510) |  | 87CFA | [17 empty] | 1-30-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.1510_87CFA | 安南小北一路(1510)87RY通訊故障 | OTHER | D26/161/1510/87CFA |  |  |  | CDC | 628 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1510 | 安南小北一路(1510) |  | RYFA | [17 empty] | 1-30-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.1510_RYFA | 安南小北一路(1510)數位電驛故障 | OTHER | D26/161/1510/RYFA |  |  |  | CDC | 629 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 小北DS.1510_PHA | 安南小北一路(1510) 相間RY | LINE161 | D26/161/1510/PHA |  |  |  | CDC | 630 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 小北DS.1520_PHA | 安南小北二路(1520) 相間RY | LINE161 | D26/161/1520/PHA |  |  |  | CDC | 631 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 小北DS.1520_87A | 安南小北二路(1520) 87RY | LINE161 | D26/161/1520/87A |  |  |  | CDC | 632 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | 87UL | [17 empty] | 1-30-04 |  | 1-42 | [5 empty] | ADCS_S | [8 empty] | 小北DS.1520_87UL | 安南小北二路(1520) 87RY U/L | LINE161 | D26/161/1520/87UL |  |  |  | CDC | 633 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 1520 | 安南小北二路(1520) |  | 87CFA | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 小北DS.1520_87CFA | 安南小北二路(1520)87RY通訊故障 | OTHER | D26/161/1520/87CFA |  |  |  | CDC | 634 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 1520 | 安南小北二路(1520) |  | RYFA | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 小北DS.1520_RYFA | 安南小北二路(1520)數位電驛故障 | OTHER | D26/161/1520/RYFA |  |  |  | CDC | 635 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 2-32-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.23KV_SC_60A | 23/11KV SC 60A | OTHER | D26//1DTR/96B2 |  |  |  | CDC | 636 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | DCE | [17 empty] | 2-33-11 | [7 empty] | ADCS_S | [8 empty] | 小北DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D26/22/KG57/79UL |  |  |  | CDC | 637 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1BUS | #1BUS |  | 15B1E | [17 empty] | 2-38-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_15B1E | #1BUS 15B1E | OTHER | D26/161/1500/ES1 |  |  |  | CDC | 638 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 2BUS | #2BUS |  | 15B2E | [17 empty] | 2-38-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_15B2E | #2BUS 15B2E | OTHER | D26/161/1500/ES2 |  |  |  | CDC | 639 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 22 | 22kV | FEEDER | 11/ |  | 79UL | [17 empty] | 1-34-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.FEEDER_79RY | 11/22KV LOA | OTHER |  |  |  |  | CDC | 640 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  |  |  |  | GEN | [17 empty] | 2-32-11 | [7 empty] | ADCS_S | [8 empty] | 小北DS.GEN | 緊急發電機運轉 | OTHER | D26/11/KG22/79UL |  |  |  | CDC | 641 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D26 | 小北DS | 0 |  |  |  |  | PMA | [17 empty] | 1-34-08 | [7 empty] | ADCS_S | [8 empty] | 小北DS.PMA | 電力量測表計故障 | OTHER |  |  |  |  | CDC | 642 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 161BUS | BUS |  | 87A | [17 empty] | 1-05-02 | [7 empty] | 161KV_S | [8 empty] | 小北DS.161BUS_87A | 161KV BUS 87RY | BUS | D26/161/BUS/87A |  |  |  | CDC | 643 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 161BUS | BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-6A | [5 empty] | ADCS_S | [8 empty] | 小北DS.161BUS_87UL | 161KV BUS 87RY U/L | OTHER | D26/161/BUS/87UL |  |  |  | CDC | 644 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | D26/161/ComPoint/87CTFA |  |  |  | CDC | 645 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D26/161/ComPoint/BUS_RYFA |  |  |  | CDC | 646 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D26 | 小北DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-32-09 | [7 empty] | ADCS_S | [8 empty] | 小北DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D26/0/ComPoint/OLTC_A |  |  |  | CDC | 647 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | 81AS | [17 empty] | 1-0A-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.310_81A/S | (310)81RY 動作/Reset | OTHER | D26/11/310/81AS |  |  |  | CDC | 648 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | 81UL | [17 empty] | 2-32-14 |  | 1-58 | [5 empty] | ADCS_S | [8 empty] | 小北DS.310_81UL | (310)81RY USE/LOCK | OTHER | D26/11/KG25/79UL |  |  |  | CDC | 649 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | 81AS | [17 empty] | 1-0A-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.320_81A/S | (320)81RY 動作/Reset | OTHER | D26/22/320/81AS |  |  |  | CDC | 650 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | 81UL | [17 empty] | 2-32-15 |  | 1-59 | [5 empty] | ADCS_S | [8 empty] | 小北DS.320_81UL | (320)81RY USE/LOCK | OTHER | D26/11/KG26/79UL |  |  |  | CDC | 651 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | 81AS | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.330_81A/S | (330)81RY 動作/Reset | OTHER | D26/22/330/81AS |  |  |  | CDC | 652 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | 81UL | [17 empty] | 2-33-01 |  | 1-5A | [5 empty] | ADCS_S | [8 empty] | 小北DS.330_81UL | (330)81RY USE/LOCK | OTHER | D26/11/220/SC_A_M |  |  |  | CDC | 653 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | 81AS | [17 empty] | 1-0A-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.340_81A/S | (340)81RY 動作/Reset | OTHER | D26/22/340/81AS |  |  |  | CDC | 654 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | 81UL | [17 empty] | 2-33-02 |  | 1-5B | [5 empty] | ADCS_S | [8 empty] | 小北DS.340_81UL | (340)81RY USE/LOCK | OTHER | D26/22/KG60/79UL |  |  |  | CDC | 655 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | 81AS | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 小北DS.350_81A/S | (350)81RY 動作/Reset | OTHER | D26/22/350/81AS |  |  |  | CDC | 656 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | 81UL | [17 empty] | 2-32-12 |  | 1-5C | [5 empty] | ADCS_S | [8 empty] | 小北DS.350_81UL | (350)81RY USE/LOCK | OTHER | D26/11/KG23/79UL |  |  |  | CDC | 657 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 小北DS.310_GDA | #1A DTR(310) 接地RY | OTHER | D26/11/310/GDA |  |  |  | CDC | 658 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-0A-06 | [7 empty] | ADCS_S | [8 empty] | 小北DS.320_GDA | #1B DTR(320) 接地RY | OTHER | D26/22/320/GDA |  |  |  | CDC | 659 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-0A-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.330_GDA | #2A DTR(330) 接地RY | OTHER | D26/22/330/GDA |  |  |  | CDC | 660 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0B-00 | [7 empty] | ADCS_S | [8 empty] | 小北DS.340_GDA | #2B DTR(340) 接地RY | OTHER | D26/22/340/GDA |  |  |  | CDC | 661 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1613DTR | #3DTR |  | DTR_86A | [17 empty] | 1-0B-03 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#3DTR_86A | 161KV #3DTR 86RY | OTHER |  |  |  |  | CDC | 662 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1613DTR | #3DTR |  | 187UL | [17 empty] | 1-33-08 |  | 2-3B | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | D26//3DTR/87UL1 |  |  |  | CDC | 663 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1613DTR | #3DTR |  | 287UL | [17 empty] | 2-33-03 |  | 2-3C | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER | D26/22/KG61/79UL |  |  |  | CDC | 664 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1613DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-33-04 |  | 2-3D | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER | D26/22/KG62/79UL |  |  |  | CDC | 665 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1613DTR | #3DTR |  | RYFA | [17 empty] | 2-33-08 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER | D26/22/KG54/79UL |  |  |  | CDC | 666 | GENERICDIPoint | DS031_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1612DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0B-02 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#2DTR_86A | 161KV #2DTR 86RY | OTHER |  |  |  |  | CDC | 667 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1612DTR | #2DTR |  | 187UL | [17 empty] | 1-33-01 |  | 2-1D | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | D26//2DTR/87UL1 |  |  |  | CDC | 668 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1612DTR | #2DTR |  | 287UL | [17 empty] | 1-33-13 |  | 2-1E | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER |  |  |  |  | CDC | 669 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1612DTR | #2DTR |  | 51Z_UL | [17 empty] | 1-33-14 |  | 2-1F | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 670 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1612DTR | #2DTR |  | RYFA | [17 empty] | 1-33-15 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER |  |  |  |  | CDC | 671 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1611DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0B-01 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#1DTR_86A | 161KV #1DTR 86RY | OTHER |  |  |  |  | CDC | 672 | GENERICDIPoint | DS031_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D26 | 小北DS | 161 | 161kV | 1611DTR | #1DTR |  | 187UL | [17 empty] | 1-32-10 |  | 2-1A | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | D26//1DTR/87UL1 |  |  |  | CDC | 673 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1611DTR | #1DTR |  | 287UL | [17 empty] | 1-32-03 |  | 2-1B | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER | D26//1DTR/87UL2 |  |  |  | CDC | 674 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1611DTR | #1DTR |  | 51Z_UL | [17 empty] | 1-32-06 |  | 2-1C | [5 empty] | ADCS_S | [8 empty] | 小北DS.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 675 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D26 | 小北DS | 161 | 161kV | 1611DTR | #1DTR |  | RYFA | [17 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 小北DS.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER |  |  |  |  | CDC | 676 | GENERICDIPoint | DS031_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D26 | 小北DS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 677 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 678 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 230_SC | #3SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 679 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 680 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 681 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 682 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 065 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_065 | 小北DS NT #2ADTR 23KV_Hi_Limit | [6 empty] | 683 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 066 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_066 | 小北DS NT #2ADTR 23KV_Lo_Limit | [6 empty] | 684 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 067 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_067 | 小北DS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 685 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 068 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_068 | 小北DS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 686 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 069 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_069 | 小北DS NT #2BDTR 23KV_Hi_Limit | [6 empty] | 687 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 070 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_070 | 小北DS NT #2BDTR 23KV_Lo_Limit | [6 empty] | 688 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 071 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_071 | 小北DS NT #1BDTR 23KV_Hi_Limit | [6 empty] | 689 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D26 | 小北DS | 0 |  | TRD | 小北DS |  | 072 | [25 empty] | TRAIN_AD | [8 empty] | 小北DS.TRD_072 | 小北DS NT #1BDTR 23KV_Lo_Limit | [6 empty] | 690 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D26 | 小北DS | 22 | 22kV | 270_SC | #7SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 691 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 22 | 22kV | 280_SC | #8SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 小北DS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 692 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1510LE | 1510LE (非取樣點) | LINE161 | D26/161/1510/LE0 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1510BE | 1510BE (非取樣點) | LINE161 | D26/161/1510/BE0 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1520LE | 1520LE (非取樣點) | LINE161 | D26/161/1520/LE0 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1520BE | 1520BE (非取樣點) | LINE161 | D26/161/1520/BE0 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG22 | KG22_DS |  | DS1 | KG22_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_DS | KG22_DS (非取樣點) | FEEDER | D26/11/KG22/DS |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG22 | KG22_ES |  | LE0 | KG22_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG22_ES | KG22_ES (非取樣點) | FEEDER | D26/11/KG22/ES |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG23 | KG23_DS |  | DS1 | KG23_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_DS | KG23_DS (非取樣點) | FEEDER | D26/11/KG23/DS |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG23 | KG23_ES |  | LE0 | KG23_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG23_ES | KG23_ES (非取樣點) | FEEDER | D26/11/KG23/ES |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG24 | KG24_DS |  | DS1 | KG24_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_DS | KG24_DS (非取樣點) | FEEDER | D26/11/KG24/DS |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG24 | KG24_ES |  | LE0 | KG24_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG24_ES | KG24_ES (非取樣點) | FEEDER | D26/11/KG24/ES |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG26 | KG26_DS |  | DS1 | KG26_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_DS | KG26_DS (非取樣點) | FEEDER | D26/11/KG26/DS |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG26 | KG26_ES |  | LE0 | KG26_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG26_ES | KG26_ES (非取樣點) | FEEDER | D26/11/KG26/ES |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG54 | KG54_DS |  | DS1 | KG54_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_DS | KG54_DS (非取樣點) | FEEDER | D26/22/KG54/DS |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG54 | KG54_ES |  | LE0 | KG54_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG54_ES | KG54_ES (非取樣點) | FEEDER | D26/22/KG54/ES |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG55 | KG55_DS |  | DS1 | KG55_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_DS | KG55_DS (非取樣點) | FEEDER | D26/22/KG55/DS |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG55 | KG55_ES |  | LE0 | KG55_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG55_ES | KG55_ES (非取樣點) | FEEDER | D26/22/KG55/ES |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG56 | KG56_DS |  | DS1 | KG56_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_DS | KG56_DS (非取樣點) | FEEDER | D26/22/KG56/DS |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG56 | KG56_ES |  | LE0 | KG56_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG56_ES | KG56_ES (非取樣點) | FEEDER | D26/22/KG56/ES |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG57 | KG57_DS |  | DS1 | KG57_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_DS | KG57_DS (非取樣點) | FEEDER | D26/22/KG57/DS |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG57 | KG57_ES |  | LE0 | KG57_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG57_ES | KG57_ES (非取樣點) | FEEDER | D26/22/KG57/ES |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG64 | KG64_DS |  | DS1 | KG64_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_DS | KG64_DS (非取樣點) | FEEDER | D26/22/KG64/DS |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG64 | KG64_ES |  | LE0 | KG64_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG64_ES | KG64_ES (非取樣點) | FEEDER | D26/22/KG64/ES |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG65 | KG65_DS |  | DS1 | KG65_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_DS | KG65_DS (非取樣點) | FEEDER | D26/22/KG65/DS |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG65 | KG65_ES |  | LE0 | KG65_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG65_ES | KG65_ES (非取樣點) | FEEDER | D26/22/KG65/ES |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG66 | KG66_DS |  | DS1 | KG66_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_DS | KG66_DS (非取樣點) | FEEDER | D26/22/KG66/DS |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG66 | KG66_ES |  | LE0 | KG66_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG66_ES | KG66_ES (非取樣點) | FEEDER | D26/22/KG66/ES |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG67 | KG67_DS |  | DS1 | KG67_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_DS | KG67_DS (非取樣點) | FEEDER | D26/22/KG67/DS |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG67 | KG67_ES |  | LE0 | KG67_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG67_ES | KG67_ES (非取樣點) | FEEDER | D26/22/KG67/ES |  |  |  |  | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1750TE | 1750TE (非取樣點) | MTR | D26/161/1750/TE0 |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1750BE | 1750BE (非取樣點) | MTR | D26/161/1750/BE0 |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | DS1 | 310_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.310_DS | 310_DS (非取樣點) | MTR | [5 empty] | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 310 | #1DTR(310) |  | LE0 | 310_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.310_ES | 310_ES (非取樣點) | MTR | D26/11/310/ES |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | DS1 | 320_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.320_DS | 320_DS (非取樣點) | MTR | D26/22/320/DS |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 320 | #1DTR(320) |  | LE0 | 320_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.320_ES | 320_ES (非取樣點) | MTR | D26/22/320/ES |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1760TE | 1760TE (非取樣點) | MTR | D26/161/1760/TE0 |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1760BE | 1760BE (非取樣點) | MTR | D26/161/1760/BE0 |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | DS1 | 330_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.330_DS | 330_DS (非取樣點) | MTR | D26/22/330/DS |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 330 | #2DTR(330) |  | LE0 | 330_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.330_ES | 330_ES (非取樣點) | MTR | D26/22/330/ES |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | DS1 | 340_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.340_DS | 340_DS (非取樣點) | MTR | D26/22/340/DS |  |  |  |  | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 340 | #2DTR(340) |  | LE0 | 340_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.340_ES | 340_ES (非取樣點) | MTR | D26/22/340/ES |  |  |  |  | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.210_ES | 210_ES (非取樣點) | SC | D26/11/210/ES |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 210 | #1SC(210) |  | SC0 | 210SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.210SC_ES | 210SC_ES (非取樣點) | SC | [5 empty] | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.210_DS | 210_DS (非取樣點) | SC | D26/11/210/DS |  |  |  |  | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.220_ES | 220_ES (非取樣點) | SC | D26/11/220/ES |  |  |  |  | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 220 | #2SC(220) |  | SC0 | 220SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.220SC_ES | 220SC_ES (非取樣點) | SC | [5 empty] | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.220_DS | 220_DS (非取樣點) | SC | D26/11/220/DS |  |  |  |  | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.230_ES | 230_ES (非取樣點) | SC | D26/22/230/ES |  |  |  |  | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 230 | #3SC(230) |  | SC0 | 230SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.230SC_ES | 230SC_ES (非取樣點) | SC | [5 empty] | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.230_DS | 230_DS (非取樣點) | SC | D26/22/230/DS |  |  |  |  | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.240_ES | 240_ES (非取樣點) | SC | D26/22/240/ES |  |  |  |  | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 240 | #4SC(240) |  | SC0 | 240SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.240SC_ES | 240SC_ES (非取樣點) | SC | [5 empty] | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.240_DS | 240_DS (非取樣點) | SC | D26/22/240/DS |  |  |  |  | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.250_ES | 250_ES (非取樣點) | SC | D26/22/250/ES |  |  |  |  | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.250_DS | 250_DS (非取樣點) | SC | D26/22/250/DS |  |  |  |  | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_S | [8 empty] | 小北DS.260_ES | 260_ES (非取樣點) | SC | D26/22/260/ES |  |  |  |  | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.260_DS | 260_DS (非取樣點) | SC | D26/22/260/DS |  |  |  |  | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 小北DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 751 | NotelDIPoint | [38 empty] | START/STOP | STOP
D26 | 小北DS | 161 | 161kV | 1530 | 備用一(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1530LE | 1530LE (非取樣點) | LINE161 | D26/161/1530/LE0 |  |  |  |  | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1530 | 備用一(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1530BE | 1530BE (非取樣點) | LINE161 | D26/161/1530/BE0 |  |  |  |  | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1540 | 備用二(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1540LE | 1540LE (非取樣點) | LINE161 | D26/161/1540/LE0 |  |  |  |  | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1540 | 備用二(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1540BE | 1540BE (非取樣點) | LINE161 | D26/161/1540/BE0 |  |  |  |  | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1770TE | 1770TE (非取樣點) | MTR | D26/161/1770/TE0 |  |  |  |  | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.1770BE | 1770BE (非取樣點) | MTR | D26/161/1770/BE0 |  |  |  |  | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 小北DS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | D26/11/1SSTR/LBS |  |  |  |  | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 小北DS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 小北DS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | D26/11/2SSTR/LBS |  |  |  |  | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 小北DS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG21 | KG21_DS |  | DS1 | KG21_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_DS | KG21_DS (非取樣點) | FEEDER | D26/11/KG21/DS |  |  |  |  | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG21 | KG21_ES |  | LE0 | KG21_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG21_ES | KG21_ES (非取樣點) | FEEDER | D26/11/KG21/ES |  |  |  |  | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG25 | KG25_DS |  | DS1 | KG25_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_DS | KG25_DS (非取樣點) | FEEDER | D26/11/KG25/DS |  |  |  |  | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG25 | KG25_ES |  | LE0 | KG25_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG25_ES | KG25_ES (非取樣點) | FEEDER | D26/11/KG25/ES |  |  |  |  | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG60 | KG60_DS |  | DS1 | KG60_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_DS | KG60_DS (非取樣點) | FEEDER | D26/22/KG60/DS |  |  |  |  | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG60 | KG60_ES |  | LE0 | KG60_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG60_ES | KG60_ES (非取樣點) | FEEDER | D26/22/KG60/ES |  |  |  |  | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG61 | KG61_DS |  | DS1 | KG61_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_DS | KG61_DS (非取樣點) | FEEDER | D26/22/KG61/DS |  |  |  |  | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG61 | KG61_ES |  | LE0 | KG61_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG61_ES | KG61_ES (非取樣點) | FEEDER | D26/22/KG61/ES |  |  |  |  | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG62 | KG62_DS |  | DS1 | KG62_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_DS | KG62_DS (非取樣點) | FEEDER | D26/22/KG62/DS |  |  |  |  | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG62 | KG62_ES |  | LE0 | KG62_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG62_ES | KG62_ES (非取樣點) | FEEDER | D26/22/KG62/ES |  |  |  |  | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG63 | KG63_DS |  | DS1 | KG63_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_DS | KG63_DS (非取樣點) | FEEDER | D26/22/KG63/DS |  |  |  |  | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG63 | KG63_ES |  | LE0 | KG63_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG63_ES | KG63_ES (非取樣點) | FEEDER | D26/22/KG63/ES |  |  |  |  | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 100 | TIE(100) |  | DS1 | 100_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.100_DS | 100_DS (非取樣點) | TIE | D26/22/100/DS |  |  |  |  | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 200 | TIE(200) |  | DS1 | 200_DS | [24 empty] | ADCS_S | [8 empty] | 小北DS.200_DS | 200_DS (非取樣點) | TIE | D26/22/200/DS |  |  |  |  | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG71 | KG71_DS |  | DS1 | KG71_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_DS | KG71_DS (非取樣點) | FEEDER | D26/22/KG71/DS |  |  |  |  | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG71 | KG71_ES |  | LE0 | KG71_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG71_ES | KG71_ES (非取樣點) | FEEDER | D26/22/KG71/ES |  |  |  |  | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG72 | KG72_DS |  | DS1 | KG72_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_DS | KG72_DS (非取樣點) | FEEDER | D26/22/KG72/DS |  |  |  |  | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG72 | KG72_ES |  | LE0 | KG72_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG72_ES | KG72_ES (非取樣點) | FEEDER | D26/22/KG72/ES |  |  |  |  | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG73 | KG73_DS |  | DS1 | KG73_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_DS | KG73_DS (非取樣點) | FEEDER | D26/22/KG73/DS |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG73 | KG73_ES |  | LE0 | KG73_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG73_ES | KG73_ES (非取樣點) | FEEDER | D26/22/KG73/ES |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG74 | KG74_DS |  | DS1 | KG74_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_DS | KG74_DS (非取樣點) | FEEDER | D26/22/KG74/DS |  |  |  |  | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG74 | KG74_ES |  | LE0 | KG74_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG74_ES | KG74_ES (非取樣點) | FEEDER | D26/22/KG74/ES |  |  |  |  | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG75 | KG75_DS |  | DS1 | KG75_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_DS | KG75_DS (非取樣點) | FEEDER | D26/22/KG75/DS |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG75 | KG75_ES |  | LE0 | KG75_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG75_ES | KG75_ES (非取樣點) | FEEDER | D26/22/KG75/ES |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG76 | KG76_DS |  | DS1 | KG76_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_DS | KG76_DS (非取樣點) | FEEDER | D26/22/KG76/DS |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG76 | KG76_ES |  | LE0 | KG76_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG76_ES | KG76_ES (非取樣點) | FEEDER | D26/22/KG76/ES |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG77 | KG77_DS |  | DS1 | KG77_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_DS | KG77_DS (非取樣點) | FEEDER | D26/22/KG77/DS |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG77 | KG77_ES |  | LE0 | KG77_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG77_ES | KG77_ES (非取樣點) | FEEDER | D26/22/KG77/ES |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | KG78 | KG78_DS |  | DS1 | KG78_DS | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_DS | KG78_DS (非取樣點) | FEEDER | D26/22/KG78/DS |  |  |  |  | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | KG78 | KG78_ES |  | LE0 | KG78_ES | [24 empty] | DDCS4_1 | [8 empty] | 小北DS.KG78_ES | KG78_ES (非取樣點) | FEEDER | D26/22/KG78/ES |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 270 | #7SC(270) |  | SC0 | 270SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.270SC_ES | 270SC_ES (非取樣點) | SC | [5 empty] | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 280 | #8SC(280) |  | SC0 | 280SC | [24 empty] | ADCS_S | [8 empty] | 小北DS.280SC_ES | 280SC_ES (非取樣點) | SC | [5 empty] | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 小北DS.301 | 301 (非取樣點) | TIE | [5 empty] | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 302 | 302 |  | 302 | 302 | [24 empty] | ADCS_S | [8 empty] | 小北DS.302 | 302 (非取樣點) | TIE | [5 empty] | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 小北DS.351 | 351 (非取樣點) | MTR | [5 empty] | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 小北DS.351E | 351E (非取樣點) | MTR | [5 empty] | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_S | [8 empty] | 小北DS.271E | 271E (非取樣點) | SC | [5 empty] | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_S | [8 empty] | 小北DS.271 | 271 (非取樣點) | SC | [5 empty] | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_S | [8 empty] | 小北DS.281E | 281E (非取樣點) | SC | [5 empty] | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_S | [8 empty] | 小北DS.281 | 281 (非取樣點) | SC | [5 empty] | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_S | [8 empty] | 小北DS.301E | 301E(非取樣點) | OTHER | D26/22/300/E1 |  |  |  |  | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  |  |  |  | 302E | 302E | [24 empty] | ADCS_S | [8 empty] | 小北DS.302E | 302E(非取樣點) | OTHER | D26/22/300/E2 |  |  |  |  | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 3 | #3 |  | BE | #3_BE | [24 empty] | ADCS_S | [8 empty] | 小北DS.#3_BE | #3 BE(非取樣點) | OTHER | [5 empty] | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D26 | 小北DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 小北DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | D26/11/1ABUS/DS1 |  |  |  |  | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 小北DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | D26/22/1BBUS/DS1 |  |  |  |  | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 小北DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | D26/22/2ABUS/DS1 |  |  |  |  | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 小北DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | D26/22/2BBUS/DS1 |  |  |  |  | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 小北DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | D26/22/3BUS/DS1 |  |  |  |  | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D26 | 小北DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_S | [8 empty] | 小北DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | D26/22/3BUS/TE0 |  |  |  |  | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo