## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.311 | 311 (非取樣點) | MTR | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.311E | 311E (非取樣點) | MTR | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.341 | 341 (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.341E | 341E (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.331 | 331 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.331E | 331E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_A1 | [8 empty] | 鹽行DS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | DS | 350_DS | del | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.350_DS | 350_DS (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | ES | 350_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.350_ES | 350_ES (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | D1 | 351(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.351 | 351 (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | E1 | 351E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.351E | 351E (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.321 | 321 (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.321E | 321E (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) | B3 | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | D1 | 301(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.301 | 301 (非取樣點) | TIE | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.301E | 301E(非取樣點) | OTHER | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | D1 | 401(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.401 | 401 (非取樣點) | TIE | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.401E | 401E(非取樣點) | OTHER | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | ES | 210_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [16 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.211E | 211E (非取樣點) | SC | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.211 | 211 (非取樣點) | SC | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_DS | KV21_DS (非取樣點) | FEEDER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_ES | KV21_ES (非取樣點) | FEEDER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_DS | KV22_DS (非取樣點) | FEEDER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_ES | KV22_ES (非取樣點) | FEEDER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_DS | KV23_DS (非取樣點) | FEEDER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_ES | KV23_ES (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_DS | KV24_DS (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_ES | KV24_ES (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_DS | KV25_DS (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_ES | KV25_ES (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_DS | KV26_DS (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_ES | KV26_ES (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | ES | 220_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [16 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.221E | 221E (非取樣點) | SC | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.221 | 221 (非取樣點) | SC | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.101 | 101 (非取樣點) | TIE | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_DS | KV27_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_ES | KV27_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_DS | KV28_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_ES | KV28_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_DS | KV29_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_ES | KV29_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_DS | KV30_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_ES | KV30_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | ES | 240_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [16 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.241E | 241E (非取樣點) | SC | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.241 | 241 (非取樣點) | SC | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | ES | 230_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [16 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.231E | 231E (非取樣點) | SC | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.231 | 231 (非取樣點) | SC | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_DS | KV31_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_ES | KV31_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_DS | KV32_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_ES | KV32_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_DS | KV33_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_ES | KV33_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_DS | KV34_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_ES | KV34_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.201 | 201 (非取樣點) | TIE | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | ES | 260_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | DS | 260_DS | del | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.261E | 261E (非取樣點) | SC | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.261 | 261 (非取樣點) | SC | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_DS | KV71_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_ES | KV71_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_DS | KV72_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_ES | KV72_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_DS | KV73_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_ES | KV73_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_DS | KV74_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_ES | KV74_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_DS | KV75_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_ES | KV75_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_DS | KV76_DS (非取樣點) | FEEDER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_ES | KV76_ES (非取樣點) | FEEDER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | ES | 250_ES | del | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | DS | 250_DS | del | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.251E | 251E (非取樣點) | SC | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D27_A1 | [8 empty] | 鹽行DS.251 | 251 (非取樣點) | SC | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aacz | B2/D27_A1 | [8 empty] | 鹽行DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | abab | B2/D27_A1 | [8 empty] | 鹽行DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 161KV #1BUS電壓 | kV_-210_210(-2000_2000) | aaa | B2/D27_A1 | [8 empty] | 鹽行DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D27 | 鹽行DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 161KV #2BUS電壓 | kV_-210_210(-2000_2000) | aba | B2/D27_A1 | [8 empty] | 鹽行DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1540 | MW | 山上盬行豐華白線 1540 瓦 | MW_-560_560(-2000_2000) |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_MW | 山上豐華白線 MW | LINE161 | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1540 | MVAR | 山上盬行豐華白線 1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_MVAR | 山上豐華白線 MVAR | LINE161 | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1530 | MW | 安南鹽行線 1530 瓦 | MW_-224_224(-2000_2000) |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_MW | 安南鹽行線 MW | LINE161 | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.448 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1530 | MVAR | 安南鹽行線 1530 乏 | MVAR_-224_224(-2000_2000) |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_MVAR | 安南鹽行線 MVAR | LINE161 | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.448 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | DC | V | DCP 電壓 | kV_-150_150(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | DC | V | DCN 電壓 | kV_-150_150(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 310 | MW | D1A 310 瓦 | MW_-54_54(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 310 | MVAR | D1A 310 乏 | MVAR_-36_36(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 310 | A | D1A 310 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 310 | A | D1A 310 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 310 | A | D1A 310 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 340 | MW | D2B 340 瓦 | MW_-54_54(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 340 | MVAR | D2B 340 乏 | MVAR_-36_36(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 340 | A | D2B 340 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 340 | A | D2B 340 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | 340 | A | D2B 340 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 330 | MW | D2A 330 瓦 | MW_-54_54(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | 330 | MVAR | D2A 330 乏 | MVAR_-36_36(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 330 | A | D2A 330 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 330 | A | D2A 330 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 330 | A | D2A 330 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 350 | MW | D3 350 瓦 | MW_-108_108(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#3DTR_MW | #3DTR二次側 MW | MTR | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 350 | MVAR | D3 350 乏 | MVAR_-72_72(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 350 | A | D3 350 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 350 | A | D3 350 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 350 | A | D3 350 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | #1DTR | ℃ | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | #1ADTR | ℃ | #1ADTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | #1BDTR | ℃ | #1BDTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0039 |  | 0097 | 1-A7 |  | 1-61 | #1ADTR | 升/降 | #1ADTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0040 |  | 0099 | 1-A8 |  | 1-63 | #1BDTR | 升/降 | #1BDTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | #2ADTR | ℃ | #2ADTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | #2BDTR | ℃ | #2BDTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0044 |  | 0101 | 1-AC |  | 1-65 | #2ADTR | 升/降 | #2ADTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0045 |  | 0103 | 1-AD |  | 1-67 | #2BDTR | 升/降 | #2BDTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | #3DTR | ℃ | #3DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 3DTR(A) | #3DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | #3ADTR | ℃ | #3ADTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 3DTR(B) | #3DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | #3BDTR | ℃ | #3BDTR 線溫 | COIL_-120_120(-2000_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS |  |  | 3DTR(A) | #3DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0049 |  | 0105 | 1-B1 |  | 1-69 | #3ADTR | 升/降 | #3ADTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS |  |  | 3DTR(B) | #3DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0050 |  | 0107 | 1-B2 |  | 1-6B | #3BDTR | 升/降 | #3BDTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0055 |  |  | 1-B7 |  |  | D2B BUS PT | KV | D2B 340 BUS #2B PT 電壓 (11KV) | kV_-9_9(-2000_2000) | bba | B3/D27_A1 | [8 empty] | 鹽行DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0056 |  |  | 1-B8 |  |  | D1A BUS PT | KV | D1A 310 BUS #1A PT 電壓(11KV) | kV_-9_9(-2000_2000) | aaa | B3/D27_A1 | [8 empty] | 鹽行DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | KV21 | MVAR | 鹽21線F1KV21 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽21線KVAR | 11KV鹽21線 KVAR | FEEDER | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | KV21 | A | 鹽21線F1KV21 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽21線A1 | 11KV鹽21線 R相AMP | FEEDER | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | KV21 | A | 鹽21線F1KV21 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽21線A2 | 11KV鹽21線 S相AMP | FEEDER | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | KV21 | A | 鹽21線F1KV21 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽21線A3 | 11KV鹽21線 T相AMP | FEEDER | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | KV22 | MVAR | 鹽22線F2KV22 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽22線KVAR | 11KV鹽22線 KVAR | FEEDER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | KV22 | A | 鹽22線F2KV22 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽22線A1 | 11KV鹽22線 R相AMP | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | KV22 | A | 鹽22線F2KV22 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽22線A2 | 11KV鹽22線 S相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | KV22 | A | 鹽22線F2KV22 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽22線A3 | 11KV鹽22線 T相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | KV23 | MVAR | 鹽23線F3KV23 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽23線KVAR | 11KV鹽23線 KVAR | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | KV23 | A | 鹽23線F3KV23 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽23線A1 | 11KV鹽23線 R相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | KV23 | A | 鹽23線F3KV23 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽23線A2 | 11KV鹽23線 S相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | KV23 | A | 鹽23線F3KV23 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽23線A3 | 11KV鹽23線 T相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | KV24 | MVAR | 鹽24線F4KV24 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽24線KVAR | 11KV鹽24線 KVAR | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | KV24 | A | 鹽24線F4KV24 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽24線A1 | 11KV鹽24線 R相AMP | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | KV24 | A | 鹽24線F4KV24 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽24線A2 | 11KV鹽24線 S相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | KV24 | A | 鹽24線F4KV24 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽24線A3 | 11KV鹽24線 T相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | KV25 | MVAR | 鹽25線F5KV25 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽25線KVAR | 11KV鹽25線 KVAR | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | KV25 | A | 鹽25線F5KV25 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽25線A1 | 11KV鹽25線 R相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | KV25 | A | 鹽25線F5KV25 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽25線A2 | 11KV鹽25線 S相AMP | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | KV25 | A | 鹽25線F5KV25 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽25線A3 | 11KV鹽25線 T相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | KV26 | MVAR | 鹽26線F6KV26 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽26線KVAR | 11KV鹽26線 KVAR | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | KV26 | A | 鹽26線F6KV26 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽26線A1 | 11KV鹽26線 R相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C05R450R | 405 | 406 | 450 | 500 | 1.43 | 8 | -200 | -201 | -202 | 1 | 0.01 | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | KV26 | A | 鹽26線F6KV26 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽26線A2 | 11KV鹽26線 S相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | KV26 | A | 鹽26線F6KV26 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽26線A3 | 11KV鹽26線 T相AMP | FEEDER | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | C05R0450 | 427.5 | 450 | 495 | 500 | 1.43 | -427.5 | -450 | -495 | -500 | 1 | 0.01 | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | #1TIE | A | #1TIE 100 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | #1TIE | A | #1TIE 100 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | #1TIE | A | #1TIE 100 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | KV27 | MVAR | 鹽27線F7KV27 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽27線KVAR | 11KV鹽27線 KVAR | FEEDER | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | KV27 | A | 鹽27線F7KV27 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽27線A1 | 11KV鹽27線 R相AMP | FEEDER | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | KV27 | A | 鹽27線F7KV27 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽27線A2 | 11KV鹽27線 S相AMP | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | KV27 | A | 鹽27線F7KV27 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽27線A3 | 11KV鹽27線 T相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | KV28 | MVAR | 鹽28線F8KV28 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽28線KVAR | 11KV鹽28線 KVAR | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | KV28 | A | 鹽28線F8KV28 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽28線A1 | 11KV鹽28線 R相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | KV28 | A | 鹽28線F8KV28 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽28線A2 | 11KV鹽28線 S相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | KV28 | A | 鹽28線F8KV28 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽28線A3 | 11KV鹽28線 T相AMP | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | KV29 | MVAR | 鹽29線F9KV29 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽29線KVAR | 11KV鹽29線 KVAR | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | KV29 | A | 鹽29線F9KV29 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽29線A1 | 11KV鹽29線 R相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | KV29 | A | 鹽29線F9KV29 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽29線A2 | 11KV鹽29線 S相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | KV29 | A | 鹽29線F9KV29 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽29線A3 | 11KV鹽29線 T相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | KV30 | MVAR | 鹽30線F10KV30 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽30線KVAR | 11KV鹽30線 KVAR | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | KV30 | A | 鹽30線F10KV30 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽30線A1 | 11KV鹽30線 R相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | KV30 | A | 鹽30線F10KV30 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽30線A2 | 11KV鹽30線 S相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | KV30 | A | 鹽30線F10KV30 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽30線A3 | 11KV鹽30線 T相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0102 |  |  | 1-E6 |  |  | D2A BUS PT | KV | D2A 330 BUS #2A PT 電壓 (11KV) | kV_-9_9(-2000_2000) | aba | B3/D27_A1 | [8 empty] | 鹽行DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | KV31 | MVAR | 鹽31線F11KV31 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽31線KVAR | 11KV鹽31線 KVAR | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | KV31 | A | 鹽31線F11KV31 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽31線A1 | 11KV鹽31線 R相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | KV31 | A | 鹽31線F11KV31 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽31線A2 | 11KV鹽31線 S相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | KV31 | A | 鹽31線F11KV31 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽31線A3 | 11KV鹽31線 T相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | KV32 | MVAR | 鹽32線F12KV32 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽32線KVAR | 11KV鹽32線 KVAR | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | KV32 | A | 鹽32線F12KV32 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽32線A1 | 11KV鹽32線 R相AMP | FEEDER | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | KV32 | A | 鹽32線F12KV32 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽32線A2 | 11KV鹽32線 S相AMP | FEEDER | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | KV32 | A | 鹽32線F12KV32 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽32線A3 | 11KV鹽32線 T相AMP | FEEDER | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | KV33 | MVAR | 鹽33線F13KV33 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽33線KVAR | 11KV鹽33線 KVAR | FEEDER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | KV33 | A | 鹽33線F13KV33 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽33線A1 | 11KV鹽33線 R相AMP | FEEDER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | KV33 | A | 鹽33線F13KV33 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽33線A2 | 11KV鹽33線 S相AMP | FEEDER | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | KV33 | A | 鹽33線F13KV33 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽33線A3 | 11KV鹽33線 T相AMP | FEEDER | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | KV34 | MVAR | 鹽34線F14KV34 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽34線KVAR | 11KV鹽34線 KVAR | FEEDER | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | KV34 | A | 鹽34線F14KV34 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽34線A1 | 11KV鹽34線 R相AMP | FEEDER | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | KV34 | A | 鹽34線F14KV34 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽34線A2 | 11KV鹽34線 S相AMP | FEEDER | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | KV34 | A | 鹽34線F14KV34 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽34線A3 | 11KV鹽34線 T相AMP | FEEDER | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | KV71 | MVAR | 鹽71線 F15 KV71 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽71線KVAR | 23KV鹽71線 KVAR | FEEDER | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | KV71 | A | 鹽71線 F15 KV71 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽71線A1 | 23KV鹽71線 R相AMP | FEEDER | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | KV71 | A | 鹽71線F15 KV71 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽71線A2 | 23KV鹽71線 S相AMP | FEEDER | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | KV71 | A | 鹽71線F15 KV71 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽71線A3 | 23KV鹽71線 T相AMP | FEEDER | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | #2TIE | A | #2TIE 200 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | #2TIE | A | #2TIE 200 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | #2TIE | A | #2TIE 200 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | KV72 | MVAR | 鹽72線F16 KV72 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽72線KVAR | 23KV鹽72線 KVAR | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | KV72 | A | 鹽72線 F16 KV72 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽72線A1 | 23KV鹽72線 R相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | KV72 | A | 鹽72線F16 KV72 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽72線A2 | 23KV鹽72線 S相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | KV72 | A | 鹽72線F16 KV72 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽72線A3 | 23KV鹽72線 T相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | KV73 | MVAR | 鹽73線F17KV73 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽73線KVAR | 23KV鹽73線 KVAR | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | KV73 | A | 鹽73線F17KV73 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽73線A1 | 23KV鹽73線 R相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | KV73 | A | 鹽73線F17KV73 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽73線A2 | 23KV鹽73線 S相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | KV73 | A | 鹽73線F17KV73 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽73線A3 | 23KV鹽73線 T相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | KV74 | MVAR | 鹽74線F18KV74 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽74線KVAR | 23KV鹽74線 KVAR | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | KV74 | A | 鹽74線F18KB74 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽74線A1 | 23KV鹽74線 R相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | KV74 | A | 鹽74線F18KB74 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽74線A2 | 23KV鹽74線 S相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | KV74 | A | 鹽74線F18KV74 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽74線A3 | 23KV鹽74線 T相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | KV75 | MVAR | 鹽75線F19KV75 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽75線KVAR | 23KV鹽75線 KVAR | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | KV75 | A | 鹽75線F19KV75 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽75線A1 | 23KV鹽75線 R相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | KV75 | A | 鹽75線F19KV75 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽75線A2 | 23KV鹽75線 S相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | KV75 | A | 鹽75線F19KV75 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽75線A3 | 23KV鹽75線 T相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | KV76 | MVAR | 鹽76線F20KV76 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽76線KVAR | 23KV鹽76線 KVAR | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | KV76 | A | 鹽76線F20KV76 R相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽76線A1 | 23KV鹽76線 R相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | KV76 | A | 鹽76線F20KV76 S相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽76線A2 | 23KV鹽76線 S相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | KV76 | A | 鹽76線F20KV76 T相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽76線A3 | 23KV鹽76線 T相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 3BUS | #3BUS |  | V |  | B2 | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0148 |  |  | 2-94 |  |  | D3A D3B PT | KV | D3A D3B 350 BUS #3 PT 電壓(22KV) | kV_-18_18(-2000_2000) | aca | B3/D27_A1 | [8 empty] | 鹽行DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | KV21 | A | 鹽21線F1 KV21 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽21線A0 | 11KV鹽21線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | KV22 | A | 鹽22線F2 KV22 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽22線A0 | 11KV鹽22線 N相AMP | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | KV23 | A | 鹽23線F3 KV23 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽23線A0 | 11KV鹽23線 N相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | KV24 | A | 鹽24線F4 KV24 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽24線A0 | 11KV鹽24線 N相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | KV25 | A | 鹽25線F5 KV25 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽25線A0 | 11KV鹽25線 N相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | KV26 | A | 鹽26線F6 KV26 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽26線A0 | 11KV鹽26線 N相AMP | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | KV27 | A | 鹽27線F7 KV27 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽27線A0 | 11KV鹽27線 N相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | KV28 | A | 鹽28線F8 KV28 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽28線A0 | 11KV鹽28線 N相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | KV29 | A | 鹽29線F9 KV29 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽29線A0 | 11KV鹽29線 N相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | KV30 | A | 鹽30線F10 KV30 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽30線A0 | 11KV鹽30線 N相AMP | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | KV31 | A | 鹽31線F11 KV31 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽31線A0 | 11KV鹽31線 N相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | KV32 | A | 鹽32線F12 KV32 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽32線A0 | 11KV鹽32線 N相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | KV33 | A | 鹽33線F13 KV33 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽33線A0 | 11KV鹽33線 N相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | KV34 | A | 鹽34線F14 KV34 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽34線A0 | 11KV鹽34線 N相AMP | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | KV71 | A | 鹽71線F15 KV71 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽71線A0 | 23KV鹽71線 N相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | KV72 | A | 鹽72線F16 KV72 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽72線A0 | 23KV鹽72線 N相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | KV73 | A | 鹽73線F17 KV73 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽73線A0 | 23KV鹽73線 N相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | KV74 | A | 鹽74線F18 KV74 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽74線A0 | 23KV鹽74線 N相AMP | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | KV75 | A | 鹽75線F19 KV75 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽75線A0 | 23KV鹽75線 N相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | KV76 | A | 鹽76線F20 KV76 零相電流 | A_-600_600(-2000_2000) |  | B2/D27_D1 | [8 empty] | 鹽行DS.鹽76線A0 | 23KV鹽76線 N相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0169 |  |  | 2-A9 |  |  | D1B BUS PT | KV | D1B 320 BUS #1B PT 電壓(11KV) | kV_-9_9(-2000_2000) | baa | B3/D27_A1 | [8 empty] | 鹽行DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 320 | MW | D1B 320 瓦 | MW_-54_54(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 320 | MVAR | D1B 320 乏 | MVAR_-36_36(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 320 | A | D1B 320 R相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 320 | A | D1B 320 S相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 320 | A | D1B 320 T相電流 | A_-3000_3000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 300 | A | 300 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_300_A1 | 11KV 300 R相AMP | TIE | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 300 | A | 300 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_300_A2 | 11KV 300 S相AMP | TIE | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 300 | A | 300 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_300_A3 | 11KV 300 T相AMP | TIE | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 400 | A | 400 R相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 400 | A | 400 S相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 400 | A | 400 T相電流 | A_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/D27_A1 | [8 empty] | 鹽行DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/1Bus | L/P02D27/T2 |  |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 1530 | ON/OFF | 安南鹽行線 1530 CB |  | aaaa | B2/D27_A1 | [8 empty] | 鹽行DS.1530_CB | 1530(安南鹽行線) CB | LINE161 | [5 empty] | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1530 | 87A | 安南鹽行線 1530 87 RY |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_87A | 安南鹽行線(1530) 87RY | LINE161 | [5 empty] | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 1530 | PHA | 安南鹽行線 1530 PHA相間 RY |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_PHA | 安南鹽行線(1530) 相間RY | LINE161 | [5 empty] | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 1530 | GDA | 安南鹽行線 1530 GDA接地 RY |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_GDA | 安南鹽行線(1530) 接地RY | LINE161 | [5 empty] | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/2Bus | L/D27TN16W/T2 |  |  | 0005 |  | 0002 | 1-00-05 |  | 1-02 | 1540 | ON/OFF | 山上盬行豐華白線 1540 CB |  | abba | B2/D27_A1 | [8 empty] | 鹽行DS.1540_CB | 1540(山上豐華白線) CB | LINE161 | [5 empty] | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1540 | 87A1 | 山上盬行豐華白線 1540 87 RY A1 |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_87A1 | 山上豐華白線(1540) #1 87RY | LINE161 | [5 empty] | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1540 | 87A2 | 山上盬行豐華白線 1540 87 RY A2 |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_87A2 | 山上豐華白線(1540) #2 87RY | LINE161 | [5 empty] | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1540 | PHA | 山上盬行豐華白線 1540 PHA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_PHA | 山上豐華白線(1540) 相間RY | LINE161 | [5 empty] | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1540 | GDA | 山上盬行豐華白線 1540 GDA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_GDA | 山上豐華白線(1540) 接地RY | LINE161 | [5 empty] | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | 12B_87A |  |  | Status | #1#2 BUS 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 161KV BUS | 87BA | 161KV BUS 87BA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161BUS_87A | 161KV BUS 87RY | BUS | [5 empty] | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/1Bus | T/1DTR |  |  | 0037 |  | 0010 | 1-04-05 |  | 1-0A | 1750 | ON/OFF | #1DTR 1750 CB |  | aabb | ELEM/D27_A1 | [8 empty] | 鹽行DS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | #1DTR | 87A 1 | #1DTR 第一套87RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_87A1 | #1DTR 第一套87RY | OTHER | [5 empty] | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | #1DTR | 51ZA | #1DTR 51Z RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | #1DTR | PHA | #1DTR 1750 PHA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.#1DTR_51A | #1DTR 51RY | MTR | [5 empty] | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | #1DTR | GDA | #1DTR 1750 GDA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.#1DTR_51NA | #1DTR 51N RY | MTR | [5 empty] | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0043 |  | 0016 | 1-05-03 |  | 1-10 | 310 | ON/OFF | D1A 310 CB |  | aaba | ELEM/D27_A1 | [8 empty] | 鹽行DS.310_CB | 310(#1DTR) CB | MTR | [5 empty] | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 310 | PHA | D1A 310 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.310_PHA | #1DTR二次側(310) PHA | OTHER | [5 empty] | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 310 | GDA | D1A 310 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.310_GDA | #1DTR二次側(310) GDA | OTHER | [5 empty] | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbM | B/2Bus | T/2DTR |  |  | 0047 |  | 0011 | 1-05-07 |  | 1-0B | 1760 | ON/OFF | #2DTR 1760 CB |  | abcb | ELEM/D27_A1 | [8 empty] | 鹽行DS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #2DTR | 87A 1 | #2DTR 第一套87RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_87A1 | #2DTR 第一套87RY | OTHER | [5 empty] | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | #2DTR | 51ZA | #2DTR 51Z RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #2DTR | PHA | #2DTR 1760 PHA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2DTR | GDA | #2DTR 1760 GDA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0053 |  | 0032 | 1-06-05 |  | 1-20 | 340 | ON/OFF | D2B 340 CB |  | bbba | ELEM/D27_A1 | [8 empty] | 鹽行DS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | 340 | PHA | D2B 340 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.340_PHA | #2DTR二次側(340) PHA | OTHER | [5 empty] | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0055 |  | 0033 | 1-06-07 |  | 1-21 | 330 | ON/OFF | D2A 330 CB |  | abga | ELEM/D27_A1 | [8 empty] | 鹽行DS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 330 | PHA | D2A 330 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.330_PHA | #2DTR二次側(330) PHA | OTHER | [5 empty] | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbR | B/2Bus | T/3DTR |  |  | 0057 |  | 0012 | 1-07-01 |  | 1-0C | 1770 | ON/OFF | #3DTR 1770 CB |  | abdb | ELEM/D27_A1 | [8 empty] | 鹽行DS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #3DTR | 87A 1 | #3DTR 第一套87RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_87A1 | #3DTR 第一套87RY | MTR | [5 empty] | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #3DTR | 96PA | #3DTR 機械保護動作(96PA) |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #3DTR | 51ZA | #3DTR 51Z RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | #3DTR | PHA | #3DTR 1770 PHA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.#3DTR_PHA | #3DTR PHA | MTR | [5 empty] | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | #3DTR | GDA | #3DTR 1770 GDA |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.#3DTR_GDA | #3DTR GDA | MTR | [5 empty] | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/3DTR(A)^T/3DTR(B) |  |  | 0063 |  | 0048 | 1-07-07 |  | 1-30 | 350 | ON/OFF | D3 350 CB |  | acka | ELEM/D27_A1 | [8 empty] | 鹽行DS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 350 | PHA | D3 350 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.350_PHA | #3DTR二次側(350) PHA | MTR | [5 empty] | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 350 | #3DTR(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 350 | GDA | D3 350 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.350_GDA | #3DTR二次側(350) GDA | OTHER | [5 empty] | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | RY 盤 | A/N | RCA線路復閉電驛監視 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/D27_A1 | [16 empty] | 311 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | #1DTR | 86A | #1DTR 86RY(50/50N/51Z/87/96併接) |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  | 0180 | 1-09-01 |  | 2-34 | #1DTR | 81A | #1DTR 81RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_81AS | #1DTR 81RY動作/復歸 | OTHER | [5 empty] | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | #1DTR | 87A2 | #1DTR 第二套87RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_87A2 | #1DTR 第二套87RY | OTHER | [5 empty] | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | #2DTR | 86A | #2DTR 86RY(50/50N/51Z/87/96併接) |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  | 0185 | 1-09-04 |  | 2-39 | #2DTR | 81A | #2DTR 81RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_81AS | #2DTR 81RY動作/復歸 | OTHER | [5 empty] | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #2DTR | 87A2 | #2DTR 第二套87RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_87A2 | #2DTR 第二套87RY | OTHER | [5 empty] | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | #3DTR | 86A | #3DTR 86RY(50/50N/51Z/87/96併接) |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | [5 empty] | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  | 0136 | 1-09-07 |  | 2-08 | #3DTR | 81A | #3DTR 81RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_81AS | #3DTR 81RY動作/復歸 | OTHER | [5 empty] | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | #3DTR | 87A 2 | #3DTR 第二套87RY |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_87A2 | #3DTR 第二套87RY | OTHER | [5 empty] | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0081 |  | 0049 | 1-0A-01 |  | 1-31 | 320 | ON/OFF | D1B 320 CB |  | baaa | ELEM/D27_A1 | [8 empty] | 鹽行DS.320_CB | 320(#1DTR) CB | MTR | [5 empty] | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 320 | PHA | D1B 320 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.320_PHA | #1DTR二次側(320) PHA | OTHER | [5 empty] | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 320 | GDA | D1B 320 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.320_GDA | #1DTR二次側(320) GDA | OTHER | [5 empty] | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 330 | GDA | D2A 330 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.330_GDA | #2DTR二次側(330) GDA | OTHER | [5 empty] | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 340 | GDA | D2B 340 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.340_GDA | #2DTR二次側(340) GDA | OTHER | [5 empty] | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0086 |  | 0050 | 1-0A-06 |  | 1-32 | 390 | ON/OFF | D1A 390 CB |  | aagb | B3/D27_A1 | [8 empty] | 鹽行DS.390_CB | 390(#1SSTR) CB | OTHER | [5 empty] | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 390 | PHA | D1A 390 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1SSTR_51A | #1SSTR 51RY | OTHER | [5 empty] | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 390 | #1SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 390 | GDA | D1A 390 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | [5 empty] | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | T/2SSTR |  |  | 0089 |  | 0051 | 1-0B-01 |  | 1-33 | 490 | ON/OFF | D3 490 CB |  | acbb | B3/D27_A1 | [8 empty] | 鹽行DS.490_CB | 490(#2SSTR) CB | OTHER | [5 empty] | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 490 | PHA | D3 490 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2SSTR_51A | #2SSTR 51RY | OTHER | [5 empty] | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 490 | GDA | D3 490 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/400 |  |  | 0092 |  | 0052 | 1-0B-04 |  | 1-34 | 300 | ON/OFF | D1B 300 CB |  | bafb | B3/D27_A1 | [8 empty] | 鹽行DS.300_CB | 300(TIE) CB | TIE | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 300 | PHA | D1B 300 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.300_51A | 11KV TIE(300) 51RY | TIE | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 300 | TIE(300) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 300 | GDA | D1B 300 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.300_51NA | 11KV TIE(300) 51N RY | TIE | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/300 |  |  | 0095 |  | 0053 | 1-0B-07 |  | 1-35 | 400 | ON/OFF | D2B 400 CB |  | bbab | B3/D27_A1 | [8 empty] | 鹽行DS.400_CB | 400(TIE) CB | TIE | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 400 | PHA | D2B 400 CB PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.400_51A | 11KV TIE(400) 51RY | TIE | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 400 | TIE(400) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 400 | GDA | D2B 400 CB GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.400_51NA | 11KV TIE(400) 51N RY | TIE | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0160 |  | 0018 | 1-14-00 |  | 1-12 | 210 | CB ON/OFF | #1SC 210 CB |  | aacb | B3/D27_A1 | [8 empty] | 鹽行DS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 210 | SCA | #1SC 210 51/51N RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | 210 | UVA | #1SC 210 27/59 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KV21/T1 |  |  | 0163 |  | 0019 | 1-14-03 |  | 1-13 | KV 21 | CB ON/OFF | 鹽21線 F1 KV 21 CB |  | aadb | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_CB | KV21(11KV鹽21線) CB | FEEDER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | KV 21 | PHA | 鹽21線 F1 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_PHA | 11KV鹽21線(KV21) 相間RY | FEEDER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-14-05 |  |  | KV 21 | GDA | 鹽21線 F1 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_GDA | 11KV鹽21線(KV21) 接地RY | FEEDER | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KV22/T1 |  |  | 0166 |  | 0020 | 1-14-06 |  | 1-14 | KV 22 | CB ON/OFF | 鹽22線 F2 KV 22 CB |  | aaeb | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_CB | KV22(11KV鹽22線) CB | FEEDER | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-14-07 |  |  | KV 22 | PHA | 鹽22線 F2 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_PHA | 11KV鹽22線(KV22) 相間RY | FEEDER | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | KV 22 | GDA | 鹽22線 F2 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_GDA | 11KV鹽22線(KV22) 接地RY | FEEDER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/KV23/T1 |  |  | 0169 |  | 0021 | 1-15-01 |  | 1-15 | KV23 | CB ON/OFF | 鹽23線 F3 KV23 CB |  | aafb | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_CB | KV23(11KV鹽23線) CB | FEEDER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | KV23 | PHA | 鹽23線 F3 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_PHA | 11KV鹽23線(KV23) 相間RY | FEEDER | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | KV23 | GDA | 鹽23線 F3 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_GDA | 11KV鹽23線(KV23) 接地RY | FEEDER | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KV24/T1 |  |  | 0172 |  | 0022 | 1-15-04 |  | 1-16 | KV 24 | CB ON/OFF | 鹽24線 F4 KV 24 CB |  | babb | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_CB | KV24(11KV鹽24線) CB | FEEDER | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-15-05 |  |  | KV 24 | PHA | 鹽24線 F4 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_PHA | 11KV鹽24線(KV24) 相間RY | FEEDER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-15-06 |  |  | KV 24 | GDA | 鹽24線 F4 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_GDA | 11KV鹽24線(KV24) 接地RY | FEEDER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KV25/T1 |  |  | 0175 |  | 0023 | 1-15-07 |  | 1-17 | KV 25 | CB ON/OFF | 鹽25線 F5 KV 25 CB |  | bacb | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_CB | KV25(11KV鹽25線) CB | FEEDER | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | KV 25 | PHA | 鹽25線 F5 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_PHA | 11KV鹽25線(KV25) 相間RY | FEEDER | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | KV 25 | GDA | 鹽25線 F5 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_GDA | 11KV鹽25線(KV25) 接地RY | FEEDER | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/KV26/T1 |  |  | 0178 |  | 0024 | 1-16-02 |  | 1-18 | KV 26 | CB ON/OFF | 鹽26線 F6 KV 26 CB |  | badb | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_CB | KV26(11KV鹽26線) CB | FEEDER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0179 |  |  | 1-16-03 |  |  | KV 26 | PHA | 鹽26線 F6 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_PHA | 11KV鹽26線(KV26) 相間RY | FEEDER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 1-16-04 |  |  | KV 26 | GDA | 鹽26線 F6 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_GDA | 11KV鹽26線(KV26) 接地RY | FEEDER | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0181 |  | 0025 | 1-16-05 |  | 1-19 | 220 | CB ON/OFF | #2SC 220 CB |  | baeb | B3/D27_A1 | [8 empty] | 鹽行DS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0182 |  |  | 1-16-06 |  |  | 220 | SCA | #2SC 220 51/51N RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 220 | UVA | #2SC 220 27/59 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/200 |  |  | 0184 |  | 0026 | 1-17-00 |  | 1-1A | 100 | CB ON/OFF | D1A 100 CB |  | aahb | B3/D27_A1 | [8 empty] | 鹽行DS.100_CB | 100(TIE) CB | TIE | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | 100 | PHA | D1A 100 PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 100 | GDA | D1A 100 GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KV27/T1 |  |  | 0187 |  | 0027 | 1-17-03 |  | 1-1B | KV 27 | CB ON/OFF | 鹽27線 F7 KV 27 CB |  | bbcb | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_CB | KV27(11KV鹽27線) CB | FEEDER | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | KV 27 | PHA | 鹽27線 F7 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_PHA | 11KV鹽27線(KV27) 相間RY | FEEDER | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 |  |  | 1-17-05 |  |  | KV 27 | GDA | 鹽27線 F7 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_GDA | 11KV鹽27線(KV27) 接地RY | FEEDER | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KV28/T1 |  |  | 0190 |  | 0028 | 1-17-06 |  | 1-1C | KV 28 | CB ON/OFF | 鹽28線 F8 KV 28 CB |  | bbeb | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_CB | KV28(11KV鹽28線) CB | FEEDER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | KV 28 | PHA | 鹽28線 F8 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_PHA | 11KV鹽28線(KV28) 相間RY | FEEDER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 |  |  | 1-18-00 |  |  | KV 28 | GDA | 鹽28線 F8 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_GDA | 11KV鹽28線(KV28) 接地RY | FEEDER | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KV29/T1 |  |  | 0193 |  | 0029 | 1-18-01 |  | 1-1D | KV 29 | ON/OFF | 鹽29線 F9 KV 29 CB |  | bbfb | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_CB | KV29(11KV鹽29線) CB | FEEDER | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | KV 29 | PHA | 鹽29線 F9 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_PHA | 11KV鹽29線(KV29) 相間RY | FEEDER | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | KV 29 | GDA | 鹽29線 F9 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_GDA | 11KV鹽29線(KV29) 接地RY | FEEDER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/KV30/T1 |  |  | 0196 |  | 0030 | 1-18-04 |  | 1-1E | KV30 | ON/OFF | 鹽30線 F10 KV 30 CB |  | bbgb | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_CB | KV30(11KV鹽30線) CB | FEEDER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | KV30 | PHA | 鹽30線 F10 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_PHA | 11KV鹽30線(KV30) 相間RY | FEEDER | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | KV30 | GDA | 鹽30線 F10 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_GDA | 11KV鹽30線(KV30) 接地RY | FEEDER | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0199 |  | 0031 | 1-18-07 |  | 1-1F | 240 | ON/OFF | #4SC 240 CB |  | bbhb | B3/D27_A1 | [8 empty] | 鹽行DS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 240 | SCA | #4SC 240 51/51N RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 240 | UVA | #4SC 240 27/59 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0202 |  | 0034 | 1-19-02 |  | 1-22 | 230 | ON/OFF | #3SC 230 CB |  | abab | B3/D27_A1 | [8 empty] | 鹽行DS.230_CB | 230(11KV #3SC) CB | SC | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 230 | SCA | #3SC 230 51/51N RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | 230 | UVA | #3SC 230 27/59 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KV31/T1 |  |  | 0205 |  | 0035 | 1-19-05 |  | 1-23 | KV 31 | ON/OFF | 鹽31線 F11 KV 31 CB |  | abbb | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_CB | KV31(11KV鹽31線) CB | FEEDER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | KV 31 | PHA | 鹽31線 F11 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_PHA | 11KV鹽31線(KV31) 相間RY | FEEDER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | KV 31 | GDA | 鹽31線 F11 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_GDA | 11KV鹽31線(KV31) 接地RY | FEEDER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KV32/T1 |  |  | 0208 |  | 0036 | 1-1A-00 |  | 1-24 | KV32 | ON/OFF | 鹽32線 F12 KV 32 CB |  | abcb | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_CB | KV32(11KV鹽32線) CB | FEEDER | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | KV32 | PHA | 鹽32線 F12 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_PHA | 11KV鹽32線(KV32) 相間RY | FEEDER | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | KV32 | GDA | 鹽32線 F12 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_GDA | 11KV鹽32線(KV32) 接地RY | FEEDER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KV33/T1 |  |  | 0211 |  | 0037 | 1-1A-03 |  | 1-25 | KV33 | ON/OFF | 鹽33線 F13 KV33 CB |  | abdb | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_CB | KV33(11KV鹽33線) CB | FEEDER | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | KV33 | PHA | 鹽33線 F13 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_PHA | 11KV鹽33線(KV33) 相間RY | FEEDER | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | KV33 | GDA | 鹽33線 F13 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_GDA | 11KV鹽33線(KV33) 接地RY | FEEDER | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/KV34/T1 |  |  | 0214 |  | 0038 | 1-1A-06 |  | 1-26 | KV34 | ON/OFF | 鹽34線 F14 KV34 CB |  | abfb | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_CB | KV34(11KV鹽34線) CB | FEEDER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | KV34 | PHA | 鹽34線 F14 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_PHA | 11KV鹽34線(KV34) 相間RY | FEEDER | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | KV34 | GDA | 鹽34線 F14 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_GDA | 11KV鹽34線(KV34) 接地RY | FEEDER | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/100 |  |  | 0217 |  | 0039 | 1-1B-01 |  | 1-27 | 200 | ON/OFF | D2A200 CB |  | abhb | B3/D27_A1 | [8 empty] | 鹽行DS.200_CB | 200(TIE) CB | TIE | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 200 | PHA | D2A200 PHA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.200_51A | 11KV TIE(200) 51RY | TIE | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 200 | GDA | D2A200 GDA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.200_51NA | 11KV TIE(200) 51N RY | TIE | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/6SC |  |  | 0220 |  | 0040 | 1-1B-04 |  | 1-28 | 260 | ON/OFF | #6SC 260 CB |  | accb | B3/D27_A1 | [8 empty] | 鹽行DS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 260 | SCA | #6SC 260 51/51 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 260 | UVA | #6SC 260 27/59 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KV71/T1 |  |  | 0223 |  | 0041 | 1-1B-07 |  | 1-29 | KV71 | ON/OFF | 鹽71線 F15 CB |  | acdb | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_CB | KV71(23KV鹽71線) CB | FEEDER | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 |  |  | 1-1C-00 |  |  | KV71 | PHA | 鹽71線F15 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_PHA | 23KV鹽71線(KV71) 相間RY | FEEDER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | KV71 | GDA | 鹽71線F15 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_GDA | 23KV鹽71線(KV71) 接地RY | FEEDER | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KV72/T1 |  |  | 0226 |  | 0042 | 1-1C-02 |  | 1-2A | KV72 | ON/OFF | 鹽72線F16 |  | aceb | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_CB | KV72(23KV鹽72線) CB | FEEDER | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | KV72 | PHA | 鹽72線F16 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_PHA | 23KV鹽72線(KV72) 相間RY | FEEDER | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | KV72 | GDA | 鹽72線F16 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_GDA | 23KV鹽72線(KV72) 接地RY | FEEDER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KV73/T1 |  |  | 0229 |  | 0043 | 1-1C-05 |  | 1-2B | KV73 | ON/OFF | 鹽73線 F17 KV 73 CB |  | acfb | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_CB | KV73(23KV鹽73線) CB | FEEDER | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | KV73 | PHA | 鹽73線F17 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_PHA | 23KV鹽73線(KV73) 相間RY | FEEDER | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | KV73 | GDA | 鹽73線F17 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_GDA | 23KV鹽73線(KV73) 接地RY | FEEDER | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KV74/T1 |  |  | 0232 |  | 0044 | 1-1D-00 |  | 1-2C | KV74 | ON/OFF | 鹽74線 F18 KV74 CB |  | acgb | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_CB | KV74(23KV鹽74線) CB | FEEDER | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | KV74 | PHA | 鹽74線F18 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_PHA | 23KV鹽74線(KV74) 相間RY | FEEDER | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | KV74 | GDA | 鹽74線F18 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_GDA | 23KV鹽74線(KV74) 接地RY | FEEDER | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KV75/T1 |  |  | 0235 |  | 0045 | 1-1D-03 |  | 1-2D | KV75 | ON/OFF | 鹽75線F19 KV75 CB |  | achb | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_CB | KV75(23KV鹽75線) CB | FEEDER | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 |  |  | 1-1D-04 |  |  | KV75 | PHA | 鹽75線F19 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_PHA | 23KV鹽75線(KV75) 相間RY | FEEDER | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | KV75 | GDA | 鹽75線F19 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_GDA | 23KV鹽75線(KV75) 接地RY | FEEDER | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/3Bus | L/KV76/T1 |  |  | 0238 |  | 0046 | 1-1D-06 |  | 1-2E | KV76 | ON/OFF | 鹽76線 F20 KV76 CB |  | acib | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_CB | KV76(23KV鹽76線) CB | FEEDER | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | KV76 | PHA | 鹽76線F20 PHA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_PHA | 23KV鹽76線(KV76) 相間RY | FEEDER | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | KV76 | GDA | 鹽76線F20 GDA |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_GDA | 23KV鹽76線(KV76) 接地RY | FEEDER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3Bus | C/5SC |  |  | 0241 |  | 0047 | 1-1E-01 |  | 1-2F | 250 | ON/OFF | #5SC 250 CB |  | acjb | B3/D27_A1 | [8 empty] | 鹽行DS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 250 | SCA | #5SC 250 51/51N RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 250 | UVA | #5SC 250 27/59 RY |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | ComPoint |  |  | 81AS1 | KV27~KV30 |  | Status | 81RY A/S(1) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  | 1-00 | KV27-KV30 | 81 RY | #340 81 RY KV27~KV30 |  |  | B3/D27_A1 | [16 empty] | 422 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | ComPoint |  |  | 81AS2 | KV31~KV34 |  | Status | 81RY A/S(2) | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0245 |  | 0159 | 1-1E-05 |  | 2-1F | KV31-KV34 | 81 RY | #330 81 RY KV31~KV34 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.81RY_A/S(2) | K31-K34低頻電驛動作/復歸 | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
D27 | 鹽行DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 鹽行DS.TEST_CB | TEST CB | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU | L/R | LOCAL/REMOTE(SUPY) |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0064 | 1-30-02 |  | 1-40 | 1530 | U/L | 安南鹽行線 1530 87 RY U/L |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_87UL | 安南鹽行線(1530) 87RY U/L | LINE161 | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0065 | 1-30-03 |  | 1-41 | 1530 | U/L | 安南鹽行線 1530 79 RY U/L |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_79UL | 安南鹽行線(1530) 79RY U/L | LINE161 | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0066 | 1-30-04 |  | 1-42 | 1540 | U/L | 山上盬行豐華白線 1540 #1 87RY U/L |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_87UL1 | 山上豐華白線(1540) #1 87RY U/L | LINE161 | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  | 0067 | 1-30-05 |  | 1-43 | 1540 | U/L | 山上盬行豐華白線 1540 79 RY U/L |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_79UL | 山上豐華白線(1540) 79RY U/L | LINE161 | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | #1DTR | 96D | #1DTR 96D |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | #1DTR | 96P | #1DTR 96P |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0522 |  |  | 1-30-10 |  |  | #1DTR | 63Q | #1DTR 63Q |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0523 |  |  | 1-30-11 |  |  | #1DTR | 96B1 | #1DTR 96B1 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | #1DTR | 96B2 | #1DTR 96B2 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 1540 | 87CFA | 山上盬行豐華白線 87CFA (通訊故障) |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_87CFA | 山上豐華白線(1540)87RY通訊故障 | OTHER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-30-14 |  |  | 1540 | RYFA | 山上盬行豐華白線 RYFA(電驛故障) |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_RYFA | 山上豐華白線(1540)數位電驛故障 | OTHER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0527 |  | 0070 | 1-30-15 |  | 1-46 | 1540 | U/L | 山上盬行豐華白線 1540 #2 87RY U/L |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1540_87UL2 | 山上豐華白線(1540) #2 87RY U/L | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0528 |  | 0108 | 1-31-00 |  | 1-6C | KV21 | U/L | 鹽21線F1 KV21 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_ADJ | 11KV鹽21線(KV21) LCO分流器 U/L | FEEDER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0529 |  | 0109 | 1-31-01 |  | 1-6D | KV22 | U/L | 鹽22線F2 KV22 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_ADJ | 11KV鹽22線(KV22) LCO分流器 U/L | FEEDER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0530 |  | 0110 | 1-31-02 |  | 1-6E | KV23 | U/L | 鹽23線F3 KV23 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_ADJ | 11KV鹽23線(KV23) LCO分流器 U/L | FEEDER | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0531 |  | 0111 | 1-31-03 |  | 1-6F | KV24 | U/L | 鹽24線F4 KV24 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_ADJ | 11KV鹽24線(KV24) LCO分流器 U/L | FEEDER | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0532 |  | 0112 | 1-31-04 |  | 1-70 | KV25 | U/L | 鹽25線F5 KV25 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_ADJ | 11KV鹽25線(KV25) LCO分流器 U/L | FEEDER | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0533 |  | 0113 | 1-31-05 |  | 1-71 | KV26 | U/L | 鹽26線F6 KV26 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_ADJ | 11KV鹽26線(KV26) LCO分流器 U/L | FEEDER | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0534 |  | 0114 | 1-31-06 |  | 1-72 | KV27 | U/L | 鹽27線F7 KV27 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_ADJ | 11KV鹽27線(KV27) LCO分流器 U/L | FEEDER | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0535 |  | 0115 | 1-31-07 |  | 1-73 | KV28 | U/L | 鹽28線F8 KV28 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_ADJ | 11KV鹽28線(KV28) LCO分流器 U/L | FEEDER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0536 |  | 0116 | 1-31-08 |  | 1-74 | KV29 | U/L | 鹽29線F9 KV29 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_ADJ | 11KV鹽29線(KV29) LCO分流器 U/L | FEEDER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0537 |  | 0117 | 1-31-09 |  | 1-75 | KV30 | U/L | 鹽30線F10 KV30 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_ADJ | 11KV鹽30線(KV30) LCO分流器 U/L | FEEDER | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0538 |  | 0118 | 1-31-10 |  | 1-76 | KV31 | U/L | 鹽31線F11 KV31 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_ADJ | 11KV鹽31線(KV31) LCO分流器 U/L | FEEDER | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0539 |  | 0119 | 1-31-11 |  | 1-77 | KV32 | U/L | 鹽32線F12 KV32 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_ADJ | 11KV鹽32線(KV32) LCO分流器 U/L | FEEDER | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0540 |  | 0120 | 1-31-12 |  | 1-78 | KV33 | U/L | 鹽33線F13 KV33 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_ADJ | 11KV鹽33線(KV33) LCO分流器 U/L | FEEDER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0541 |  | 0121 | 1-31-13 |  | 1-79 | KV34 | U/L | 鹽34線F14 KV34 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_ADJ | 11KV鹽34線(KV34) LCO分流器 U/L | FEEDER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0542 |  | 0122 | 1-31-14 |  | 1-7A | KV71 | U/L | 鹽71線F15 KV71 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_ADJ | 23KV鹽71線(KV71) LCO分流器 U/L | FEEDER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0543 |  | 0123 | 1-31-15 |  | 1-7B | KV72 | U/L | 鹽72線F16 KV72 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_ADJ | 23KV鹽72線(KV72) LCO分流器 U/L | FEEDER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0544 |  | 0124 | 1-32-00 |  | 1-7C | KV73 | U/L | 鹽73線F17 KV73 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_ADJ | 23KV鹽73線(KV73) LCO分流器 U/L | FEEDER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0545 |  | 0125 | 1-32-01 |  | 1-7D | KV74 | U/L | 鹽74線F18 KV74 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_ADJ | 23KV鹽74線(KV74) LCO分流器 U/L | FEEDER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0546 |  | 0126 | 1-32-02 |  | 1-7E | KV75 | U/L | 鹽75線F19 KV75 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_ADJ | 23KV鹽75線(KV75) LCO分流器 U/L | FEEDER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0547 |  | 0127 | 1-32-03 |  | 1-7F | KV76 | U/L | 鹽76線F20 KV76 LCO分流器 |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_ADJ | 23KV鹽76線(KV76) LCO分流器 U/L | FEEDER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D27 | 鹽行DS | 0 |  | ComPoint |  |  | RYFA | 低頻電驛故障 |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | RYFA | A/N | 低頻電驛故障 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.FEEDER_81RYFA | 饋線低頻電驛故障 | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | Locate Empty | PMA | POWER METER 故障 |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | 161kV BUS | RYFA | 161KV BUS數位電驛故障 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA |  | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0551 |  |  | 1-32-07 |  |  | 161kV BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161KV_BUS_CTFA | 161KV BUS CT迴路故障 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | 12B_87UL |  |  | Status | #1#2 BUS 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0552 |  | 0060 | 1-32-08 |  | 1-3C | 161kV BUS | U/L | 161KV BUS╴87UL |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161BUS_87UL | 161KV BUS 87RY U/L | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0182 | 1-32-10 |  | 2-36 | #1DTR | U/L | #1DTR 第一套87RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_87UL1 | #1DTR 87RY1 U/L | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | #1ADTR | R/L | #1ADTR OLTC R/L |  | c | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0556 |  | 0096 | 1-32-12 |  | 1-60 | #1ADTR | A/M | #1ADTR OLTC A/M |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0557 |  |  | 1-32-13 |  |  | #1DTR | A/N | #1DTR TRA |  | a | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | #1DTR | A/N | #1DTR TRF |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0559 |  |  | 1-32-15 |  |  | #1BDTR | R/L | #1BDTR OLTC R/L |  | b | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0560 |  | 0098 | 1-33-00 |  | 1-62 | #1BDTR | A/M | #1BDTR OLTC A/M |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0561 |  | 0187 | 1-33-01 |  | 2-3B | #2DTR | U/L | #2DTR 第一套87RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_87UL1 | #2DTR 87RY1 U/L | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | #2ADTR | R/L | #2ADTR OLTC R/L |  | c | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0563 |  | 0100 | 1-33-03 |  | 1-64 | #2ADTR | A/M | #2ADTR OLTC A/M |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0564 |  |  | 1-33-04 |  |  | #2DTR | A/N | #2DTR TRA |  | a | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | #2DTR | A/N | #2DTR TRF |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | #2BDTR | R/L | #2BDTR OLTC R/L |  | b | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0567 |  | 0102 | 1-33-07 |  | 1-66 | #2BDTR | A/M | #2BDTR OLTC A/M |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0568 |  | 0138 | 1-33-08 |  | 2-0A | #3DTR | U/L | #3DTR 第一套87RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_87UL1 | #3DTR 第一套87RY U/L | OTHER | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 3DTR(A) | #3DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | #3ADTR | R/L | #3ADTR OLTC R/L |  | c | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS |  |  | 3DTR(A) | #3DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0570 |  | 0104 | 1-33-10 |  | 1-68 | #3ADTR | A/M | #3ADTR OLTC A/M |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0571 |  |  | 1-33-11 |  |  | #3DTR | A/N | #3DTR TRA |  | a | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | #3DTR | A/N | #3DTR TRF |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR(B) | #3DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | #3BDTR | R/L | #3BDTR OLTC R/L |  | b | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS |  |  | 3DTR(B) | #3DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0574 |  | 0106 | 1-33-14 |  | 1-6A | #3BDTR | A/M | #3BDTR OLTC A/M |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0832 |  |  | 2-30-00 |  |  | #2DTR | 96D | #2DTR 96D |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0833 |  |  | 2-30-01 |  |  | #2DTR | 96P | #2DTR 96P |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0834 |  |  | 2-30-02 |  |  | #2DTR | 63Q | #2DTR 63Q |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0835 |  |  | 2-30-03 |  |  | #2DTR | 96B1 | #2DTR 96B1 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0836 |  |  | 2-30-04 |  |  | #2DTR | 96B2 | #2DTR 96B2 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0837 |  |  | 2-30-05 |  |  | #3DTR | 96D | #3DTR 96D |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0838 |  |  | 2-30-06 |  |  | #3DTR | 96P | #3DTR 96P |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0839 |  |  | 2-30-07 |  |  | #3DTR | 63Q | #3DTR 63Q |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 2-30-08 |  |  | #3DTR | 96B1 | #3DTR 96B1 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0841 |  |  | 2-30-09 |  |  | #3DTR | 96B2 | #3DTR 96B2 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0842 |  | 0160 | 2-30-10 |  | 2-20 | KV21 | U/L | 鹽21線F1 KV21 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV21_79UL | 11KV鹽21線(KV21) 79RY U/L | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0843 |  | 0161 | 2-30-11 |  | 2-21 | KV22 | U/L | 鹽22線F2 KV22 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV22_79UL | 11KV鹽22線(KV22) 79RY U/L | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0844 |  | 0162 | 2-30-12 |  | 2-22 | KV23 | U/L | 鹽23線F3 KV23 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV23_79UL | 11KV鹽23線(KV23) 79RY U/L | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0845 |  | 0163 | 2-30-13 |  | 2-23 | KV24 | U/L | 鹽24線F4 KV24 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV24_79UL | 11KV鹽24線(KV24) 79RY U/L | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0846 |  | 0164 | 2-30-14 |  | 2-24 | KV25 | U/L | 鹽25線F5 KV25 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV25_79UL | 11KV鹽25線(KV25) 79RY U/L | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0847 |  | 0165 | 2-30-15 |  | 2-25 | KV26 | U/L | 鹽26線F6 KV26 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV26_79UL | 11KV鹽26線(KV26) 79RY U/L | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0848 |  | 0166 | 2-31-00 |  | 2-26 | KV27 | U/L | 鹽27線F7 KV27 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV27_79UL | 11KV鹽27線(KV27) 79RY U/L | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0849 |  | 0167 | 2-31-01 |  | 2-27 | KV28 | U/L | 鹽28線F8 KV28 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV28_79UL | 11KV鹽28線(KV28) 79RY U/L | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0850 |  | 0168 | 2-31-02 |  | 2-28 | KV29 | U/L | 鹽29線F9 KV29 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV29_79UL | 11KV鹽29線(KV29) 79RY U/L | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0851 |  | 0169 | 2-31-03 |  | 2-29 | KV30 | U/L | 鹽30線F10 KV30 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV30_79UL | 11KV鹽30線(KV30) 79RY U/L | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0852 |  | 0170 | 2-31-04 |  | 2-2A | KV31 | U/L | 鹽31線F11 KV31 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV31_79UL | 11KV鹽31線(KV31) 79RY U/L | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0853 |  | 0171 | 2-31-05 |  | 2-2B | KV32 | U/L | 鹽32線F12 KV32 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV32_79UL | 11KV鹽32線(KV32) 79RY U/L | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0854 |  | 0172 | 2-31-06 |  | 2-2C | KV33 | U/L | 鹽33線F13 KV33 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV33_79UL | 11KV鹽33線(KV33) 79RY U/L | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0855 |  | 0173 | 2-31-07 |  | 2-2D | KV34 | U/L | 鹽34線F14 KV34 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV34_79UL | 11KV鹽34線(KV34) 79RY U/L | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0856 |  | 0174 | 2-31-08 |  | 2-2E | KV71 | U/L | 鹽71線F15 KV71 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV71_79UL | 23KV鹽71線(KV71) 79RY U/L | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0857 |  | 0175 | 2-31-09 |  | 2-2F | KV72 | U/L | 鹽72線F16 KV72 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV72_79UL | 23KV鹽72線(KV72) 79RY U/L | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0858 |  | 0176 | 2-31-10 |  | 2-30 | KV73 | U/L | 鹽73線F17 KV73 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV73_79UL | 23KV鹽73線(KV73) 79RY U/L | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0859 |  | 0177 | 2-31-11 |  | 2-31 | KV74 | U/L | 鹽74線F18 KV74 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV74_79UL | 23KV鹽74線(KV74) 79RY U/L | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0860 |  | 0178 | 2-31-12 |  | 2-32 | KV75 | U/L | 鹽75線F19 KV75 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV75_79UL | 23KV鹽75線(KV75) 79RY U/L | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0861 |  | 0179 | 2-31-13 |  | 2-33 | KV76 | U/L | 鹽76線F20 KV76 79RY U/L |  |  | B2/D27_D1 | [8 empty] | 鹽行DS.KV76_79UL | 23KV鹽76線(KV76) 79RY U/L | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0862 |  |  | 2-31-14 |  |  | Locate Empty | LOA | 11,23KV LOA 79RY復閉失敗 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.11/23KV_LOA | 11/23KV饋線復閉失敗 | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0864 |  |  | 2-32-00 |  |  | #1DTR | RYFA | #1DTR 數位電驛故障 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_RYFA | #1DTR 數位電驛故障 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0865 |  | 0183 | 2-32-01 |  | 2-37 | #1DTR | U/L | #1DTR 第二套87RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_87UL2 | #1DTR 87RY2 U/L | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0866 |  | 0184 | 2-32-02 |  | 2-38 | #1DTR | U/L | #1DTR 51Z RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_51ZUL | #1DTR 51Z RY U/L | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 1DTR | #1DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0181 | 2-32-03 |  | 2-35 | #1DTR | U/L | #1DTR 81 RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#1DTR_81UL | #1DTR 81RY U/L | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0872 |  |  | 2-32-08 |  |  | 1530 | A/N | 安南鹽行線 1530 RYFA(電驛故障) |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_RYFA | 安南鹽行線(1530)數位電驛故障 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0873 |  |  | 2-32-09 |  |  | 1530 | A/N | 安南鹽行線 1530 87CFA (87L通訊故障) |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1530_87CFA | 安南鹽行線(1530)87RY通訊故障 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0874 |  |  | 2-32-10 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | B3, Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0875 |  |  | 2-32-11 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 保全系統 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0877 |  |  | 2-32-13 |  |  | 保全總機 | A/N | 無人化防盜(1)保全系統 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Door1 | 大小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0880 |  |  | 2-33-00 |  |  | 大小門 | A/N | 無人化門禁(1)大小門 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.無人化門禁(1) | 無人化門禁(1)大小門 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0882 |  | 0154 | 2-33-02 |  | 2-1A | ACB TIE | ON/OFF | 所內電源ACB TIE |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場照明(A) |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0883 |  | 0190 | 2-33-03 |  | 2-3E | 開關場 | ON/OFF | 開關場照明(A) |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明(B) |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0884 |  | 0191 | 2-33-04 |  | 2-3F | 開關場 | ON/OFF | 開關場照明(B) |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D27 | 鹽行DS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0885 |  |  | 2-33-05 |  |  | Locate Empty | A/N | OPA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0886 |  | 0152 | 2-33-06 |  | 2-18 | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0887 |  | 0153 | 2-33-07 |  | 2-19 | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0888 |  |  | 2-33-08 |  |  | M盤 | A/N | 所內欠壓警報 STUV |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | ComPoint |  |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 2-33-09 |  |  | M5盤 | A/N | VUA1 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0893 |  |  | 2-33-13 |  |  | SC 60RY | A/N | 11KV 22KV SC 60A |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0894 |  |  | 2-33-14 |  |  | 充電機 | A/N | 直流電源故障 DCA |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0895 |  |  | 2-33-15 |  |  | RY 盤 | A/N | DCE |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0640 |  |  | 1-34-00 |  |  | 161 KV | A/N | 161KV CBF |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0641 |  |  | 1-34-01 |  |  | 161KV | A/N | 161KV CBA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0642 |  |  | 1-34-02 |  |  | 11KV | A/N | 11KV CBF |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0643 |  |  | 1-34-03 |  |  | 11KV | A/N | 11KV CBA |  |  | ELEM/D27_A1 | [8 empty] | 鹽行DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0644 |  |  | 1-34-04 |  |  | 所內電源 | A/N | ACBA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0645 |  |  | 1-34-05 |  |  | 充電機 | A/N | CHG1 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0646 |  |  | 1-34-06 |  |  | 充電機 | A/N | 通訊充電機故障 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0647 |  |  | 1-34-07 |  |  | 集油池 | A/N | 集油池警報 OWA |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.洩油池水位警報 | 洩油池水位警報 | OTHER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0648 |  |  | 1-34-08 |  |  | 冷氣機 | A/N | 冷氣機警報 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.空調機跳脫警報 | 空調機故障電源跳脫 | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
D27 | 鹽行DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0649 |  |  | 1-34-09 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Water1 | 第一段警報 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0650 |  |  | 1-34-10 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | Water2 | 第二段警報 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0651 |  |  | 1-34-11 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0652 |  |  | 1-34-12 |  |  | 通訊設備 | A/N | 通訊設備 AC故障 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0655 |  |  | 1-34-15 |  |  | 通訊設備 | A/N | 通信室溫控警報 |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0656 |  |  | 1-35-00 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0658 |  |  | 1-35-02 |  |  | #2DTR | RYFA | #2DTR 數位電驛故障 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0659 |  | 0188 | 1-35-03 |  | 2-3C | #2DTR | U/L | #2DTR 第二套87RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_87UL2 | #2DTR 87RY2 U/L | OTHER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0660 |  | 0189 | 1-35-04 |  | 2-3D | #2DTR | U/L | #2DTR 51Z RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 2DTR | #2DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0661 |  | 0186 | 1-35-05 |  | 2-3A | #2DTR | U/L | #2DTR 81 RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#2DTR_81UL | #2DTR 81RY U/L | OTHER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0663 |  |  | 1-35-07 |  |  | #3DTR | RYFA | #3DTR 數位電驛故障 |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0664 |  | 0139 | 1-35-08 |  | 2-0B | #3DTR | U/L | #3DTR 第二套87RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_87UL2 | #3DTR 第二套87RY U/L | OTHER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0665 |  | 0140 | 1-35-09 |  | 2-0C | #3DTR | U/L | #3DTR 51Z RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS |  |  | 3DTR | #3DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0666 |  | 0137 | 1-35-10 |  | 2-09 | #3DTR | U/L | #3DTR 81 RY U/L |  |  | B1/D27_A1 | [8 empty] | 鹽行DS.#3DTR_81UL | #3DTR 81RY U/L | OTHER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0667 |  |  | 1-35-11 |  |  | 310 | U/L | 310 81RY U/L |  |  | B3/D27_A1 | [16 empty] | 560 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0668 |  | 0056 | 1-35-12 |  | 1-38 | 320 | U/L | 320 81RY U/L |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.320_81UL | (320)81RY USE/LOCK | OTHER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0669 |  |  | 1-35-13 |  |  | 330 | U/L | 330 81RY U/L |  |  | B3/D27_A1 | [16 empty] | 562 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0670 |  |  | 1-35-14 |  |  | 340 | U/L | 340 81RY U/L |  |  | B3/D27_A1 | [16 empty] | 563 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 22 | 22KV | 350 | #3DTR(350) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0671 |  |  | 1-35-15 |  |  | 350 | U/L | 350 81RY U/L |  |  | B3/D27_A1 | [16 empty] | 564 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | DS1 | 1531 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0928 | 929 | 0128 | 2-34-00 | 2-34-01 | 2-00 | 1531 | ON/OFF | 安南鹽行線1531 ABS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1531_DS | 1531(安南鹽行線) DS | LINE161 | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | DS2 | 1532 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0930 | 931 | 0129 | 2-34-02 | 2-34-03 | 2-01 | 1532 | ON/OFF | 安南鹽行線1532 ABS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1532_DS | 1532(安南鹽行線) DS | LINE161 | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | ES2 | 1532E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0932 | 933 | 0130 | 2-34-04 | 2-34-05 | 2-02 | 1532E | ON/OFF | 安南鹽行線1532 EABS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1532E_ES | 1532E(安南鹽行線) ES | LINE161 | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | DS1 | 1541 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0936 | 937 | 0132 | 2-34-08 | 2-34-09 | 2-04 | 1541 | ON/OFF | 山上盬行豐華白線 1541 ABS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1541_DS | 1541(山上豐華白線) DS | LINE161 | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | DS2 | 1542 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0938 | 939 | 0133 | 2-34-10 | 2-34-11 | 2-05 | 1542 | ON/OFF | 山上盬行豐華白線 1542 ABS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1542_DS | 1542(山上豐華白線) DS | LINE161 | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1540 | 鹽行～王行、豐華線(1540) |  | ES2 | 1542E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0940 | 941 | 0134 | 2-34-12 | 2-34-13 | 2-06 | 1542E | ON/OFF | 山上盬行豐華白線 1542 EABS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1542E_ES | 1542E(山上豐華白線) ES | LINE161 | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D27 | 鹽行DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Sect2C | B/1Bus | B/2Bus |  |  | 0992 | 993 | 0144 | 2-38-00 | 2-38-01 | 2-10 | 1501 | ON/OFF | 161KV TIE 1501 ABS |  | no rule | B2/D27_A1 | [8 empty] | 鹽行DS.1501_DS | 1501 DS | BUS | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0996 | 997 | 0146 | 2-38-04 | 2-38-05 | 2-12 | 1751 | ON/OFF | #1DTR 1751 DS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 | 0148 | 2-38-08 | 2-38-09 | 2-14 | 1761 | ON/OFF | #2DTR 1761 DS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 | 0150 | 2-38-12 | 2-38-13 | 2-16 | 1771 | ON/OFF | #3DTR 1771 DS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1006 | 1007 |  | 2-38-14 | 2-38-15 |  | 1772 | ON/OFF | #3DTR 1772 DS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | ES2 | 1772E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1008 | 1009 |  | 2-39-00 | 2-39-01 |  | 1772E | ON/OFF | #3DTR 1772E DS |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.1772E_ES | 1772E(#3DTR) ES | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D27 | 鹽行DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 2-33-10 |  |  | M5盤 | A/N | VUA2 |  |  | B2/D27_A1 | [8 empty] | 鹽行DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 577 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 320 | #1DTR(320) |  | 81AS |  |  | Status | 81RY A/S | Reset/Trip | Y | 1 | DI-SP | [6 empty] | 0246 |  |  | 1-1E-06 |  |  | 320 | 81AS | #320 81 RY (KV24~KV26) |  |  | B3/D27_A1 | [8 empty] | 鹽行DS.320_81A/S | (320)81RY動作/Reset | OTHER | [5 empty] | 578 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Reset/Trip | Trip | 1 |  |  | TRIP/RESET | RESET

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D27/161/1BUS/V; OPRD2: D27/161/2BUS/V
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D27_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D27/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D27_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: D27/161/1530/MW; OPRD2: D27/161/1540/MW
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D27_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D27/0/CalcPoint/OPRN2_MW
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D27_A1 | [17 empty] | none
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D27_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D27/0/CalcPoint/OPRN1; OPRD2: D27/0/CalcPoint/OPRN2; OPRD3: D27/0/CalcPoint/PRFL_UL
D27 | 鹽行DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D27_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D27/11/310/I_R; OPRD2: D27/11/320/I_R
D27 | 鹽行DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D27_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D27/11/310/I_S; OPRD2: D27/11/320/I_S
D27 | 鹽行DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D27_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D27/11/310/I_T; OPRD2: D27/11/320/I_T
D27 | 鹽行DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D27_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D27/11/340/I_R; OPRD2: D27/11/330/I_R
D27 | 鹽行DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D27_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D27/11/340/I_S; OPRD2: D27/11/330/I_S
D27 | 鹽行DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D27_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D27/11/340/I_T; OPRD2: D27/11/330/I_T
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D27_A1 | [12 empty] | 鹽行DS.1530_AMP | 安南鹽行線 AMP | LINE161 | AMP_CAL | C08R0800 | amp_cal | OPRD1: D27/161/1530/MW; OPRD2: D27/161/1530/MVAR; OPRD3: D27/0/CalcPoint/Vbs4
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上～鹽行、豐華白線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D27_A1 | [12 empty] | 鹽行DS.1540_AMP | 山上豐華白線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: D27/161/1540/MW; OPRD2: D27/161/1540/MVAR; OPRD3: D27/0/CalcPoint/Vbs4
D27 | 鹽行DS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D27_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D27/11/1ABUS/V
D27 | 鹽行DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D27_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D27/11/1BBUS/V
D27 | 鹽行DS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D27_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D27/11/2ABUS/V
D27 | 鹽行DS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D27_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D27/11/2BBUS/V
D27 | 鹽行DS | 22 | 22kV | 3BUS | #3BUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D27_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D27/22/3BUS/V
D27 | 鹽行DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D27//1DTR(A)/SupLocal; OPRD2: D27//1DTR(A)/Tap Chan
D27 | 鹽行DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D27//1DTR(B)/SupLocal; OPRD2: D27//1DTR(B)/Tap Chan
D27 | 鹽行DS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D27//2DTR(A)/SupLocal; OPRD2: D27//2DTR(A)/Tap Chan
D27 | 鹽行DS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D27//2DTR(B)/SupLocal; OPRD2: D27//2DTR(B)/Tap Chan
D27 | 鹽行DS |  |  | 3DTR(A) | #3DTR(A) |  | TR_PERM | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D27//3DTR(A)/SupLocal; OPRD2: D27//3DTR(A)/Tap Chan
D27 | 鹽行DS |  |  | 3DTR(B) | #3DTR(B) |  | TR_PERM | [9 empty] | B1/D27_A1 | [12 empty] | 鹽行DS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D27//3DTR(B)/SupLocal; OPRD2: D27//3DTR(B)/Tap Chan
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/1ABUS/V; OPRD2: D27/11/KV21/I_R; OPRD3: D27/11/KV21/I_S; OPRD4: D27/11/KV21/I_T
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/1ABUS/V; OPRD2: D27/11/KV22/I_R; OPRD3: D27/11/KV22/I_S; OPRD4: D27/11/KV22/I_T
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/1ABUS/V; OPRD2: D27/11/KV23/I_R; OPRD3: D27/11/KV23/I_S; OPRD4: D27/11/KV23/I_T
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/1BBUS/V; OPRD2: D27/11/KV24/I_R; OPRD3: D27/11/KV24/I_S; OPRD4: D27/11/KV24/I_T
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/1BBUS/V; OPRD2: D27/11/KV25/I_R; OPRD3: D27/11/KV25/I_S; OPRD4: D27/11/KV25/I_T
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/1BBUS/V; OPRD2: D27/11/KV26/I_R; OPRD3: D27/11/KV26/I_S; OPRD4: D27/11/KV26/I_T
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2BBUS/V; OPRD2: D27/11/KV27/I_R; OPRD3: D27/11/KV27/I_S; OPRD4: D27/11/KV27/I_T
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2BBUS/V; OPRD2: D27/11/KV28/I_R; OPRD3: D27/11/KV28/I_S; OPRD4: D27/11/KV28/I_T
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2BBUS/V; OPRD2: D27/11/KV29/I_R; OPRD3: D27/11/KV29/I_S; OPRD4: D27/11/KV29/I_T
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2BBUS/V; OPRD2: D27/11/KV30/I_R; OPRD3: D27/11/KV30/I_S; OPRD4: D27/11/KV30/I_T
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2ABUS/V; OPRD2: D27/11/KV31/I_R; OPRD3: D27/11/KV31/I_S; OPRD4: D27/11/KV31/I_T
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2ABUS/V; OPRD2: D27/11/KV32/I_R; OPRD3: D27/11/KV32/I_S; OPRD4: D27/11/KV32/I_T
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2ABUS/V; OPRD2: D27/11/KV33/I_R; OPRD3: D27/11/KV33/I_S; OPRD4: D27/11/KV33/I_T
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/11/2ABUS/V; OPRD2: D27/11/KV34/I_R; OPRD3: D27/11/KV34/I_S; OPRD4: D27/11/KV34/I_T
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/22/3BUS/V; OPRD2: D27/22/KV71/I_R; OPRD3: D27/22/KV71/I_S; OPRD4: D27/22/KV71/I_T
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/22/3BUS/V; OPRD2: D27/22/KV72/I_R; OPRD3: D27/22/KV72/I_S; OPRD4: D27/22/KV72/I_T
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/22/3BUS/V; OPRD2: D27/22/KV73/I_R; OPRD3: D27/22/KV73/I_S; OPRD4: D27/22/KV73/I_T
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/22/3BUS/V; OPRD2: D27/22/KV74/I_R; OPRD3: D27/22/KV74/I_S; OPRD4: D27/22/KV74/I_T
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/22/3BUS/V; OPRD2: D27/22/KV75/I_R; OPRD3: D27/22/KV75/I_S; OPRD4: D27/22/KV75/I_T
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D27/22/3BUS/V; OPRD2: D27/22/KV76/I_R; OPRD3: D27/22/KV76/I_S; OPRD4: D27/22/KV76/I_T
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV21/kVA; OPRD2: D27/11/KV21/KVAR
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV22/kVA; OPRD2: D27/11/KV22/KVAR
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV23/kVA; OPRD2: D27/11/KV23/KVAR
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV24/kVA; OPRD2: D27/11/KV24/KVAR
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV25/kVA; OPRD2: D27/11/KV25/KVAR
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV26/kVA; OPRD2: D27/11/KV26/KVAR
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV27/kVA; OPRD2: D27/11/KV27/KVAR
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV28/kVA; OPRD2: D27/11/KV28/KVAR
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV29/kVA; OPRD2: D27/11/KV29/KVAR
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV30/kVA; OPRD2: D27/11/KV30/KVAR
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV31/kVA; OPRD2: D27/11/KV31/KVAR
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV32/kVA; OPRD2: D27/11/KV32/KVAR
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV33/kVA; OPRD2: D27/11/KV33/KVAR
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/11/KV34/kVA; OPRD2: D27/11/KV34/KVAR
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/22/KV71/kVA; OPRD2: D27/22/KV71/KVAR
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/22/KV72/kVA; OPRD2: D27/22/KV72/KVAR
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/22/KV73/kVA; OPRD2: D27/22/KV73/KVAR
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/22/KV74/kVA; OPRD2: D27/22/KV74/KVAR
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/22/KV75/kVA; OPRD2: D27/22/KV75/KVAR
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D27_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D27/22/KV76/kVA; OPRD2: D27/22/KV76/KVAR
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D27_A1 | [12 empty] | 鹽行DS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D27/11/210/CB; OPRD2: 6.9; OPRD3: 0
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D27_A1 | [12 empty] | 鹽行DS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D27/11/220/CB; OPRD2: 6.9; OPRD3: 0
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D27_A1 | [12 empty] | 鹽行DS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D27/11/230/CB; OPRD2: 6.9; OPRD3: 0
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D27_A1 | [12 empty] | 鹽行DS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: D27/11/240/CB; OPRD2: 6.9; OPRD3: 0
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D27_A1 | [12 empty] | 鹽行DS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D27/22/250/CB; OPRD2: 13.8; OPRD3: 0
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D27_A1 | [12 empty] | 鹽行DS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D27/22/260/CB; OPRD2: 13.8; OPRD3: 0
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D27_A1 | [12 empty] | 鹽行DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_16 |  | com_alarm_37 | D27//1DTR/96B1 | D27//1DTR/96B2 | D27//1DTR/TRA | D27//1DTR/63Q | D27//1DTR/96PA | D27//1DTR/51ZA | D27//1DTR/96D | D27//2DTR/63Q | D27//2DTR/96B1 | D27//2DTR/TRA | D27//2DTR/96D | D27//2DTR/96PA | D27//2DTR/51ZA | D27//2DTR/96B2 | D27//3DTR/96B2 | D27//3DTR/96B1 | D27//3DTR/TRA | D27//3DTR/96PA | D27//3DTR/51ZA | D27//3DTR/63Q | D27//3DTR/96D | D27/11/310/GDA | D27/11/310/PHA | D27/11/320/GDA | D27/11/320/PHA | D27/11/330/PHA | D27/11/330/GDA | D27/11/340/PHA | D27/11/340/GDA | D27/161/1750/GDA | D27/161/1750/PHA | D27/161/1760/PHA | D27/161/1760/GDA | D27/161/1770/GDA | D27/161/1770/PHA | D27/22/350/GDA | D27/22/350/PHA
D27 | 鹽行DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D27_A1 | [12 empty] | 鹽行DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: D27//1DTR/TRF; OPRD2: D27//2DTR/TRF; OPRD3: D27//3DTR/TRF
D27 | 鹽行DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/161/1750/CB
D27 | 鹽行DS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/11/310/CB
D27 | 鹽行DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/161/1760/CB
D27 | 鹽行DS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/11/340/CB
D27 | 鹽行DS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/11/330/CB
D27 | 鹽行DS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/161/1770/CB
D27 | 鹽行DS | 22 | 22kV | 350_D1 | #3DTR(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/22/350/CB
D27 | 鹽行DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/11/320/CB
D27 | 鹽行DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/0/RTU/RTU_R_L
D27 | 鹽行DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/0/StaDev/PMA
D27 | 鹽行DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/0/StaDev/STUV
D27 | 鹽行DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/0/StaDev/DCA
D27 | 鹽行DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/0/StaDev/DCE
D27 | 鹽行DS | 11 | 11kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/11/ComPoint/CBF
D27 | 鹽行DS | 11 | 11kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D27_D1 | [17 empty] | lamp2CC | OPRD1: D27/11/ComPoint/CBA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D27 | 鹽行DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D27/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.1530_AMP | 安南鹽行線 AMP | LINE161 | D27/161/1530/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C08R0800 | 720.000000 | 720.000000 | 800.000000 | 800.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_AMP | 山上豐華白線 AMP | LINE161 | D27/161/1540/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D27 | 鹽行DS | 11 | 11kV | 210_SC | #1SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.210_SC_MVAR | 11KV#1SC MVAR | SC | D27/11/210/MVAR |  | SC_CAL_11 |  |  | 5 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 11 | 11kV | 220_SC | #2SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.220_SC_MVAR | 11KV#2SC MVAR | SC | D27/11/220/MVAR |  | SC_CAL_11 |  |  | 6 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 11 | 11kV | 230_SC | #3SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.230_SC_MVAR | 11KV#3SC MVAR | SC | D27/11/230/MVAR |  | SC_CAL_11 |  |  | 7 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 11 | 11kV | 240_SC | #4SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.240_SC_MVAR | 11KV#4SC MVAR | SC | D27/11/240/MVAR |  | SC_CAL_11 |  |  | 8 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 22 | 22kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.250_SC_MVAR | 23KV#5SC MVAR | SC | D27/22/250/MVAR |  | SC_CAL_23 |  |  | 9 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 22 | 22kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.260_SC_MVAR | 23KV#6SC MVAR | SC | D27/22/260/MVAR |  | SC_CAL_23 |  |  | 10 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | TRTOT | 鹽行主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 鹽行DS.TRTOT_MW | 鹽行主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 11 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | TRTOT | 鹽行主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 鹽行DS.TRTOT_MVAR | 鹽行主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 12 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽21線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線KVA | 11KV鹽21線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽21線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線KW | 11KV鹽21線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽22線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線KVA | 11KV鹽22線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽22線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線KW | 11KV鹽22線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽23線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線KVA | 11KV鹽23線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽23線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線KW | 11KV鹽23線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽24線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線KVA | 11KV鹽24線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽24線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線KW | 11KV鹽24線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽25線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線KVA | 11KV鹽25線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽25線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線KW | 11KV鹽25線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽26線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線KVA | 11KV鹽26線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽26線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線KW | 11KV鹽26線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽27線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線KVA | 11KV鹽27線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽27線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線KW | 11KV鹽27線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽28線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線KVA | 11KV鹽28線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽28線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線KW | 11KV鹽28線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽29線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線KVA | 11KV鹽29線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽29線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線KW | 11KV鹽29線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽30線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線KVA | 11KV鹽30線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽30線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線KW | 11KV鹽30線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽31線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線KVA | 11KV鹽31線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽31線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線KW | 11KV鹽31線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽32線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線KVA | 11KV鹽32線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽32線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線KW | 11KV鹽32線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽33線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線KVA | 11KV鹽33線KVA | FEEDER |  |  | KVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽33線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線KW | 11KV鹽33線KW | FEEDER |  |  | KW_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽34線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線KVA | 11KV鹽34線KVA | FEEDER |  |  | KVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽34線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線KW | 11KV鹽34線KW | FEEDER |  |  | KW_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽71線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線KVA | 23KV鹽71線KVA | FEEDER |  |  | KVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽71線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線KW | 23KV鹽71線KW | FEEDER |  |  | KW_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽72線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線KVA | 23KV鹽72線KVA | FEEDER |  |  | KVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽72線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線KW | 23KV鹽72線KW | FEEDER |  |  | KW_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽73線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線KVA | 23KV鹽73線KVA | FEEDER |  |  | KVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽73線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線KW | 23KV鹽73線KW | FEEDER |  |  | KW_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽74線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線KVA | 23KV鹽74線KVA | FEEDER |  |  | KVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽74線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線KW | 23KV鹽74線KW | FEEDER |  |  | KW_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽75線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線KVA | 23KV鹽75線KVA | FEEDER |  |  | KVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽75線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線KW | 23KV鹽75線KW | FEEDER |  |  | KW_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽76線KVA | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線KVA | 23KV鹽76線KVA | FEEDER |  |  | KVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  |  |  |  | 鹽76線KW | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線KW | 23KV鹽76線KW | FEEDER |  |  | KW_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 56 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 58 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_MW | #2DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_MVAR | #2DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 69 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 71 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 74 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D27 | 鹽行DS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 76 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 77 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 78 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 79 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 80 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 81 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 82 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 83 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 84 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.240_CB_4 | 240(11KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 85 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 86 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 87 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 88 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 89 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 90 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D27 | 鹽行DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D27/0/CalcPoint/SUBA |  | STATION_FAULT_16 |  |  | 91 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D27/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 92 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 93 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 94 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530_AMP | 安南鹽行線 | [27 empty] | ADCS_S | [8 empty] | 鹽行DS.1530_AMP_A | 安南鹽行線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540_AMP | 山上豐華白線 | [27 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_AMP_A | 山上豐華白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 97 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 98 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 99 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | D27//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | D27//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | D27//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | D27//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR(A) | #3DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | D27//3DTR(A)/TR_PERM |  | DTR_PERM |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR(B) | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | D27//3DTR(B)/TR_PERM |  | DTR_PERM |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR_MVA | #1DTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.#1DTR_MVA_4 | #1DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 109 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.#2DTR_MVA_4 | #2DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 110 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 5 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.#2DTR_MVA_5 | #2DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 111 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 112 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR_MVA | #3DTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.#3DTR_MVA_4 | #3DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 113 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 鹽行DS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 114 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 鹽行DS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 115 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 3BUS | #3BUS |  | 23KV#3BUSC | [25 empty] | CDCS | [8 empty] | 鹽行DS.23KV#3BUSC | #3BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 116 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T6 |  |  | 117 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B5 |  |  | 118 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 500_CB | 500(500_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.500_CB_4 | 500 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 120 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 22 | 22kV | 11__LOA | 11/饋線復閉失敗 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.11/23KV_LOA_4 | 11/23KV饋線復閉失敗 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 121 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 122 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 鹽行DS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 123 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 鹽行DS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 124 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D27 | 鹽行DS | 0 |  | 400_CB | 400(400_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 鹽行DS.400_CB_4 | 400 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 125 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 126 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | D27/0/RTU/ADCH1 |  |  |  | CDC | 127 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | D27/0/RTU/ADCH2 |  |  |  | CDC | 128 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | D27/0/RTU/ADCH3 |  |  |  | CDC | 129 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | D27/0/RTU/ADCH4 |  |  |  | CDC | 130 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | D27/0/RTU/ADCL1 |  |  |  | CDC | 131 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | D27/0/RTU/ADCL2 |  |  |  | CDC | 132 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | D27/0/RTU/ADCL3 |  |  |  | CDC | 133 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | D27/0/RTU/ADCL4 |  |  |  | CDC | 134 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D27/161/1BUS/V |  |  |  | CDC | 135 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D27 | 鹽行DS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D27/161/2BUS/V |  |  |  | CDC | 136 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D27 | 鹽行DS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-E6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | D27/11/2ABUS/V |  |  |  | CDC | 137 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-B7 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | D27/11/2BBUS/V |  |  |  | CDC | 138 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 22 | 22kV | 3BUS | #3BUS |  | V | [17 empty] | 2-94 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.23KV#3BUS_KV | 23KV #3BUS KV | BUS | D27/22/3BUS/V |  |  |  | CDC | 139 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-224_224(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.1530_MW | 安南鹽行線 MW | LINE161 | D27/161/1530/MW |  |  |  | CDC | 140 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-224_224(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.1530_MVAR | 安南鹽行線 MVAR | LINE161 | D27/161/1530/MVAR |  |  |  | CDC | 141 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.448000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.1540_MW | 山上豐華白線 MW | LINE161 | D27/161/1540/MW |  |  |  | CDC | 142 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.1540_MVAR | 山上豐華白線 MVAR | LINE161 | D27/161/1540/MVAR |  |  |  | CDC | 143 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
D27 | 鹽行DS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-8F | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D27/0/StaDev/DCV_N |  |  |  | CDC | 144 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D27 | 鹽行DS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-8E | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D27/0/StaDev/DCV_P |  |  |  | CDC | 145 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽21線 | 鹽21線 |  | 鹽21線KVAR | [17 empty] | 1-B9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線KVAR | 11KV鹽21線 KVAR | FEEDER | D27/11/KV21/KVAR |  |  |  | CDC | 146 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽21線 | 鹽21線 |  | 鹽21線A1 | [17 empty] | 1-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線A1 | 11KV鹽21線 R相AMP | FEEDER | D27/11/KV21/I_R |  |  |  | CDC | 147 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽21線 | 鹽21線 |  | 鹽21線A2 | [17 empty] | 1-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線A2 | 11KV鹽21線 S相AMP | FEEDER | D27/11/KV21/I_S |  |  |  | CDC | 148 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽21線 | 鹽21線 |  | 鹽21線A3 | [17 empty] | 1-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線A3 | 11KV鹽21線 T相AMP | FEEDER | D27/11/KV21/I_T |  |  |  | CDC | 149 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽21線 | 鹽21線 |  | 鹽21線A0 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽21線A0 | 11KV鹽21線 N相AMP | FEEDER | D27/11/KV21/I_N |  |  |  | CDC | 150 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽22線 | 鹽22線 |  | 鹽22線KVAR | [17 empty] | 1-BD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線KVAR | 11KV鹽22線 KVAR | FEEDER | D27/11/KV22/KVAR |  |  |  | CDC | 151 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽22線 | 鹽22線 |  | 鹽22線A1 | [17 empty] | 1-BE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線A1 | 11KV鹽22線 R相AMP | FEEDER | D27/11/KV22/I_R |  |  |  | CDC | 152 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽22線 | 鹽22線 |  | 鹽22線A2 | [17 empty] | 1-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線A2 | 11KV鹽22線 S相AMP | FEEDER | D27/11/KV22/I_S |  |  |  | CDC | 153 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽22線 | 鹽22線 |  | 鹽22線A3 | [17 empty] | 1-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線A3 | 11KV鹽22線 T相AMP | FEEDER | D27/11/KV22/I_T |  |  |  | CDC | 154 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽22線 | 鹽22線 |  | 鹽22線A0 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽22線A0 | 11KV鹽22線 N相AMP | FEEDER | D27/11/KV22/I_N |  |  |  | CDC | 155 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽23線 | 鹽23線 |  | 鹽23線KVAR | [17 empty] | 1-C3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線KVAR | 11KV鹽23線 KVAR | FEEDER | D27/11/KV23/KVAR |  |  |  | CDC | 156 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽23線 | 鹽23線 |  | 鹽23線A1 | [17 empty] | 1-C4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線A1 | 11KV鹽23線 R相AMP | FEEDER | D27/11/KV23/I_R |  |  |  | CDC | 157 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽23線 | 鹽23線 |  | 鹽23線A2 | [17 empty] | 1-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線A2 | 11KV鹽23線 S相AMP | FEEDER | D27/11/KV23/I_S |  |  |  | CDC | 158 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽23線 | 鹽23線 |  | 鹽23線A3 | [17 empty] | 1-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線A3 | 11KV鹽23線 T相AMP | FEEDER | D27/11/KV23/I_T |  |  |  | CDC | 159 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽23線 | 鹽23線 |  | 鹽23線A0 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽23線A0 | 11KV鹽23線 N相AMP | FEEDER | D27/11/KV23/I_N |  |  |  | CDC | 160 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽24線 | 鹽24線 |  | 鹽24線KVAR | [17 empty] | 1-C7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線KVAR | 11KV鹽24線 KVAR | FEEDER | D27/11/KV24/KVAR |  |  |  | CDC | 161 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽24線 | 鹽24線 |  | 鹽24線A1 | [17 empty] | 1-C8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線A1 | 11KV鹽24線 R相AMP | FEEDER | D27/11/KV24/I_R |  |  |  | CDC | 162 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽24線 | 鹽24線 |  | 鹽24線A2 | [17 empty] | 1-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線A2 | 11KV鹽24線 S相AMP | FEEDER | D27/11/KV24/I_S |  |  |  | CDC | 163 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽24線 | 鹽24線 |  | 鹽24線A3 | [17 empty] | 1-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線A3 | 11KV鹽24線 T相AMP | FEEDER | D27/11/KV24/I_T |  |  |  | CDC | 164 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽24線 | 鹽24線 |  | 鹽24線A0 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽24線A0 | 11KV鹽24線 N相AMP | FEEDER | D27/11/KV24/I_N |  |  |  | CDC | 165 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽25線 | 鹽25線 |  | 鹽25線KVAR | [17 empty] | 1-CB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線KVAR | 11KV鹽25線 KVAR | FEEDER | D27/11/KV25/KVAR |  |  |  | CDC | 166 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽25線 | 鹽25線 |  | 鹽25線A1 | [17 empty] | 1-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線A1 | 11KV鹽25線 R相AMP | FEEDER | D27/11/KV25/I_R |  |  |  | CDC | 167 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽25線 | 鹽25線 |  | 鹽25線A2 | [17 empty] | 1-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線A2 | 11KV鹽25線 S相AMP | FEEDER | D27/11/KV25/I_S |  |  |  | CDC | 168 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽25線 | 鹽25線 |  | 鹽25線A3 | [17 empty] | 1-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線A3 | 11KV鹽25線 T相AMP | FEEDER | D27/11/KV25/I_T |  |  |  | CDC | 169 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽25線 | 鹽25線 |  | 鹽25線A0 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽25線A0 | 11KV鹽25線 N相AMP | FEEDER | D27/11/KV25/I_N |  |  |  | CDC | 170 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽26線 | 鹽26線 |  | 鹽26線KVAR | [17 empty] | 1-CF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線KVAR | 11KV鹽26線 KVAR | FEEDER | D27/11/KV26/KVAR |  |  |  | CDC | 171 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽26線 | 鹽26線 |  | 鹽26線A1 | [17 empty] | 1-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線A1 | 11KV鹽26線 R相AMP | FEEDER | D27/11/KV26/I_R |  |  |  | CDC | 172 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R450R | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽26線 | 鹽26線 |  | 鹽26線A2 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線A2 | 11KV鹽26線 S相AMP | FEEDER | D27/11/KV26/I_S |  |  |  | CDC | 173 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽26線 | 鹽26線 |  | 鹽26線A3 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線A3 | 11KV鹽26線 T相AMP | FEEDER | D27/11/KV26/I_T |  |  |  | CDC | 174 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C05R0450 | 405.000000 | 405.000000 | 450.000000 | 500.000000 | 1.430000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽26線 | 鹽26線 |  | 鹽26線A0 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽26線A0 | 11KV鹽26線 N相AMP | FEEDER | D27/11/KV26/I_N |  |  |  | CDC | 175 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽27線 | 鹽27線 |  | 鹽27線KVAR | [17 empty] | 1-D6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線KVAR | 11KV鹽27線 KVAR | FEEDER | D27/11/KV27/KVAR |  |  |  | CDC | 176 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽27線 | 鹽27線 |  | 鹽27線A1 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線A1 | 11KV鹽27線 R相AMP | FEEDER | D27/11/KV27/I_R |  |  |  | CDC | 177 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽27線 | 鹽27線 |  | 鹽27線A2 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線A2 | 11KV鹽27線 S相AMP | FEEDER | D27/11/KV27/I_S |  |  |  | CDC | 178 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽27線 | 鹽27線 |  | 鹽27線A3 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線A3 | 11KV鹽27線 T相AMP | FEEDER | D27/11/KV27/I_T |  |  |  | CDC | 179 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽27線 | 鹽27線 |  | 鹽27線A0 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽27線A0 | 11KV鹽27線 N相AMP | FEEDER | D27/11/KV27/I_N |  |  |  | CDC | 180 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽28線 | 鹽28線 |  | 鹽28線KVAR | [17 empty] | 1-DA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線KVAR | 11KV鹽28線 KVAR | FEEDER | D27/11/KV28/KVAR |  |  |  | CDC | 181 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽28線 | 鹽28線 |  | 鹽28線A1 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線A1 | 11KV鹽28線 R相AMP | FEEDER | D27/11/KV28/I_R |  |  |  | CDC | 182 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽28線 | 鹽28線 |  | 鹽28線A2 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線A2 | 11KV鹽28線 S相AMP | FEEDER | D27/11/KV28/I_S |  |  |  | CDC | 183 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽28線 | 鹽28線 |  | 鹽28線A3 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線A3 | 11KV鹽28線 T相AMP | FEEDER | D27/11/KV28/I_T |  |  |  | CDC | 184 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽28線 | 鹽28線 |  | 鹽28線A0 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽28線A0 | 11KV鹽28線 N相AMP | FEEDER | D27/11/KV28/I_N |  |  |  | CDC | 185 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽29線 | 鹽29線 |  | 鹽29線KVAR | [17 empty] | 1-DE | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線KVAR | 11KV鹽29線 KVAR | FEEDER | D27/11/KV29/KVAR |  |  |  | CDC | 186 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽29線 | 鹽29線 |  | 鹽29線A1 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線A1 | 11KV鹽29線 R相AMP | FEEDER | D27/11/KV29/I_R |  |  |  | CDC | 187 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽29線 | 鹽29線 |  | 鹽29線A2 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線A2 | 11KV鹽29線 S相AMP | FEEDER | D27/11/KV29/I_S |  |  |  | CDC | 188 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽29線 | 鹽29線 |  | 鹽29線A3 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線A3 | 11KV鹽29線 T相AMP | FEEDER | D27/11/KV29/I_T |  |  |  | CDC | 189 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽29線 | 鹽29線 |  | 鹽29線A0 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽29線A0 | 11KV鹽29線 N相AMP | FEEDER | D27/11/KV29/I_N |  |  |  | CDC | 190 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽30線 | 鹽30線 |  | 鹽30線KVAR | [17 empty] | 1-E2 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線KVAR | 11KV鹽30線 KVAR | FEEDER | D27/11/KV30/KVAR |  |  |  | CDC | 191 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽30線 | 鹽30線 |  | 鹽30線A1 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線A1 | 11KV鹽30線 R相AMP | FEEDER | D27/11/KV30/I_R |  |  |  | CDC | 192 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽30線 | 鹽30線 |  | 鹽30線A2 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線A2 | 11KV鹽30線 S相AMP | FEEDER | D27/11/KV30/I_S |  |  |  | CDC | 193 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽30線 | 鹽30線 |  | 鹽30線A3 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線A3 | 11KV鹽30線 T相AMP | FEEDER | D27/11/KV30/I_T |  |  |  | CDC | 194 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽30線 | 鹽30線 |  | 鹽30線A0 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽30線A0 | 11KV鹽30線 N相AMP | FEEDER | D27/11/KV30/I_N |  |  |  | CDC | 195 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽31線 | 鹽31線 |  | 鹽31線KVAR | [17 empty] | 1-E7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線KVAR | 11KV鹽31線 KVAR | FEEDER | D27/11/KV31/KVAR |  |  |  | CDC | 196 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽31線 | 鹽31線 |  | 鹽31線A1 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線A1 | 11KV鹽31線 R相AMP | FEEDER | D27/11/KV31/I_R |  |  |  | CDC | 197 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽31線 | 鹽31線 |  | 鹽31線A2 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線A2 | 11KV鹽31線 S相AMP | FEEDER | D27/11/KV31/I_S |  |  |  | CDC | 198 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽31線 | 鹽31線 |  | 鹽31線A3 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線A3 | 11KV鹽31線 T相AMP | FEEDER | D27/11/KV31/I_T |  |  |  | CDC | 199 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽31線 | 鹽31線 |  | 鹽31線A0 | [17 empty] | 2-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽31線A0 | 11KV鹽31線 N相AMP | FEEDER | D27/11/KV31/I_N |  |  |  | CDC | 200 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽32線 | 鹽32線 |  | 鹽32線KVAR | [17 empty] | 1-EB | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線KVAR | 11KV鹽32線 KVAR | FEEDER | D27/11/KV32/KVAR |  |  |  | CDC | 201 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽32線 | 鹽32線 |  | 鹽32線A1 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線A1 | 11KV鹽32線 R相AMP | FEEDER | D27/11/KV32/I_R |  |  |  | CDC | 202 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽32線 | 鹽32線 |  | 鹽32線A2 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線A2 | 11KV鹽32線 S相AMP | FEEDER | D27/11/KV32/I_S |  |  |  | CDC | 203 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽32線 | 鹽32線 |  | 鹽32線A3 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線A3 | 11KV鹽32線 T相AMP | FEEDER | D27/11/KV32/I_T |  |  |  | CDC | 204 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽32線 | 鹽32線 |  | 鹽32線A0 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽32線A0 | 11KV鹽32線 N相AMP | FEEDER | D27/11/KV32/I_N |  |  |  | CDC | 205 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽33線 | 鹽33線 |  | 鹽33線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線KVAR | 11KV鹽33線 KVAR | FEEDER | D27/11/KV33/KVAR |  |  |  | CDC | 206 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽33線 | 鹽33線 |  | 鹽33線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線A1 | 11KV鹽33線 R相AMP | FEEDER | D27/11/KV33/I_R |  |  |  | CDC | 207 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽33線 | 鹽33線 |  | 鹽33線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線A2 | 11KV鹽33線 S相AMP | FEEDER | D27/11/KV33/I_S |  |  |  | CDC | 208 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽33線 | 鹽33線 |  | 鹽33線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線A3 | 11KV鹽33線 T相AMP | FEEDER | D27/11/KV33/I_T |  |  |  | CDC | 209 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽33線 | 鹽33線 |  | 鹽33線A0 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽33線A0 | 11KV鹽33線 N相AMP | FEEDER | D27/11/KV33/I_N |  |  |  | CDC | 210 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽34線 | 鹽34線 |  | 鹽34線KVAR | [17 empty] | 1-F3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線KVAR | 11KV鹽34線 KVAR | FEEDER | D27/11/KV34/KVAR |  |  |  | CDC | 211 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽34線 | 鹽34線 |  | 鹽34線A1 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線A1 | 11KV鹽34線 R相AMP | FEEDER | D27/11/KV34/I_R |  |  |  | CDC | 212 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽34線 | 鹽34線 |  | 鹽34線A2 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線A2 | 11KV鹽34線 S相AMP | FEEDER | D27/11/KV34/I_S |  |  |  | CDC | 213 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽34線 | 鹽34線 |  | 鹽34線A3 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線A3 | 11KV鹽34線 T相AMP | FEEDER | D27/11/KV34/I_T |  |  |  | CDC | 214 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 鹽34線 | 鹽34線 |  | 鹽34線A0 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽34線A0 | 11KV鹽34線 N相AMP | FEEDER | D27/11/KV34/I_N |  |  |  | CDC | 215 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽71線 | 鹽71線 |  | 鹽71線KVAR | [17 empty] | 1-F7 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線KVAR | 23KV鹽71線 KVAR | FEEDER | D27/22/KV71/KVAR |  |  |  | CDC | 216 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽71線 | 鹽71線 |  | 鹽71線A1 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線A1 | 23KV鹽71線 R相AMP | FEEDER | D27/22/KV71/I_R |  |  |  | CDC | 217 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽71線 | 鹽71線 |  | 鹽71線A2 | [17 empty] | 1-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線A2 | 23KV鹽71線 S相AMP | FEEDER | D27/22/KV71/I_S |  |  |  | CDC | 218 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽71線 | 鹽71線 |  | 鹽71線A3 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線A3 | 23KV鹽71線 T相AMP | FEEDER | D27/22/KV71/I_T |  |  |  | CDC | 219 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽71線 | 鹽71線 |  | 鹽71線A0 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽71線A0 | 23KV鹽71線 N相AMP | FEEDER | D27/22/KV71/I_N |  |  |  | CDC | 220 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽72線 | 鹽72線 |  | 鹽72線KVAR | [17 empty] | 1-FE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線KVAR | 23KV鹽72線 KVAR | FEEDER | D27/22/KV72/KVAR |  |  |  | CDC | 221 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽72線 | 鹽72線 |  | 鹽72線A1 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線A1 | 23KV鹽72線 R相AMP | FEEDER | D27/22/KV72/I_R |  |  |  | CDC | 222 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽72線 | 鹽72線 |  | 鹽72線A2 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線A2 | 23KV鹽72線 S相AMP | FEEDER | D27/22/KV72/I_S |  |  |  | CDC | 223 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽72線 | 鹽72線 |  | 鹽72線A3 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線A3 | 23KV鹽72線 T相AMP | FEEDER | D27/22/KV72/I_T |  |  |  | CDC | 224 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽72線 | 鹽72線 |  | 鹽72線A0 | [17 empty] | 2-A4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽72線A0 | 23KV鹽72線 N相AMP | FEEDER | D27/22/KV72/I_N |  |  |  | CDC | 225 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽73線 | 鹽73線 |  | 鹽73線KVAR | [17 empty] | 2-84 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線KVAR | 23KV鹽73線 KVAR | FEEDER | D27/22/KV73/KVAR |  |  |  | CDC | 226 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽73線 | 鹽73線 |  | 鹽73線A1 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線A1 | 23KV鹽73線 R相AMP | FEEDER | D27/22/KV73/I_R |  |  |  | CDC | 227 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽73線 | 鹽73線 |  | 鹽73線A2 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線A2 | 23KV鹽73線 S相AMP | FEEDER | D27/22/KV73/I_S |  |  |  | CDC | 228 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽73線 | 鹽73線 |  | 鹽73線A3 | [17 empty] | 2-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線A3 | 23KV鹽73線 T相AMP | FEEDER | D27/22/KV73/I_T |  |  |  | CDC | 229 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽73線 | 鹽73線 |  | 鹽73線A0 | [17 empty] | 2-A5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽73線A0 | 23KV鹽73線 N相AMP | FEEDER | D27/22/KV73/I_N |  |  |  | CDC | 230 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽74線 | 鹽74線 |  | 鹽74線KVAR | [17 empty] | 2-88 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線KVAR | 23KV鹽74線 KVAR | FEEDER | D27/22/KV74/KVAR |  |  |  | CDC | 231 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽74線 | 鹽74線 |  | 鹽74線A1 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線A1 | 23KV鹽74線 R相AMP | FEEDER | D27/22/KV74/I_R |  |  |  | CDC | 232 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽74線 | 鹽74線 |  | 鹽74線A2 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線A2 | 23KV鹽74線 S相AMP | FEEDER | D27/22/KV74/I_S |  |  |  | CDC | 233 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽74線 | 鹽74線 |  | 鹽74線A3 | [17 empty] | 2-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線A3 | 23KV鹽74線 T相AMP | FEEDER | D27/22/KV74/I_T |  |  |  | CDC | 234 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽74線 | 鹽74線 |  | 鹽74線A0 | [17 empty] | 2-A6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽74線A0 | 23KV鹽74線 N相AMP | FEEDER | D27/22/KV74/I_N |  |  |  | CDC | 235 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽75線 | 鹽75線 |  | 鹽75線KVAR | [17 empty] | 2-8C | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線KVAR | 23KV鹽75線 KVAR | FEEDER | D27/22/KV75/KVAR |  |  |  | CDC | 236 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽75線 | 鹽75線 |  | 鹽75線A1 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線A1 | 23KV鹽75線 R相AMP | FEEDER | D27/22/KV75/I_R |  |  |  | CDC | 237 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽75線 | 鹽75線 |  | 鹽75線A2 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線A2 | 23KV鹽75線 S相AMP | FEEDER | D27/22/KV75/I_S |  |  |  | CDC | 238 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽75線 | 鹽75線 |  | 鹽75線A3 | [17 empty] | 2-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線A3 | 23KV鹽75線 T相AMP | FEEDER | D27/22/KV75/I_T |  |  |  | CDC | 239 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽75線 | 鹽75線 |  | 鹽75線A0 | [17 empty] | 2-A7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽75線A0 | 23KV鹽75線 N相AMP | FEEDER | D27/22/KV75/I_N |  |  |  | CDC | 240 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽76線 | 鹽76線 |  | 鹽76線KVAR | [17 empty] | 2-90 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線KVAR | 23KV鹽76線 KVAR | FEEDER | D27/22/KV76/KVAR |  |  |  | CDC | 241 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽76線 | 鹽76線 |  | 鹽76線A1 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線A1 | 23KV鹽76線 R相AMP | FEEDER | D27/22/KV76/I_R |  |  |  | CDC | 242 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽76線 | 鹽76線 |  | 鹽76線A2 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線A2 | 23KV鹽76線 S相AMP | FEEDER | D27/22/KV76/I_S |  |  |  | CDC | 243 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽76線 | 鹽76線 |  | 鹽76線A3 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線A3 | 23KV鹽76線 T相AMP | FEEDER | D27/22/KV76/I_T |  |  |  | CDC | 244 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | 鹽76線 | 鹽76線 |  | 鹽76線A0 | [17 empty] | 2-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 鹽行DS.鹽76線A0 | 23KV鹽76線 N相AMP | FEEDER | D27/22/KV76/I_N |  |  |  | CDC | 245 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-D3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_100_A1 | 11KV 100 R相AMP | TIE | D27/11/100/I_R |  |  |  | CDC | 246 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-D4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_100_A2 | 11KV 100 S相AMP | TIE | D27/11/100/I_S |  |  |  | CDC | 247 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-D5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_100_A3 | 11KV 100 T相AMP | TIE | D27/11/100/I_T |  |  |  | CDC | 248 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-FB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_200_A1 | 11KV 200 R相AMP | TIE | D27/11/200/I_R |  |  |  | CDC | 249 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-FC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_200_A2 | 11KV 200 S相AMP | TIE | D27/11/200/I_S |  |  |  | CDC | 250 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-FD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_200_A3 | 11KV 200 T相AMP | TIE | D27/11/200/I_T |  |  |  | CDC | 251 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-A4 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR_OIL | #1DTR 油溫 | MTR | D27//1DTR/OilTemp |  |  |  | CDC | 252 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-A5 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | D27//1DTR(A)/CoilTemp |  |  |  | CDC | 253 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-A7 |  | 1-61 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | D27//1DTR(A)/TapPosMv |  |  |  | CDC | 254 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-A6 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | D27//1DTR(B)/CoilTemp |  |  |  | CDC | 255 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-A8 |  | 1-63 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | D27//1DTR(B)/TapPosMv |  |  |  | CDC | 256 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-9A | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D27/11/330/KW |  |  |  | CDC | 257 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-9B | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D27/11/330/KVAR |  |  |  | CDC | 258 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-9C | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D27/11/330/I_R |  |  |  | CDC | 259 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-9D | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D27/11/330/I_S |  |  |  | CDC | 260 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-9E | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D27/11/330/I_T |  |  |  | CDC | 261 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-A9 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR_OIL | #2DTR 油溫 | MTR | D27//2DTR/OilTemp |  |  |  | CDC | 262 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-AA | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | D27//2DTR(A)/CoilTemp |  |  |  | CDC | 263 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-AC |  | 1-65 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | D27//2DTR(A)/TapPosMv |  |  |  | CDC | 264 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D27/11/340/KW |  |  |  | CDC | 265 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D27/11/340/KVAR |  |  |  | CDC | 266 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 1-97 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D27/11/340/I_R |  |  |  | CDC | 267 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 1-98 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D27/11/340/I_S |  |  |  | CDC | 268 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 1-99 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D27/11/340/I_T |  |  |  | CDC | 269 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-AB | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | D27//2DTR(B)/CoilTemp |  |  |  | CDC | 270 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-AD |  | 1-67 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | D27//2DTR(B)/TapPosMv |  |  |  | CDC | 271 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 1-9F | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR_MW | #3DTR二次側 MW | MTR | D27/22/350/KW |  |  |  | CDC | 272 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 1-A0 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | D27/22/350/KVAR |  |  |  | CDC | 273 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 1-A1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | D27/22/350/I_R |  |  |  | CDC | 274 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 1-A2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | D27/22/350/I_S |  |  |  | CDC | 275 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 1-A3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | D27/22/350/I_T |  |  |  | CDC | 276 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-AE | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR_OIL | #3DTR 油溫 | MTR | D27//3DTR/OilTemp |  |  |  | CDC | 277 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 3DTR(A) | #3DTR(A) |  | CoilTemp | [17 empty] | 1-AF | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | D27//3DTR(A)/CoilTemp |  |  |  | CDC | 278 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 3DTR(A) | #3DTR(A) |  | TapPosMv | [17 empty] | 1-B1 |  | 1-69 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | D27//3DTR(A)/TapPosMv |  |  |  | CDC | 279 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 0 |  | 3DTR(B) | #3DTR(B) |  | CoilTemp | [17 empty] | 1-B0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | D27//3DTR(B)/CoilTemp |  |  |  | CDC | 280 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D27 | 鹽行DS | 0 |  | 3DTR(B) | #3DTR(B) |  | TapPosMv | [17 empty] | 1-B2 |  | 1-6B |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | D27//3DTR(B)/TapPosMv |  |  |  | CDC | 281 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D27 | 鹽行DS | 22 | 22kV | _500 | 500 |  | I_R | [17 empty] | 2-B5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.23KV_500_A1 | 23KV 500 R相AMP | TIE |  |  |  |  | CDC | 282 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | _500 | 500 |  | I_S | [17 empty] | 2-B6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.23KV_500_A2 | 23KV 500 S相AMP | TIE |  |  |  |  | CDC | 283 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 22 | 22kV | _500 | 500 |  | I_T | [17 empty] | 2-B7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.23KV_500_A3 | 23KV 500 T相AMP | TIE |  |  |  |  | CDC | 284 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-B8 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | D27/11/1ABUS/V |  |  |  | CDC | 285 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 2-A9 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | D27/11/1BBUS/V |  |  |  | CDC | 286 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
D27 | 鹽行DS | 11 | 11kV | _300 | 300 |  | I_R | [17 empty] | 2-AF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_300_A1 | 11KV 300 R相AMP | TIE | D27/11/300/I_R |  |  |  | CDC | 287 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _300 | 300 |  | I_S | [17 empty] | 2-B0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_300_A2 | 11KV 300 S相AMP | TIE | D27/11/300/I_S |  |  |  | CDC | 288 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _300 | 300 |  | I_T | [17 empty] | 2-B1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_300_A3 | 11KV 300 T相AMP | TIE | D27/11/300/I_T |  |  |  | CDC | 289 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D27/11/310/KW |  |  |  | CDC | 290 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D27/11/310/KVAR |  |  |  | CDC | 291 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-92 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D27/11/310/I_R |  |  |  | CDC | 292 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-93 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D27/11/310/I_S |  |  |  | CDC | 293 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-94 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D27/11/310/I_T |  |  |  | CDC | 294 | GENERICAIPoint | DS032_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 2-AA | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D27/11/320/KW |  |  |  | CDC | 295 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 2-AB | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D27/11/320/KVAR |  |  |  | CDC | 296 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 2-AC | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D27/11/320/I_R |  |  |  | CDC | 297 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 2-AD | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D27/11/320/I_S |  |  |  | CDC | 298 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 2-AE | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D27/11/320/I_T |  |  |  | CDC | 299 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _400 | 400 |  | I_R | [17 empty] | 2-B2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_400_A1 | 11KV 400 R相AMP | TIE | D27/11/400/I_R |  |  |  | CDC | 300 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _400 | 400 |  | I_S | [17 empty] | 2-B3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_400_A2 | 11KV 400 S相AMP | TIE | D27/11/400/I_S |  |  |  | CDC | 301 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 11 | 11kV | _400 | 400 |  | I_T | [17 empty] | 2-B4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹽行DS.11KV_400_A3 | 11KV 400 T相AMP | TIE | D27/11/400/I_T |  |  |  | CDC | 302 | GENERICAIPoint | DS032_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | GDA | [17 empty] | 1-00-04 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1530_GDA | 安南鹽行線(1530) 接地RY | LINE161 | D27/161/1530/GDA |  |  |  | CDC | 303 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.1530_CB | 1530(安南鹽行線) CB | LINE161 | D27/161/1530/CB |  |  |  | CDC | 304 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | 79UL | [17 empty] | 1-30-03 |  | 1-41 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1530_79UL | 安南鹽行線(1530) 79RY U/L | LINE161 | D27/161/1530/79UL |  |  |  | CDC | 305 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | DS1 | 1531 | [16 empty] | 2-34-00 | 2-34-01 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1531_DS | 1531(安南鹽行線) DS | LINE161 | D27/161/1530/DS1 |  |  |  | CDC | 306 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | DS2 | 1532 | [16 empty] | 2-34-02 | 2-34-03 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1532_DS | 1532(安南鹽行線) DS | LINE161 | D27/161/1530/DS2 |  |  |  | CDC | 307 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | E2 | 1532E | [16 empty] | 2-34-04 | 2-34-05 | 2-02 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1532E_ES | 1532E(安南鹽行線) ES | LINE161 | D27/161/1530/ES2 |  |  |  | CDC | 308 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1540_GDA | 山上豐華白線(1540) 接地RY | LINE161 | D27/161/1540/GDA |  |  |  | CDC | 309 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | 85CA | [17 empty] | 2-33-12 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_85CA | 山上豐華白線(1540) 載波機故障 | LINE161 |  |  |  |  | CDC | 310 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.1540_CB | 1540(山上豐華白線) CB | LINE161 | D27/161/1540/CB |  |  |  | CDC | 311 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | 79UL | [17 empty] | 1-30-05 |  | 1-43 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_79UL | 山上豐華白線(1540) 79RY U/L | LINE161 | D27/161/1540/79UL |  |  |  | CDC | 312 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | DS1 | 1541 | [16 empty] | 2-34-08 | 2-34-09 | 2-04 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1541_DS | 1541(山上豐華白線) DS | LINE161 | D27/161/1540/DS1 |  |  |  | CDC | 313 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | DS2 | 1542 | [16 empty] | 2-34-10 | 2-34-11 | 2-05 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1542_DS | 1542(山上豐華白線) DS | LINE161 | D27/161/1540/DS2 |  |  |  | CDC | 314 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | E2 | 1542E | [16 empty] | 2-34-12 | 2-34-13 | 2-06 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1542E_ES | 1542E(山上豐華白線) ES | LINE161 | D27/161/1540/ES2 |  |  |  | CDC | 315 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | PHA | [17 empty] | 1-14-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_PHA | 11KV鹽21線(KV21) 相間RY | FEEDER | D27/11/KV21/PHA |  |  |  | CDC | 316 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) |  | GDA | [17 empty] | 1-14-05 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_GDA | 11KV鹽21線(KV21) 接地RY | FEEDER | D27/11/KV21/GDA |  |  |  | CDC | 317 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) 79RY |  | 79UL | [17 empty] | 2-30-10 |  | 2-20 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_79UL | 11KV鹽21線(KV21) 79RY U/L | FEEDER | D27/11/KV21/79UL |  |  |  | CDC | 318 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV21 | 鹽21線(KV21) LCO分流器 |  | ADJ | [17 empty] | 1-31-00 |  | 1-6C | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_ADJ | 11KV鹽21線(KV21) LCO分流器 U/L | FEEDER | D27/11/KV21/ADJ |  |  |  | CDC | 319 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV21 | KV21(11KV鹽21線) |  | CB | [17 empty] | 1-14-03 |  | 1-13 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_CB | KV21(11KV鹽21線) CB | FEEDER | D27/11/KV21/CB |  |  |  | CDC | 320 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | PHA | [17 empty] | 1-14-07 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_PHA | 11KV鹽22線(KV22) 相間RY | FEEDER | D27/11/KV22/PHA |  |  |  | CDC | 321 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) |  | GDA | [17 empty] | 1-15-00 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_GDA | 11KV鹽22線(KV22) 接地RY | FEEDER | D27/11/KV22/GDA |  |  |  | CDC | 322 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) 79RY |  | 79UL | [17 empty] | 2-30-11 |  | 2-21 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_79UL | 11KV鹽22線(KV22) 79RY U/L | FEEDER | D27/11/KV22/79UL |  |  |  | CDC | 323 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV22 | 鹽22線(KV22) LCO分流器 |  | ADJ | [17 empty] | 1-31-01 |  | 1-6D | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_ADJ | 11KV鹽22線(KV22) LCO分流器 U/L | FEEDER | D27/11/KV22/ADJ |  |  |  | CDC | 324 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV22 | KV22(11KV鹽22線) |  | CB | [17 empty] | 1-14-06 |  | 1-14 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_CB | KV22(11KV鹽22線) CB | FEEDER | D27/11/KV22/CB |  |  |  | CDC | 325 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | PHA | [17 empty] | 1-15-02 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_PHA | 11KV鹽23線(KV23) 相間RY | FEEDER | D27/11/KV23/PHA |  |  |  | CDC | 326 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) |  | GDA | [17 empty] | 1-15-03 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_GDA | 11KV鹽23線(KV23) 接地RY | FEEDER | D27/11/KV23/GDA |  |  |  | CDC | 327 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) 79RY |  | 79UL | [17 empty] | 2-30-12 |  | 2-22 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_79UL | 11KV鹽23線(KV23) 79RY U/L | FEEDER | D27/11/KV23/79UL |  |  |  | CDC | 328 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV23 | 鹽23線(KV23) LCO分流器 |  | ADJ | [17 empty] | 1-31-02 |  | 1-6E | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_ADJ | 11KV鹽23線(KV23) LCO分流器 U/L | FEEDER | D27/11/KV23/ADJ |  |  |  | CDC | 329 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV23 | KV23(11KV鹽23線) |  | CB | [17 empty] | 1-15-01 |  | 1-15 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_CB | KV23(11KV鹽23線) CB | FEEDER | D27/11/KV23/CB |  |  |  | CDC | 330 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | PHA | [17 empty] | 1-15-05 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_PHA | 11KV鹽24線(KV24) 相間RY | FEEDER | D27/11/KV24/PHA |  |  |  | CDC | 331 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_GDA | 11KV鹽24線(KV24) 接地RY | FEEDER | D27/11/KV24/GDA |  |  |  | CDC | 332 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) 79RY |  | 79UL | [17 empty] | 2-30-13 |  | 2-23 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_79UL | 11KV鹽24線(KV24) 79RY U/L | FEEDER | D27/11/KV24/79UL |  |  |  | CDC | 333 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV24 | 鹽24線(KV24) LCO分流器 |  | ADJ | [17 empty] | 1-31-03 |  | 1-6F | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_ADJ | 11KV鹽24線(KV24) LCO分流器 U/L | FEEDER | D27/11/KV24/ADJ |  |  |  | CDC | 334 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV24 | KV24(11KV鹽24線) |  | CB | [17 empty] | 1-15-04 |  | 1-16 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_CB | KV24(11KV鹽24線) CB | FEEDER | D27/11/KV24/CB |  |  |  | CDC | 335 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | PHA | [17 empty] | 1-16-00 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_PHA | 11KV鹽25線(KV25) 相間RY | FEEDER | D27/11/KV25/PHA |  |  |  | CDC | 336 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) |  | GDA | [17 empty] | 1-16-01 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_GDA | 11KV鹽25線(KV25) 接地RY | FEEDER | D27/11/KV25/GDA |  |  |  | CDC | 337 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) 79RY |  | 79UL | [17 empty] | 2-30-14 |  | 2-24 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_79UL | 11KV鹽25線(KV25) 79RY U/L | FEEDER | D27/11/KV25/79UL |  |  |  | CDC | 338 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV25 | 鹽25線(KV25) LCO分流器 |  | ADJ | [17 empty] | 1-31-04 |  | 1-70 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_ADJ | 11KV鹽25線(KV25) LCO分流器 U/L | FEEDER | D27/11/KV25/ADJ |  |  |  | CDC | 339 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV25 | KV25(11KV鹽25線) |  | CB | [17 empty] | 1-15-07 |  | 1-17 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_CB | KV25(11KV鹽25線) CB | FEEDER | D27/11/KV25/CB |  |  |  | CDC | 340 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | PHA | [17 empty] | 1-16-03 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_PHA | 11KV鹽26線(KV26) 相間RY | FEEDER | D27/11/KV26/PHA |  |  |  | CDC | 341 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) |  | GDA | [17 empty] | 1-16-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_GDA | 11KV鹽26線(KV26) 接地RY | FEEDER | D27/11/KV26/GDA |  |  |  | CDC | 342 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) 79RY |  | 79UL | [17 empty] | 2-30-15 |  | 2-25 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_79UL | 11KV鹽26線(KV26) 79RY U/L | FEEDER | D27/11/KV26/79UL |  |  |  | CDC | 343 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV26 | 鹽26線(KV26) LCO分流器 |  | ADJ | [17 empty] | 1-31-05 |  | 1-71 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_ADJ | 11KV鹽26線(KV26) LCO分流器 U/L | FEEDER | D27/11/KV26/ADJ |  |  |  | CDC | 344 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV26 | KV26(11KV鹽26線) |  | CB | [17 empty] | 1-16-02 |  | 1-18 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_CB | KV26(11KV鹽26線) CB | FEEDER | D27/11/KV26/CB |  |  |  | CDC | 345 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | PHA | [17 empty] | 1-17-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_PHA | 11KV鹽27線(KV27) 相間RY | FEEDER | D27/11/KV27/PHA |  |  |  | CDC | 346 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_GDA | 11KV鹽27線(KV27) 接地RY | FEEDER | D27/11/KV27/GDA |  |  |  | CDC | 347 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) 79RY |  | 79UL | [17 empty] | 2-31-00 |  | 2-26 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_79UL | 11KV鹽27線(KV27) 79RY U/L | FEEDER | D27/11/KV27/79UL |  |  |  | CDC | 348 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV27 | 鹽27線(KV27) LCO分流器 |  | ADJ | [17 empty] | 1-31-06 |  | 1-72 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_ADJ | 11KV鹽27線(KV27) LCO分流器 U/L | FEEDER | D27/11/KV27/ADJ |  |  |  | CDC | 349 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV27 | KV27(11KV鹽27線) |  | CB | [17 empty] | 1-17-03 |  | 1-1B | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_CB | KV27(11KV鹽27線) CB | FEEDER | D27/11/KV27/CB |  |  |  | CDC | 350 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | PHA | [17 empty] | 1-17-07 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_PHA | 11KV鹽28線(KV28) 相間RY | FEEDER | D27/11/KV28/PHA |  |  |  | CDC | 351 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_GDA | 11KV鹽28線(KV28) 接地RY | FEEDER | D27/11/KV28/GDA |  |  |  | CDC | 352 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) 79RY |  | 79UL | [17 empty] | 2-31-01 |  | 2-27 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_79UL | 11KV鹽28線(KV28) 79RY U/L | FEEDER | D27/11/KV28/79UL |  |  |  | CDC | 353 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV28 | 鹽28線(KV28) LCO分流器 |  | ADJ | [17 empty] | 1-31-07 |  | 1-73 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_ADJ | 11KV鹽28線(KV28) LCO分流器 U/L | FEEDER | D27/11/KV28/ADJ |  |  |  | CDC | 354 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV28 | KV28(11KV鹽28線) |  | CB | [17 empty] | 1-17-06 |  | 1-1C | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_CB | KV28(11KV鹽28線) CB | FEEDER | D27/11/KV28/CB |  |  |  | CDC | 355 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_PHA | 11KV鹽29線(KV29) 相間RY | FEEDER | D27/11/KV29/PHA |  |  |  | CDC | 356 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_GDA | 11KV鹽29線(KV29) 接地RY | FEEDER | D27/11/KV29/GDA |  |  |  | CDC | 357 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) 79RY |  | 79UL | [17 empty] | 2-31-02 |  | 2-28 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_79UL | 11KV鹽29線(KV29) 79RY U/L | FEEDER | D27/11/KV29/79UL |  |  |  | CDC | 358 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV29 | 鹽29線(KV29) LCO分流器 |  | ADJ | [17 empty] | 1-31-08 |  | 1-74 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_ADJ | 11KV鹽29線(KV29) LCO分流器 U/L | FEEDER | D27/11/KV29/ADJ |  |  |  | CDC | 359 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV29 | KV29(11KV鹽29線) |  | CB | [17 empty] | 1-18-01 |  | 1-1D | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_CB | KV29(11KV鹽29線) CB | FEEDER | D27/11/KV29/CB |  |  |  | CDC | 360 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | PHA | [17 empty] | 1-18-05 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_PHA | 11KV鹽30線(KV30) 相間RY | FEEDER | D27/11/KV30/PHA |  |  |  | CDC | 361 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) |  | GDA | [17 empty] | 1-18-06 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_GDA | 11KV鹽30線(KV30) 接地RY | FEEDER | D27/11/KV30/GDA |  |  |  | CDC | 362 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) 79RY |  | 79UL | [17 empty] | 2-31-03 |  | 2-29 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_79UL | 11KV鹽30線(KV30) 79RY U/L | FEEDER | D27/11/KV30/79UL |  |  |  | CDC | 363 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV30 | 鹽30線(KV30) LCO分流器 |  | ADJ | [17 empty] | 1-31-09 |  | 1-75 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_ADJ | 11KV鹽30線(KV30) LCO分流器 U/L | FEEDER | D27/11/KV30/ADJ |  |  |  | CDC | 364 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV30 | KV30(11KV鹽30線) |  | CB | [17 empty] | 1-18-04 |  | 1-1E | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_CB | KV30(11KV鹽30線) CB | FEEDER | D27/11/KV30/CB |  |  |  | CDC | 365 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | PHA | [17 empty] | 1-19-06 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_PHA | 11KV鹽31線(KV31) 相間RY | FEEDER | D27/11/KV31/PHA |  |  |  | CDC | 366 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) |  | GDA | [17 empty] | 1-19-07 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_GDA | 11KV鹽31線(KV31) 接地RY | FEEDER | D27/11/KV31/GDA |  |  |  | CDC | 367 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) 79RY |  | 79UL | [17 empty] | 2-31-04 |  | 2-2A | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_79UL | 11KV鹽31線(KV31) 79RY U/L | FEEDER | D27/11/KV31/79UL |  |  |  | CDC | 368 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV31 | 鹽31線(KV31) LCO分流器 |  | ADJ | [17 empty] | 1-31-10 |  | 1-76 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_ADJ | 11KV鹽31線(KV31) LCO分流器 U/L | FEEDER | D27/11/KV31/ADJ |  |  |  | CDC | 369 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV31 | KV31(11KV鹽31線) |  | CB | [17 empty] | 1-19-05 |  | 1-23 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_CB | KV31(11KV鹽31線) CB | FEEDER | D27/11/KV31/CB |  |  |  | CDC | 370 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | PHA | [17 empty] | 1-1A-01 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_PHA | 11KV鹽32線(KV32) 相間RY | FEEDER | D27/11/KV32/PHA |  |  |  | CDC | 371 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) |  | GDA | [17 empty] | 1-1A-02 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_GDA | 11KV鹽32線(KV32) 接地RY | FEEDER | D27/11/KV32/GDA |  |  |  | CDC | 372 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) 79RY |  | 79UL | [17 empty] | 2-31-05 |  | 2-2B | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_79UL | 11KV鹽32線(KV32) 79RY U/L | FEEDER | D27/11/KV32/79UL |  |  |  | CDC | 373 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV32 | 鹽32線(KV32) LCO分流器 |  | ADJ | [17 empty] | 1-31-11 |  | 1-77 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_ADJ | 11KV鹽32線(KV32) LCO分流器 U/L | FEEDER | D27/11/KV32/ADJ |  |  |  | CDC | 374 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV32 | KV32(11KV鹽32線) |  | CB | [17 empty] | 1-1A-00 |  | 1-24 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_CB | KV32(11KV鹽32線) CB | FEEDER | D27/11/KV32/CB |  |  |  | CDC | 375 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | PHA | [17 empty] | 1-1A-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_PHA | 11KV鹽33線(KV33) 相間RY | FEEDER | D27/11/KV33/PHA |  |  |  | CDC | 376 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) |  | GDA | [17 empty] | 1-1A-05 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_GDA | 11KV鹽33線(KV33) 接地RY | FEEDER | D27/11/KV33/GDA |  |  |  | CDC | 377 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) 79RY |  | 79UL | [17 empty] | 2-31-06 |  | 2-2C | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_79UL | 11KV鹽33線(KV33) 79RY U/L | FEEDER | D27/11/KV33/79UL |  |  |  | CDC | 378 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV33 | 鹽33線(KV33) LCO分流器 |  | ADJ | [17 empty] | 1-31-12 |  | 1-78 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_ADJ | 11KV鹽33線(KV33) LCO分流器 U/L | FEEDER | D27/11/KV33/ADJ |  |  |  | CDC | 379 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV33 | KV33(11KV鹽33線) |  | CB | [17 empty] | 1-1A-03 |  | 1-25 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_CB | KV33(11KV鹽33線) CB | FEEDER | D27/11/KV33/CB |  |  |  | CDC | 380 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | PHA | [17 empty] | 1-1A-07 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_PHA | 11KV鹽34線(KV34) 相間RY | FEEDER | D27/11/KV34/PHA |  |  |  | CDC | 381 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) |  | GDA | [17 empty] | 1-1B-00 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_GDA | 11KV鹽34線(KV34) 接地RY | FEEDER | D27/11/KV34/GDA |  |  |  | CDC | 382 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) 79RY |  | 79UL | [17 empty] | 2-31-07 |  | 2-2D | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_79UL | 11KV鹽34線(KV34) 79RY U/L | FEEDER | D27/11/KV34/79UL |  |  |  | CDC | 383 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | KV34 | 鹽34線(KV34) LCO分流器 |  | ADJ | [17 empty] | 1-31-13 |  | 1-79 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_ADJ | 11KV鹽34線(KV34) LCO分流器 U/L | FEEDER | D27/11/KV34/ADJ |  |  |  | CDC | 384 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 11 | 11kV | KV34 | KV34(11KV鹽34線) |  | CB | [17 empty] | 1-1A-06 |  | 1-26 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_CB | KV34(11KV鹽34線) CB | FEEDER | D27/11/KV34/CB |  |  |  | CDC | 385 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | PHA | [17 empty] | 1-1C-06 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_PHA | 23KV鹽73線(KV73) 相間RY | FEEDER | D27/22/KV73/PHA |  |  |  | CDC | 386 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) |  | GDA | [17 empty] | 1-1C-07 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_GDA | 23KV鹽73線(KV73) 接地RY | FEEDER | D27/22/KV73/GDA |  |  |  | CDC | 387 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) 79RY |  | 79UL | [17 empty] | 2-31-10 |  | 2-30 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_79UL | 23KV鹽73線(KV73) 79RY U/L | FEEDER | D27/22/KV73/79UL |  |  |  | CDC | 388 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV73 | 鹽73線(KV73) LCO分流器 |  | ADJ | [17 empty] | 1-32-00 |  | 1-7C | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_ADJ | 23KV鹽73線(KV73) LCO分流器 U/L | FEEDER | D27/22/KV73/ADJ |  |  |  | CDC | 389 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV73 | KV73(23KV鹽73線) |  | CB | [17 empty] | 1-1C-05 |  | 1-2B | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_CB | KV73(23KV鹽73線) CB | FEEDER | D27/22/KV73/CB |  |  |  | CDC | 390 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | PHA | [17 empty] | 1-1D-01 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_PHA | 23KV鹽74線(KV74) 相間RY | FEEDER | D27/22/KV74/PHA |  |  |  | CDC | 391 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) |  | GDA | [17 empty] | 1-1D-02 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_GDA | 23KV鹽74線(KV74) 接地RY | FEEDER | D27/22/KV74/GDA |  |  |  | CDC | 392 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) 79RY |  | 79UL | [17 empty] | 2-31-11 |  | 2-31 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_79UL | 23KV鹽74線(KV74) 79RY U/L | FEEDER | D27/22/KV74/79UL |  |  |  | CDC | 393 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV74 | 鹽74線(KV74) LCO分流器 |  | ADJ | [17 empty] | 1-32-01 |  | 1-7D | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_ADJ | 23KV鹽74線(KV74) LCO分流器 U/L | FEEDER | D27/22/KV74/ADJ |  |  |  | CDC | 394 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV74 | KV74(23KV鹽74線) |  | CB | [17 empty] | 1-1D-00 |  | 1-2C | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_CB | KV74(23KV鹽74線) CB | FEEDER | D27/22/KV74/CB |  |  |  | CDC | 395 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | PHA | [17 empty] | 1-1D-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_PHA | 23KV鹽75線(KV75) 相間RY | FEEDER | D27/22/KV75/PHA |  |  |  | CDC | 396 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) |  | GDA | [17 empty] | 1-1D-05 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_GDA | 23KV鹽75線(KV75) 接地RY | FEEDER | D27/22/KV75/GDA |  |  |  | CDC | 397 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) 79RY |  | 79UL | [17 empty] | 2-31-12 |  | 2-32 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_79UL | 23KV鹽75線(KV75) 79RY U/L | FEEDER | D27/22/KV75/79UL |  |  |  | CDC | 398 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV75 | 鹽75線(KV75) LCO分流器 |  | ADJ | [17 empty] | 1-32-02 |  | 1-7E | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_ADJ | 23KV鹽75線(KV75) LCO分流器 U/L | FEEDER | D27/22/KV75/ADJ |  |  |  | CDC | 399 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV75 | KV75(23KV鹽75線) |  | CB | [17 empty] | 1-1D-03 |  | 1-2D | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_CB | KV75(23KV鹽75線) CB | FEEDER | D27/22/KV75/CB |  |  |  | CDC | 400 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | PHA | [17 empty] | 1-1D-07 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_PHA | 23KV鹽76線(KV76) 相間RY | FEEDER | D27/22/KV76/PHA |  |  |  | CDC | 401 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) |  | GDA | [17 empty] | 1-1E-00 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_GDA | 23KV鹽76線(KV76) 接地RY | FEEDER | D27/22/KV76/GDA |  |  |  | CDC | 402 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) 79RY |  | 79UL | [17 empty] | 2-31-13 |  | 2-33 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_79UL | 23KV鹽76線(KV76) 79RY U/L | FEEDER | D27/22/KV76/79UL |  |  |  | CDC | 403 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV76 | 鹽76線(KV76) LCO分流器 |  | ADJ | [17 empty] | 1-32-03 |  | 1-7F | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_ADJ | 23KV鹽76線(KV76) LCO分流器 U/L | FEEDER | D27/22/KV76/ADJ |  |  |  | CDC | 404 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV76 | KV76(23KV鹽76線) |  | CB | [17 empty] | 1-1D-06 |  | 1-2E | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_CB | KV76(23KV鹽76線) CB | FEEDER | D27/22/KV76/CB |  |  |  | CDC | 405 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-04-05 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.1750_CB | 1750(#1DTR) CB | MTR | D27/161/1750/CB |  |  |  | CDC | 406 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-05-03 |  | 1-10 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.310_CB | 310(#1DTR) CB | MTR | D27/11/310/CB |  |  |  | CDC | 407 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 2-38-04 | 2-38-05 | 2-12 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1751_DS | 1751(#1DTR) DS | MTR | D27/161/1750/DS1 |  |  |  | CDC | 408 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-05-07 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.1760_CB | 1760(#2DTR) CB | MTR | D27/161/1760/CB |  |  |  | CDC | 409 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-0A-01 |  | 1-31 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.320_CB | 320(#1DTR) CB | MTR | D27/11/320/CB |  |  |  | CDC | 410 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-06-05 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.340_CB | 340(#2DTR) CB | MTR | D27/11/340/CB |  |  |  | CDC | 411 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 2-38-08 | 2-38-09 | 2-14 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1761_DS | 1761(#2DTR) DS | MTR | D27/161/1760/DS1 |  |  |  | CDC | 412 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-07-01 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.1770_CB | 1770(#3DTR) CB | MTR | D27/161/1770/CB |  |  |  | CDC | 413 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-06-07 |  | 1-21 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.330_CB | 330(#2DTR) CB | MTR | D27/11/330/CB |  |  |  | CDC | 414 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 2-38-12 | 2-38-13 | 2-16 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1771_DS | 1771(#3DTR) DS | MTR | D27/161/1770/DS1 |  |  |  | CDC | 415 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-14-00 |  | 1-12 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.210_CB | 210(11KV #1SC) CB | SC | D27/11/210/CB |  |  |  | CDC | 416 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.210_SCA | 11KV #1SC 51,51N RY | SC | D27/11/210/SCA |  |  |  | CDC | 417 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-14-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | D27/11/210/UVA |  |  |  | CDC | 418 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-16-05 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.220_CB | 220(11KV #2SC) CB | SC | D27/11/220/CB |  |  |  | CDC | 419 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-16-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.220_SCA | 11KV #2SC 51,51N RY | SC | D27/11/220/SCA |  |  |  | CDC | 420 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-16-07 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | D27/11/220/UVA |  |  |  | CDC | 421 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-19-02 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.230_CB | 230(11KV #3SC) CB | SC | D27/11/230/CB |  |  |  | CDC | 422 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-19-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.230_SCA | 11KV #3SC 51,51N RY | SC | D27/11/230/SCA |  |  |  | CDC | 423 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-19-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | D27/11/230/UVA |  |  |  | CDC | 424 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-18-07 |  | 1-1F | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.240_CB | 240(11KV #4SC) CB | SC | D27/11/240/CB |  |  |  | CDC | 425 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-19-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.240_SCA | 11KV #4SC 51,51N RY | SC | D27/11/240/SCA |  |  |  | CDC | 426 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-19-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | D27/11/240/UVA |  |  |  | CDC | 427 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-1E-01 |  | 1-2F | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.250_CB | 250(23KV #5SC) CB | SC | D27/22/250/CB |  |  |  | CDC | 428 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-1E-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.250_SCA | 23KV #5SC 51,51N RY | SC | D27/22/250/SCA |  |  |  | CDC | 429 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-1E-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | D27/22/250/UVA |  |  |  | CDC | 430 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-1B-04 |  | 1-28 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.260_CB | 260(23KV #6SC) CB | SC | D27/22/260/CB |  |  |  | CDC | 431 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-1B-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.260_SCA | 23KV #6SC 51,51N RY | SC | D27/22/260/SCA |  |  |  | CDC | 432 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-1B-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | D27/22/260/UVA |  |  |  | CDC | 433 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-33-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D27/0/ComPoint/BUS_VUA |  |  |  | CDC | 434 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1500 | 1501(1500) |  | DS1 | 1501 | [16 empty] | 2-38-00 | 2-38-01 | 2-10 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1501_DS | 1501 DS | BUS | D27/161/1500/DS1 |  |  |  | CDC | 435 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-33-10 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D27/161/2BUS/BUS_VUA |  |  |  | CDC | 436 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 1-34-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D27/11/ComPoint/CBA |  |  |  | CDC | 437 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 1-34-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D27/11/ComPoint/CBF |  |  |  | CDC | 438 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 11 | 11kV | _SC | 23/ SC |  | 60A | [17 empty] | 2-33-13 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.11KV_SC_60A | 23/11KV SC 60A | OTHER | D27/0/ComPoint/60A |  |  |  | CDC | 439 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-34-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D27/161/ComPoint/CBA |  |  |  | CDC | 440 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-34-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D27/161/ComPoint/CBF |  |  |  | CDC | 441 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-08-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D27/0/ComPoint/RCA |  |  |  | CDC | 442 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 81RY | 81RY |  | A/S(2) | [17 empty] | 1-1E-05 |  | 2-1F | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.81RY_A/S(2) | K31-K34低頻電驛動作/復歸 | OTHER | D27/11/ComPoint/81AS2 |  |  |  | CDC | 443 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D27 | 鹽行DS | 0 |  |  |  |  | OSCA | [17 empty] | 1-08-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.OSC啟動 | 示波器啟動警報 | OTHER | D27/161/ComPoint/OSCA |  |  |  | CDC | 444 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.RTU_S/L | RTU SUPY/LOCAL | OTHER | D27/0/RTU/RTU_R_L |  |  |  | CDC | 445 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D27 | 鹽行DS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.TEST_CB | TEST CB | OTHER | D27/0/RTU/Test_CB |  |  |  | CDC | 446 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-32-10 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D27/0/StaDev/Fire1 |  |  |  | CDC | 447 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | OPA | [17 empty] | 2-33-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | D27/0/ComPoint/OPA |  |  |  | CDC | 448 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-33-06 |  | 2-18 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D27/0/StaDev/ACB1 |  |  |  | CDC | 449 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D27 | 鹽行DS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-33-07 |  | 2-19 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D27/0/StaDev/ACB2 |  |  |  | CDC | 450 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
D27 | 鹽行DS | 0 |  |  |  |  | ACBA | [17 empty] | 1-34-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.所內電源ACBA | 所內電源故障警報 | OTHER | D27/0/StaDev/ACBA |  |  |  | CDC | 451 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | STUV | [17 empty] | 2-33-08 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D27/0/StaDev/STUV |  |  |  | CDC | 452 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | DCA | [17 empty] | 2-33-14 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.直流電源DCA | 直流電源故障警報 | OTHER | D27/0/StaDev/DCA |  |  |  | CDC | 453 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | DCE | [17 empty] | 2-33-15 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D27/0/StaDev/DCE |  |  |  | CDC | 454 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-34-07 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.洩油池水位警報 | 洩油池水位警報 | OTHER | D27/0/StaDev/OilLeak1 |  |  |  | CDC | 455 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | CommACF | [17 empty] | 1-34-12 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D27/0/StaDev/CommACF |  |  |  | CDC | 456 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-13 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D27/0/StaDev/Burglar1 |  |  |  | CDC | 457 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | Door1 | [17 empty] | 2-33-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.無人化門禁(1) | 無人化門禁(1)大小門 | OTHER | D27/0/StaDev/Door1 |  |  |  | CDC | 458 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-33-03 |  | 2-3E | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.開關場照明(A) | 開關場照明(A) | OTHER | D27/0/StaDev/Lights1 |  |  |  | CDC | 459 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D27 | 鹽行DS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-33-04 |  | 2-3F | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.開關場照明(B) | 開關場照明(B) | OTHER | D27/0/StaDev/Lights2 |  |  |  | CDC | 460 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D27 | 鹽行DS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 1-34-08 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.空調機跳脫警報 | 空調機故障電源跳脫 | OTHER | D27/0/StaDev/AIRCON |  |  |  | CDC | 461 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | PHA | [17 empty] | 1-1C-03 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_PHA | 23KV鹽72線(KV72) 相間RY | FEEDER | D27/22/KV72/PHA |  |  |  | CDC | 462 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) |  | GDA | [17 empty] | 1-1C-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_GDA | 23KV鹽72線(KV72) 接地RY | FEEDER | D27/22/KV72/GDA |  |  |  | CDC | 463 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) 79RY |  | 79UL | [17 empty] | 2-31-09 |  | 2-2F | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_79UL | 23KV鹽72線(KV72) 79RY U/L | FEEDER | D27/22/KV72/79UL |  |  |  | CDC | 464 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV72 | 鹽72線(KV72) LCO分流器 |  | ADJ | [17 empty] | 1-31-15 |  | 1-7B | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_ADJ | 23KV鹽72線(KV72) LCO分流器 U/L | FEEDER | D27/22/KV72/ADJ |  |  |  | CDC | 465 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV72 | KV72(23KV鹽72線) |  | CB | [17 empty] | 1-1C-02 |  | 1-2A | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_CB | KV72(23KV鹽72線) CB | FEEDER | D27/22/KV72/CB |  |  |  | CDC | 466 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.水位警報(1) | 地下室水位警報(1) | OTHER | D27/0/StaDev/Water1 |  |  |  | CDC | 467 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-34-11 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.水位警報(2) | 地下室水位警報(2) | OTHER | D27/0/StaDev/Water2 |  |  |  | CDC | 468 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | PHA | [17 empty] | 1-1C-00 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_PHA | 23KV鹽71線(KV71) 相間RY | FEEDER | D27/22/KV71/PHA |  |  |  | CDC | 469 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) |  | GDA | [17 empty] | 1-1C-01 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_GDA | 23KV鹽71線(KV71) 接地RY | FEEDER | D27/22/KV71/GDA |  |  |  | CDC | 470 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) 79RY |  | 79UL | [17 empty] | 2-31-08 |  | 2-2E | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_79UL | 23KV鹽71線(KV71) 79RY U/L | FEEDER | D27/22/KV71/79UL |  |  |  | CDC | 471 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 22 | 22kV | KV71 | 鹽71線(KV71) LCO分流器 |  | ADJ | [17 empty] | 1-31-14 |  | 1-7A | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_ADJ | 23KV鹽71線(KV71) LCO分流器 U/L | FEEDER | D27/22/KV71/ADJ |  |  |  | CDC | 472 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
D27 | 鹽行DS | 22 | 22kV | KV71 | KV71(23KV鹽71線) |  | CB | [17 empty] | 1-1B-07 |  | 1-29 | [5 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_CB | KV71(23KV鹽71線) CB | FEEDER | D27/22/KV71/CB |  |  |  | CDC | 473 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-34-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | D27/0/StaDev/CHG1 |  |  |  | CDC | 474 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-34-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D27/0/StaDev/CHG2 |  |  |  | CDC | 475 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-34-15 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.通信機房溫度 | 通信機房溫度警報 | OTHER | D27/0/StaDev/R_Temp |  |  |  | CDC | 476 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-17-00 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.100_CB | 100(TIE) CB | TIE | D27/11/100/CB |  |  |  | CDC | 477 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-17-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.100_51A | 11KV TIE(100) 51RY | TIE | D27/11/100/PHA |  |  |  | CDC | 478 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-17-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.100_51NA | 11KV TIE(100) 51N RY | TIE | D27/11/100/GDA |  |  |  | CDC | 479 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-1B-01 |  | 1-27 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.200_CB | 200(TIE) CB | TIE | D27/11/200/CB |  |  |  | CDC | 480 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-1B-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.200_51A | 11KV TIE(200) 51RY | TIE | D27/11/200/PHA |  |  |  | CDC | 481 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-1B-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.200_51NA | 11KV TIE(200) 51N RY | TIE | D27/11/200/GDA |  |  |  | CDC | 482 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-05-01 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#1DTR_51A | #1DTR 51RY | MTR | D27/161/1750/PHA |  |  |  | CDC | 483 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-05-02 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#1DTR_51NA | #1DTR 51N RY | MTR | D27/161/1750/GDA |  |  |  | CDC | 484 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-05-00 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D27//1DTR/51ZA |  |  |  | CDC | 485 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-04-07 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D27//1DTR/96PA |  |  |  | CDC | 486 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_96D | #1DTR 96D RY | MTR | D27//1DTR/96D |  |  |  | CDC | 487 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_96P | #1DTR 96P RY | MTR | D27//1DTR/96P |  |  |  | CDC | 488 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-30-10 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D27//1DTR/63Q |  |  |  | CDC | 489 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-30-11 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D27//1DTR/96B1 |  |  |  | CDC | 490 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-30-12 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D27//1DTR/96B2 |  |  |  | CDC | 491 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_TRA | #1DTR 重故障 | MTR | D27//1DTR/TRA |  |  |  | CDC | 492 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D27//1DTR/TRF |  |  |  | CDC | 493 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | D27//1DTR(A)/SupLocal |  |  |  | CDC | 494 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-32-12 |  | 1-60 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | D27//1DTR(A)/Tap Chan |  |  |  | CDC | 495 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-32-15 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | D27//1DTR(B)/SupLocal |  |  |  | CDC | 496 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-33-00 |  | 1-62 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | D27//1DTR(B)/Tap Chan |  |  |  | CDC | 497 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-06-03 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#2DTR_51A | #2DTR 51RY | MTR | D27/161/1760/PHA |  |  |  | CDC | 498 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-06-04 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#2DTR_51NA | #2DTR 51N RY | MTR | D27/161/1760/GDA |  |  |  | CDC | 499 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-06-02 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D27//2DTR/51ZA |  |  |  | CDC | 500 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-06-01 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D27//2DTR/96PA |  |  |  | CDC | 501 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-30-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_96D | #2DTR 96D RY | MTR | D27//2DTR/96D |  |  |  | CDC | 502 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-30-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_96P | #2DTR 96P RY | MTR | D27//2DTR/96P |  |  |  | CDC | 503 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-30-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D27//2DTR/63Q |  |  |  | CDC | 504 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-30-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D27//2DTR/96B1 |  |  |  | CDC | 505 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-30-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D27//2DTR/96B2 |  |  |  | CDC | 506 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-33-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_TRA | #2DTR 重故障 | MTR | D27//2DTR/TRA |  |  |  | CDC | 507 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D27//2DTR/TRF |  |  |  | CDC | 508 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | D27//2DTR(A)/SupLocal |  |  |  | CDC | 509 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-33-03 |  | 1-64 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | D27//2DTR(A)/Tap Chan |  |  |  | CDC | 510 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | D27//2DTR(B)/SupLocal |  |  |  | CDC | 511 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-33-07 |  | 1-66 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | D27//2DTR(B)/Tap Chan |  |  |  | CDC | 512 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D27 | 鹽行DS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-07-07 |  | 1-30 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.350_CB | 350(#3DTR) CB | MTR | D27/22/350/CB |  |  |  | CDC | 513 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#3DTR_51ZA | #3DTR 51Z RY | MTR | D27//3DTR/51ZA |  |  |  | CDC | 514 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | D27//3DTR/96PA |  |  |  | CDC | 515 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 2-30-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_96D | #3DTR 96D RY | MTR | D27//3DTR/96D |  |  |  | CDC | 516 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 2-30-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_96P | #3DTR 96P RY | MTR | D27//3DTR/96P |  |  |  | CDC | 517 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 2-30-07 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_63Q | #3DTR 63Q RY | MTR | D27//3DTR/63Q |  |  |  | CDC | 518 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 2-30-08 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | D27//3DTR/96B1 |  |  |  | CDC | 519 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 2-30-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | D27//3DTR/96B2 |  |  |  | CDC | 520 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_TRA | #3DTR 重故障 | MTR | D27//3DTR/TRA |  |  |  | CDC | 521 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-33-12 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_TRF | #3DTR 輕故障 | MTR | D27//3DTR/TRF |  |  |  | CDC | 522 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR(A) | #3DTR(A) |  | SupLocal | [17 empty] | 1-33-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | D27//3DTR(A)/SupLocal |  |  |  | CDC | 523 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS | 0 |  | 3DTR(A) | #3DTR(A) |  | A_M | [17 empty] | 1-33-10 |  | 1-68 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | D27//3DTR(A)/Tap Chan |  |  |  | CDC | 524 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D27 | 鹽行DS | 0 |  | 3DTR(B) | #3DTR(B) |  | SupLocal | [17 empty] | 1-33-13 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | D27//3DTR(B)/SupLocal |  |  |  | CDC | 525 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D27 | 鹽行DS | 0 |  | 3DTR(B) | #3DTR(B) |  | A_M | [17 empty] | 1-33-14 |  | 1-6A | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | D27//3DTR(B)/Tap Chan |  |  |  | CDC | 526 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D27 | 鹽行DS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-34-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | D27/161/ComPoint/OSCF |  |  |  | CDC | 527 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | PHA | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1530_PHA | 安南鹽行線(1530) 相間RY | LINE161 | D27/161/1530/PHA |  |  |  | CDC | 528 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1530_87A | 安南鹽行線(1530) 87RY | LINE161 | D27/161/1530/87A |  |  |  | CDC | 529 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | 87UL | [17 empty] | 1-30-02 |  | 1-40 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1530_87UL | 安南鹽行線(1530) 87RY U/L | LINE161 | D27/161/1530/87UL |  |  |  | CDC | 530 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 1530 | 安南鹽行線(1530) |  | 87CFA | [17 empty] | 2-32-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.1530_87CFA | 安南鹽行線(1530)87RY通訊故障 | OTHER | D27/161/1530/87CFA |  |  |  | CDC | 531 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1530 | 安南鹽行線(1530) |  | RYFA | [17 empty] | 2-32-08 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.1530_RYFA | 安南鹽行線(1530)數位電驛故障 | OTHER | D27/161/1530/RYFA |  |  |  | CDC | 532 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | FEEDER | FEEDER |  | 81RYFA | [17 empty] | 1-32-04 | [7 empty] | DDCS4_2 | [8 empty] | 鹽行DS.FEEDER_81RYFA | 饋線低頻電驛故障 | OTHER | D27/0/ComPoint/RYFA |  |  |  | CDC | 533 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | BVS | BVS |  | RY | [17 empty] | 1-35-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.BVS_RY | BVS GRZ100 RY U/L | OTHER | D27/0/ComPoint/GRZ100 |  |  |  | CDC | 534 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1540_PHA | 山上豐華白線(1540) 相間RY | LINE161 | D27/161/1540/PHA |  |  |  | CDC | 535 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | 87A1 | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1540_87A1 | 山上豐華白線(1540) #1 87RY | LINE161 | D27/161/1540/87A1 |  |  |  | CDC | 536 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | 87A2 | [17 empty] | 1-00-07 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.1540_87A2 | 山上豐華白線(1540) #2 87RY | LINE161 | D27/161/1540/87A2 |  |  |  | CDC | 537 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | 1_87UL1 | [17 empty] | 1-30-04 |  | 1-42 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_87UL1 | 山上豐華白線(1540) #1 87RY U/L | LINE161 | D27/161/1540/1_87UL1 |  |  |  | CDC | 538 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | 1_87UL2 | [17 empty] | 1-30-15 |  | 1-46 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_87UL2 | 山上豐華白線(1540) #2 87RY U/L | LINE161 | D27/161/1540/1_87UL2 |  |  |  | CDC | 539 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 1540 | 山上豐華白線(1540) |  | 87CFA | [17 empty] | 1-30-13 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_87CFA | 山上豐華白線(1540)87RY通訊故障 | OTHER | D27/161/1540/87CFA |  |  |  | CDC | 540 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1540 | 山上豐華白線(1540) |  | RYFA | [17 empty] | 1-30-14 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.1540_RYFA | 山上豐華白線(1540)數位電驛故障 | OTHER | D27/161/1540/RYFA |  |  |  | CDC | 541 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | GEN | [17 empty] | 2-32-11 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.GEN | 緊急發電機運轉 | OTHER | D27/0/ComPoint/1A5Other |  |  |  | CDC | 542 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D27 | 鹽行DS | 0 |  | 500 | TIE(500) |  | CB | [17 empty] | 1-0C-02 |  | 1-36 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.500_CB | 500(TIE) CB | TIE |  |  |  |  | CDC | 543 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 500 | TIE(500) |  | 51A | [17 empty] | 1-0C-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.500_51A | 23KV TIE(500) 51RY | TIE |  |  |  |  | CDC | 544 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 500 | TIE(500) |  | 51NA | [17 empty] | 1-0C-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.500_51NA | 23KV TIE(500) 51N RY | TIE |  |  |  |  | CDC | 545 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 1-0B-01 |  | 1-33 | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.490_CB | 490(#2SSTR) CB | OTHER | D27/22/490/CB |  |  |  | CDC | 546 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 1-0B-02 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D27/22/490/PHA |  |  |  | CDC | 547 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 1-0B-03 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D27/22/490/GDA |  |  |  | CDC | 548 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 2-38-14 | 2-38-15 | [6 empty] | ADCS_S | [8 empty] | 鹽行DS.1772_DS | 1772(#3DTR) DS | MTR | D27/161/1770/DS2 |  |  |  | CDC | 549 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [17 empty] | 1-35-09 |  | 2-0C | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_51ZUL | #3DTR 51Z RY U/L | OTHER | D27//3DTR/51Z_UL |  |  |  | CDC | 550 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 81AS | [17 empty] | 1-09-07 |  | 2-08 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_81AS | #3DTR 81RY動作/復歸 | OTHER | D27//3DTR/81A |  |  |  | CDC | 551 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 81UL | [17 empty] | 1-35-10 |  | 2-09 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_81UL | #3DTR 81RY U/L | OTHER | D27//3DTR/81UL |  |  |  | CDC | 552 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_86A | #3DTR 86(50/50N/51Z/87/96)RY | OTHER | D27//3DTR/DTR_86A |  |  |  | CDC | 553 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [17 empty] | 1-33-08 |  | 2-0A | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_87UL1 | #3DTR 第一套87RY U/L | OTHER | D27//3DTR/1_87UL1 |  |  |  | CDC | 554 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [17 empty] | 1-35-08 |  | 2-0B | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_87UL2 | #3DTR 第二套87RY U/L | OTHER | D27//3DTR/1_87UL2 |  |  |  | CDC | 555 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | RYFA | [17 empty] | 1-35-07 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_RYFA | #3DTR 數位電驛故障 | OTHER | D27//3DTR/RYFA |  |  |  | CDC | 556 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 22 | 22kV | 11_ | 11/ |  | LOA | [17 empty] | 2-31-14 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.11/23KV_LOA | 11/23KV饋線復閉失敗 | OTHER | D27/0/ComPoint/LOA |  |  |  | CDC | 557 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | E2 | 1772E | [16 empty] | 2-39-00 | 2-39-01 | [6 empty] | ADCS_S | [8 empty] | 鹽行DS.1772E_ES | 1772E(#3DTR) ES | OTHER | D27/161/1770/ES2 |  |  |  | CDC | 558 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D27 | 鹽行DS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.350_GDA | #3DTR二次側(350) GDA | OTHER | D27/22/350/GDA |  |  |  | CDC | 559 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 350 | #3DTR(350) |  | PHA | [17 empty] | 1-08-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.350_PHA | #3DTR二次側(350) PHA | MTR | D27/22/350/PHA |  |  |  | CDC | 560 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | PHA | [17 empty] | 1-07-05 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#3DTR_PHA | #3DTR PHA | MTR | D27/161/1770/PHA |  |  |  | CDC | 561 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | GDA | [17 empty] | 1-07-06 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#3DTR_GDA | #3DTR GDA | MTR | D27/161/1770/GDA |  |  |  | CDC | 562 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  |  |  |  | PMA | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.PMA | 電力量測表計故障 | OTHER | D27/0/StaDev/PMA |  |  |  | CDC | 563 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 87A1 | [17 empty] | 1-07-02 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#3DTR_87A1 | #3DTR 第一套87RY | MTR | D27//3DTR/87A1 |  |  |  | CDC | 564 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 3DTR | #3DTR |  | 87A2 | [17 empty] | 1-0A-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#3DTR_87A2 | #3DTR 第二套87RY | OTHER | D27//3DTR/87A2 |  |  |  | CDC | 565 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 1-0B-04 |  | 1-34 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.300_CB | 300(TIE) CB | TIE | D27/11/300/CB |  |  |  | CDC | 566 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 1-0B-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.300_51A | 11KV TIE(300) 51RY | TIE | D27/11/300/PHA |  |  |  | CDC | 567 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 1-0B-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.300_51NA | 11KV TIE(300) 51N RY | TIE | D27/11/300/GDA |  |  |  | CDC | 568 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 1-0A-06 |  | 1-32 | [5 empty] | 161KV_S | [8 empty] | 鹽行DS.390_CB | 390(#1SSTR) CB | OTHER | D27/11/390/CB |  |  |  | CDC | 569 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 1-0A-07 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D27/11/390/PHA |  |  |  | CDC | 570 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 1-0B-00 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D27/11/390/GDA |  |  |  | CDC | 571 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-32-02 |  | 2-38 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_51ZUL | #1DTR 51Z RY U/L | OTHER | D27//1DTR/51Z_UL |  |  |  | CDC | 572 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 81AS | [17 empty] | 1-09-01 |  | 2-34 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_81AS | #1DTR 81RY動作/復歸 | OTHER | D27//1DTR/81A |  |  |  | CDC | 573 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 81UL | [17 empty] | 2-32-03 |  | 2-35 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_81UL | #1DTR 81RY U/L | OTHER | D27//1DTR/81UL |  |  |  | CDC | 574 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [17 empty] | 1-09-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_86A | #1DTR 86(50/50N/51Z/87/96)RY | OTHER | D27//1DTR/DTR_86A |  |  |  | CDC | 575 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 87A2 | [17 empty] | 1-09-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_87A2 | #1DTR 第二套87RY | OTHER | D27//1DTR/87A2 |  |  |  | CDC | 576 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [17 empty] | 1-32-10 |  | 2-36 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_87UL1 | #1DTR 87RY1 U/L | OTHER | D27//1DTR/1_87UL1 |  |  |  | CDC | 577 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [17 empty] | 2-32-01 |  | 2-37 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_87UL2 | #1DTR 87RY2 U/L | OTHER | D27//1DTR/1_87UL2 |  |  |  | CDC | 578 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | RYFA | [17 empty] | 2-32-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_RYFA | #1DTR 數位電驛故障 | OTHER | D27//1DTR/RYFA |  |  |  | CDC | 579 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-05-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.310_GDA | #1DTR二次側(310) GDA | OTHER | D27/11/310/GDA |  |  |  | CDC | 580 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 310 | #1DTR(310) |  | PHA | [17 empty] | 1-05-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.310_PHA | #1DTR二次側(310) PHA | OTHER | D27/11/310/PHA |  |  |  | CDC | 581 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.320_GDA | #1DTR二次側(320) GDA | OTHER | D27/11/320/GDA |  |  |  | CDC | 582 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 320 | #1DTR(320) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.320_PHA | #1DTR二次側(320) PHA | OTHER | D27/11/320/PHA |  |  |  | CDC | 583 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 1DTR | #1DTR |  | 87A1 | [17 empty] | 1-04-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#1DTR_87A1 | #1DTR 第一套87RY | OTHER | D27//1DTR/87A1 |  |  |  | CDC | 584 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 1-0B-07 |  | 1-35 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.400_CB | 400(TIE) CB | TIE | D27/11/400/CB |  |  |  | CDC | 585 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 1-0C-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.400_51A | 11KV TIE(400) 51RY | TIE | D27/11/400/PHA |  |  |  | CDC | 586 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 1-0C-01 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.400_51NA | 11KV TIE(400) 51N RY | TIE | D27/11/400/GDA |  |  |  | CDC | 587 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 1-35-04 |  | 2-3D | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_51ZUL | #2DTR 51Z RY U/L | OTHER | D27//2DTR/51Z_UL |  |  |  | CDC | 588 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 81AS | [17 empty] | 1-09-04 |  | 2-39 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_81AS | #2DTR 81RY動作/復歸 | OTHER | D27//2DTR/81A |  |  |  | CDC | 589 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 81UL | [17 empty] | 1-35-05 |  | 2-3A | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_81UL | #2DTR 81RY U/L | OTHER | D27//2DTR/81UL |  |  |  | CDC | 590 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 1-09-03 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_86A | #2DTR 86(50/50N/51Z/87/96)RY | OTHER | D27//2DTR/DTR_86A |  |  |  | CDC | 591 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 87A1 | [17 empty] | 1-06-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_87A1 | #2DTR 第一套87RY | OTHER | D27//2DTR/87A1 |  |  |  | CDC | 592 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 87A2 | [17 empty] | 1-09-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_87A2 | #2DTR 第二套87RY | OTHER | D27//2DTR/87A2 |  |  |  | CDC | 593 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 1-33-01 |  | 2-3B | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_87UL1 | #2DTR 87RY1 U/L | OTHER | D27//2DTR/1_87UL1 |  |  |  | CDC | 594 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 1-35-03 |  | 2-3C | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_87UL2 | #2DTR 87RY2 U/L | OTHER | D27//2DTR/1_87UL2 |  |  |  | CDC | 595 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 1-35-02 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.#2DTR_RYFA | #2DTR 數位電驛故障 | OTHER | D27//2DTR/RYFA |  |  |  | CDC | 596 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.330_GDA | #2DTR二次側(330) GDA | OTHER | D27/11/330/GDA |  |  |  | CDC | 597 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 330 | #2DTR(330) |  | PHA | [17 empty] | 1-07-00 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.330_PHA | #2DTR二次側(330) PHA | OTHER | D27/11/330/PHA |  |  |  | CDC | 598 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.340_GDA | #2DTR二次側(340) GDA | OTHER | D27/11/340/GDA |  |  |  | CDC | 599 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 340 | #2DTR(340) |  | PHA | [17 empty] | 1-06-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.340_PHA | #2DTR二次側(340) PHA | OTHER | D27/11/340/PHA |  |  |  | CDC | 600 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 2-33-02 |  | 2-1A | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D27/0/StaDev/ACBT |  |  |  | CDC | 601 | GENERICDIPoint | DS032_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
D27 | 鹽行DS | 161 | 161kV | 161BUS | BUS |  | 87A | [17 empty] | 1-04-02 | [7 empty] | 161KV_S | [8 empty] | 鹽行DS.161BUS_87A | 161KV BUS 87RY | BUS | D27/161/ComPoint/12B_87A |  |  |  | CDC | 602 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | 161BUS | BUS |  | 87UL | [17 empty] | 1-32-08 |  | 1-3C | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.161BUS_87UL | 161KV BUS 87RY U/L | OTHER | D27/161/ComPoint/12B_87UL |  |  |  | CDC | 603 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-32-07 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_BUS_CTFA | 161KV BUS CT迴路故障 | OTHER | D27/161/ComPoint/12B_CTFA |  |  |  | CDC | 604 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-32-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D27/161/ComPoint/BUS_RYFA |  |  |  | CDC | 605 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-32-09 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D27/0/ComPoint/OLTC_A |  |  |  | CDC | 606 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D27 | 鹽行DS | 0 |  | 320 | #1DTR(320) |  | 81AS | [17 empty] | 1-1E-06 | [7 empty] | ADCS_S | [8 empty] | 鹽行DS.320_81A/S | (320)81RY動作/Reset | OTHER | D27/11/320/81AS |  |  |  | CDC | 607 | GENERICDIPoint | DS032_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
D27 | 鹽行DS | 0 |  | 320 | #1DTR(320) |  | 81UL | [17 empty] | 1-35-12 |  | 1-38 | [5 empty] | ADCS_S | [8 empty] | 鹽行DS.320_81UL | (320)81RY USE/LOCK | OTHER | D27/11/320/81UL |  |  |  | CDC | 608 | GENERICDIPoint | DS032_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
D27 | 鹽行DS | 11 | 11kV | 210_SC | #1SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 609 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 11 | 11kV | 220_SC | #2SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 610 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 11 | 11kV | 230_SC | #3SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 611 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 11 | 11kV | 240_SC | #4SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 612 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 22 | 22kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 613 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 22 | 22kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹽行DS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 614 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 057 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_057 | 鹽行DS NT #3DTR 23KV_Hi_Limit | [6 empty] | 615 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 058 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_058 | 鹽行DS NT #3DTR 23KV_Lo_Limit | [6 empty] | 616 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 059 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_059 | 鹽行DS NT #1DTR 11KV_Hi_Limit | [6 empty] | 617 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 060 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_060 | 鹽行DS NT #1DTR 11KV_Lo_Limit | [6 empty] | 618 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 061 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_061 | 鹽行DS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 619 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 062 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_062 | 鹽行DS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 620 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 063 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_063 | 鹽行DS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 621 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D27 | 鹽行DS | 0 |  | TRD | 鹽行DS |  | 064 | [25 empty] | TRAIN_AD | [8 empty] | 鹽行DS.TRD_064 | 鹽行DS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 622 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1530LE | 1530LE (非取樣點) | LINE161 | D27/161/1530/LE0 |  |  |  |  | 623 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1530BE | 1530BE (非取樣點) | LINE161 | D27/161/1530/BE0 |  |  |  |  | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1540LE | 1540LE (非取樣點) | LINE161 | D27/161/1540/LE0 |  |  |  |  | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1540 | 山上豐華白線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1540BE | 1540BE (非取樣點) | LINE161 | D27/161/1540/BE0 |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV21 | KV21_DS |  | DS1 | KV21_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_DS | KV21_DS (非取樣點) | FEEDER | D27/11/KV21/DS |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV21 | KV21_ES |  | LE0 | KV21_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV21_ES | KV21_ES (非取樣點) | FEEDER | D27/11/KV21/ES |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV22 | KV22_DS |  | DS1 | KV22_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_DS | KV22_DS (非取樣點) | FEEDER | D27/11/KV22/DS |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV22 | KV22_ES |  | LE0 | KV22_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV22_ES | KV22_ES (非取樣點) | FEEDER | D27/11/KV22/ES |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV23 | KV23_DS |  | DS1 | KV23_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_DS | KV23_DS (非取樣點) | FEEDER | D27/11/KV23/DS |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV23 | KV23_ES |  | LE0 | KV23_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV23_ES | KV23_ES (非取樣點) | FEEDER | D27/11/KV23/ES |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV24 | KV24_DS |  | DS1 | KV24_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_DS | KV24_DS (非取樣點) | FEEDER | D27/11/KV24/DS |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV24 | KV24_ES |  | LE0 | KV24_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV24_ES | KV24_ES (非取樣點) | FEEDER | D27/11/KV24/ES |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV25 | KV25_DS |  | DS1 | KV25_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_DS | KV25_DS (非取樣點) | FEEDER | D27/11/KV25/DS |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV25 | KV25_ES |  | LE0 | KV25_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV25_ES | KV25_ES (非取樣點) | FEEDER | D27/11/KV25/ES |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV26 | KV26_DS |  | DS1 | KV26_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_DS | KV26_DS (非取樣點) | FEEDER | D27/11/KV26/DS |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV26 | KV26_ES |  | LE0 | KV26_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV26_ES | KV26_ES (非取樣點) | FEEDER | D27/11/KV26/ES |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV27 | KV27_DS |  | DS1 | KV27_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_DS | KV27_DS (非取樣點) | FEEDER | D27/11/KV27/DS |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV27 | KV27_ES |  | LE0 | KV27_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV27_ES | KV27_ES (非取樣點) | FEEDER | D27/11/KV27/ES |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV28 | KV28_DS |  | DS1 | KV28_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_DS | KV28_DS (非取樣點) | FEEDER | D27/11/KV28/DS |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV28 | KV28_ES |  | LE0 | KV28_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV28_ES | KV28_ES (非取樣點) | FEEDER | D27/11/KV28/ES |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV29 | KV29_DS |  | DS1 | KV29_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_DS | KV29_DS (非取樣點) | FEEDER | D27/11/KV29/DS |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV29 | KV29_ES |  | LE0 | KV29_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV29_ES | KV29_ES (非取樣點) | FEEDER | D27/11/KV29/ES |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV30 | KV30_DS |  | DS1 | KV30_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_DS | KV30_DS (非取樣點) | FEEDER | D27/11/KV30/DS |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV30 | KV30_ES |  | LE0 | KV30_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV30_ES | KV30_ES (非取樣點) | FEEDER | D27/11/KV30/ES |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV31 | KV31_DS |  | DS1 | KV31_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_DS | KV31_DS (非取樣點) | FEEDER | D27/11/KV31/DS |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV31 | KV31_ES |  | LE0 | KV31_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV31_ES | KV31_ES (非取樣點) | FEEDER | D27/11/KV31/ES |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV32 | KV32_DS |  | DS1 | KV32_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_DS | KV32_DS (非取樣點) | FEEDER | D27/11/KV32/DS |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV32 | KV32_ES |  | LE0 | KV32_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV32_ES | KV32_ES (非取樣點) | FEEDER | D27/11/KV32/ES |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV33 | KV33_DS |  | DS1 | KV33_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_DS | KV33_DS (非取樣點) | FEEDER | D27/11/KV33/DS |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV33 | KV33_ES |  | LE0 | KV33_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV33_ES | KV33_ES (非取樣點) | FEEDER | D27/11/KV33/ES |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV34 | KV34_DS |  | DS1 | KV34_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_DS | KV34_DS (非取樣點) | FEEDER | D27/11/KV34/DS |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV34 | KV34_ES |  | LE0 | KV34_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV34_ES | KV34_ES (非取樣點) | FEEDER | D27/11/KV34/ES |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV73 | KV73_DS |  | DS1 | KV73_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_DS | KV73_DS (非取樣點) | FEEDER | D27/22/KV73/DS |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV73 | KV73_ES |  | LE0 | KV73_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV73_ES | KV73_ES (非取樣點) | FEEDER | D27/22/KV73/ES |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV74 | KV74_DS |  | DS1 | KV74_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_DS | KV74_DS (非取樣點) | FEEDER | D27/22/KV74/DS |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV74 | KV74_ES |  | LE0 | KV74_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV74_ES | KV74_ES (非取樣點) | FEEDER | D27/22/KV74/ES |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV75 | KV75_DS |  | DS1 | KV75_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_DS | KV75_DS (非取樣點) | FEEDER | D27/22/KV75/DS |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV75 | KV75_ES |  | LE0 | KV75_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV75_ES | KV75_ES (非取樣點) | FEEDER | D27/22/KV75/ES |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | KV76 | KV76_DS |  | DS1 | KV76_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_DS | KV76_DS (非取樣點) | FEEDER | D27/22/KV76/DS |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV76 | KV76_ES |  | LE0 | KV76_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV76_ES | KV76_ES (非取樣點) | FEEDER | D27/22/KV76/ES |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1750TE | 1750TE (非取樣點) | MTR | D27/161/1750/TE0 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1750BE | 1750BE (非取樣點) | MTR | D27/161/1750/BE0 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1760TE | 1760TE (非取樣點) | MTR | D27/161/1760/TE0 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1760BE | 1760BE (非取樣點) | MTR | D27/161/1760/BE0 |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1770TE | 1770TE (非取樣點) | MTR | D27/161/1770/TE0 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1770BE | 1770BE (非取樣點) | MTR | D27/161/1770/BE0 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 210 | #1SC(210) |  | SC0 | 210SC | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.210SC_ES | 210SC_ES (非取樣點) | SC | [5 empty] | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 220 | #2SC(220) |  | SC0 | 220SC | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.220SC_ES | 220SC_ES (非取樣點) | SC | [5 empty] | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 230 | #3SC(230) |  | SC0 | 230SC | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.230SC_ES | 230SC_ES (非取樣點) | SC | [5 empty] | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 240 | #4SC(240) |  | SC0 | 240SC | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.240SC_ES | 240SC_ES (非取樣點) | SC | [5 empty] | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.250_ES | 250_ES (非取樣點) | SC | D27/22/250/ES |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.250_DS | 250_DS (非取樣點) | SC | D27/22/250/DS |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.260_ES | 260_ES (非取樣點) | SC | D27/22/260/ES |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.260_DS | 260_DS (非取樣點) | SC | D27/22/260/DS |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.15B1E | 15B1E (非取樣點) | BUS | D27/161/161B1E/BE1 |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.15B2E | 15B2E (非取樣點) | BUS | D27/161/161B2E/BE2 |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 681 | NotelDIPoint | [38 empty] | START/STOP | STOP
D27 | 鹽行DS | 0 |  | KV72 | KV72_DS |  | DS1 | KV72_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_DS | KV72_DS (非取樣點) | FEEDER | D27/22/KV72/DS |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV72 | KV72_ES |  | LE0 | KV72_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV72_ES | KV72_ES (非取樣點) | FEEDER | D27/22/KV72/ES |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV71 | KV71_DS |  | DS1 | KV71_DS | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_DS | KV71_DS (非取樣點) | FEEDER | D27/22/KV71/DS |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | KV71 | KV71_ES |  | LE0 | KV71_ES | [24 empty] | DDCS4_2 | [8 empty] | 鹽行DS.KV71_ES | KV71_ES (非取樣點) | FEEDER | D27/22/KV71/ES |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 350 | #3DTR(350) |  | DS1 | 350_DS | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.350_DS | 350_DS (非取樣點) | MTR | D27/22/350/DS |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 350 | #3DTR(350) |  | LE0 | 350_ES | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.350_ES | 350_ES (非取樣點) | MTR | D27/22/350/ES |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 501 | 501 |  | 501 | 501 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.501 | 501 (非取樣點) | TIE | [5 empty] | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 502 | 502 |  | 502 | 502 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.502 | 502 (非取樣點) | TIE | [5 empty] | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.491 | 491 (非取樣點) | OTHER | D27/22/490/D1 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.491E | 491E (非取樣點) | OTHER | D27/22/490/E1 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.351 | 351 (非取樣點) | MTR | D27/22/350/D1 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 350 | #3DTR(350) |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.351E | 351E (非取樣點) | MTR | D27/22/350/E1 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.251E | 251E (非取樣點) | SC | D27/22/250/E1 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.251 | 251 (非取樣點) | SC | D27/22/250/D1 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.261E | 261E (非取樣點) | SC | D27/22/260/E1 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.261 | 261 (非取樣點) | SC | D27/22/260/D1 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  |  |  |  | 501E | 501E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.501E | 501E(非取樣點) | OTHER | [5 empty] | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  |  |  |  | 502E | 502E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.502E | 502E(非取樣點) | OTHER | [5 empty] | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 3B | #3B |  | BE | #3B_BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#3B_BE | #3B BE(非取樣點) | OTHER | [5 empty] | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.101 | 101 (非取樣點) | TIE | D27/11/100/D1 |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.301 | 301 (非取樣點) | TIE | D27/11/300/D1 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.391 | 391 (非取樣點) | OTHER | D27/11/390/D1 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.391E | 391E (非取樣點) | OTHER | D27/11/390/E1 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.311 | 311 (非取樣點) | MTR | D27/11/310/D1 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.311E | 311E (非取樣點) | MTR | D27/11/310/E1 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.321 | 321 (非取樣點) | MTR | D27/11/320/D1 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.321E | 321E (非取樣點) | MTR | D27/11/320/E1 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.211E | 211E (非取樣點) | SC | D27/11/210/E1 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.211 | 211 (非取樣點) | SC | D27/11/210/D1 |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.221E | 221E (非取樣點) | SC | D27/11/220/E1 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.221 | 221 (非取樣點) | SC | D27/11/220/D1 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  |  |  |  | 101E | 101E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.101E | 101E(非取樣點) | OTHER | D27/11/100/E1 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  |  |  |  | 301E | 301E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.301E | 301E(非取樣點) | OTHER | D27/11/300/E1 |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 1A | #1A |  | BE | #1A_BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#1A_BE | #1A BE(非取樣點) | OTHER | [5 empty] | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 1B | #1B |  | BE | #1B_BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#1B_BE | #1B BE(非取樣點) | OTHER | [5 empty] | 720 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.201 | 201 (非取樣點) | TIE | D27/11/200/D1 |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.401 | 401 (非取樣點) | TIE | D27/11/400/D1 |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.331 | 331 (非取樣點) | MTR | D27/11/330/D1 |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.331E | 331E (非取樣點) | MTR | D27/11/330/E1 |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.341 | 341 (非取樣點) | MTR | D27/11/340/D1 |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.341E | 341E (非取樣點) | MTR | D27/11/340/E1 |  |  |  |  | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.231E | 231E (非取樣點) | SC | D27/11/230/E1 |  |  |  |  | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.231 | 231 (非取樣點) | SC | D27/11/230/D1 |  |  |  |  | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.241E | 241E (非取樣點) | SC | D27/11/240/E1 |  |  |  |  | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.241 | 241 (非取樣點) | SC | D27/11/240/D1 |  |  |  |  | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 2A | #2A |  | BE | #2A_BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#2A_BE | #2A BE(非取樣點) | OTHER | [5 empty] | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 2B | #2B |  | BE | #2B_BE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.#2B_BE | #2B BE(非取樣點) | OTHER | [5 empty] | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  |  |  |  | 201E | 201E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.201E | 201E(非取樣點) | OTHER | D27/11/200/E1 |  |  |  |  | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  |  |  |  | 401E | 401E | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.401E | 401E(非取樣點) | OTHER | D27/11/400/E1 |  |  |  |  | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D27 | 鹽行DS | 0 |  | 3BUS | 3BUS |  | PTD | 3BUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.3BUS_PTD | #3BUS_PTD(非取樣點) | OTHER | [5 empty] | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D27 | 鹽行DS | 0 |  | 3BUS | 3BUS |  | PTE | 3BUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹽行DS.3BUS_PTE | #3BUS_PTE(非取樣點) | OTHER | [5 empty] | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo