## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | D1 | 311(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.311 | 311 (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | E1 | 311E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.311E | 311E (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | D1 | 321(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.321 | 321 (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | E1 | 321E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.321E | 321E (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | D1 | 331(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.331 | 331 (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | 331E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.331E | 331E (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | 341(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.341 | 341 (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | 341E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.341E | 341E (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.101E | 101E (非取樣點) | TIE | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.102E | 102E (非取樣點) | TIE | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.101 | 101 (非取樣點) | TIE | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.102 | 102 (非取樣點) | TIE | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.201E | 201E (非取樣點) | TIE | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.202E | 202E (非取樣點) | TIE | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.201 | 201 (非取樣點) | TIE | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | D2 | 202(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.202 | 202 (非取樣點) | TIE | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.211E | 211E (非取樣點) | SC | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.211 | 211 (非取樣點) | SC | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.221E | 221E (非取樣點) | SC | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.221 | 221 (非取樣點) | SC | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.231E | 231E (非取樣點) | SC | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.231 | 231 (非取樣點) | SC | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.241E | 241E (非取樣點) | SC | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.241 | 241 (非取樣點) | SC | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D28_A1 | [8 empty] | 鹿耳DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_DS | 4D51_DS (非取樣點) | FEEDER | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_ES | 4D51_ES (非取樣點) | FEEDER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_DS | 4D52_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_ES | 4D52_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_DS | 4D53_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_ES | 4D53_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_DS | 4D54_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_ES | 4D54_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_DS | 4D55_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_ES | 4D55_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_DS | 4D56_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_ES | 4D56_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_DS | 4D57_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_ES | 4D57_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_DS | 4D58_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_ES | 4D58_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_DS | 4D61_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_ES | 4D61_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_DS | 4D62_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_ES | 4D62_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_DS | 4D63_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_ES | 4D63_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_DS | 4D64_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_ES | 4D64_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_DS | 4D65_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_ES | 4D65_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_DS | 4D66_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_ES | 4D66_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_DS | 4D67_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_ES | 4D67_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_DS | 4D68_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_ES | 4D68_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | 15B1E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/D28_A1 | [8 empty] | 鹿耳DS.15B1E | 15B1E (非取樣點) | BUS | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | 15B2E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaaz | B2/D28_A1 | [8 empty] | 鹿耳DS.15B2E | 15B2E (非取樣點) | BUS | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | NO.1 DTR | TAP | NO.1 DTR TAP | TAP_-8.5_8.5(0_2000) |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | [5 empty] | 74 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | NO.1 DTR | 線溫 | NO.1 DTR 線溫 (溫度) | COIL_-120_120(-2000_2000) |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_COIL | #1DTR 線溫 | MTR | [5 empty] | 75 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | NO.1 DTR | 油溫 | NO.1 DTR 油溫 (溫度) | OIL_-120_120(-2000_2000) |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 76 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | NO.2 DTR | TAP | NO.2 DTR TAP | TAP_-8.5_8.5(0_2000) |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | [5 empty] | 77 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | NO.2 DTR | 線溫 | NO.2 DTR 線溫 (溫度) | COIL_-120_120(-2000_2000) |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_COIL | #2DTR 線溫 | MTR | [5 empty] | 78 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | NO.2 DTR | 油溫 | NO.2 DTR 油溫 (溫度) | OIL_-120_120(-2000_2000) |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 79 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 南濱鹿耳紅線 | W | 1510 (南濱鹿耳紅線) W (瓦) | MW_-560_560(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_MW | 南濱鹿耳紅線 MW | LINE161 | [5 empty] | 80 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 南濱鹿耳紅線 | Var | 1510 (南濱鹿耳紅線) Var (乏) | MVAR_-560_560(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_MVAR | 南濱鹿耳紅線 MVAR | LINE161 | [5 empty] | 81 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 南濱鹿耳白線 | W | 1520 (南濱鹿耳白線) W (瓦) | MW_-560_560(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_MW | 南濱鹿耳白線 MW | LINE161 | [5 empty] | 82 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 南濱鹿耳白線 | Var | 1520 (南濱鹿耳白線) Var (乏) | MVAR_-560_560(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_MVAR | 南濱鹿耳白線 MVAR | LINE161 | [5 empty] | 83 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | TIE | Ia | 1500 (TIE) Ia (電流) | A_-2000_2000(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 84 |  |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | V |  | B3 | MvMoment | kV |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 南濱鹿耳紅線LPT | Vab | 1510 (南濱鹿耳紅線LPT) Vab (電壓) | kV_-210_210(-2000_2000) | aaa | B2/D28_A1 | [8 empty] | 鹿耳DS.1510LPD_KV | 南濱鹿耳紅線(1510) LPD KV | LINE161 | [5 empty] | 85 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | V |  | B3 | MvMoment | kV |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 南濱鹿耳白線LPT | Vab | 1520 (南濱鹿耳白線LPT) Vab (電壓) | kV_-210_210(-2000_2000) | aab | B2/D28_A1 | [8 empty] | 鹿耳DS.1520LPD_KV | 南濱鹿耳白線(1520) LPD KV | LINE161 | [5 empty] | 86 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D28 | 鹿耳DS | 22 | 22kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0043 |  |  | 1-AB |  |  | M-1A | Van | PT-1A (M-1A) Van (電壓) | kV_-18_18(-2000_2000) | aaa | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | [5 empty] | 87 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | M-1A | W | 310 (M-1A) W (瓦) | MW_-108_108(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | M-1A | Var | 310 (M-1A) Var (乏) | MVAR_-72_72(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 89 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | M-1A | Ia | 310 (M-1A) Ia (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 90 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | M-1A | Ib | 310 (M-1A) Ib (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 91 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | M-1A | Ic | 310 (M-1A) Ic (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 92 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 鹿51 | Var | 4D51 (鹿51) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿51線KVAR | 23KV鹿51線 KVAR | FEEDER | [5 empty] | 93 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 鹿51 | Ia | 4D51 (鹿51) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿51線A1 | 23KV鹿51線 R相AMP | FEEDER | [5 empty] | 94 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 鹿51 | Ib | 4D51 (鹿51) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿51線A2 | 23KV鹿51線 S相AMP | FEEDER | [5 empty] | 95 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 鹿51 | Ic | 4D51 (鹿51) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿51線A3 | 23KV鹿51線 T相AMP | FEEDER | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 鹿51 | Io | 4D51 (鹿51) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿51線A0 | 23KV鹿51線 N相AMP | FEEDER | [5 empty] | 97 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 鹿52 | Var | 4D52 (鹿52) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿52線KVAR | 23KV鹿52線 KVAR | FEEDER | [5 empty] | 98 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 鹿52 | Ia | 4D52 (鹿52) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿52線A1 | 23KV鹿52線 R相AMP | FEEDER | [5 empty] | 99 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 鹿52 | Ib | 4D52 (鹿52) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿52線A2 | 23KV鹿52線 S相AMP | FEEDER | [5 empty] | 100 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 鹿52 | Ic | 4D52 (鹿52) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿52線A3 | 23KV鹿52線 T相AMP | FEEDER | [5 empty] | 101 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 鹿52 | Io | 4D52 (鹿52) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿52線A0 | 23KV鹿52線 N相AMP | FEEDER | [5 empty] | 102 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 鹿53 | Var | 4D53 (鹿53) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿53線KVAR | 23KV鹿53線 KVAR | FEEDER | [5 empty] | 103 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 鹿53 | Ia | 4D53 (鹿53) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿53線A1 | 23KV鹿53線 R相AMP | FEEDER | [5 empty] | 104 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 鹿53 | Ib | 4D53 (鹿53) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿53線A2 | 23KV鹿53線 S相AMP | FEEDER | [5 empty] | 105 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 鹿53 | Ic | 4D53 (鹿53) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿53線A3 | 23KV鹿53線 T相AMP | FEEDER | [5 empty] | 106 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 鹿53 | Io | 4D53 (鹿53) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿53線A0 | 23KV鹿53線 N相AMP | FEEDER | [5 empty] | 107 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 鹿54 | Var | 4D54 (鹿54) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿54線KVAR | 23KV鹿54線 KVAR | FEEDER | [5 empty] | 108 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 鹿54 | Ia | 4D54 (鹿54) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿54線A1 | 23KV鹿54線 R相AMP | FEEDER | [5 empty] | 109 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 鹿54 | Ib | 4D54 (鹿54) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿54線A2 | 23KV鹿54線 S相AMP | FEEDER | [5 empty] | 110 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 鹿54 | Ic | 4D54 (鹿54) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿54線A3 | 23KV鹿54線 T相AMP | FEEDER | [5 empty] | 111 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 鹿54 | Io | 4D54 (鹿54) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿54線A0 | 23KV鹿54線 N相AMP | FEEDER | [5 empty] | 112 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | TIE-1A | Ia | 100 (TIE-1A) Ia (電流) | A_-2000_2000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | [5 empty] | 113 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | TIE-1A | Ib | 100 (TIE-1A) Ib (電流) | A_-2000_2000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | [5 empty] | 114 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | TIE-1A | Ic | 100 (TIE-1A) Ic (電流) | A_-2000_2000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | [5 empty] | 115 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0072 |  |  | 1-C8 |  |  | M-1B | Van | PT-1B (M-1B) Van (電壓) | kV_-18_18(-2000_2000) | baa | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | [5 empty] | 116 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | M-1B | W | 320 (M-1B) W (瓦) | MW_-108_108(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 117 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | M-1B | Var | 320 (M-1B) Var (乏) | MVAR_-72_72(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 118 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | M-1B | Ia | 320 (M-1B) Ia (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 119 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | M-1B | Ib | 320 (M-1B) Ib (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 120 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | M-1B | Ic | 320 (M-1B) Ic (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 121 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 鹿55 | Var | 4D55 (鹿55) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿55線KVAR | 23KV鹿55線 KVAR | FEEDER | [5 empty] | 122 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 鹿55 | Ia | 4D55 (鹿55) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿55線A1 | 23KV鹿55線 R相AMP | FEEDER | [5 empty] | 123 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 鹿55 | Ib | 4D55 (鹿55) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿55線A2 | 23KV鹿55線 S相AMP | FEEDER | [5 empty] | 124 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 鹿55 | Ic | 4D55 (鹿55) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿55線A3 | 23KV鹿55線 T相AMP | FEEDER | [5 empty] | 125 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 鹿55 | Io | 4D55 (鹿55) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿55線A0 | 23KV鹿55線 N相AMP | FEEDER | [5 empty] | 126 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 鹿56 | Var | 4D56 (鹿56) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿56線KVAR | 23KV鹿56線 KVAR | FEEDER | [5 empty] | 127 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 鹿56 | Ia | 4D56 (鹿56) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿56線A1 | 23KV鹿56線 R相AMP | FEEDER | [5 empty] | 128 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 鹿56 | Ib | 4D56 (鹿56) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿56線A2 | 23KV鹿56線 S相AMP | FEEDER | [5 empty] | 129 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 鹿56 | Ic | 4D56 (鹿56) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿56線A3 | 23KV鹿56線 T相AMP | FEEDER | [5 empty] | 130 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 鹿56 | Io | 4D56 (鹿56) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿56線A0 | 23KV鹿56線 N相AMP | FEEDER | [5 empty] | 131 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 鹿57 | Var | 4D57 (鹿57) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿57線KVAR | 23KV鹿57線 KVAR | FEEDER | [5 empty] | 132 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 鹿57 | Ia | 4D57 (鹿57) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿57線A1 | 23KV鹿57線 R相AMP | FEEDER | [5 empty] | 133 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 鹿57 | Ib | 4D57 (鹿57) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿57線A2 | 23KV鹿57線 S相AMP | FEEDER | [5 empty] | 134 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 鹿57 | Ic | 4D57 (鹿57) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿57線A3 | 23KV鹿57線 T相AMP | FEEDER | [5 empty] | 135 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 鹿57 | Io | 4D57 (鹿57) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿57線A0 | 23KV鹿57線 N相AMP | FEEDER | [5 empty] | 136 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 鹿58 | Var | 4D58 (鹿58) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿58線KVAR | 23KV鹿58線 KVAR | FEEDER | [5 empty] | 137 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 鹿58 | Ia | 4D58 (鹿58) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿58線A1 | 23KV鹿58線 R相AMP | FEEDER | [5 empty] | 138 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 鹿58 | Ib | 4D58 (鹿58) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿58線A2 | 23KV鹿58線 S相AMP | FEEDER | [5 empty] | 139 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 鹿58 | Ic | 4D58 (鹿58) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿58線A3 | 23KV鹿58線 T相AMP | FEEDER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 鹿58 | Io | 4D58 (鹿58) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿58線A0 | 23KV鹿58線 N相AMP | FEEDER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | Locate Empty |  | DC P+ () (瓦) | kV_-150_150(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | Locate Empty |  | DC N- () (瓦) | kV_-150_150(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0100 |  |  | 1-E4 |  |  | M-2A | Van | PT-2A (M-2A) Van (電壓) | kV_-18_18(-2000_2000) | aba | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | M-2A | W | 330 (M-2A) W (瓦) | MW_-108_108(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | M-2A | Var | 330 (M-2A) Var (乏) | MVAR_-72_72(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | M-2A | Ia | 330 (M-2A) Ia (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | M-2A | Ib | 330 (M-2A) Ib (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | M-2A | Ic | 330 (M-2A) Ic (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 鹿61 | Var | 4D61 (鹿61) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿61線KVAR | 23KV鹿61線 KVAR | FEEDER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 鹿61 | Ia | 4D61 (鹿61) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿61線A1 | 23KV鹿61線 R相AMP | FEEDER | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 鹿61 | Ib | 4D61 (鹿61) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿61線A2 | 23KV鹿61線 S相AMP | FEEDER | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 鹿61 | Ic | 4D61 (鹿61) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿61線A3 | 23KV鹿61線 T相AMP | FEEDER | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 鹿61 | Io | 4D61 (鹿61) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿61線A0 | 23KV鹿61線 N相AMP | FEEDER | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 鹿62 | Var | 4D62 (鹿62) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿62線KVAR | 23KV鹿62線 KVAR | FEEDER | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 鹿62 | Ia | 4D62 (鹿62) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿62線A1 | 23KV鹿62線 R相AMP | FEEDER | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 鹿62 | Ib | 4D62 (鹿62) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿62線A2 | 23KV鹿62線 S相AMP | FEEDER | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 鹿62 | Ic | 4D62 (鹿62) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿62線A3 | 23KV鹿62線 T相AMP | FEEDER | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 鹿62 | Io | 4D62 (鹿62) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿62線A0 | 23KV鹿62線 N相AMP | FEEDER | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 鹿63 | Var | 4D63 (鹿63) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿63線KVAR | 23KV鹿63線 KVAR | FEEDER | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 鹿63 | Ia | 4D63 (鹿63) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿63線A1 | 23KV鹿63線 R相AMP | FEEDER | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 鹿63 | Ib | 4D63 (鹿63) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿63線A2 | 23KV鹿63線 S相AMP | FEEDER | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 鹿63 | Ic | 4D63 (鹿63) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿63線A3 | 23KV鹿63線 T相AMP | FEEDER | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 鹿63 | Io | 4D63 (鹿63) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿63線A0 | 23KV鹿63線 N相AMP | FEEDER | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 鹿64 | Var | 4D64 (鹿64) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿64線KVAR | 23KV鹿64線 KVAR | FEEDER | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 鹿64 | Ia | 4D64 (鹿64) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿64線A1 | 23KV鹿64線 R相AMP | FEEDER | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 鹿64 | Ib | 4D64 (鹿64) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿64線A2 | 23KV鹿64線 S相AMP | FEEDER | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 鹿64 | Ic | 4D64 (鹿64) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿64線A3 | 23KV鹿64線 T相AMP | FEEDER | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 鹿64 | Io | 4D64 (鹿64) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿64線A0 | 23KV鹿64線 N相AMP | FEEDER | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0126 |  |  | 1-FE |  |  | M-2B | Van | PT-2B (M-2B) Van (電壓) | kV_-18_18(-2000_2000) | bba | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | M-2B | W | 340 (M-2B) W (瓦) | MW_-108_108(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | M-2B | Var | 340 (M-2B) Var (乏) | MVAR_-72_72(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | M-2B | Ia | 340 (M-2B) Ia (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | M-2B | Ib | 340 (M-2B) Ib (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | M-2B | Ic | 340 (M-2B) Ic (電流) | A_-3000_3000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_0 | 0 | 1 | 2 | 3 | 0.1 | 0 | -1 | -2 | -3 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 鹿65 | Var | 4D65 (鹿65) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿65線KVAR | 23KV鹿65線 KVAR | FEEDER | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 鹿65 | Ia | 4D65 (鹿65) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿65線A1 | 23KV鹿65線 R相AMP | FEEDER | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 鹿65 | Ib | 4D65 (鹿65) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿65線A2 | 23KV鹿65線 S相AMP | FEEDER | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 鹿65 | Ic | 4D65 (鹿65) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿65線A3 | 23KV鹿65線 T相AMP | FEEDER | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 鹿65 | Io | 4D65 (鹿65) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿65線A0 | 23KV鹿65線 N相AMP | FEEDER | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 鹿66 | Var | 4D66 (鹿66) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿66線KVAR | 23KV鹿66線 KVAR | FEEDER | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 鹿66 | Ia | 4D66 (鹿66) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿66線A1 | 23KV鹿66線 R相AMP | FEEDER | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 鹿66 | Ib | 4D66 (鹿66) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿66線A2 | 23KV鹿66線 S相AMP | FEEDER | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 鹿66 | Ic | 4D66 (鹿66) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿66線A3 | 23KV鹿66線 T相AMP | FEEDER | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 鹿66 | Io | 4D66 (鹿66) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿66線A0 | 23KV鹿66線 N相AMP | FEEDER | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 鹿67 | Var | 4D67 (鹿67) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿67線KVAR | 23KV鹿67線 KVAR | FEEDER | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 鹿67 | Ia | 4D67 (鹿67) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿67線A1 | 23KV鹿67線 R相AMP | FEEDER | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 鹿67 | Ib | 4D67 (鹿67) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿67線A2 | 23KV鹿67線 S相AMP | FEEDER | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 鹿67 | Ic | 4D67 (鹿67) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿67線A3 | 23KV鹿67線 T相AMP | FEEDER | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 鹿67 | Io | 4D67 (鹿67) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿67線A0 | 23KV鹿67線 N相AMP | FEEDER | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 鹿68 | Var | 4D68 (鹿68) Var (乏) | KVAR_-21600_21600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿68線KVAR | 23KV鹿68線 KVAR | FEEDER | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 鹿68 | Ia | 4D68 (鹿68) Ia (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿68線A1 | 23KV鹿68線 R相AMP | FEEDER | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 鹿68 | Ib | 4D68 (鹿68) Ib (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿68線A2 | 23KV鹿68線 S相AMP | FEEDER | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 鹿68 | Ic | 4D68 (鹿68) Ic (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿68線A3 | 23KV鹿68線 T相AMP | FEEDER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 鹿68 | Io | 4D68 (鹿68) Io (電流) | A_-600_600(-2000_2000) |  | B2/D28_D1 | [8 empty] | 鹿耳DS.鹿68線A0 | 23KV鹿68線 N相AMP | FEEDER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | TIE-2B | Ia | 200 (TIE-2B) Ia (電流) | A_-2000_2000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | TIE-2B | Ib | 200 (TIE-2B) Ib (電流) | A_-2000_2000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | TIE-2B | Ic | 200 (TIE-2B) Ic (電流) | A_-2000_2000(-2000_2000) |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D03D28R/T2 |  | 0000 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  | aaca | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_CB | 1510(南濱鹿耳紅線) CB | LINE161 |  | CDC_Mon1_DPC |  |  |  | 199 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_87A | 南濱鹿耳紅線(1510) 87RY | LINE161 |  | CDC_Mon1_DPC |  |  |  | 200 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_PHA | 南濱鹿耳紅線(1510) 相間RY | LINE161 |  | CDC_Mon1_DPC |  |  |  | 201 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_GDA | 南濱鹿耳紅線(1510) 接地RY | LINE161 |  | CDC_Mon1_DPC |  |  |  | 202 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/D03D28W/T2 |  | 0004 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  | aada | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_CB | 1520(南濱鹿耳白線) CB | LINE161 |  | CDC_Mon1_DPC |  |  |  | 203 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_87A | 南濱鹿耳白線(1520) 87RY | LINE161 |  | CDC_Mon1_DPC |  |  |  | 204 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_PHA | 南濱鹿耳白線(1520) 相間RY | LINE161 |  | CDC_Mon1_DPC |  |  |  | 205 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_GDA | 南濱鹿耳白線(1520) 接地RY | LINE161 |  | CDC_Mon1_DPC |  |  |  | 206 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0032 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  | aafz | B2/D28_A1 | [8 empty] | 鹿耳DS.1500_CB | 1500(TIE) CB | TIE |  | CDC_Mon1_DPC |  |  |  | 207 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1500_50A | 161KV TIE(1500) 50RY | TIE |  | CDC_Mon1_DPC |  |  |  | 208 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0034 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  | aabb | ELEM/D28_A1 | [8 empty] | 鹿耳DS.1750_CB | 1750(#1DTR) CB | MTR |  | CDC_Mon1_DPC |  |  |  | 209 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_87A | #1DTR 87RY | MTR |  | CDC_Mon1_DPC |  |  |  | 210 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR |  | CDC_Mon1_DPC |  |  |  | 211 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_51ZA | #1DTR 51Z RY | MTR |  | CDC_Mon1_DPC |  |  |  | 212 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_51A | #1DTR 51RY | MTR |  | CDC_Mon1_DPC |  |  |  | 213 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_51NA | #1DTR 51N RY | MTR |  | CDC_Mon1_DPC |  |  |  | 214 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0040 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  | aaeb | ELEM/D28_A1 | [8 empty] | 鹿耳DS.1760_CB | 1760(#2DTR) CB | MTR |  | CDC_Mon1_DPC |  |  |  | 215 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_87A | #2DTR 87RY | MTR |  | CDC_Mon1_DPC |  |  |  | 216 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR |  | CDC_Mon1_DPC |  |  |  | 217 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_51ZA | #2DTR 51Z RY | MTR |  | CDC_Mon1_DPC |  |  |  | 218 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_51A | #2DTR 51RY | MTR |  | CDC_Mon1_DPC |  |  |  | 219 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_51NA | #2DTR 51N RY | MTR |  | CDC_Mon1_DPC |  |  |  | 220 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS |  | CDC_Mon1_DPC |  |  |  | 221 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS |  | CDC_Mon1_DPC |  |  |  | 222 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | A/320^T/1DTR(A) |  |  | 0060 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  | aaca | ELEM/D28_A1 | [8 empty] | 鹿耳DS.310_CB | 310(#1DTR) CB | MTR |  | CDC_Mon1_DPC |  |  |  | 223 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.310_51A | #1DTR二次側(310) 51RY | MTR |  | CDC_Mon1_DPC |  |  |  | 224 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.310_GDA | 310開關箱IED RY GDA | OTHER |  | CDC_Mon1_DPC |  |  |  | 225 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/310^T/1DTR(B) |  |  | 0063 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  | baaa | ELEM/D28_A1 | [8 empty] | 鹿耳DS.320_CB | 320(#1DTR) CB | MTR |  | CDC_Mon1_DPC |  |  |  | 226 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.320_51A | #1DTR二次側(320) 51RY | MTR |  | CDC_Mon1_DPC |  |  |  | 227 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.320_GDA | 320開關箱IED RY GDA | OTHER |  | CDC_Mon1_DPC |  |  |  | 228 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/340^T/2DTR(A) |  |  | 0066 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  | abca | ELEM/D28_A1 | [8 empty] | 鹿耳DS.330_CB | 330(#2DTR) CB | MTR |  | CDC_Mon1_DPC |  |  |  | 229 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.330_51A | #2DTR二次側(330) 51RY | MTR |  | CDC_Mon1_DPC |  |  |  | 230 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.330_GDA | 330開關箱IED RY GDA | OTHER |  | CDC_Mon1_DPC |  |  |  | 231 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/330^T/2DTR(B) |  |  | 0069 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  | bbaa | ELEM/D28_A1 | [8 empty] | 鹿耳DS.340_CB | 340(#2DTR) CB | MTR |  | CDC_Mon1_DPC |  |  |  | 232 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.340_51A | #2DTR二次側(340) 51RY | MTR |  | CDC_Mon1_DPC |  |  |  | 233 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.340_GDA | 340開關箱IED RY GDA | OTHER |  | CDC_Mon1_DPC |  |  |  | 234 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0072 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 235 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0074 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER |  | CDC_Mon1_DPC |  |  |  | 236 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0075 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.11/23KV_LOA | 23KV饋線復閉失敗閉鎖 | OTHER |  | CDC_Mon1_DPC |  |  |  | 237 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0256 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  | aaib | B3/D28_A1 | [8 empty] | 鹿耳DS.100_CB | 100(TIE) CB | TIE |  | CDC_Mon1_DPC |  |  |  | 238 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.100_51A | 23KV TIE(100) 51RY | TIE |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 239 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.100_51NA | 23KV TIE(100) 51N RY | TIE |  | CDC_Mon1_DPC |  |  |  | 240 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/1BBus |  |  | 0259 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  | bbhb | B3/D28_A1 | [8 empty] | 鹿耳DS.200_CB | 200(TIE) CB | TIE |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 241 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.200_51A | 23KV TIE(200) 51RY | TIE |  | CDC_Mon1_DPC |  |  |  | 242 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.200_51NA | 23KV TIE(200) 51N RY | TIE |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 243 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0262 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  | aadb | B3/D28_A1 | [8 empty] | 鹿耳DS.210_CB | 210(23KV #1SC) CB | SC |  | CDC_Mon1_DPC |  |  |  | 244 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0263 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.210_SCA | 23KV #1SC 51,51N RY | SC |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 245 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0264 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.210_OUVA | 23KV #1SC 27,59RY(欠壓或過壓) | SC |  | CDC_Mon1_DPC |  |  |  | 246 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | C/2SC |  |  | 0265 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  | babb | B3/D28_A1 | [8 empty] | 鹿耳DS.220_CB | 220(23KV #2SC) CB | SC |  | CDC_Mon1_DPC |  |  |  | 247 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0266 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.220_SCA | 23KV #2SC 51,51N RY | SC |  | CDC_Mon1_DPC |  |  |  | 248 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0267 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC |  | CDC_Mon1_DPC |  |  |  | 249 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0268 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  | abdb | B3/D28_A1 | [8 empty] | 鹿耳DS.230_CB | 230(23KV #3SC) CB | SC |  | CDC_Mon1_DPC |  |  |  | 250 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.230_SCA | 23KV #3SC 51,51N RY | SC |  | CDC_Mon1_DPC |  |  |  | 251 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0270 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC |  | CDC_Mon1_DPC |  |  |  | 252 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0271 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  | bbbb | B3/D28_A1 | [8 empty] | 鹿耳DS.240_CB | 240(23KV #4SC) CB | SC |  | CDC_Mon1_DPC |  |  |  | 253 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.240_SCA | 23KV #4SC 51,51N RY | SC |  | CDC_Mon1_DPC |  |  |  | 254 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC |  | CDC_Mon1_DPC |  |  |  | 255 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0274 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  | aaab | B3/D28_A1 | [8 empty] | 鹿耳DS.390_CB | 390(#1SSTR) CB | OTHER |  | CDC_Mon1_DPC |  |  |  | 256 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1SSTR_51A | #1SSTR 51RY | OTHER |  | CDC_Mon1_DPC |  |  |  | 257 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0276 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER |  | CDC_Mon1_DPC |  |  |  | 258 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2SSTR |  |  | 0277 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  | abab | B3/D28_A1 | [8 empty] | 鹿耳DS.490_CB | 490(#2SSTR) CB | OTHER |  | CDC_Mon1_DPC |  |  |  | 259 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2SSTR_51A | #2SSTR 51RY | OTHER |  | CDC_Mon1_DPC |  |  |  | 260 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0279 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER |  | CDC_Mon1_DPC |  |  |  | 261 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4D51/T1 |  |  | 0280 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  | aaeb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_CB | 4D51(23KV鹿51線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 262 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_PHA | 23KV鹿51線(4D51) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 263 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_GDA | 23KV鹿51線(4D51) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 264 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4D52/T1 |  |  | 0283 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  | aafb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_CB | 4D52(23KV鹿52線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 265 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_PHA | 23KV鹿52線(4D52) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 266 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_GDA | 23KV鹿52線(4D52) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 267 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4D53/T1 |  |  | 0286 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  | aagb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_CB | 4D53(23KV鹿53線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 268 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_PHA | 23KV鹿53線(4D53) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 269 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_GDA | 23KV鹿53線(4D53) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 270 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1ABus | L/4D54/T1 |  |  | 0289 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  | aahb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_CB | 4D54(23KV鹿54線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 271 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_PHA | 23KV鹿54線(4D54) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 272 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_GDA | 23KV鹿54線(4D54) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 273 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4D55/T1 |  |  | 0292 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  | badb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_CB | 4D55(23KV鹿55線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 274 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_PHA | 23KV鹿55線(4D55) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 275 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_GDA | 23KV鹿55線(4D55) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 276 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4D56/T1 |  |  | 0295 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  | baeb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_CB | 4D56(23KV鹿56線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 277 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_PHA | 23KV鹿56線(4D56) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 278 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_GDA | 23KV鹿56線(4D56) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 279 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4D57/T1 |  |  | 0298 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  | bafb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_CB | 4D57(23KV鹿57線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 280 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_PHA | 23KV鹿57線(4D57) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 281 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_GDA | 23KV鹿57線(4D57) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 282 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/1BBus | L/4D58/T1 |  |  | 0301 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  | bagb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_CB | 4D58(23KV鹿58線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 283 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_PHA | 23KV鹿58線(4D58) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 284 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_GDA | 23KV鹿58線(4D58) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 285 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4D61/T1 |  |  | 0304 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  | abeb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_CB | 4D61(23KV鹿61線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 286 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_PHA | 23KV鹿61線(4D61) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 287 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_GDA | 23KV鹿61線(4D61) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 288 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4D62/T1 |  |  | 0307 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  | abfb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_CB | 4D62(23KV鹿62線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 289 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_PHA | 23KV鹿62線(4D62) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 290 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_GDA | 23KV鹿62線(4D62) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 291 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4D63/T1 |  |  | 0310 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  | abgb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_CB | 4D63(23KV鹿63線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 292 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_PHA | 23KV鹿63線(4D63) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 293 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_GDA | 23KV鹿63線(4D63) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 294 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2ABus | L/4D64/T1 |  |  | 0313 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  | abhb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_CB | 4D64(23KV鹿64線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 295 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_PHA | 23KV鹿64線(4D64) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 296 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_GDA | 23KV鹿64線(4D64) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 297 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4D65/T1 |  |  | 0316 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  | bbdb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_CB | 4D65(23KV鹿65線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 298 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_PHA | 23KV鹿65線(4D65) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 299 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_GDA | 23KV鹿65線(4D65) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 300 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4D66/T1 |  |  | 0319 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  | bbeb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_CB | 4D66(23KV鹿66線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 301 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_PHA | 23KV鹿66線(4D66) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 302 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_GDA | 23KV鹿66線(4D66) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 303 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4D67/T1 |  |  | 0322 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  | bbfb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_CB | 4D67(23KV鹿67線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 304 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_PHA | 23KV鹿67線(4D67) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 305 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-04-00 |  |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_GDA | 23KV鹿67線(4D67) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 306 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrE | B/2BBus | L/4D68/T1 |  |  | 0325 |  |  | 2-05-00 |  |  | TIE-2B | GDA | 200 (TIE-2B) GDA 動作/正常 |  | bbgb | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_CB | 4D68(23KV鹿68線) CB | FEEDER |  | CDC_Mon1_DPC |  |  |  | 307 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-06-00 |  |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_PHA | 23KV鹿68線(4D68) 相間RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 308 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-07-00 |  |  | SC-1 | SCA | 210 (SC-1) SCA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_GDA | 23KV鹿68線(4D68) 接地RY | FEEDER |  | CDC_Mon1_DPC |  |  |  | 309 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Comm_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0512 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.COMM_S/L | IED控制權 | OTHER |  | CDC_Mon1_DPC |  |  |  | 310 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
D28 | 鹿耳DS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0513 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | ELEM/ALL | [8 empty] | 鹿耳DS.TEST_CB | TEST CB | OTHER |  | CDC_Mon1_DPC |  |  |  | 311 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0514 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_RYFA | 南濱鹿耳紅線(1510)數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 312 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0515 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_RYFA | 南濱鹿耳白線(1520)數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 313 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0522 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  | a | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_TRA | #1DTR 重故障 | MTR |  | CDC_Mon1_DPC |  |  |  | 314 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0523 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_TRF | #1DTR 輕故障 | MTR |  | CDC_Mon1_DPC |  |  |  | 315 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0524 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_63Q | #1DTR 63Q RY | MTR |  | CDC_Mon1_DPC |  |  |  | 316 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0525 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_96D | #1DTR 96D RY | MTR |  | CDC_Mon1_DPC |  |  |  | 317 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0526 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR |  | CDC_Mon1_DPC |  |  |  | 318 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0527 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR |  | CDC_Mon1_DPC |  |  |  | 319 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_A/M | #1DTR OLTC A/M | MTR |  | CDC_Mon1_DPC |  |  |  | 320 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0530 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_S/L | #1DTR OLTC S/L | MTR |  | CDC_Mon1_DPC |  |  |  | 321 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0532 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_96P | #1DTR 96P RY | MTR |  | CDC_Mon1_DPC |  |  |  | 322 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0533 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  | a | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_TRA | #2DTR 重故障 | MTR |  | CDC_Mon1_DPC |  |  |  | 323 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0534 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_TRF | #2DTR 輕故障 | MTR |  | CDC_Mon1_DPC |  |  |  | 324 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0535 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_63Q | #2DTR 63Q RY | MTR |  | CDC_Mon1_DPC |  |  |  | 325 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0536 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_96D | #2DTR 96D RY | MTR |  | CDC_Mon1_DPC |  |  |  | 326 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR |  | CDC_Mon1_DPC |  |  |  | 327 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0538 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR |  | CDC_Mon1_DPC |  |  |  | 328 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0539 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_A/M | #2DTR OLTC A/M | MTR |  | CDC_Mon1_DPC |  |  |  | 329 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_S/L | #2DTR OLTC S/L | MTR |  | CDC_Mon1_DPC |  |  |  | 330 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0543 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_96P | #2DTR 96P RY | MTR |  | CDC_Mon1_DPC |  |  |  | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_87UL | 南濱鹿耳紅線(1510) 87RY U/L | LINE161 |  | CDC_Mon1_DPC |  |  |  | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0567 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_79UL | 南濱鹿耳紅線(1510) 79RY U/L | LINE161 |  | CDC_Mon1_DPC |  |  |  | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0568 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_87UL | 南濱鹿耳白線(1520) 87RY U/L | LINE161 |  | CDC_Mon1_DPC |  |  |  | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_79UL | 南濱鹿耳白線(1520) 79RY U/L | LINE161 |  | CDC_Mon1_DPC |  |  |  | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0582 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_87UL | #1DTR 87RY U/L | MTR |  | CDC_Mon1_DPC |  |  |  | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0583 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_87UL | #2DTR 87RY U/L | MTR |  | CDC_Mon1_DPC |  |  |  | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0586 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  | CDC_Mon1_DPC |  |  |  | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0587 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  | CDC_Mon1_DPC |  |  |  | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0588 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_CBA | 161KV斷路器重故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0589 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_CBF | 161KV斷路器輕故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0590 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1510_87CFA | 南濱鹿耳紅線(1510)87RY通訊故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0591 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1520_87CFA | 南濱鹿耳白線(1520)87RY通訊故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0598 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.直流充電機故障 | 直流充電機故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0600 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.直流電源DCE | 直流電源接地故障警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0601 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.直流電源DCA | 直流電源故障警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Door1 | 控制室大門及正門開啟 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0602 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.無人化門禁(1) | 無人化門禁(1)圍牆大小門 | OTHER |  | CDC_Mon1_DPC |  |  |  | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Door2 | 無人化門禁警報 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0603 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.無人化門禁(2) | 無人化門禁(2)建築物門禁 | OTHER |  | CDC_Mon1_DPC |  |  |  | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0604 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.火災警報(1) | 火災警報(1)受信總機 | OTHER |  | CDC_Mon1_DPC |  |  |  | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0606 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Burglar |  |  | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0607 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER |  | CDC_Mon1_DPC |  |  |  | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Lights1 | 景觀照明 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0608 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.開關場照明(A) | 景觀照明 | OTHER |  | CDC_Mon1_DPC |  |  |  | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Lights2 | 路燈照明 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0609 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.開關場照明(B) | 路燈照明 | OTHER |  | CDC_Mon1_DPC |  |  |  | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0610 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_OSCF | 161KV示波器故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0611 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.OLTCA | OLTC 15分鐘連動3次 | OTHER |  | CDC_Mon1_DPC |  |  |  | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 控制室或通訊室 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0615 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  | CDC_Mon1_DPC |  |  |  | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  | CDC_Mon1_DPC |  |  |  | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 | 集油池抽水泵 |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0618 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.抽水泵警報 | 集油池抽水泵故障警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 | 第一段集油池淹水 |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0619 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.集油池警報(1) | 集油池第一段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | OilLeak3 | 第二段集油池 |  | Status | 洩油池水位警報3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0620 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.集油池警報(2) | 集油池第二段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Water1 | 第一區淹水第一段 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0621 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.水位警報(1) | 地下室第一區第一段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Water2 | 第一區淹水第二段 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0622 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.水位警報(2) | 地下室第一區第二段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Water3 | 第二區淹水第一段 |  | Status | 地下室淹水3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0623 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.水位警報(3) | 地下室第二區第一段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Water4 | 第二區淹水第二段 |  | Status | 地下室淹水4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0624 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.水位警報(4) | 地下室第二區第二段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0625 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  | CDC_Mon1_DPC |  |  |  | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0626 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  | CDC_Mon1_DPC |  |  |  | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0627 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER |  | CDC_Mon1_DPC |  |  |  | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0628 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.所內電源ACBA | 所內電源故障警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | SCADAA | SCADA_A故障 | Element | Status | LocalSCADA故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0629 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.SCADA_A | SCADA A故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0631 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 變電所監視系統警報SUPA | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0632 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B3/D28_A1 | [12 empty] | CDC_Mon1_DPC |  |  |  | 374 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | UPSA |  |  | Status | UPS故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0633 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.SCADA_UPS | SCADA UPS故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0634 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0635 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | GPSA |  |  | Status | GPS故障警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0636 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.GPSA | LOCAL GPS故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0637 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_SC_60A | 23KV SC 60A | OTHER |  | CDC_Mon1_DPC |  |  |  | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0638 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE |  | CDC_Mon1_DPC |  |  |  | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | MCC |  |  | Status | MCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.MCCA | MCC電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | PMCC |  |  | Status | PMCC電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0640 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.PMCCA | PMCC電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | TCA |  |  | Status | 斷路器跳脫迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0641 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.TCA | 斷路器跳脫回路故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | R_Temp | IED盤內溫控警報 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0642 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.IED盤內溫度 | IED盤內溫控警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | FiberA |  |  | Status | SCADA光纖故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0644 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.FIBERA | SCADA光纖故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | FiberA | 光纖網路交換機故障 | Element | Status | SCADA光纖故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0645 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.SWITCHA | 光纖網路交換機故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Gateway1 | 通訊處理單元A(GATEWAYA)故障 |  | Status | Gateway 1故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0646 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.PASGTWAA | 通訊處理單元A(GATEWAYA)故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Gateway2 | 通訊處理單元B(GATEWAYB)故障 |  | Status | Gateway 2故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0647 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.PASGTWBA | 通訊處理單元B(GATEWAYB)故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0648 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_79UL | 23KV鹿51線(4D51) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0649 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D51_LCO_TAP | 23KV鹿51線(4D51) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0650 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_79UL | 23KV鹿52線(4D52) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0651 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D52_LCO_TAP | 23KV鹿52線(4D52) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0652 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_79UL | 23KV鹿53線(4D53) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0653 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D53_LCO_TAP | 23KV鹿53線(4D53) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0654 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_79UL | 23KV鹿54線(4D54) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0655 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D54_LCO_TAP | 23KV鹿54線(4D54) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0656 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_79UL | 23KV鹿55線(4D55) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0657 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D55_LCO_TAP | 23KV鹿55線(4D55) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0658 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_79UL | 23KV鹿56線(4D56) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0659 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D56_LCO_TAP | 23KV鹿56線(4D56) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0660 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_79UL | 23KV鹿57線(4D57) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0661 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D57_LCO_TAP | 23KV鹿57線(4D57) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0662 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_79UL | 23KV鹿58線(4D58) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0663 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D58_LCO_TAP | 23KV鹿58線(4D58) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0664 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_79UL | 23KV鹿61線(4D61) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0665 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D61_LCO_TAP | 23KV鹿61線(4D61) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0666 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_79UL | 23KV鹿62線(4D62) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0667 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D62_LCO_TAP | 23KV鹿62線(4D62) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0668 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_79UL | 23KV鹿63線(4D63) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0669 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D63_LCO_TAP | 23KV鹿63線(4D63) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0670 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_79UL | 23KV鹿64線(4D64) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0671 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D64_LCO_TAP | 23KV鹿64線(4D64) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0672 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_79UL | 23KV鹿65線(4D65) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0673 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D65_LCO_TAP | 23KV鹿65線(4D65) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0674 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_79UL | 23KV鹿66線(4D66) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0675 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D66_LCO_TAP | 23KV鹿66線(4D66) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0676 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_79UL | 23KV鹿67線(4D67) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0677 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D67_LCO_TAP | 23KV鹿67線(4D67) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0678 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_79UL | 23KV鹿68線(4D68) 79RY U/L | FEEDER |  | CDC_Mon1_DPC |  |  |  | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | 50_51NUL |  |  | Status | 50/51/50N/51N RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0679 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B2/D28_D1 | [8 empty] | 鹿耳DS.4D68_LCO_TAP | 23KV鹿68線(4D68) LCO TAP | FEEDER |  | CDC_Mon1_DPC |  |  |  | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0680 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.310_81UL | 310 #1DTR(A) 81RY U/L | OTHER |  | CDC_Mon1_DPC |  |  |  | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(B)(320) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0681 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.320_81UL | 320 #1DTR(B) 81RY U/L | OTHER |  | CDC_Mon1_DPC |  |  |  | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0682 |  |  | 1-10-00 |  |  | NO.1 DTR | TRA | NO.1 DTR TRA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.330_81UL | 330 #2DTR(A) 81RY U/L | OTHER |  | CDC_Mon1_DPC |  |  |  | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0683 |  |  | 1-11-00 |  |  | NO.1 DTR | TRF | NO.1 DTR TRF 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.340_81UL | 340 #2DTR(B) 81RY U/L | OTHER |  | CDC_Mon1_DPC |  |  |  | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | 3A5Other | 排水泵故障1_電纜涵洞 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0684 |  |  | 1-12-00 |  |  | NO.1 DTR | 63Q | NO.1 DTR 63Q 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.涵洞泵浦 | 電纜涵洞泵浦故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Water | 161KV 電纜涵洞 |  | Status | 地下室淹水 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0686 |  |  | 1-14-00 |  |  | NO.1 DTR | 96B1 | NO.1 DTR 96B1 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.涵洞水位(2) | 電纜涵洞第二段水位警報 | OTHER |  | CDC_Mon1_DPC |  |  |  | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0687 |  |  | 1-15-00 |  |  | NO.1 DTR | 96B2 | NO.1 DTR 96B2 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.GEN | 緊急發電機運轉 | OTHER |  | CDC_Mon1_DPC |  |  |  | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | AIRCON | 161KV 電纜涵洞 |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0688 |  |  | 1-00-00 |  |  | 南濱鹿耳紅線 | 52AS | 1510 (南濱鹿耳紅線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.涵洞風機故障 | 電纜涵洞風機故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | Fire2 | 161KV 電纜涵洞 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0689 |  |  | 1-01-00 |  |  | 南濱鹿耳紅線 | 87A | 1510 (南濱鹿耳紅線) 87A 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.火災警報(2) | 火災警報(2)建物-電纜涵洞 | OTHER |  | CDC_Mon1_DPC |  |  |  | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 |  | 2-00-00 | 2-01-00 |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1501_DS | 1501(TIE) DS | TIE |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 |  | 2-02-00 | 2-03-00 |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1502_DS | 1502(TIE) DS | TIE |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0772 | 773 |  | 2-04-00 | 2-05-00 |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1511_DS | 1511(南濱鹿耳紅線) DS | LINE161 |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0774 | 775 |  | 2-06-00 | 2-07-00 |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1512_DS | 1512(南濱鹿耳紅線) DS | LINE161 |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0776 | 777 |  | 2-08-00 | 2-09-00 |  | 南濱鹿耳紅線 | DS | 1513 ( 南濱鹿耳紅線) DS ON |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1513_DS | 1513(南濱鹿耳紅線) DS | LINE161 |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0778 | 779 |  | 2-10-00 | 2-11-00 |  | 南濱鹿耳紅線 | ES | 1513E ( 南濱鹿耳紅線) ES ON |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1513E_ES | 1513E(南濱鹿耳紅線) ES | LINE161 |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0780 | 781 |  | 2-12-00 | 2-13-00 |  | 南濱鹿耳白線 | DS | 1521 ( 南濱鹿耳白線) DS ON |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1521_DS | 1521(南濱鹿耳白線) DS | LINE161 | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0782 | 783 |  | 2-14-00 | 2-15-00 |  | 南濱鹿耳白線 | DS | 1522 ( 南濱鹿耳白線) DS ON |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1522_DS | 1522(南濱鹿耳白線) DS | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 |  | 2-00-00 | 2-01-00 |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1523_DS | 1523(南濱鹿耳白線) DS | LINE161 |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0786 | 787 |  | 2-02-00 | 2-03-00 |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1523E_ES | 1523E(南濱鹿耳白線) ES | LINE161 |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0836 | 837 |  | 2-04-00 | 2-05-00 |  | TIE-2B | PHA | 200 (TIE-2B) PHA 動作/正常 |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1751_DS | 1751(#1DTR) DS | MTR |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0838 | 839 |  | 2-06-00 | 2-07-00 |  | SC-1 | 52AS | 210 (SC-1) 52AS ON/OFF |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1752_DS | 1752(#1DTR) DS | MTR |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0840 | 841 |  | 2-08-00 | 2-09-00 |  | 南濱鹿耳紅線 | DS | 1513 ( 南濱鹿耳紅線) DS ON |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1761_DS | 1761(#2DTR) DS | MTR |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0842 | 843 |  | 2-10-00 | 2-11-00 |  | 南濱鹿耳紅線 | ES | 1513E ( 南濱鹿耳紅線) ES ON |  |  | B2/D28_A1 | [8 empty] | 鹿耳DS.1762_DS | 1762(#2DTR) DS | MTR |  | CDC_Mon1_DPC,CDC_Mon2_DPC |  |  |  | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1BUS | #1BUS |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0032 |  |  | 1-A0 |  |  | NO. 1 BUS | Vbc |  | kV_-210_210(-2000_2000) | aaa | B2/D28_A1 | [8 empty] | 鹿耳DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 444 | DNPAIPoint | DS048 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D28 | 鹿耳DS | 161 | 161kV | 2BUS | #2BUS |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0033 |  |  | 1-A1 |  |  | NO. 2 BUS | Vbc |  | kV_-210_210(-2000_2000) | aab | B2/D28_A1 | [8 empty] | 鹿耳DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 445 | DNPAIPoint | DS048 |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D28 | 鹿耳DS | 0 |  | StaDev | 所內設施 |  | SCADAA | LocalSCADA故障B | INSERT | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0630 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.SCADA_B | SCADA B故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 446 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | ComPoint |  |  | RCA | 23KV 79RY(復閉)動作 | INSERT | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0076 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.23KV_RCA | 23KV 79RY(復閉)動作 | OTHER |  | CDC_Mon1_DPC |  |  |  | 447 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 310 | #1DTR(310) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 2-00-00 |  |  | TIE-1A | 52AS | 100 (TIE-1A) 52AS ON/OFF |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.310_81A | 310 #1DTR(A) 81RY動作 | OTHER |  | CDC_Mon1_DPC |  |  |  | 448 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 320 | #1DTR(320) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-01-00 |  |  | TIE-1A | PHA | 100 (TIE-1A) PHA 動作/正常 |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.320_81A | 320 #1DTR(B) 81RY動作 | OTHER |  | CDC_Mon1_DPC |  |  |  | 449 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 330 | #2DTR(330) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 2-02-00 |  |  | TIE-1A | GDA | 100 (TIE-1A) GDA 動作/正常 |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.330_81A | 330 #2DTR(A) 81RY動作 | OTHER |  | CDC_Mon1_DPC |  |  |  | 450 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 340 | #2DTR(340) |  | 81A |  | INSERT | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 2-03-00 |  |  | TIE-2B | 52AS | 200 (TIE-2B) 52AS ON/OFF |  |  | ELEM/D28_A1 | [8 empty] | 鹿耳DS.340_81A | 340 #2DTR(B) 81RY動作 | OTHER |  | CDC_Mon1_DPC |  |  |  | 451 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA |  | INSERT | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0690 |  |  | 1-02-00 |  |  | 南濱鹿耳紅線 | PHA | 1510 (南濱鹿耳紅線) PHA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 452 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  | INSERT | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0691 |  |  | 1-03-00 |  |  | 南濱鹿耳紅線 | GDA | 1510 (南濱鹿耳紅線) GDA 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 453 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | 1A5Other | 51RYFA | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0693 |  |  | 1-05-00 |  |  | 南濱鹿耳白線 | 87A | 1520 (南濱鹿耳白線) 87A 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_51RYFA | #1DTR 51RY數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 454 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | RYFA | 51Z | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0694 |  |  | 1-06-00 |  |  | 南濱鹿耳白線 | PHA | 1520 (南濱鹿耳白線) PHA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_51ZRYFA | #1DTR 51Z RY數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 455 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | RYFA |  | INSERT | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0692 |  |  | 1-04-00 |  |  | 南濱鹿耳白線 | 52AS | 1520 (南濱鹿耳白線) 52AS ON/OFF |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#1DTR_87RYFA | #1DTR 87RY數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 456 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | 1A5Other | 51RYFA | INSERT | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0696 |  |  | 1-08-00 |  |  | L7 | RYFA | 1570 (L7) RYFA 動作/正常 (FUTURE) |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_51RYFA | #2DTR 51RY數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 457 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | RYFA | 51Z | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0697 |  |  | 1-09-00 |  |  | L8 | RYFA | 1580 (L8) RYFA 動作/正常 (FUTURE) |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_51ZRYFA | #2DTR 51Z RY數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 458 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | RYFA |  | INSERT | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0695 |  |  | 1-07-00 |  |  | 南濱鹿耳白線 | GDA | 1520 (南濱鹿耳白線) GDA 動作/正常 |  |  | B1/D28_A1 | [8 empty] | 鹿耳DS.#2DTR_87RYFA | #2DTR 87RY數位電驛故障 | OTHER |  | CDC_Mon1_DPC |  |  |  | 459 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | ComPoint |  |  | Fire3 | 火災警報(3) | INSERT | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0605 |  |  | 1-13-00 |  |  | NO.1 DTR | 96D | NO.1 DTR 96D 動作/正常 |  |  | B3/D28_A1 | [8 empty] | 鹿耳DS.火災警報(3) | 火災警報(3) | OTHER |  | CDC_Mon1_DPC |  |  |  | 460 | DNPDIPoint | DS048 |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0698 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_87UL | 161KV #1SHR 87RY U/L | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0701 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0702 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0703 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0704 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_GDA | 1950(#1SHR) GDA | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_PHA | 1950(#1SHR) PHA | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRA |  |  | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0700 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | SHRF |  |  | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0699 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0705 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 | [10 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.#1SHR_96PA | #1SHR 機械保護動作 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1SHR/T1 |  | 0077 | [9 empty] | not found | B2/D28_A1 | [8 empty] | 鹿耳DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 |  |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0852 | 853 | [9 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 |  |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0854 | 855 | [9 empty] | B2/D28_A1 | [8 empty] | 鹿耳DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0164 | [8 empty] | COIL_-120_120(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | [5 empty] | 476 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0165 | [8 empty] | OIL_-120_120(-2000_2000) |  | B2/D28_A1 | [8 empty] | 鹿耳DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | [5 empty] | 477 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | BE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [16 empty] | 478 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | RE0 |  |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D28_A1 | [16 empty] | 479 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: D28/161/1BUS/V; OPRD2: D28/161/2BUS/V
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR_MVAR | #1DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: D28/22/310/MVAR; OPRD2: D28/22/320/MVAR
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR_MW | #1DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: D28/22/310/MW; OPRD2: D28/22/320/MW
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR_MVAR | #2DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: D28/22/330/MVAR; OPRD2: D28/22/340/MVAR
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR_MW | #2DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: D28/22/330/MW; OPRD2: D28/22/340/MW
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D28_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D28/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D28_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_2 | OPRD1: D28/161/1510/MW; OPRD2: D28/161/1520/MW
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D28_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: D28/0/CalcPoint/OPRN2_MW
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D28_A1 | [17 empty] | none
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D28_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: D28/0/CalcPoint/OPRN1; OPRD2: D28/0/CalcPoint/OPRN2; OPRD3: D28/0/CalcPoint/PRFL_UL
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D28_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D28/22/310/I_R; OPRD2: D28/22/320/I_R
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D28_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D28/22/310/I_S; OPRD2: D28/22/320/I_S
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D28_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D28/22/310/I_T; OPRD2: D28/22/320/I_T
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D28_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D28/22/330/I_R; OPRD2: D28/22/340/I_R
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D28_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D28/22/330/I_S; OPRD2: D28/22/340/I_S
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D28_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: D28/22/330/I_T; OPRD2: D28/22/340/I_T
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱～鹿耳紅線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D28_A1 | [12 empty] | 鹿耳DS.1510_AMP | 南濱鹿耳紅線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D28/161/1510/MW; OPRD2: D28/161/1510/MVAR; OPRD3: D28/0/CalcPoint/Vbs4
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱～鹿耳白線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D28_A1 | [12 empty] | 鹿耳DS.1520_AMP | 南濱鹿耳白線 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: D28/161/1520/MW; OPRD2: D28/161/1520/MVAR; OPRD3: D28/0/CalcPoint/Vbs4
D28 | 鹿耳DS | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D28_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D28/22/1ABUS/V
D28 | 鹿耳DS | 22 | 22kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D28_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D28/22/1BBUS/V
D28 | 鹿耳DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D28_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D28/22/2ABUS/V
D28 | 鹿耳DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D28_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: D28/22/2BBUS/V
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D28_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 鹿耳DS.#1DTR_MVA | #1DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: D28//1DTR/MW; OPRD2: D28//1DTR/MVAR
D28 | 鹿耳DS |  |  | 1DTR(A) | #1DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D28_A1 | LG_0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 鹿耳DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: D28/22/310/MW; OPRD2: D28/22/310/MVAR
D28 | 鹿耳DS |  |  | 1DTR(B) | #1DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D28_A1 | LG_0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 鹿耳DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: D28/22/320/MW; OPRD2: D28/22/320/MVAR
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D28_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 鹿耳DS.#2DTR_MVA | #2DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: D28//2DTR/MW; OPRD2: D28//2DTR/MVAR
D28 | 鹿耳DS |  |  | 2DTR(A) | #2DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D28_A1 | LG_0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 鹿耳DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: D28/22/330/MW; OPRD2: D28/22/330/MVAR
D28 | 鹿耳DS |  |  | 2DTR(B) | #2DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/D28_A1 | LG_0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  | 鹿耳DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: D28/22/340/MW; OPRD2: D28/22/340/MVAR
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | LOAD | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR_LOAD | #1DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: D28//1DTR/MVA; OPRD2: 0
D28 | 鹿耳DS |  |  | 1DTR(A) | #1DTR(A) |  | LOAD | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: D28//1DTR(A)/MVA; OPRD2: 0
D28 | 鹿耳DS |  |  | 1DTR(B) | #1DTR(B) |  | LOAD | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: D28//1DTR(B)/MVA; OPRD2: 0
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | LOAD | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR_LOAD | #2DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: D28//2DTR/MVA; OPRD2: 0
D28 | 鹿耳DS |  |  | 2DTR(A) | #2DTR(A) |  | LOAD | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: D28//2DTR(A)/MVA; OPRD2: 0
D28 | 鹿耳DS |  |  | 2DTR(B) | #2DTR(B) |  | LOAD | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: D28//2DTR(B)/MVA; OPRD2: 0
D28 | 鹿耳DS |  |  | 1DTR | 1DTR |  | PF | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR_PF | #1DTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D28//1DTR/MW; OPRD2: D28//1DTR/MVAR
D28 | 鹿耳DS |  |  | 1DTR(A) | #1DTR(A) |  | PF | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D28/22/310/MW; OPRD2: D28/22/310/MVAR
D28 | 鹿耳DS |  |  | 1DTR(B) | #1DTR(B) |  | PF | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D28/22/320/MW; OPRD2: D28/22/320/MVAR
D28 | 鹿耳DS |  |  | 2DTR | 2DTR |  | PF | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR_PF | #2DTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D28//2DTR/MW; OPRD2: D28//2DTR/MVAR
D28 | 鹿耳DS |  |  | 2DTR(A) | #2DTR(A) |  | PF | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D28/22/330/MW; OPRD2: D28/22/330/MVAR
D28 | 鹿耳DS |  |  | 2DTR(B) | #2DTR(B) |  | PF | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: D28/22/340/MW; OPRD2: D28/22/340/MVAR
D28 | 鹿耳DS |  |  | 1DTR | #1DTR |  | TR_PERM | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#1DTR_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D28//1DTR/SupLocal; OPRD2: D28//1DTR/Tap Chan
D28 | 鹿耳DS |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B1/D28_A1 | [12 empty] | 鹿耳DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: D28//2DTR/SupLocal; OPRD2: D28//2DTR/Tap Chan
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1ABUS/V; OPRD2: D28/22/4D51/I_R; OPRD3: D28/22/4D51/I_S; OPRD4: D28/22/4D51/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1ABUS/V; OPRD2: D28/22/4D52/I_R; OPRD3: D28/22/4D52/I_S; OPRD4: D28/22/4D52/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1ABUS/V; OPRD2: D28/22/4D53/I_R; OPRD3: D28/22/4D53/I_S; OPRD4: D28/22/4D53/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1ABUS/V; OPRD2: D28/22/4D54/I_R; OPRD3: D28/22/4D54/I_S; OPRD4: D28/22/4D54/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1BBUS/V; OPRD2: D28/22/4D55/I_R; OPRD3: D28/22/4D55/I_S; OPRD4: D28/22/4D55/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1BBUS/V; OPRD2: D28/22/4D56/I_R; OPRD3: D28/22/4D56/I_S; OPRD4: D28/22/4D56/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1BBUS/V; OPRD2: D28/22/4D57/I_R; OPRD3: D28/22/4D57/I_S; OPRD4: D28/22/4D57/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/1BBUS/V; OPRD2: D28/22/4D58/I_R; OPRD3: D28/22/4D58/I_S; OPRD4: D28/22/4D58/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2ABUS/V; OPRD2: D28/22/4D61/I_R; OPRD3: D28/22/4D61/I_S; OPRD4: D28/22/4D61/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2ABUS/V; OPRD2: D28/22/4D62/I_R; OPRD3: D28/22/4D62/I_S; OPRD4: D28/22/4D62/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2ABUS/V; OPRD2: D28/22/4D63/I_R; OPRD3: D28/22/4D63/I_S; OPRD4: D28/22/4D63/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2ABUS/V; OPRD2: D28/22/4D64/I_R; OPRD3: D28/22/4D64/I_S; OPRD4: D28/22/4D64/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2BBUS/V; OPRD2: D28/22/4D65/I_R; OPRD3: D28/22/4D65/I_S; OPRD4: D28/22/4D65/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2BBUS/V; OPRD2: D28/22/4D66/I_R; OPRD3: D28/22/4D66/I_S; OPRD4: D28/22/4D66/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2BBUS/V; OPRD2: D28/22/4D67/I_R; OPRD3: D28/22/4D67/I_S; OPRD4: D28/22/4D67/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: D28/22/2BBUS/V; OPRD2: D28/22/4D68/I_R; OPRD3: D28/22/4D68/I_S; OPRD4: D28/22/4D68/I_T
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51(4D51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D51/kVA; OPRD2: D28/22/4D51/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52(4D52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D52/kVA; OPRD2: D28/22/4D52/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53(4D53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D53/kVA; OPRD2: D28/22/4D53/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54(4D54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D54/kVA; OPRD2: D28/22/4D54/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55(4D55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D55/kVA; OPRD2: D28/22/4D55/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56(4D56) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D56/kVA; OPRD2: D28/22/4D56/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57(4D57) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D57/kVA; OPRD2: D28/22/4D57/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58(4D58) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D58/kVA; OPRD2: D28/22/4D58/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61(4D61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D61/kVA; OPRD2: D28/22/4D61/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62(4D62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D62/kVA; OPRD2: D28/22/4D62/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63(4D63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D63/kVA; OPRD2: D28/22/4D63/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64(4D64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D64/kVA; OPRD2: D28/22/4D64/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65(4D65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D65/kVA; OPRD2: D28/22/4D65/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66(4D66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D66/kVA; OPRD2: D28/22/4D66/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67(4D67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D67/kVA; OPRD2: D28/22/4D67/KVAR
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68(4D68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D28_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: D28/22/4D68/kVA; OPRD2: D28/22/4D68/KVAR
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | DTR_MW | [9 empty] | B1/D28_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: D28//1DTR/MW; OPRD2: D28//2DTR/MW
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | DTR_MVAR | [9 empty] | B1/D28_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_2 | OPRD1: D28//1DTR/MVAR; OPRD2: D28//2DTR/MVAR
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D28_A1 | [12 empty] | 鹿耳DS.210_SC_MVAR | 23KV#1SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D28/22/210/CB; OPRD2: 13.8; OPRD3: 0
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D28_A1 | [12 empty] | 鹿耳DS.220_SC_MVAR | 23KV#2SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D28/22/220/CB; OPRD2: 13.8; OPRD3: 0
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D28_A1 | [12 empty] | 鹿耳DS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D28/22/230/CB; OPRD2: 13.8; OPRD3: 0
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D28_A1 | [12 empty] | 鹿耳DS.240_SC_MVAR | 23KV#4SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: D28/22/240/CB; OPRD2: 13.8; OPRD3: 0
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D28_A1 | [12 empty] | 鹿耳DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_10 |  | com_alarm_30 | D28//1DTR/63Q | D28//1DTR/96B2 | D28//1DTR/96D | D28//1DTR/TRA | D28//1DTR/96B1 | D28//1DTR/96PA | D28//1DTR/87A | D28//1DTR/51ZA | D28//1DTR/GDA | D28//1DTR/PHA | D28//2DTR/63Q | D28//2DTR/TRA | D28//2DTR/96B1 | D28//2DTR/96D | D28//2DTR/96B2 | D28//2DTR/96PA | D28//2DTR/87A | D28//2DTR/51ZA | D28//2DTR/GDA | D28//2DTR/PHA | D28/161/1BUS/87A | D28/161/2BUS/87A | D28/22/310/PHA | D28/22/310/GDA | D28/22/320/GDA | D28/22/320/PHA | D28/22/330/PHA | D28/22/330/GDA | D28/22/340/GDA | D28/22/340/PHA
D28 | 鹿耳DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D28_A1 | [12 empty] | 鹿耳DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_2 |  | com_alarm_2 | OPRD1: D28//1DTR/TRF; OPRD2: D28//2DTR/TRF
D28 | 鹿耳DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/161/1750/CB
D28 | 鹿耳DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/161/1760/CB
D28 | 鹿耳DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/310/CB
D28 | 鹿耳DS | 22 | 22kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/320/CB
D28 | 鹿耳DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/330/CB
D28 | 鹿耳DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/340/CB
D28 | 鹿耳DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/0/StaDev/DCE
D28 | 鹿耳DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/0/StaDev/DCA
D28 | 鹿耳DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/0/StaDev/STUV
D28 | 鹿耳DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/ComPoint/CBA
D28 | 鹿耳DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/ComPoint/CBF
D28 | 鹿耳DS | 22 | 22kV | 310_D1 | #1DTR(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/310/81A
D28 | 鹿耳DS | 22 | 22kV | 320_D1 | #1DTR(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/320/81A
D28 | 鹿耳DS | 22 | 22kV | 330_D1 | #2DTR(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/330/81A
D28 | 鹿耳DS | 22 | 22kV | 340_D1 | #2DTR(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D28_D1 | [17 empty] | lamp2CC | OPRD1: D28/22/340/81A

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D28 | 鹿耳DS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | D28/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510_AMP | 南濱鹿耳紅線 AMP | LINE161 | D28/161/1510/I |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520_AMP | 南濱鹿耳白線 AMP | LINE161 | D28/161/1520/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿51線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線KVA | 23KV鹿51線KVA | FEEDER |  |  | KVA_CAL |  |  | 5 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿51線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線KW | 23KV鹿51線KW | FEEDER |  |  | KW_CAL |  |  | 6 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿52線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線KVA | 23KV鹿52線KVA | FEEDER |  |  | KVA_CAL |  |  | 7 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿52線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線KW | 23KV鹿52線KW | FEEDER |  |  | KW_CAL |  |  | 8 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿53線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線KVA | 23KV鹿53線KVA | FEEDER |  |  | KVA_CAL |  |  | 9 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿53線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線KW | 23KV鹿53線KW | FEEDER |  |  | KW_CAL |  |  | 10 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿54線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線KVA | 23KV鹿54線KVA | FEEDER |  |  | KVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿54線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線KW | 23KV鹿54線KW | FEEDER |  |  | KW_CAL |  |  | 12 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿55線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線KVA | 23KV鹿55線KVA | FEEDER |  |  | KVA_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿55線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線KW | 23KV鹿55線KW | FEEDER |  |  | KW_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿56線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線KVA | 23KV鹿56線KVA | FEEDER |  |  | KVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿56線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線KW | 23KV鹿56線KW | FEEDER |  |  | KW_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿57線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線KVA | 23KV鹿57線KVA | FEEDER |  |  | KVA_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿57線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線KW | 23KV鹿57線KW | FEEDER |  |  | KW_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿58線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線KVA | 23KV鹿58線KVA | FEEDER |  |  | KVA_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿58線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線KW | 23KV鹿58線KW | FEEDER |  |  | KW_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿61線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線KVA | 23KV鹿61線KVA | FEEDER |  |  | KVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿61線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線KW | 23KV鹿61線KW | FEEDER |  |  | KW_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿62線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線KVA | 23KV鹿62線KVA | FEEDER |  |  | KVA_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿62線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線KW | 23KV鹿62線KW | FEEDER |  |  | KW_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿63線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線KVA | 23KV鹿63線KVA | FEEDER |  |  | KVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿63線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線KW | 23KV鹿63線KW | FEEDER |  |  | KW_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿64線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線KVA | 23KV鹿64線KVA | FEEDER |  |  | KVA_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿64線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線KW | 23KV鹿64線KW | FEEDER |  |  | KW_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿65線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線KVA | 23KV鹿65線KVA | FEEDER |  |  | KVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿65線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線KW | 23KV鹿65線KW | FEEDER |  |  | KW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿66線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線KVA | 23KV鹿66線KVA | FEEDER |  |  | KVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿66線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線KW | 23KV鹿66線KW | FEEDER |  |  | KW_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿67線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線KVA | 23KV鹿67線KVA | FEEDER |  |  | KVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿67線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線KW | 23KV鹿67線KW | FEEDER |  |  | KW_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿68線KVA | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線KVA | 23KV鹿68線KVA | FEEDER |  |  | KVA_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  |  |  |  | 鹿68線KW | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線KW | 23KV鹿68線KW | FEEDER |  |  | KW_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR | D28//1DTR(A)/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR | D28//1DTR(A)/Loading |  | TR_LOAD_30 |  |  | 38 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR | D28//1DTR(A)/PF |  | RPDC_PF_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR | D28//1DTR(B)/MVA |  | MVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR | D28//1DTR(B)/Loading |  | TR_LOAD_30 |  |  | 41 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR | D28//1DTR(B)/PF |  | RPDC_PF_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR | D28//2DTR(A)/MVA |  | MVA_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR | D28//2DTR(A)/Loading |  | TR_LOAD_30 |  |  | 44 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR | D28//2DTR(A)/PF |  | RPDC_PF_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR | D28//2DTR(B)/MVA |  | MVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR | D28//2DTR(B)/Loading |  | TR_LOAD_30 |  |  | 47 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR | D28//2DTR(B)/PF |  | RPDC_PF_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_MW | #1DTR MW | MTR | D28//1DTR/MW |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_MVAR | #1DTR MVAR | MTR | D28//1DTR/MVAR |  | MTR_PQ_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_MVA | #1DTR二次側 MVA | MTR | D28//1DTR/MVA |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_LOAD | #1DTR 負載率 | MTR | D28//1DTR/Loading |  | TR_LOAD_60 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_PF | #1DTR 功率因素 | MTR | D28//1DTR/PF |  | RPDC_PF_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_MW | #2DTR MW | MTR | D28//2DTR/MW |  | MTR_PQ_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_MVAR | #2DTR MVAR | MTR | D28//2DTR/MVAR |  | MTR_PQ_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_MVA | #2DTR二次側 MVA | MTR | D28//2DTR/MVA |  | MVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_LOAD | #2DTR 負載率 | MTR | D28//2DTR/Loading |  | TR_LOAD_60 |  |  | 57 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_PF | #2DTR 功率因素 | MTR | D28//2DTR/PF |  | RPDC_PF_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
D28 | 鹿耳DS | 22 | 22kV | 210_SC | #1SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.210_SC_MVAR | 23KV#1SC MVAR | SC | D28/22/210/MVAR |  | SC_CAL_23 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 220_SC | #2SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.220_SC_MVAR | 23KV#2SC MVAR | SC | D28/22/220/MVAR |  | SC_CAL_23 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.230_SC_MVAR | 23KV#3SC MVAR | SC | D28/22/230/MVAR |  | SC_CAL_23 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.240_SC_MVAR | 23KV#4SC MVAR | SC | D28/22/240/MVAR |  | SC_CAL_23 |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | TRTOT | 鹿耳主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 鹿耳DS.TRTOT_MW | 鹿耳主變瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 0 |  | TRTOT | 鹿耳主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 鹿耳DS.TRTOT_MVAR | 鹿耳主變瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 1BUS | #1BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.23KV#1BUS_KV | 23KV #1BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 65 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D28 | 鹿耳DS | 22 | 22kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.23KV#2BUS_KV | 23KV #2BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 66 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
D28 | 鹿耳DS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 67 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 68 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 69 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 70 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | COMM_S_L | 通訊處理單元 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.COMM_S/L_4 | 通訊處理單元 SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 71 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D28 | 鹿耳DS | 0 |  | PMCCA | PMCC電驛故障 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.PMCCA_4 | PMCC電驛故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 72 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | TCA | 斷路器跳脫回路故障 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.TCA_4 | 斷路器跳脫回路故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 73 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | D28/0/CalcPoint/SUBA |  | STATION_FAULT_10 |  |  | 74 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | D28/0/CalcPoint/SUBF |  | STATION_FAULT_2 |  |  | 75 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510_AMP | 南濱鹿耳紅線 | [27 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510_AMP_A | 南濱鹿耳紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520_AMP | 南濱鹿耳白線 | [27 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520_AMP_A | 南濱鹿耳白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_PERM | #1DTR TAP PERMISSION POINT | MTR | D28//1DTR/TR_PERM |  | DTR_PERM |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR | D28//2DTR/TR_PERM |  | DTR_PERM |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_DS |  |  | 82 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1ABUS | #1ABUS |  | 23KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 鹿耳DS.23KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 1BBUS | #1BBUS |  | 23KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 鹿耳DS.23KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 鹿耳DS.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 鹿耳DS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T2 |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
D28 | 鹿耳DS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 89 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1BUS | #1BUS |  | V | [14 empty] | 0032 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | D28/161/1BUS/V |  |  |  | DNP | 90 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D28 | 鹿耳DS | 161 | 161kV | 2BUS | #2BUS |  | V | [14 empty] | 0033 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | D28/161/2BUS/V |  |  |  | DNP | 91 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
D28 | 鹿耳DS | 22 | 22kV | 1ABUS | #1ABUS |  | V | [14 empty] | 0043 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | D28/22/1ABUS/V |  |  |  | DNP | 92 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 1BBUS | #1BBUS |  | V | [14 empty] | 0072 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV#1BBUS_KV | 23KV #1BBUS KV | BUS | D28/22/1BBUS/V |  |  |  | DNP | 93 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 2ABUS | #2ABUS |  | V | [14 empty] | 0100 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | D28/22/2ABUS/V |  |  |  | DNP | 94 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [14 empty] | 0126 | [8 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | D28/22/2BBUS/V |  |  |  | DNP | 95 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | MW | [14 empty] | 0016 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1510_MW | 南濱鹿耳紅線 MW | LINE161 | D28/161/1510/MW |  |  |  | DNP | 96 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | MVAR | [14 empty] | 0017 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1510_MVAR | 南濱鹿耳紅線 MVAR | LINE161 | D28/161/1510/MVAR |  |  |  | DNP | 97 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1510LPD | 南濱鹿耳紅線(1510) |  | V | [14 empty] | 0035 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1510LPD_KV | 南濱鹿耳紅線(1510) LPD KV | LINE161 | D28/161/1510/V |  |  |  | DNP | 98 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | MW | [14 empty] | 0018 | [8 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1520_MW | 南濱鹿耳白線 MW | LINE161 | D28/161/1520/MW |  |  |  | DNP | 99 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | MVAR | [14 empty] | 0019 | [8 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1520_MVAR | 南濱鹿耳白線 MVAR | LINE161 | D28/161/1520/MVAR |  |  |  | DNP | 100 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1520LPD | 南濱鹿耳白線(1520) |  | V | [14 empty] | 0036 | [8 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1520LPD_KV | 南濱鹿耳白線(1520) LPD KV | LINE161 | D28/161/1520/V |  |  |  | DNP | 101 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
D28 | 鹿耳DS | 22 | 22kV | 鹿51線 | 鹿51線 |  | 鹿51線KVAR | [14 empty] | 0049 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線KVAR | 23KV鹿51線 KVAR | FEEDER | D28/22/4D51/KVAR |  |  |  | DNP | 102 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿51線 | 鹿51線 |  | 鹿51線A1 | [14 empty] | 0050 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線A1 | 23KV鹿51線 R相AMP | FEEDER | D28/22/4D51/I_R |  |  |  | DNP | 103 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿51線 | 鹿51線 |  | 鹿51線A2 | [14 empty] | 0051 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線A2 | 23KV鹿51線 S相AMP | FEEDER | D28/22/4D51/I_S |  |  |  | DNP | 104 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿51線 | 鹿51線 |  | 鹿51線A3 | [14 empty] | 0052 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線A3 | 23KV鹿51線 T相AMP | FEEDER | D28/22/4D51/I_T |  |  |  | DNP | 105 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿51線 | 鹿51線 |  | 鹿51線A0 | [14 empty] | 0053 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿51線A0 | 23KV鹿51線 N相AMP | FEEDER | D28/22/4D51/I_N |  |  |  | DNP | 106 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿52線 | 鹿52線 |  | 鹿52線KVAR | [14 empty] | 0054 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線KVAR | 23KV鹿52線 KVAR | FEEDER | D28/22/4D52/KVAR |  |  |  | DNP | 107 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿52線 | 鹿52線 |  | 鹿52線A1 | [14 empty] | 0055 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線A1 | 23KV鹿52線 R相AMP | FEEDER | D28/22/4D52/I_R |  |  |  | DNP | 108 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿52線 | 鹿52線 |  | 鹿52線A2 | [14 empty] | 0056 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線A2 | 23KV鹿52線 S相AMP | FEEDER | D28/22/4D52/I_S |  |  |  | DNP | 109 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿52線 | 鹿52線 |  | 鹿52線A3 | [14 empty] | 0057 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線A3 | 23KV鹿52線 T相AMP | FEEDER | D28/22/4D52/I_T |  |  |  | DNP | 110 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿52線 | 鹿52線 |  | 鹿52線A0 | [14 empty] | 0058 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿52線A0 | 23KV鹿52線 N相AMP | FEEDER | D28/22/4D52/I_N |  |  |  | DNP | 111 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿53線 | 鹿53線 |  | 鹿53線KVAR | [14 empty] | 0059 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線KVAR | 23KV鹿53線 KVAR | FEEDER | D28/22/4D53/KVAR |  |  |  | DNP | 112 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿53線 | 鹿53線 |  | 鹿53線A1 | [14 empty] | 0060 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線A1 | 23KV鹿53線 R相AMP | FEEDER | D28/22/4D53/I_R |  |  |  | DNP | 113 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿53線 | 鹿53線 |  | 鹿53線A2 | [14 empty] | 0061 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線A2 | 23KV鹿53線 S相AMP | FEEDER | D28/22/4D53/I_S |  |  |  | DNP | 114 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿53線 | 鹿53線 |  | 鹿53線A3 | [14 empty] | 0062 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線A3 | 23KV鹿53線 T相AMP | FEEDER | D28/22/4D53/I_T |  |  |  | DNP | 115 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿53線 | 鹿53線 |  | 鹿53線A0 | [14 empty] | 0063 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿53線A0 | 23KV鹿53線 N相AMP | FEEDER | D28/22/4D53/I_N |  |  |  | DNP | 116 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿54線 | 鹿54線 |  | 鹿54線KVAR | [14 empty] | 0064 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線KVAR | 23KV鹿54線 KVAR | FEEDER | D28/22/4D54/KVAR |  |  |  | DNP | 117 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿54線 | 鹿54線 |  | 鹿54線A1 | [14 empty] | 0065 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線A1 | 23KV鹿54線 R相AMP | FEEDER | D28/22/4D54/I_R |  |  |  | DNP | 118 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿54線 | 鹿54線 |  | 鹿54線A2 | [14 empty] | 0066 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線A2 | 23KV鹿54線 S相AMP | FEEDER | D28/22/4D54/I_S |  |  |  | DNP | 119 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿54線 | 鹿54線 |  | 鹿54線A3 | [14 empty] | 0067 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線A3 | 23KV鹿54線 T相AMP | FEEDER | D28/22/4D54/I_T |  |  |  | DNP | 120 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿54線 | 鹿54線 |  | 鹿54線A0 | [14 empty] | 0068 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿54線A0 | 23KV鹿54線 N相AMP | FEEDER | D28/22/4D54/I_N |  |  |  | DNP | 121 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿55線 | 鹿55線 |  | 鹿55線KVAR | [14 empty] | 0078 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線KVAR | 23KV鹿55線 KVAR | FEEDER | D28/22/4D55/KVAR |  |  |  | DNP | 122 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿55線 | 鹿55線 |  | 鹿55線A1 | [14 empty] | 0079 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線A1 | 23KV鹿55線 R相AMP | FEEDER | D28/22/4D55/I_R |  |  |  | DNP | 123 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿55線 | 鹿55線 |  | 鹿55線A2 | [14 empty] | 0080 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線A2 | 23KV鹿55線 S相AMP | FEEDER | D28/22/4D55/I_S |  |  |  | DNP | 124 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿55線 | 鹿55線 |  | 鹿55線A3 | [14 empty] | 0081 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線A3 | 23KV鹿55線 T相AMP | FEEDER | D28/22/4D55/I_T |  |  |  | DNP | 125 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿55線 | 鹿55線 |  | 鹿55線A0 | [14 empty] | 0082 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿55線A0 | 23KV鹿55線 N相AMP | FEEDER | D28/22/4D55/I_N |  |  |  | DNP | 126 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿56線 | 鹿56線 |  | 鹿56線KVAR | [14 empty] | 0083 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線KVAR | 23KV鹿56線 KVAR | FEEDER | D28/22/4D56/KVAR |  |  |  | DNP | 127 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿56線 | 鹿56線 |  | 鹿56線A1 | [14 empty] | 0084 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線A1 | 23KV鹿56線 R相AMP | FEEDER | D28/22/4D56/I_R |  |  |  | DNP | 128 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿56線 | 鹿56線 |  | 鹿56線A2 | [14 empty] | 0085 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線A2 | 23KV鹿56線 S相AMP | FEEDER | D28/22/4D56/I_S |  |  |  | DNP | 129 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿56線 | 鹿56線 |  | 鹿56線A3 | [14 empty] | 0086 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線A3 | 23KV鹿56線 T相AMP | FEEDER | D28/22/4D56/I_T |  |  |  | DNP | 130 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿56線 | 鹿56線 |  | 鹿56線A0 | [14 empty] | 0087 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿56線A0 | 23KV鹿56線 N相AMP | FEEDER | D28/22/4D56/I_N |  |  |  | DNP | 131 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿57線 | 鹿57線 |  | 鹿57線KVAR | [14 empty] | 0088 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線KVAR | 23KV鹿57線 KVAR | FEEDER | D28/22/4D57/KVAR |  |  |  | DNP | 132 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿57線 | 鹿57線 |  | 鹿57線A1 | [14 empty] | 0089 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線A1 | 23KV鹿57線 R相AMP | FEEDER | D28/22/4D57/I_R |  |  |  | DNP | 133 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿57線 | 鹿57線 |  | 鹿57線A2 | [14 empty] | 0090 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線A2 | 23KV鹿57線 S相AMP | FEEDER | D28/22/4D57/I_S |  |  |  | DNP | 134 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿57線 | 鹿57線 |  | 鹿57線A3 | [14 empty] | 0091 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線A3 | 23KV鹿57線 T相AMP | FEEDER | D28/22/4D57/I_T |  |  |  | DNP | 135 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿57線 | 鹿57線 |  | 鹿57線A0 | [14 empty] | 0092 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿57線A0 | 23KV鹿57線 N相AMP | FEEDER | D28/22/4D57/I_N |  |  |  | DNP | 136 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿58線 | 鹿58線 |  | 鹿58線KVAR | [14 empty] | 0093 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線KVAR | 23KV鹿58線 KVAR | FEEDER | D28/22/4D58/KVAR |  |  |  | DNP | 137 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿58線 | 鹿58線 |  | 鹿58線A1 | [14 empty] | 0094 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線A1 | 23KV鹿58線 R相AMP | FEEDER | D28/22/4D58/I_R |  |  |  | DNP | 138 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿58線 | 鹿58線 |  | 鹿58線A2 | [14 empty] | 0095 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線A2 | 23KV鹿58線 S相AMP | FEEDER | D28/22/4D58/I_S |  |  |  | DNP | 139 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿58線 | 鹿58線 |  | 鹿58線A3 | [14 empty] | 0096 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線A3 | 23KV鹿58線 T相AMP | FEEDER | D28/22/4D58/I_T |  |  |  | DNP | 140 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿58線 | 鹿58線 |  | 鹿58線A0 | [14 empty] | 0097 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿58線A0 | 23KV鹿58線 N相AMP | FEEDER | D28/22/4D58/I_N |  |  |  | DNP | 141 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿61線 | 鹿61線 |  | 鹿61線KVAR | [14 empty] | 0106 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線KVAR | 23KV鹿61線 KVAR | FEEDER | D28/22/4D61/KVAR |  |  |  | DNP | 142 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿61線 | 鹿61線 |  | 鹿61線A1 | [14 empty] | 0107 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線A1 | 23KV鹿61線 R相AMP | FEEDER | D28/22/4D61/I_R |  |  |  | DNP | 143 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿61線 | 鹿61線 |  | 鹿61線A2 | [14 empty] | 0108 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線A2 | 23KV鹿61線 S相AMP | FEEDER | D28/22/4D61/I_S |  |  |  | DNP | 144 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿61線 | 鹿61線 |  | 鹿61線A3 | [14 empty] | 0109 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線A3 | 23KV鹿61線 T相AMP | FEEDER | D28/22/4D61/I_T |  |  |  | DNP | 145 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿61線 | 鹿61線 |  | 鹿61線A0 | [14 empty] | 0110 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿61線A0 | 23KV鹿61線 N相AMP | FEEDER | D28/22/4D61/I_N |  |  |  | DNP | 146 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿62線 | 鹿62線 |  | 鹿62線KVAR | [14 empty] | 0111 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線KVAR | 23KV鹿62線 KVAR | FEEDER | D28/22/4D62/KVAR |  |  |  | DNP | 147 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿62線 | 鹿62線 |  | 鹿62線A1 | [14 empty] | 0112 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線A1 | 23KV鹿62線 R相AMP | FEEDER | D28/22/4D62/I_R |  |  |  | DNP | 148 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿62線 | 鹿62線 |  | 鹿62線A2 | [14 empty] | 0113 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線A2 | 23KV鹿62線 S相AMP | FEEDER | D28/22/4D62/I_S |  |  |  | DNP | 149 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿62線 | 鹿62線 |  | 鹿62線A3 | [14 empty] | 0114 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線A3 | 23KV鹿62線 T相AMP | FEEDER | D28/22/4D62/I_T |  |  |  | DNP | 150 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿62線 | 鹿62線 |  | 鹿62線A0 | [14 empty] | 0115 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿62線A0 | 23KV鹿62線 N相AMP | FEEDER | D28/22/4D62/I_N |  |  |  | DNP | 151 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿63線 | 鹿63線 |  | 鹿63線KVAR | [14 empty] | 0116 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線KVAR | 23KV鹿63線 KVAR | FEEDER | D28/22/4D63/KVAR |  |  |  | DNP | 152 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿63線 | 鹿63線 |  | 鹿63線A1 | [14 empty] | 0117 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線A1 | 23KV鹿63線 R相AMP | FEEDER | D28/22/4D63/I_R |  |  |  | DNP | 153 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿63線 | 鹿63線 |  | 鹿63線A2 | [14 empty] | 0118 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線A2 | 23KV鹿63線 S相AMP | FEEDER | D28/22/4D63/I_S |  |  |  | DNP | 154 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿63線 | 鹿63線 |  | 鹿63線A3 | [14 empty] | 0119 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線A3 | 23KV鹿63線 T相AMP | FEEDER | D28/22/4D63/I_T |  |  |  | DNP | 155 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿63線 | 鹿63線 |  | 鹿63線A0 | [14 empty] | 0120 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿63線A0 | 23KV鹿63線 N相AMP | FEEDER | D28/22/4D63/I_N |  |  |  | DNP | 156 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿64線 | 鹿64線 |  | 鹿64線KVAR | [14 empty] | 0121 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線KVAR | 23KV鹿64線 KVAR | FEEDER | D28/22/4D64/KVAR |  |  |  | DNP | 157 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿64線 | 鹿64線 |  | 鹿64線A1 | [14 empty] | 0122 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線A1 | 23KV鹿64線 R相AMP | FEEDER | D28/22/4D64/I_R |  |  |  | DNP | 158 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿64線 | 鹿64線 |  | 鹿64線A2 | [14 empty] | 0123 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線A2 | 23KV鹿64線 S相AMP | FEEDER | D28/22/4D64/I_S |  |  |  | DNP | 159 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿64線 | 鹿64線 |  | 鹿64線A3 | [14 empty] | 0124 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線A3 | 23KV鹿64線 T相AMP | FEEDER | D28/22/4D64/I_T |  |  |  | DNP | 160 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿64線 | 鹿64線 |  | 鹿64線A0 | [14 empty] | 0125 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿64線A0 | 23KV鹿64線 N相AMP | FEEDER | D28/22/4D64/I_N |  |  |  | DNP | 161 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿65線 | 鹿65線 |  | 鹿65線KVAR | [14 empty] | 0132 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線KVAR | 23KV鹿65線 KVAR | FEEDER | D28/22/4D65/KVAR |  |  |  | DNP | 162 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿65線 | 鹿65線 |  | 鹿65線A1 | [14 empty] | 0133 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線A1 | 23KV鹿65線 R相AMP | FEEDER | D28/22/4D65/I_R |  |  |  | DNP | 163 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿65線 | 鹿65線 |  | 鹿65線A2 | [14 empty] | 0134 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線A2 | 23KV鹿65線 S相AMP | FEEDER | D28/22/4D65/I_S |  |  |  | DNP | 164 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿65線 | 鹿65線 |  | 鹿65線A3 | [14 empty] | 0135 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線A3 | 23KV鹿65線 T相AMP | FEEDER | D28/22/4D65/I_T |  |  |  | DNP | 165 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿65線 | 鹿65線 |  | 鹿65線A0 | [14 empty] | 0136 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿65線A0 | 23KV鹿65線 N相AMP | FEEDER | D28/22/4D65/I_N |  |  |  | DNP | 166 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿66線 | 鹿66線 |  | 鹿66線KVAR | [14 empty] | 0137 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線KVAR | 23KV鹿66線 KVAR | FEEDER | D28/22/4D66/KVAR |  |  |  | DNP | 167 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿66線 | 鹿66線 |  | 鹿66線A1 | [14 empty] | 0138 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線A1 | 23KV鹿66線 R相AMP | FEEDER | D28/22/4D66/I_R |  |  |  | DNP | 168 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿66線 | 鹿66線 |  | 鹿66線A2 | [14 empty] | 0139 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線A2 | 23KV鹿66線 S相AMP | FEEDER | D28/22/4D66/I_S |  |  |  | DNP | 169 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿66線 | 鹿66線 |  | 鹿66線A3 | [14 empty] | 0140 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線A3 | 23KV鹿66線 T相AMP | FEEDER | D28/22/4D66/I_T |  |  |  | DNP | 170 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿66線 | 鹿66線 |  | 鹿66線A0 | [14 empty] | 0141 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿66線A0 | 23KV鹿66線 N相AMP | FEEDER | D28/22/4D66/I_N |  |  |  | DNP | 171 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿67線 | 鹿67線 |  | 鹿67線KVAR | [14 empty] | 0142 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線KVAR | 23KV鹿67線 KVAR | FEEDER | D28/22/4D67/KVAR |  |  |  | DNP | 172 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿67線 | 鹿67線 |  | 鹿67線A1 | [14 empty] | 0143 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線A1 | 23KV鹿67線 R相AMP | FEEDER | D28/22/4D67/I_R |  |  |  | DNP | 173 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿67線 | 鹿67線 |  | 鹿67線A2 | [14 empty] | 0144 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線A2 | 23KV鹿67線 S相AMP | FEEDER | D28/22/4D67/I_S |  |  |  | DNP | 174 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿67線 | 鹿67線 |  | 鹿67線A3 | [14 empty] | 0145 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線A3 | 23KV鹿67線 T相AMP | FEEDER | D28/22/4D67/I_T |  |  |  | DNP | 175 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿67線 | 鹿67線 |  | 鹿67線A0 | [14 empty] | 0146 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿67線A0 | 23KV鹿67線 N相AMP | FEEDER | D28/22/4D67/I_N |  |  |  | DNP | 176 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿68線 | 鹿68線 |  | 鹿68線KVAR | [14 empty] | 0147 | [8 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線KVAR | 23KV鹿68線 KVAR | FEEDER | D28/22/4D68/KVAR |  |  |  | DNP | 177 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿68線 | 鹿68線 |  | 鹿68線A1 | [14 empty] | 0148 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線A1 | 23KV鹿68線 R相AMP | FEEDER | D28/22/4D68/I_R |  |  |  | DNP | 178 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿68線 | 鹿68線 |  | 鹿68線A2 | [14 empty] | 0149 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線A2 | 23KV鹿68線 S相AMP | FEEDER | D28/22/4D68/I_S |  |  |  | DNP | 179 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿68線 | 鹿68線 |  | 鹿68線A3 | [14 empty] | 0150 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線A3 | 23KV鹿68線 T相AMP | FEEDER | D28/22/4D68/I_T |  |  |  | DNP | 180 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 鹿68線 | 鹿68線 |  | 鹿68線A0 | [14 empty] | 0151 | [8 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.鹿68線A0 | 23KV鹿68線 N相AMP | FEEDER | D28/22/4D68/I_N |  |  |  | DNP | 181 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1500TIE | 1500TIE |  | I | [14 empty] | 0034 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.1500TIE_AMP | 1500TIE AMP | TIE | D28/161/1500/I_R |  |  |  | DNP | 182 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | _100 | 100 |  | I_R | [14 empty] | 0069 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV_100_A1 | 23KV 100 R相AMP | TIE | D28/22/100/I_R |  |  |  | DNP | 183 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | _100 | 100 |  | I_S | [14 empty] | 0070 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV_100_A2 | 23KV 100 S相AMP | TIE | D28/22/100/I_S |  |  |  | DNP | 184 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | _100 | 100 |  | I_T | [14 empty] | 0071 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV_100_A3 | 23KV 100 T相AMP | TIE | D28/22/100/I_T |  |  |  | DNP | 185 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | _200 | 200 |  | I_R | [14 empty] | 0152 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV_200_A1 | 23KV 200 R相AMP | TIE | D28/22/200/I_R |  |  |  | DNP | 186 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | _200 | 200 |  | I_S | [14 empty] | 0153 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV_200_A2 | 23KV 200 S相AMP | TIE | D28/22/200/I_S |  |  |  | DNP | 187 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | _200 | 200 |  | I_T | [14 empty] | 0154 | [8 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.23KV_200_A3 | 23KV 200 T相AMP | TIE | D28/22/200/I_T |  |  |  | DNP | 188 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | OilTemp | [14 empty] | 0002 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_OIL | #1DTR 油溫 | MTR | D28//1DTR/OilTemp |  |  |  | DNP | 189 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | CoilTemp | [14 empty] | 0001 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_COIL | #1DTR 線溫 | MTR | D28//1DTR/CoilTemp |  |  |  | DNP | 190 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | TapPosMv | [14 empty] | 0000 |  | 0002 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_TAP | #1DTR OLTC TAP | MTR | D28//1DTR/TapPosMv |  |  |  | DNP | 191 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [14 empty] | 0044 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | D28/22/310/MW |  |  |  | DNP | 192 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [14 empty] | 0045 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | D28/22/310/MVAR |  |  |  | DNP | 193 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [14 empty] | 0046 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | D28/22/310/I_R |  |  |  | DNP | 194 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [14 empty] | 0047 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | D28/22/310/I_S |  |  |  | DNP | 195 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [14 empty] | 0048 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | D28/22/310/I_T |  |  |  | DNP | 196 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [14 empty] | 0073 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | D28/22/320/MW |  |  |  | DNP | 197 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [14 empty] | 0074 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | D28/22/320/MVAR |  |  |  | DNP | 198 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [14 empty] | 0075 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | D28/22/320/I_R |  |  |  | DNP | 199 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [14 empty] | 0076 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | D28/22/320/I_S |  |  |  | DNP | 200 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [14 empty] | 0077 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | D28/22/320/I_T |  |  |  | DNP | 201 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | OilTemp | [14 empty] | 0005 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_OIL | #2DTR 油溫 | MTR | D28//2DTR/OilTemp |  |  |  | DNP | 202 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | CoilTemp | [14 empty] | 0004 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_COIL | #2DTR 線溫 | MTR | D28//2DTR/CoilTemp |  |  |  | DNP | 203 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | TapPosMv | [14 empty] | 0003 |  | 0006 | [6 empty] | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_TAP | #2DTR OLTC TAP | MTR | D28//2DTR/TapPosMv |  |  |  | DNP | 204 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [14 empty] | 0101 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | D28/22/330/MW |  |  |  | DNP | 205 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [14 empty] | 0102 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | D28/22/330/MVAR |  |  |  | DNP | 206 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [14 empty] | 0103 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | D28/22/330/I_R |  |  |  | DNP | 207 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [14 empty] | 0104 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | D28/22/330/I_S |  |  |  | DNP | 208 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [14 empty] | 0105 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | D28/22/330/I_T |  |  |  | DNP | 209 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [14 empty] | 0127 | [8 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | D28/22/340/MW |  |  |  | DNP | 210 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [14 empty] | 0128 | [8 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | D28/22/340/MVAR |  |  |  | DNP | 211 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [14 empty] | 0129 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | D28/22/340/I_R |  |  |  | DNP | 212 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [14 empty] | 0130 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | D28/22/340/I_S |  |  |  | DNP | 213 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [14 empty] | 0131 | [8 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | D28/22/340/I_T |  |  |  | DNP | 214 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 0 |  |  |  |  | DCV_N | [14 empty] | 0099 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.直流N電源電壓 | 直流N電源電壓 | OTHER | D28/0/StaDev/DCV_N |  |  |  | DNP | 215 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
D28 | 鹿耳DS | 0 |  |  |  |  | DCV_P | [14 empty] | 0098 | [8 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.直流P電源電壓 | 直流P電源電壓 | OTHER | D28/0/StaDev/DCV_P |  |  |  | DNP | 216 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | 永勁線A1 | [14 empty] | 0157 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線A1 | 23KV永勁線 R相AMP | FEEDER |  |  |  |  | DNP | 217 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | 永勁線A2 | [14 empty] | 0158 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線A2 | 23KV永勁線 S相AMP | FEEDER |  |  |  |  | DNP | 218 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | 永勁線A3 | [14 empty] | 0159 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線A3 | 23KV永勁線 T相AMP | FEEDER |  |  |  |  | DNP | 219 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | 永勁線A0 | [14 empty] | 0160 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線A0 | 23KV永勁線 N相AMP | FEEDER |  |  |  |  | DNP | 220 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | V | [14 empty] | 0161 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線_KV | 23KV永勁線 KV | OTHER |  |  |  |  | DNP | 221 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | KW | [14 empty] | 0155 | [8 empty] | KW_-7200_7200(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線_KW | 23KV永勁線 KW | OTHER |  |  |  |  | DNP | 222 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
D28 | 鹿耳DS | 22 | 22kV | 永勁線 | 永勁線 |  | 永勁線KVAR | [14 empty] | 0156 | [8 empty] | KVAR_-7200_7200(-2000_2000) |  | DDCS4_1 | [8 empty] | 鹿耳DS.永勁線KVAR | 23KV永勁線 KVAR | FEEDER |  |  |  |  | DNP | 223 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | CoilTemp | [14 empty] | 0164 | [8 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | D28/161/1SHR/CoilTemp |  |  |  | DNP | 224 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | OilTemp | [14 empty] | 0165 | [8 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | D28/161/1SHR/OilTemp |  |  |  | DNP | 225 | DNPAIPoint | DS048 |  |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | PHA | [14 empty] | 0002 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1510_PHA | 南濱鹿耳紅線(1510) 相間RY | LINE161 | D28/161/1510/PHA |  |  |  | DNP | 226 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | GDA | [14 empty] | 0003 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1510_GDA | 南濱鹿耳紅線(1510) 接地RY | LINE161 | D28/161/1510/GDA |  |  |  | DNP | 227 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | 87A | [14 empty] | 0001 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1510_87A | 南濱鹿耳紅線(1510) 87RY | LINE161 | D28/161/1510/87A |  |  |  | DNP | 228 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | 87UL | [14 empty] | 0566 |  | 0017 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510_87UL | 南濱鹿耳紅線(1510) 87RY U/L | LINE161 | D28/161/1510/87UL |  |  |  | DNP | 229 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | CB | [14 empty] | 0000 |  | 0036 | [8 empty] | 161KV_S | [8 empty] | 鹿耳DS.1510_CB | 1510(南濱鹿耳紅線) CB | LINE161 | D28/161/1510/CB |  |  |  | DNP | 230 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | 79UL | [14 empty] | 0567 |  | 0018 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510_79UL | 南濱鹿耳紅線(1510) 79RY U/L | LINE161 | D28/161/1510/79UL |  |  |  | DNP | 231 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | DS1 | 1511 | [13 empty] | 0772 | 773 | 0037 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1511_DS | 1511(南濱鹿耳紅線) DS | LINE161 | D28/161/1510/DS1 |  |  |  | DNP | 232 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | DS2 | 1512 | [13 empty] | 0774 | 775 | 0038 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1512_DS | 1512(南濱鹿耳紅線) DS | LINE161 | D28/161/1510/DS2 |  |  |  | DNP | 233 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | DS3 | 1513 | [13 empty] | 0776 | 777 | 0039 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1513_DS | 1513(南濱鹿耳紅線) DS | LINE161 | D28/161/1510/DS3 |  |  |  | DNP | 234 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | E3 | 1513E | [13 empty] | 0778 | 779 | 0040 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1513E_ES | 1513E(南濱鹿耳紅線) ES | LINE161 | D28/161/1510/ES3 |  |  |  | DNP | 235 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | PHA | [14 empty] | 0006 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1520_PHA | 南濱鹿耳白線(1520) 相間RY | LINE161 | D28/161/1520/PHA |  |  |  | DNP | 236 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | GDA | [14 empty] | 0007 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1520_GDA | 南濱鹿耳白線(1520) 接地RY | LINE161 | D28/161/1520/GDA |  |  |  | DNP | 237 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | 87A | [14 empty] | 0005 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1520_87A | 南濱鹿耳白線(1520) 87RY | LINE161 | D28/161/1520/87A |  |  |  | DNP | 238 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | 87UL | [14 empty] | 0568 |  | 0019 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520_87UL | 南濱鹿耳白線(1520) 87RY U/L | LINE161 | D28/161/1520/87UL |  |  |  | DNP | 239 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | CB | [14 empty] | 0004 |  | 0041 | [8 empty] | 161KV_S | [8 empty] | 鹿耳DS.1520_CB | 1520(南濱鹿耳白線) CB | LINE161 | D28/161/1520/CB |  |  |  | DNP | 240 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | 79UL | [14 empty] | 0569 |  | 0020 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520_79UL | 南濱鹿耳白線(1520) 79RY U/L | LINE161 | D28/161/1520/79UL |  |  |  | DNP | 241 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | DS1 | 1521 | [13 empty] | 0780 | 781 | 0042 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1521_DS | 1521(南濱鹿耳白線) DS | LINE161 | D28/161/1520/DS1 |  |  |  | DNP | 242 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | DS2 | 1522 | [13 empty] | 0782 | 783 | 0043 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1522_DS | 1522(南濱鹿耳白線) DS | LINE161 | D28/161/1520/DS2 |  |  |  | DNP | 243 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | DS3 | 1523 | [13 empty] | 0784 | 785 | 0044 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1523_DS | 1523(南濱鹿耳白線) DS | LINE161 | D28/161/1520/DS3 |  |  |  | DNP | 244 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | E3 | 1523E | [13 empty] | 0786 | 787 | 0045 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1523E_ES | 1523E(南濱鹿耳白線) ES | LINE161 | D28/161/1520/ES3 |  |  |  | DNP | 245 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51線(4D51) |  | PHA | [14 empty] | 0281 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_PHA | 23KV鹿51線(4D51) 相間RY | FEEDER | D28/22/4D51/PHA |  |  |  | DNP | 246 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51線(4D51) |  | GDA | [14 empty] | 0282 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_GDA | 23KV鹿51線(4D51) 接地RY | FEEDER | D28/22/4D51/GDA |  |  |  | DNP | 247 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51線(4D51) 79RY |  | 79UL | [14 empty] | 0648 |  | 0094 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_79UL | 23KV鹿51線(4D51) 79RY U/L | FEEDER | D28/22/4D51/79UL |  |  |  | DNP | 248 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D51_LCO | 鹿51線(4D51) LCO |  | TapPosMv | [14 empty] | 0649 |  | 0095 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_LCO_TAP | 23KV鹿51線(4D51) LCO TAP | FEEDER | D28/22/4D51/50_51NUL |  |  |  | DNP | 249 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D51 | 鹿51線 |  | CB | [14 empty] | 0280 |  | 0093 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_CB | 4D51(23KV鹿51線) CB | FEEDER | D28/22/4D51/CB |  |  |  | DNP | 250 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52線(4D52) |  | PHA | [14 empty] | 0284 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_PHA | 23KV鹿52線(4D52) 相間RY | FEEDER | D28/22/4D52/PHA |  |  |  | DNP | 251 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52線(4D52) |  | GDA | [14 empty] | 0285 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_GDA | 23KV鹿52線(4D52) 接地RY | FEEDER | D28/22/4D52/GDA |  |  |  | DNP | 252 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52線(4D52) 79RY |  | 79UL | [14 empty] | 0650 |  | 0097 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_79UL | 23KV鹿52線(4D52) 79RY U/L | FEEDER | D28/22/4D52/79UL |  |  |  | DNP | 253 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D52_LCO | 鹿52線(4D52) LCO |  | TapPosMv | [14 empty] | 0651 |  | 0098 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_LCO_TAP | 23KV鹿52線(4D52) LCO TAP | FEEDER | D28/22/4D52/50_51NUL |  |  |  | DNP | 254 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D52 | 鹿52線 |  | CB | [14 empty] | 0283 |  | 0096 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_CB | 4D52(23KV鹿52線) CB | FEEDER | D28/22/4D52/CB |  |  |  | DNP | 255 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53線(4D53) |  | PHA | [14 empty] | 0287 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_PHA | 23KV鹿53線(4D53) 相間RY | FEEDER | D28/22/4D53/PHA |  |  |  | DNP | 256 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53線(4D53) |  | GDA | [14 empty] | 0288 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_GDA | 23KV鹿53線(4D53) 接地RY | FEEDER | D28/22/4D53/GDA |  |  |  | DNP | 257 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53線(4D53) 79RY |  | 79UL | [14 empty] | 0652 |  | 0100 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_79UL | 23KV鹿53線(4D53) 79RY U/L | FEEDER | D28/22/4D53/79UL |  |  |  | DNP | 258 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D53_LCO | 鹿53線(4D53) LCO |  | TapPosMv | [14 empty] | 0653 |  | 0101 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_LCO_TAP | 23KV鹿53線(4D53) LCO TAP | FEEDER | D28/22/4D53/50_51NUL |  |  |  | DNP | 259 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D53 | 鹿53線 |  | CB | [14 empty] | 0286 |  | 0099 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_CB | 4D53(23KV鹿53線) CB | FEEDER | D28/22/4D53/CB |  |  |  | DNP | 260 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54線(4D54) |  | PHA | [14 empty] | 0290 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_PHA | 23KV鹿54線(4D54) 相間RY | FEEDER | D28/22/4D54/PHA |  |  |  | DNP | 261 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54線(4D54) |  | GDA | [14 empty] | 0291 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_GDA | 23KV鹿54線(4D54) 接地RY | FEEDER | D28/22/4D54/GDA |  |  |  | DNP | 262 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54線(4D54) 79RY |  | 79UL | [14 empty] | 0654 |  | 0103 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_79UL | 23KV鹿54線(4D54) 79RY U/L | FEEDER | D28/22/4D54/79UL |  |  |  | DNP | 263 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D54_LCO | 鹿54線(4D54) LCO |  | TapPosMv | [14 empty] | 0655 |  | 0104 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_LCO_TAP | 23KV鹿54線(4D54) LCO TAP | FEEDER | D28/22/4D54/50_51NUL |  |  |  | DNP | 264 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D54 | 鹿54線 |  | CB | [14 empty] | 0289 |  | 0102 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_CB | 4D54(23KV鹿54線) CB | FEEDER | D28/22/4D54/CB |  |  |  | DNP | 265 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55線(4D55) |  | PHA | [14 empty] | 0293 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_PHA | 23KV鹿55線(4D55) 相間RY | FEEDER | D28/22/4D55/PHA |  |  |  | DNP | 266 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55線(4D55) |  | GDA | [14 empty] | 0294 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_GDA | 23KV鹿55線(4D55) 接地RY | FEEDER | D28/22/4D55/GDA |  |  |  | DNP | 267 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55線(4D55) 79RY |  | 79UL | [14 empty] | 0656 |  | 0111 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_79UL | 23KV鹿55線(4D55) 79RY U/L | FEEDER | D28/22/4D55/79UL |  |  |  | DNP | 268 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D55_LCO | 鹿55線(4D55) LCO |  | TapPosMv | [14 empty] | 0657 |  | 0112 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_LCO_TAP | 23KV鹿55線(4D55) LCO TAP | FEEDER | D28/22/4D55/50_51NUL |  |  |  | DNP | 269 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D55 | 鹿55線 |  | CB | [14 empty] | 0292 |  | 0110 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_CB | 4D55(23KV鹿55線) CB | FEEDER | D28/22/4D55/CB |  |  |  | DNP | 270 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56線(4D56) |  | PHA | [14 empty] | 0296 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_PHA | 23KV鹿56線(4D56) 相間RY | FEEDER | D28/22/4D56/PHA |  |  |  | DNP | 271 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56線(4D56) |  | GDA | [14 empty] | 0297 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_GDA | 23KV鹿56線(4D56) 接地RY | FEEDER | D28/22/4D56/GDA |  |  |  | DNP | 272 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56線(4D56) 79RY |  | 79UL | [14 empty] | 0658 |  | 0114 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_79UL | 23KV鹿56線(4D56) 79RY U/L | FEEDER | D28/22/4D56/79UL |  |  |  | DNP | 273 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D56_LCO | 鹿56線(4D56) LCO |  | TapPosMv | [14 empty] | 0659 |  | 0115 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_LCO_TAP | 23KV鹿56線(4D56) LCO TAP | FEEDER | D28/22/4D56/50_51NUL |  |  |  | DNP | 274 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D56 | 鹿56線 |  | CB | [14 empty] | 0295 |  | 0113 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_CB | 4D56(23KV鹿56線) CB | FEEDER | D28/22/4D56/CB |  |  |  | DNP | 275 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57線(4D57) |  | PHA | [14 empty] | 0299 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_PHA | 23KV鹿57線(4D57) 相間RY | FEEDER | D28/22/4D57/PHA |  |  |  | DNP | 276 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57線(4D57) |  | GDA | [14 empty] | 0300 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_GDA | 23KV鹿57線(4D57) 接地RY | FEEDER | D28/22/4D57/GDA |  |  |  | DNP | 277 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57線(4D57) 79RY |  | 79UL | [14 empty] | 0660 |  | 0117 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_79UL | 23KV鹿57線(4D57) 79RY U/L | FEEDER | D28/22/4D57/79UL |  |  |  | DNP | 278 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D57_LCO | 鹿57線(4D57) LCO |  | TapPosMv | [14 empty] | 0661 |  | 0118 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_LCO_TAP | 23KV鹿57線(4D57) LCO TAP | FEEDER | D28/22/4D57/50_51NUL |  |  |  | DNP | 279 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D57 | 鹿57線 |  | CB | [14 empty] | 0298 |  | 0116 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_CB | 4D57(23KV鹿57線) CB | FEEDER | D28/22/4D57/CB |  |  |  | DNP | 280 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58線(4D58) |  | PHA | [14 empty] | 0302 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_PHA | 23KV鹿58線(4D58) 相間RY | FEEDER | D28/22/4D58/PHA |  |  |  | DNP | 281 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58線(4D58) |  | GDA | [14 empty] | 0303 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_GDA | 23KV鹿58線(4D58) 接地RY | FEEDER | D28/22/4D58/GDA |  |  |  | DNP | 282 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58線(4D58) 79RY |  | 79UL | [14 empty] | 0662 |  | 0120 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_79UL | 23KV鹿58線(4D58) 79RY U/L | FEEDER | D28/22/4D58/79UL |  |  |  | DNP | 283 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D58_LCO | 鹿58線(4D58) LCO |  | TapPosMv | [14 empty] | 0663 |  | 0121 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_LCO_TAP | 23KV鹿58線(4D58) LCO TAP | FEEDER | D28/22/4D58/50_51NUL |  |  |  | DNP | 284 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D58 | 鹿58線 |  | CB | [14 empty] | 0301 |  | 0119 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_CB | 4D58(23KV鹿58線) CB | FEEDER | D28/22/4D58/CB |  |  |  | DNP | 285 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61線(4D61) |  | PHA | [14 empty] | 0305 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_PHA | 23KV鹿61線(4D61) 相間RY | FEEDER | D28/22/4D61/PHA |  |  |  | DNP | 286 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61線(4D61) |  | GDA | [14 empty] | 0306 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_GDA | 23KV鹿61線(4D61) 接地RY | FEEDER | D28/22/4D61/GDA |  |  |  | DNP | 287 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61線(4D61) 79RY |  | 79UL | [14 empty] | 0664 |  | 0128 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_79UL | 23KV鹿61線(4D61) 79RY U/L | FEEDER | D28/22/4D61/79UL |  |  |  | DNP | 288 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D61_LCO | 鹿61線(4D61) LCO |  | TapPosMv | [14 empty] | 0665 |  | 0129 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_LCO_TAP | 23KV鹿61線(4D61) LCO TAP | FEEDER | D28/22/4D61/50_51NUL |  |  |  | DNP | 289 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D61 | 鹿61線 |  | CB | [14 empty] | 0304 |  | 0127 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_CB | 4D61(23KV鹿61線) CB | FEEDER | D28/22/4D61/CB |  |  |  | DNP | 290 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62線(4D62) |  | PHA | [14 empty] | 0308 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_PHA | 23KV鹿62線(4D62) 相間RY | FEEDER | D28/22/4D62/PHA |  |  |  | DNP | 291 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62線(4D62) |  | GDA | [14 empty] | 0309 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_GDA | 23KV鹿62線(4D62) 接地RY | FEEDER | D28/22/4D62/GDA |  |  |  | DNP | 292 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62線(4D62) 79RY |  | 79UL | [14 empty] | 0666 |  | 0131 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_79UL | 23KV鹿62線(4D62) 79RY U/L | FEEDER | D28/22/4D62/79UL |  |  |  | DNP | 293 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D62_LCO | 鹿62線(4D62) LCO |  | TapPosMv | [14 empty] | 0667 |  | 0132 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_LCO_TAP | 23KV鹿62線(4D62) LCO TAP | FEEDER | D28/22/4D62/50_51NUL |  |  |  | DNP | 294 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D62 | 鹿62線 |  | CB | [14 empty] | 0307 |  | 0130 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_CB | 4D62(23KV鹿62線) CB | FEEDER | D28/22/4D62/CB |  |  |  | DNP | 295 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63線(4D63) |  | PHA | [14 empty] | 0311 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_PHA | 23KV鹿63線(4D63) 相間RY | FEEDER | D28/22/4D63/PHA |  |  |  | DNP | 296 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63線(4D63) |  | GDA | [14 empty] | 0312 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_GDA | 23KV鹿63線(4D63) 接地RY | FEEDER | D28/22/4D63/GDA |  |  |  | DNP | 297 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63線(4D63) 79RY |  | 79UL | [14 empty] | 0668 |  | 0134 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_79UL | 23KV鹿63線(4D63) 79RY U/L | FEEDER | D28/22/4D63/79UL |  |  |  | DNP | 298 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D63_LCO | 鹿63線(4D63) LCO |  | TapPosMv | [14 empty] | 0669 |  | 0135 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_LCO_TAP | 23KV鹿63線(4D63) LCO TAP | FEEDER | D28/22/4D63/50_51NUL |  |  |  | DNP | 299 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D63 | 鹿63線 |  | CB | [14 empty] | 0310 |  | 0133 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_CB | 4D63(23KV鹿63線) CB | FEEDER | D28/22/4D63/CB |  |  |  | DNP | 300 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64線(4D64) |  | PHA | [14 empty] | 0314 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_PHA | 23KV鹿64線(4D64) 相間RY | FEEDER | D28/22/4D64/PHA |  |  |  | DNP | 301 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64線(4D64) |  | GDA | [14 empty] | 0315 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_GDA | 23KV鹿64線(4D64) 接地RY | FEEDER | D28/22/4D64/GDA |  |  |  | DNP | 302 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64線(4D64) 79RY |  | 79UL | [14 empty] | 0670 |  | 0137 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_79UL | 23KV鹿64線(4D64) 79RY U/L | FEEDER | D28/22/4D64/79UL |  |  |  | DNP | 303 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D64_LCO | 鹿64線(4D64) LCO |  | TapPosMv | [14 empty] | 0671 |  | 0138 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_LCO_TAP | 23KV鹿64線(4D64) LCO TAP | FEEDER | D28/22/4D64/50_51NUL |  |  |  | DNP | 304 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D64 | 鹿64線 |  | CB | [14 empty] | 0313 |  | 0136 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_CB | 4D64(23KV鹿64線) CB | FEEDER | D28/22/4D64/CB |  |  |  | DNP | 305 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65線(4D65) |  | PHA | [14 empty] | 0317 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_PHA | 23KV鹿65線(4D65) 相間RY | FEEDER | D28/22/4D65/PHA |  |  |  | DNP | 306 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65線(4D65) |  | GDA | [14 empty] | 0318 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_GDA | 23KV鹿65線(4D65) 接地RY | FEEDER | D28/22/4D65/GDA |  |  |  | DNP | 307 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65線(4D65) 79RY |  | 79UL | [14 empty] | 0672 |  | 0144 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_79UL | 23KV鹿65線(4D65) 79RY U/L | FEEDER | D28/22/4D65/79UL |  |  |  | DNP | 308 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D65_LCO | 鹿65線(4D65) LCO |  | TapPosMv | [14 empty] | 0673 |  | 0145 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_LCO_TAP | 23KV鹿65線(4D65) LCO TAP | FEEDER | D28/22/4D65/50_51NUL |  |  |  | DNP | 309 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D65 | 鹿65線 |  | CB | [14 empty] | 0316 |  | 0143 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_CB | 4D65(23KV鹿65線) CB | FEEDER | D28/22/4D65/CB |  |  |  | DNP | 310 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66線(4D66) |  | PHA | [14 empty] | 0320 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_PHA | 23KV鹿66線(4D66) 相間RY | FEEDER | D28/22/4D66/PHA |  |  |  | DNP | 311 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66線(4D66) |  | GDA | [14 empty] | 0321 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_GDA | 23KV鹿66線(4D66) 接地RY | FEEDER | D28/22/4D66/GDA |  |  |  | DNP | 312 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66線(4D66) 79RY |  | 79UL | [14 empty] | 0674 |  | 0147 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_79UL | 23KV鹿66線(4D66) 79RY U/L | FEEDER | D28/22/4D66/79UL |  |  |  | DNP | 313 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D66_LCO | 鹿66線(4D66) LCO |  | TapPosMv | [14 empty] | 0675 |  | 0148 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_LCO_TAP | 23KV鹿66線(4D66) LCO TAP | FEEDER | D28/22/4D66/50_51NUL |  |  |  | DNP | 314 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D66 | 鹿66線 |  | CB | [14 empty] | 0319 |  | 0146 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_CB | 4D66(23KV鹿66線) CB | FEEDER | D28/22/4D66/CB |  |  |  | DNP | 315 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67線(4D67) |  | PHA | [14 empty] | 0323 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_PHA | 23KV鹿67線(4D67) 相間RY | FEEDER | D28/22/4D67/PHA |  |  |  | DNP | 316 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67線(4D67) |  | GDA | [14 empty] | 0324 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_GDA | 23KV鹿67線(4D67) 接地RY | FEEDER | D28/22/4D67/GDA |  |  |  | DNP | 317 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67線(4D67) 79RY |  | 79UL | [14 empty] | 0676 |  | 0150 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_79UL | 23KV鹿67線(4D67) 79RY U/L | FEEDER | D28/22/4D67/79UL |  |  |  | DNP | 318 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D67_LCO | 鹿67線(4D67) LCO |  | TapPosMv | [14 empty] | 0677 |  | 0151 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_LCO_TAP | 23KV鹿67線(4D67) LCO TAP | FEEDER | D28/22/4D67/50_51NUL |  |  |  | DNP | 319 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D67 | 鹿67線 |  | CB | [14 empty] | 0322 |  | 0149 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_CB | 4D67(23KV鹿67線) CB | FEEDER | D28/22/4D67/CB |  |  |  | DNP | 320 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68線(4D68) |  | PHA | [14 empty] | 0326 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_PHA | 23KV鹿68線(4D68) 相間RY | FEEDER | D28/22/4D68/PHA |  |  |  | DNP | 321 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68線(4D68) |  | GDA | [14 empty] | 0327 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_GDA | 23KV鹿68線(4D68) 接地RY | FEEDER | D28/22/4D68/GDA |  |  |  | DNP | 322 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68線(4D68) 79RY |  | 79UL | [14 empty] | 0678 |  | 0153 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_79UL | 23KV鹿68線(4D68) 79RY U/L | FEEDER | D28/22/4D68/79UL |  |  |  | DNP | 323 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 4D68_LCO | 鹿68線(4D68) LCO |  | TapPosMv | [14 empty] | 0679 |  | 0154 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_LCO_TAP | 23KV鹿68線(4D68) LCO TAP | FEEDER | D28/22/4D68/50_51NUL |  |  |  | DNP | 324 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | LOCK
D28 | 鹿耳DS | 22 | 22kV | 4D68 | 鹿68線 |  | CB | [14 empty] | 0325 |  | 0152 | [8 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_CB | 4D68(23KV鹿68線) CB | FEEDER | D28/22/4D68/CB |  |  |  | DNP | 325 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 100 | TIE(100) |  | CB | [14 empty] | 0256 |  | 0105 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.100_CB | 100(TIE) CB | TIE | D28/22/100/CB |  |  |  | DNP | 326 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 100 | TIE(100) |  | 51A | [14 empty] | 0257 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.100_51A | 23KV TIE(100) 51RY | TIE | D28/22/100/PHA |  |  |  | DNP | 327 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 100 | TIE(100) |  | 51NA | [14 empty] | 0258 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.100_51NA | 23KV TIE(100) 51N RY | TIE | D28/22/100/GDA |  |  |  | DNP | 328 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [14 empty] | 0032 |  | 0033 | [8 empty] | 161KV_S | [8 empty] | 鹿耳DS.1500_CB | 1500(TIE) CB | TIE | D28/161/1500/CB |  |  |  | DNP | 329 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 1500 | TIE(1500) |  | 50A | [14 empty] | 0033 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.1500_50A | 161KV TIE(1500) 50RY | TIE | D28/161/1500/50A |  |  |  | DNP | 330 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [13 empty] | 0768 | 769 | 0034 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1501_DS | 1501(TIE) DS | TIE | D28/161/1500/DS1 |  |  |  | DNP | 331 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [13 empty] | 0770 | 771 | 0035 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1502_DS | 1502(TIE) DS | TIE | D28/161/1500/DS2 |  |  |  | DNP | 332 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 0 |  | 1500 | TIE(1500) |  | 50SA | [14 empty] | 0638 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.1500_50SA | 161KV TIE(1500) 50RY 測試/正常 | TIE | D28/161/1500/50SA |  |  |  | DNP | 333 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TEST/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 200 | TIE(200) |  | CB | [14 empty] | 0259 |  | 0155 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.200_CB | 200(TIE) CB | TIE | D28/22/200/CB |  |  |  | DNP | 334 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 200 | TIE(200) |  | 51A | [14 empty] | 0260 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.200_51A | 23KV TIE(200) 51RY | TIE | D28/22/200/PHA |  |  |  | DNP | 335 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 200 | TIE(200) |  | 51NA | [14 empty] | 0261 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.200_51NA | 23KV TIE(200) 51N RY | TIE | D28/22/200/GDA |  |  |  | DNP | 336 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 390 | #1SSTR(390) |  | CB | [14 empty] | 0274 |  | 0088 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.390_CB | 390(#1SSTR) CB | OTHER | D28/22/390/CB |  |  |  | DNP | 337 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 1SSTR | #1SSTR |  | 51A | [14 empty] | 0275 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1SSTR_51A | #1SSTR 51RY | OTHER | D28/22/390/PHA |  |  |  | DNP | 338 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1SSTR | #1SSTR |  | 51NA | [14 empty] | 0276 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1SSTR_51NA | #1SSTR 51N RY | OTHER | D28/22/390/GDA |  |  |  | DNP | 339 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 490 | #2SSTR(490) |  | CB | [14 empty] | 0277 |  | 0122 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.490_CB | 490(#2SSTR) CB | OTHER | D28/22/490/CB |  |  |  | DNP | 340 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 2SSTR | #2SSTR |  | 51A | [14 empty] | 0278 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2SSTR_51A | #2SSTR 51RY | OTHER | D28/22/490/PHA |  |  |  | DNP | 341 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2SSTR | #2SSTR |  | 51NA | [14 empty] | 0279 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2SSTR_51NA | #2SSTR 51N RY | OTHER | D28/22/490/GDA |  |  |  | DNP | 342 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [14 empty] | 0034 |  | 0076 | [8 empty] | 161KV_S | [8 empty] | 鹿耳DS.1750_CB | 1750(#1DTR) CB | MTR | D28/161/1750/CB |  |  |  | DNP | 343 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 310 | #1DTR(310) |  | CB | [14 empty] | 0060 |  | 0089 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.310_CB | 310(#1DTR) CB | MTR | D28/22/310/CB |  |  |  | DNP | 344 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 320 | #1DTR(320) |  | CB | [14 empty] | 0063 |  | 0106 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.320_CB | 320(#1DTR) CB | MTR | D28/22/320/CB |  |  |  | DNP | 345 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 51A | [14 empty] | 0038 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#1DTR_51A | #1DTR 51RY | MTR | D28//1DTR/PHA |  |  |  | DNP | 346 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 51NA | [14 empty] | 0039 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#1DTR_51NA | #1DTR 51N RY | MTR | D28//1DTR/GDA |  |  |  | DNP | 347 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 51ZA | [14 empty] | 0037 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#1DTR_51ZA | #1DTR 51Z RY | MTR | D28//1DTR/51ZA |  |  |  | DNP | 348 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 87A | [14 empty] | 0035 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#1DTR_87A | #1DTR 87RY | MTR | D28//1DTR/87A |  |  |  | DNP | 349 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 87UL | [14 empty] | 0582 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_87UL | #1DTR 87RY U/L | MTR | D28/161/1750/87UL |  |  |  | DNP | 350 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  | 310 | #1DTR(310) |  | 51A | [14 empty] | 0061 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.310_51A | #1DTR二次側(310) 51RY | MTR | D28/22/310/PHA |  |  |  | DNP | 351 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 320 | #1DTR(320) |  | 51A | [14 empty] | 0064 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.320_51A | #1DTR二次側(320) 51RY | MTR | D28/22/320/PHA |  |  |  | DNP | 352 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 96PA | [14 empty] | 0036 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | D28//1DTR/96PA |  |  |  | DNP | 353 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 96D | [14 empty] | 0525 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_96D | #1DTR 96D RY | MTR | D28//1DTR/96D |  |  |  | DNP | 354 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 96P | [14 empty] | 0532 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_96P | #1DTR 96P RY | MTR | D28//1DTR/96P |  |  |  | DNP | 355 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 63Q | [14 empty] | 0524 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_63Q | #1DTR 63Q RY | MTR | D28//1DTR/63Q |  |  |  | DNP | 356 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 96B1 | [14 empty] | 0526 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | D28//1DTR/96B1 |  |  |  | DNP | 357 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 96B2 | [14 empty] | 0527 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | D28//1DTR/96B2 |  |  |  | DNP | 358 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | TRA | [14 empty] | 0522 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_TRA | #1DTR 重故障 | MTR | D28//1DTR/TRA |  |  |  | DNP | 359 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | TRF | [14 empty] | 0523 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_TRF | #1DTR 輕故障 | MTR | D28//1DTR/TRF |  |  |  | DNP | 360 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | SupLocal | [14 empty] | 0530 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_S/L | #1DTR OLTC S/L | MTR | D28//1DTR/SupLocal |  |  |  | DNP | 361 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | A_M | [14 empty] | 0528 |  | 0001 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_A/M | #1DTR OLTC A/M | MTR | D28//1DTR/Tap Chan |  |  |  | DNP | 362 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [13 empty] | 0836 | 837 | 0077 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1751_DS | 1751(#1DTR) DS | MTR | D28/161/1750/DS1 |  |  |  | DNP | 363 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [13 empty] | 0838 | 839 | 0078 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1752_DS | 1752(#1DTR) DS | MTR | D28/161/1750/DS2 |  |  |  | DNP | 364 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [14 empty] | 0040 |  | 0079 | [8 empty] | 161KV_S | [8 empty] | 鹿耳DS.1760_CB | 1760(#2DTR) CB | MTR | D28/161/1760/CB |  |  |  | DNP | 365 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 330 | #2DTR(330) |  | CB | [14 empty] | 0066 |  | 0123 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.330_CB | 330(#2DTR) CB | MTR | D28/22/330/CB |  |  |  | DNP | 366 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 340 | #2DTR(340) |  | CB | [14 empty] | 0069 |  | 0139 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.340_CB | 340(#2DTR) CB | MTR | D28/22/340/CB |  |  |  | DNP | 367 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 51A | [14 empty] | 0044 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#2DTR_51A | #2DTR 51RY | MTR | D28//2DTR/PHA |  |  |  | DNP | 368 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 51NA | [14 empty] | 0045 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#2DTR_51NA | #2DTR 51N RY | MTR | D28//2DTR/GDA |  |  |  | DNP | 369 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 51ZA | [14 empty] | 0043 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#2DTR_51ZA | #2DTR 51Z RY | MTR | D28//2DTR/51ZA |  |  |  | DNP | 370 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 87A | [14 empty] | 0041 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#2DTR_87A | #2DTR 87RY | MTR | D28//2DTR/87A |  |  |  | DNP | 371 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 87UL | [14 empty] | 0583 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_87UL | #2DTR 87RY U/L | MTR | D28/161/1760/87UL |  |  |  | DNP | 372 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  | 330 | #2DTR(330) |  | 51A | [14 empty] | 0067 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.330_51A | #2DTR二次側(330) 51RY | MTR | D28/22/330/PHA |  |  |  | DNP | 373 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 340 | #2DTR(340) |  | 51A | [14 empty] | 0070 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.340_51A | #2DTR二次側(340) 51RY | MTR | D28/22/340/PHA |  |  |  | DNP | 374 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 96PA | [14 empty] | 0042 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | D28//2DTR/96PA |  |  |  | DNP | 375 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 96D | [14 empty] | 0536 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_96D | #2DTR 96D RY | MTR | D28//2DTR/96D |  |  |  | DNP | 376 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 96P | [14 empty] | 0543 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_96P | #2DTR 96P RY | MTR | D28//2DTR/96P |  |  |  | DNP | 377 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 63Q | [14 empty] | 0535 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_63Q | #2DTR 63Q RY | MTR | D28//2DTR/63Q |  |  |  | DNP | 378 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 96B1 | [14 empty] | 0537 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | D28//2DTR/96B1 |  |  |  | DNP | 379 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 96B2 | [14 empty] | 0538 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | D28//2DTR/96B2 |  |  |  | DNP | 380 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | TRA | [14 empty] | 0533 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_TRA | #2DTR 重故障 | MTR | D28//2DTR/TRA |  |  |  | DNP | 381 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | TRF | [14 empty] | 0534 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_TRF | #2DTR 輕故障 | MTR | D28//2DTR/TRF |  |  |  | DNP | 382 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | SupLocal | [14 empty] | 0541 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_S/L | #2DTR OLTC S/L | MTR | D28//2DTR/SupLocal |  |  |  | DNP | 383 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | A_M | [14 empty] | 0539 |  | 0005 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_A/M | #2DTR OLTC A/M | MTR | D28//2DTR/Tap Chan |  |  |  | DNP | 384 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | AUTO/MANUAL | AUTO
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [13 empty] | 0840 | 841 | 0080 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1761_DS | 1761(#2DTR) DS | MTR | D28/161/1760/DS1 |  |  |  | DNP | 385 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [13 empty] | 0842 | 843 | 0081 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1762_DS | 1762(#2DTR) DS | MTR | D28/161/1760/DS2 |  |  |  | DNP | 386 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | CB | [14 empty] | 0262 |  | 0090 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.210_CB | 210(23KV #1SC) CB | SC | D28/22/210/CB |  |  |  | DNP | 387 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | SCA | [14 empty] | 0263 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.210_SCA | 23KV #1SC 51,51N RY | SC | D28/22/210/SCA |  |  |  | DNP | 388 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 210 | #1SC(210) |  | UVA | [14 empty] | 0264 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.210_OUVA | 23KV #1SC 27,59RY(欠壓或過壓) | SC | D28/22/210/UVA |  |  |  | DNP | 389 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | CB | [14 empty] | 0265 |  | 0107 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.220_CB | 220(23KV #2SC) CB | SC | D28/22/220/CB |  |  |  | DNP | 390 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | SCA | [14 empty] | 0266 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.220_SCA | 23KV #2SC 51,51N RY | SC | D28/22/220/SCA |  |  |  | DNP | 391 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 220 | #2SC(220) |  | UVA | [14 empty] | 0267 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.220_OUVA | 23KV #2SC 27,59RY(欠壓或過壓) | SC | D28/22/220/UVA |  |  |  | DNP | 392 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | CB | [14 empty] | 0268 |  | 0124 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.230_CB | 230(23KV #3SC) CB | SC | D28/22/230/CB |  |  |  | DNP | 393 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [14 empty] | 0269 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.230_SCA | 23KV #3SC 51,51N RY | SC | D28/22/230/SCA |  |  |  | DNP | 394 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [14 empty] | 0270 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.230_OUVA | 23KV #3SC 27,59RY(欠壓或過壓) | SC | D28/22/230/UVA |  |  |  | DNP | 395 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | CB | [14 empty] | 0271 |  | 0140 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.240_CB | 240(23KV #4SC) CB | SC | D28/22/240/CB |  |  |  | DNP | 396 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | SCA | [14 empty] | 0272 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.240_SCA | 23KV #4SC 51,51N RY | SC | D28/22/240/SCA |  |  |  | DNP | 397 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 240 | #4SC(240) |  | UVA | [14 empty] | 0273 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.240_OUVA | 23KV #4SC 27,59RY(欠壓或過壓) | SC | D28/22/240/UVA |  |  |  | DNP | 398 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [14 empty] | 0616 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | D28/161/1BUS/BUS_VUA |  |  |  | DNP | 399 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [14 empty] | 0058 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | D28/161/1BUS/87A |  |  |  | DNP | 400 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [14 empty] | 0586 |  | 0163 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | D28/161/1BUS/87UL |  |  |  | DNP | 401 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [14 empty] | 0617 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | D28/161/2BUS/BUS_VUA |  |  |  | DNP | 402 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [14 empty] | 0059 | [10 empty] | 161KV_S | [8 empty] | 鹿耳DS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | D28/161/2BUS/87A |  |  |  | DNP | 403 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [14 empty] | 0587 |  | 0164 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | D28/161/2BUS/87UL |  |  |  | DNP | 404 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 22 | 22kV | 11_ | 11/ |  | CBA | [14 empty] | 0634 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | D28/22/ComPoint/CBA |  |  |  | DNP | 405 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 11_ | 11/ |  | CBF | [14 empty] | 0635 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | D28/22/ComPoint/CBF |  |  |  | DNP | 406 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV |  |  |  | CBA | [14 empty] | 0588 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_CBA | 161KV斷路器重故障 | OTHER | D28/161/ComPoint/CBA |  |  |  | DNP | 407 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV |  |  |  | CBF | [14 empty] | 0589 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_CBF | 161KV斷路器輕故障 | OTHER | D28/161/ComPoint/CBF |  |  |  | DNP | 408 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | LINE | LINE |  | RCA | [14 empty] | 0074 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | D28/161/ComPoint/RCA |  |  |  | DNP | 409 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | _SC | SC |  | 60A | [14 empty] | 0637 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.23KV_SC_60A | 23KV SC 60A | OTHER | D28/22/ComPoint/FDR_60A |  |  |  | DNP | 410 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | TEST | TEST |  | CB | [14 empty] | 0513 |  | 0000 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.TEST_CB | TEST CB | OTHER | D28/0/RTU/Test_CB |  |  |  | DNP | 411 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  |  |  |  | Fire1 | [14 empty] | 0604 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.火災警報(1) | 火災警報(1)受信總機 | OTHER | D28/0/StaDev/Fire1 |  |  |  | DNP | 412 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | Fire2 | [14 empty] | 0689 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.火災警報(2) | 火災警報(2)建物-電纜涵洞 | OTHER | D28/0/StaDev/Fire2 |  |  |  | DNP | 413 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 25TA | [14 empty] | 0631 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | D28/161/ComPoint/25TA |  |  |  | DNP | 414 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | ACB1 | [14 empty] | 0625 |  | 0160 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | D28/0/StaDev/ACB1 |  |  |  | DNP | 415 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ON/OFF | ON
D28 | 鹿耳DS | 0 |  |  |  |  | ACB2 | [14 empty] | 0626 |  | 0161 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | D28/0/StaDev/ACB2 |  |  |  | DNP | 416 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ON/OFF | ON
D28 | 鹿耳DS | 0 |  |  |  |  | ACBA | [14 empty] | 0628 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.所內電源ACBA | 所內電源故障警報 | OTHER | D28/0/StaDev/ACBA |  |  |  | DNP | 417 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [14 empty] | 0627 |  | 0162 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | D28/0/StaDev/ACBT |  |  |  | DNP | 418 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ON/OFF | OFF
D28 | 鹿耳DS | 0 |  |  |  |  | STUV | [14 empty] | 0606 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | D28/0/StaDev/STUV |  |  |  | DNP | 419 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | CHG1 | [14 empty] | 0598 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.直流充電機故障 | 直流充電機故障 | OTHER | D28/0/StaDev/CHG1 |  |  |  | DNP | 420 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | DCA | [14 empty] | 0601 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.直流電源DCA | 直流電源故障警報 | OTHER | D28/0/StaDev/DCA |  |  |  | DNP | 421 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | DCE | [14 empty] | 0600 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.直流電源DCE | 直流電源接地故障警報 | OTHER | D28/0/StaDev/DCE |  |  |  | DNP | 422 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | CHG2 | [14 empty] | 0599 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | D28/0/StaDev/CHG2 |  |  |  | DNP | 423 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | CommACF | [14 empty] | 0612 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | D28/0/StaDev/CommACF |  |  |  | DNP | 424 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | Burglar1 | [14 empty] | 0607 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | D28/0/StaDev/Burglar |  |  |  | DNP | 425 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | Door1 | [14 empty] | 0602 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.無人化門禁(1) | 無人化門禁(1)圍牆大小門 | OTHER | D28/0/StaDev/Door1 |  |  |  | DNP | 426 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  |  |  |  | Door2 | [14 empty] | 0603 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.無人化門禁(2) | 無人化門禁(2)建築物門禁 | OTHER | D28/0/StaDev/Door2 |  |  |  | DNP | 427 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  |  |  |  | Lights1 | [14 empty] | 0608 |  | 0156 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.開關場照明(A) | 景觀照明 | OTHER | D28/0/StaDev/Lights1 |  |  |  | DNP | 428 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ON/OFF | OFF
D28 | 鹿耳DS | 0 |  |  |  |  | Lights2 | [14 empty] | 0609 |  | 0157 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.開關場照明(B) | 路燈照明 | OTHER | D28/0/StaDev/Lights2 |  |  |  | DNP | 429 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ON/OFF | OFF
D28 | 鹿耳DS | 22 | 22kV | 11_ | 11/ |  | LOA | [14 empty] | 0075 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.11/23KV_LOA | 23KV饋線復閉失敗閉鎖 | OTHER | D28/22/ComPoint/LOA |  |  |  | DNP | 430 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1510 | 南濱鹿耳紅線(1510) |  | 87CFA | [14 empty] | 0590 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510_87CFA | 南濱鹿耳紅線(1510)87RY通訊故障 | OTHER | D28/161/1510/87CFA |  |  |  | DNP | 431 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1510 | 南濱鹿耳紅線(1510) |  | RYFA | [14 empty] | 0514 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510_RYFA | 南濱鹿耳紅線(1510)數位電驛故障 | OTHER | D28/161/1510/RYFA |  |  |  | DNP | 432 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1520 | 南濱鹿耳白線(1520) |  | 87CFA | [14 empty] | 0591 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520_87CFA | 南濱鹿耳白線(1520)87RY通訊故障 | OTHER | D28/161/1520/87CFA |  |  |  | DNP | 433 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1520 | 南濱鹿耳白線(1520) |  | RYFA | [14 empty] | 0515 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520_RYFA | 南濱鹿耳白線(1520)數位電驛故障 | OTHER | D28/161/1520/RYFA |  |  |  | DNP | 434 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV |  |  |  | OSCA | [14 empty] | 0072 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | D28/161/ComPoint/OSCA |  |  |  | DNP | 435 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 310 | #1DTR(310) |  | GDA | [14 empty] | 0062 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.310_GDA | 310開關箱IED RY GDA | OTHER | D28/22/310/GDA |  |  |  | DNP | 436 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 320 | #1DTR(320) |  | GDA | [14 empty] | 0065 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.320_GDA | 320開關箱IED RY GDA | OTHER | D28/22/320/GDA |  |  |  | DNP | 437 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 330 | #2DTR(330) |  | GDA | [14 empty] | 0068 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.330_GDA | 330開關箱IED RY GDA | OTHER | D28/22/330/GDA |  |  |  | DNP | 438 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 340 | #2DTR(340) |  | GDA | [14 empty] | 0071 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.340_GDA | 340開關箱IED RY GDA | OTHER | D28/22/340/GDA |  |  |  | DNP | 439 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | COMM | COMM |  | SupLocal | [14 empty] | 0512 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.COMM_S/L | IED控制權 | OTHER | D28/0/StaDev/Comm_R_L |  |  |  | DNP | 440 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
D28 | 鹿耳DS | 0 |  |  |  |  | FiberA | [14 empty] | 0644 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.FIBERA | SCADA光纖故障 | OTHER | D28/0/StaDev/FiberA |  |  |  | DNP | 441 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | LOCAL | LOCAL |  | GPSA | [14 empty] | 0636 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.GPSA | LOCAL GPS故障 | OTHER | D28/0/StaDev/GPSA |  |  |  | DNP | 442 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | MCCA | [14 empty] | 0639 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.MCCA | MCC電驛故障 | OTHER | D28/0/StaDev/MCC |  |  |  | DNP | 443 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | PASBA | [14 empty] | 0643 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.PASBA | 前端處理器B(PASB)故障 | OTHER |  |  |  |  | DNP | 444 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | PASGTWAA | [14 empty] | 0646 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.PASGTWAA | 通訊處理單元A(GATEWAYA)故障 | OTHER | D28/0/StaDev/Gateway1 |  |  |  | DNP | 445 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | PASGTWBA | [14 empty] | 0647 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.PASGTWBA | 通訊處理單元B(GATEWAYB)故障 | OTHER | D28/0/StaDev/Gateway2 |  |  |  | DNP | 446 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | PMCCA | [14 empty] | 0640 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.PMCCA | PMCC電驛故障 | OTHER | D28/0/StaDev/PMCC |  |  |  | DNP | 447 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | SCADA | SCADA |  | UPS | [14 empty] | 0633 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.SCADA_UPS | SCADA UPS故障 | OTHER | D28/0/StaDev/UPSA |  |  |  | DNP | 448 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | SWITCHA | [14 empty] | 0645 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.SWITCHA | 光纖網路交換機故障 | OTHER | D28/0/StaDev/FiberA |  |  |  | DNP | 449 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | TCA | [14 empty] | 0641 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.TCA | 斷路器跳脫回路故障 | OTHER | D28/0/StaDev/TCA |  |  |  | DNP | 450 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 水位警報(1) | [14 empty] | 0621 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.水位警報(1) | 地下室第一區第一段水位警報 | OTHER | D28/0/StaDev/Water1 |  |  |  | DNP | 451 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 水位警報(2) | [14 empty] | 0622 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.水位警報(2) | 地下室第一區第二段水位警報 | OTHER | D28/0/StaDev/Water2 |  |  |  | DNP | 452 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 水位警報(3) | [14 empty] | 0623 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.水位警報(3) | 地下室第二區第一段水位警報 | OTHER | D28/0/StaDev/Water3 |  |  |  | DNP | 453 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 水位警報(4) | [14 empty] | 0624 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.水位警報(4) | 地下室第二區第二段水位警報 | OTHER | D28/0/StaDev/Water4 |  |  |  | DNP | 454 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 抽水泵警報 | [14 empty] | 0618 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.抽水泵警報 | 集油池抽水泵故障警報 | OTHER | D28/0/StaDev/OilLeak1 |  |  |  | DNP | 455 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 通信機房溫度 | [14 empty] | 0615 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.通信機房溫度 | 通訊室或控制室溫度警報 | OTHER | D28/0/StaDev/R_Temp1 |  |  |  | DNP | 456 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 集油池警報(1) | [14 empty] | 0619 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.集油池警報(1) | 集油池第一段水位警報 | OTHER | D28/0/StaDev/OilLeak2 |  |  |  | DNP | 457 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 集油池警報(2) | [14 empty] | 0620 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.集油池警報(2) | 集油池第二段水位警報 | OTHER | D28/0/StaDev/OilLeak3 |  |  |  | DNP | 458 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV |  |  |  | OSCF | [14 empty] | 0610 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_OSCF | 161KV示波器故障 | OTHER | D28/161/ComPoint/OSCF |  |  |  | DNP | 459 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | SCADA | SCADA | [16 empty] | 0629 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.SCADA_A | SCADA A故障 | OTHER | D28/0/StaDev/SCADAA |  |  |  | DNP | 460 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | SCADA | SCADA |  | B | [14 empty] | 0630 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.SCADA_B | SCADA B故障 | OTHER | D28/0/StaDev/5A5Other |  |  |  | DNP | 461 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV |  |  |  | RCA | [14 empty] | 0076 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.23KV_RCA | 23KV 79RY(復閉)動作 | OTHER | D28/22/ComPoint/RCA |  |  |  | DNP | 462 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 310 | #1DTR(310) |  | 81A | [14 empty] | 0328 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.310_81A | 310 #1DTR(A) 81RY動作 | OTHER | D28/22/310/81A |  |  |  | DNP | 463 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 310 | #1DTR(310) |  | 81UL | [14 empty] | 0680 |  | 0091 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.310_81UL | 310 #1DTR(A) 81RY U/L | OTHER | D28/22/310/81UL |  |  |  | DNP | 464 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  | 320 | #1DTR(320) |  | 81A | [14 empty] | 0329 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.320_81A | 320 #1DTR(B) 81RY動作 | OTHER | D28/22/320/81A |  |  |  | DNP | 465 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 320 | #1DTR(320) |  | 81UL | [14 empty] | 0681 |  | 0108 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.320_81UL | 320 #1DTR(B) 81RY U/L | OTHER | D28/22/320/81UL |  |  |  | DNP | 466 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  | 330 | #2DTR(330) |  | 81A | [14 empty] | 0330 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.330_81A | 330 #2DTR(A) 81RY動作 | OTHER | D28/22/330/81A |  |  |  | DNP | 467 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 330 | #2DTR(330) |  | 81UL | [14 empty] | 0682 |  | 0125 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.330_81UL | 330 #2DTR(A) 81RY U/L | OTHER | D28/22/330/81UL |  |  |  | DNP | 468 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  | 340 | #2DTR(340) |  | 81A | [14 empty] | 0331 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.340_81A | 340 #2DTR(B) 81RY動作 | OTHER | D28/22/340/81A |  |  |  | DNP | 469 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 340 | #2DTR(340) |  | 81UL | [14 empty] | 0683 |  | 0141 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.340_81UL | 340 #2DTR(B) 81RY U/L | OTHER | D28/22/340/81UL |  |  |  | DNP | 470 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 0 |  |  |  |  | 涵洞水位(2) | [14 empty] | 0686 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.涵洞水位(2) | 電纜涵洞第二段水位警報 | OTHER | D28/0/StaDev/Water |  |  |  | DNP | 471 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 涵洞泵浦 | [14 empty] | 0684 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.涵洞泵浦 | 電纜涵洞泵浦故障 | OTHER | D28/0/StaDev/3A5Other |  |  |  | DNP | 472 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | 涵洞風機故障 | [14 empty] | 0688 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.涵洞風機故障 | 電纜涵洞風機故障 | OTHER | D28/0/StaDev/AIRCON |  |  |  | DNP | 473 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [14 empty] | 0690 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | D28/161/ComPoint/12B_CTFA |  |  |  | DNP | 474 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | _BUS | BUS |  | RYFA | [14 empty] | 0691 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | D28/161/ComPoint/BUS_RYFA |  |  |  | DNP | 475 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 51RYFA | [14 empty] | 0693 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_51RYFA | #1DTR 51RY數位電驛故障 | OTHER | D28//1DTR/1A5Other |  |  |  | DNP | 476 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 51ZRYFA | [14 empty] | 0694 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_51ZRYFA | #1DTR 51Z RY數位電驛故障 | OTHER | D28//1DTR/RYFA |  |  |  | DNP | 477 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1DTR | #1DTR |  | 87RYFA | [14 empty] | 0692 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1DTR_87RYFA | #1DTR 87RY數位電驛故障 | OTHER | D28//1DTR/3A5Other |  |  |  | DNP | 478 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 51RYFA | [14 empty] | 0696 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_51RYFA | #2DTR 51RY數位電驛故障 | OTHER | D28//2DTR/1A5Other |  |  |  | DNP | 479 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 51ZRYFA | [14 empty] | 0697 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_51ZRYFA | #2DTR 51Z RY數位電驛故障 | OTHER | D28//2DTR/RYFA |  |  |  | DNP | 480 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 2DTR | #2DTR |  | 87RYFA | [14 empty] | 0695 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#2DTR_87RYFA | #2DTR 87RY數位電驛故障 | OTHER | D28//2DTR/3A5Other |  |  |  | DNP | 481 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | Fire3 | [14 empty] | 0605 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.火災警報(3) | 火災警報(3) | OTHER | D28/0/ComPoint/Fire3 |  |  |  | DNP | 482 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  |  |  |  | GEN | [14 empty] | 0687 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.GEN | 緊急發電機運轉 | OTHER | D28/0/StaDev/4A5Other |  |  |  | DNP | 483 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ON/OFF | OFF
D28 | 鹿耳DS | 0 |  | OLTC | OLTC |  | OLTCA | [14 empty] | 0611 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.OLTCA | OLTC 15分鐘連動3次 | OTHER | D28/0/ComPoint/OLTC_A |  |  |  | DNP | 484 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | CFI | CFI(永勁電廠) |  | CB | [14 empty] | 0332 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.CFI_CB | CFI(永勁電廠) MVCB | OTHER |  |  |  |  | DNP | 485 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | CFI | CFI(永勁電廠) |  | DS1 | CFI | [13 empty] | 0333 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.CFI_DS | CFI(永勁電廠) DS | OTHER |  |  |  |  | DNP | 486 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | CFI_GPT | CFI(永勁電廠) |  | DS1 | CFI_GPT | [13 empty] | 0334 | [10 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.CFI_GPT_DS | CFI(永勁電廠) GPT DS | OTHER |  |  |  |  | DNP | 487 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  |  |  |  | IED盤內溫度 | [14 empty] | 0642 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.IED盤內溫度 | IED盤內溫控警報 | OTHER | D28/0/StaDev/R_Temp |  |  |  | DNP | 488 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | 87A | [14 empty] | 0078 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | D28/161/1SHR/87A |  |  |  | DNP | 489 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | 87UL | [14 empty] | 0698 |  | 0168 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_87UL | 161KV #1SHR 87RY U/L | OTHER | D28/161/1SHR/87UL |  |  |  | DNP | 490 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | USE/LOCK | USE
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B1 | [14 empty] | 0701 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | D28/161/1SHR/96B1 |  |  |  | DNP | 491 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | 96B2 | [14 empty] | 0702 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | D28/161/1SHR/96B2 |  |  |  | DNP | 492 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | 96D | [14 empty] | 0703 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | D28/161/1SHR/96D |  |  |  | DNP | 493 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | 96P | [14 empty] | 0704 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | D28/161/1SHR/96P |  |  |  | DNP | 494 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1611SHR | #1SHR |  | GDA | [14 empty] | 0081 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_GDA | 1950(#1SHR) GDA | OTHER | D28/161/1950/GDA |  |  |  | DNP | 495 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 0 |  | 1611SHR | #1SHR |  | PHA | [14 empty] | 0080 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_PHA | 1950(#1SHR) PHA | OTHER | D28/161/1950/PHA |  |  |  | DNP | 496 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | SHRA | [14 empty] | 0700 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | D28/161/1SHR/SHRA |  |  |  | DNP | 497 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1611SHR | #1SHR |  | SRF | [14 empty] | 0699 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | D28/161/1SHR/SHRF |  |  |  | DNP | 498 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 161_1SHR | 161_1SHR |  | RYFA | [14 empty] | 0705 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | D28/161/1950/RYFA |  |  |  | DNP | 499 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB | [14 empty] | 0077 |  | 0165 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1950_CB | 1950(161KV #1SHR) CB | OTHER | D28/161/1950/CB |  |  |  | DNP | 500 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS1 | 1951 | [13 empty] | 0852 | 853 | 0166 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1951_DS | 1951(161KV #1SHR) DS | OTHER | D28/161/1950/DS1 |  |  |  | DNP | 501 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1950 | #1SHR(1950) |  | DS2 | 1952 | [13 empty] | 0854 | 855 | 0167 | [8 empty] | ADCS_S | [8 empty] | 鹿耳DS.1952_DS | 1952(161KV #1SHR) DS | OTHER | D28/161/1950/DS2 |  |  |  | DNP | 502 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
D28 | 鹿耳DS | 0 |  | 1SHR | #1SHR |  | 96PA | [14 empty] | 0079 | [10 empty] | ADCS_S | [8 empty] | 鹿耳DS.#1SHR_96PA | #1SHR 機械保護動作 | OTHER | D28/161/1SHR/96PA |  |  |  | DNP | 503 | DNPDIPoint | DS048 |  |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
D28 | 鹿耳DS | 22 | 22kV | 210_SC | #1SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.210_SC_CAP | 23KV#1SC 容量 | SC | [5 empty] | 504 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 220_SC | #2SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.220_SC_CAP | 23KV#2SC 容量 | SC | [5 empty] | 505 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 506 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 鹿耳DS.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 507 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510LE | 1510LE (非取樣點) | LINE161 | D28/161/1510/LE0 |  |  |  |  | 508 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1510 | 南濱鹿耳紅線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1510BE | 1510BE (非取樣點) | LINE161 | D28/161/1510/BE0 |  |  |  |  | 509 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520LE | 1520LE (非取樣點) | LINE161 | D28/161/1520/LE0 |  |  |  |  | 510 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1520 | 南濱鹿耳白線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1520BE | 1520BE (非取樣點) | LINE161 | D28/161/1520/BE0 |  |  |  |  | 511 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D51 | 4D51_DS |  | DS1 | 4D51_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_DS | 4D51_DS (非取樣點) | FEEDER | D28/22/4D51/DS |  |  |  |  | 512 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D51 | 4D51_ES |  | D510 | 4D51_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D51_ES | 4D51_ES (非取樣點) | FEEDER | D28/22/4D51/ES |  |  |  |  | 513 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D52 | 4D52_DS |  | DS1 | 4D52_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_DS | 4D52_DS (非取樣點) | FEEDER | D28/22/4D52/DS |  |  |  |  | 514 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D52 | 4D52_ES |  | D520 | 4D52_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D52_ES | 4D52_ES (非取樣點) | FEEDER | D28/22/4D52/ES |  |  |  |  | 515 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D53 | 4D53_DS |  | DS1 | 4D53_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_DS | 4D53_DS (非取樣點) | FEEDER | D28/22/4D53/DS |  |  |  |  | 516 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D53 | 4D53_ES |  | D530 | 4D53_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D53_ES | 4D53_ES (非取樣點) | FEEDER | D28/22/4D53/ES |  |  |  |  | 517 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D54 | 4D54_DS |  | DS1 | 4D54_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_DS | 4D54_DS (非取樣點) | FEEDER | D28/22/4D54/DS |  |  |  |  | 518 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D54 | 4D54_ES |  | D540 | 4D54_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D54_ES | 4D54_ES (非取樣點) | FEEDER | D28/22/4D54/ES |  |  |  |  | 519 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D55 | 4D55_DS |  | DS1 | 4D55_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_DS | 4D55_DS (非取樣點) | FEEDER | D28/22/4D55/DS |  |  |  |  | 520 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D55 | 4D55_ES |  | D550 | 4D55_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D55_ES | 4D55_ES (非取樣點) | FEEDER | D28/22/4D55/ES |  |  |  |  | 521 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D56 | 4D56_DS |  | DS1 | 4D56_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_DS | 4D56_DS (非取樣點) | FEEDER | D28/22/4D56/DS |  |  |  |  | 522 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D56 | 4D56_ES |  | D560 | 4D56_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D56_ES | 4D56_ES (非取樣點) | FEEDER | D28/22/4D56/ES |  |  |  |  | 523 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D57 | 4D57_DS |  | DS1 | 4D57_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_DS | 4D57_DS (非取樣點) | FEEDER | D28/22/4D57/DS |  |  |  |  | 524 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D57 | 4D57_ES |  | D570 | 4D57_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D57_ES | 4D57_ES (非取樣點) | FEEDER | D28/22/4D57/ES |  |  |  |  | 525 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D58 | 4D58_DS |  | DS1 | 4D58_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_DS | 4D58_DS (非取樣點) | FEEDER | D28/22/4D58/DS |  |  |  |  | 526 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D58 | 4D58_ES |  | D580 | 4D58_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D58_ES | 4D58_ES (非取樣點) | FEEDER | D28/22/4D58/ES |  |  |  |  | 527 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D61 | 4D61_DS |  | DS1 | 4D61_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_DS | 4D61_DS (非取樣點) | FEEDER | D28/22/4D61/DS |  |  |  |  | 528 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D61 | 4D61_ES |  | D610 | 4D61_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D61_ES | 4D61_ES (非取樣點) | FEEDER | D28/22/4D61/ES |  |  |  |  | 529 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D62 | 4D62_DS |  | DS1 | 4D62_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_DS | 4D62_DS (非取樣點) | FEEDER | D28/22/4D62/DS |  |  |  |  | 530 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D62 | 4D62_ES |  | D620 | 4D62_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D62_ES | 4D62_ES (非取樣點) | FEEDER | D28/22/4D62/ES |  |  |  |  | 531 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D63 | 4D63_DS |  | DS1 | 4D63_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_DS | 4D63_DS (非取樣點) | FEEDER | D28/22/4D63/DS |  |  |  |  | 532 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D63 | 4D63_ES |  | D630 | 4D63_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D63_ES | 4D63_ES (非取樣點) | FEEDER | D28/22/4D63/ES |  |  |  |  | 533 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D64 | 4D64_DS |  | DS1 | 4D64_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_DS | 4D64_DS (非取樣點) | FEEDER | D28/22/4D64/DS |  |  |  |  | 534 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D64 | 4D64_ES |  | D640 | 4D64_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D64_ES | 4D64_ES (非取樣點) | FEEDER | D28/22/4D64/ES |  |  |  |  | 535 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D65 | 4D65_DS |  | DS1 | 4D65_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_DS | 4D65_DS (非取樣點) | FEEDER | D28/22/4D65/DS |  |  |  |  | 536 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D65 | 4D65_ES |  | D650 | 4D65_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D65_ES | 4D65_ES (非取樣點) | FEEDER | D28/22/4D65/ES |  |  |  |  | 537 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D66 | 4D66_DS |  | DS1 | 4D66_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_DS | 4D66_DS (非取樣點) | FEEDER | D28/22/4D66/DS |  |  |  |  | 538 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D66 | 4D66_ES |  | D660 | 4D66_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D66_ES | 4D66_ES (非取樣點) | FEEDER | D28/22/4D66/ES |  |  |  |  | 539 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D67 | 4D67_DS |  | DS1 | 4D67_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_DS | 4D67_DS (非取樣點) | FEEDER | D28/22/4D67/DS |  |  |  |  | 540 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D67 | 4D67_ES |  | D670 | 4D67_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D67_ES | 4D67_ES (非取樣點) | FEEDER | D28/22/4D67/ES |  |  |  |  | 541 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 4D68 | 4D68_DS |  | DS1 | 4D68_DS | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_DS | 4D68_DS (非取樣點) | FEEDER | D28/22/4D68/DS |  |  |  |  | 542 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 4D68 | 4D68_ES |  | D680 | 4D68_ES | [24 empty] | DDCS4_1 | [8 empty] | 鹿耳DS.4D68_ES | 4D68_ES (非取樣點) | FEEDER | D28/22/4D68/ES |  |  |  |  | 543 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 100 | TIE(100) |  | E1 | 101E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.101E | 101E (非取樣點) | TIE | D28/22/100/E1 |  |  |  |  | 544 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 100 | TIE(100) |  | E2 | 102E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.102E | 102E (非取樣點) | TIE | D28/22/100/E2 |  |  |  |  | 545 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.101 | 101 (非取樣點) | TIE | D28/22/100/D1 |  |  |  |  | 546 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 102 | 102 |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.102 | 102 (非取樣點) | TIE | D28/22/100/D2 |  |  |  |  | 547 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1501E | 1501E (非取樣點) | TIE | D28/161/1500/E1 |  |  |  |  | 548 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1502E | 1502E (非取樣點) | TIE | D28/161/1500/E2 |  |  |  |  | 549 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 200 | TIE(200) |  | E1 | 201E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.201E | 201E (非取樣點) | TIE | D28/22/200/E1 |  |  |  |  | 550 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 200 | TIE(200) |  | E2 | 202E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.202E | 202E (非取樣點) | TIE | D28/22/200/E2 |  |  |  |  | 551 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.201 | 201 (非取樣點) | TIE | D28/22/200/D1 |  |  |  |  | 552 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 202 | 202 |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.202 | 202 (非取樣點) | TIE | D28/22/200/D2 |  |  |  |  | 553 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.391 | 391 (非取樣點) | OTHER | D28/22/390/D1 |  |  |  |  | 554 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.391E | 391E (非取樣點) | OTHER | D28/22/390/E1 |  |  |  |  | 555 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.491 | 491 (非取樣點) | OTHER | D28/22/490/D1 |  |  |  |  | 556 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.491E | 491E (非取樣點) | OTHER | D28/22/490/E1 |  |  |  |  | 557 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1750TE | 1750TE (非取樣點) | MTR | D28/161/1750/TE0 |  |  |  |  | 558 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1750BE | 1750BE (非取樣點) | MTR | D28/161/1750/BE0 |  |  |  |  | 559 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.311 | 311 (非取樣點) | MTR | D28/22/310/D1 |  |  |  |  | 560 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 310 | #1DTR(310) |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.311E | 311E (非取樣點) | MTR | D28/22/310/E1 |  |  |  |  | 561 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.321 | 321 (非取樣點) | MTR | D28/22/320/D1 |  |  |  |  | 562 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 320 | #1DTR(320) |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.321E | 321E (非取樣點) | MTR | D28/22/320/E1 |  |  |  |  | 563 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1760TE | 1760TE (非取樣點) | MTR | D28/161/1760/TE0 |  |  |  |  | 564 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1760BE | 1760BE (非取樣點) | MTR | D28/161/1760/BE0 |  |  |  |  | 565 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.331 | 331 (非取樣點) | MTR | D28/22/330/D1 |  |  |  |  | 566 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 330 | #2DTR(330) |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.331E | 331E (非取樣點) | MTR | D28/22/330/E1 |  |  |  |  | 567 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.341 | 341 (非取樣點) | MTR | D28/22/340/D1 |  |  |  |  | 568 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 340 | #2DTR(340) |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.341E | 341E (非取樣點) | MTR | D28/22/340/E1 |  |  |  |  | 569 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.211E | 211E (非取樣點) | SC | D28/22/210/E1 |  |  |  |  | 570 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.211 | 211 (非取樣點) | SC | D28/22/210/D1 |  |  |  |  | 571 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.221E | 221E (非取樣點) | SC | D28/22/220/E1 |  |  |  |  | 572 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.221 | 221 (非取樣點) | SC | D28/22/220/D1 |  |  |  |  | 573 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.231E | 231E (非取樣點) | SC | D28/22/230/E1 |  |  |  |  | 574 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.231 | 231 (非取樣點) | SC | D28/22/230/D1 |  |  |  |  | 575 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.241E | 241E (非取樣點) | SC | D28/22/240/E1 |  |  |  |  | 576 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.241 | 241 (非取樣點) | SC | D28/22/240/D1 |  |  |  |  | 577 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 15B1E | 15B1E |  | BE1 | 15B1E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.15B1E | 15B1E (非取樣點) | BUS | D28/161/161B1E/BE1 |  |  |  |  | 578 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 15B2E | 15B2E |  | BE2 | 15B2E | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.15B2E | 15B2E (非取樣點) | BUS | D28/161/161B2E/BE2 |  |  |  |  | 579 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 580 | NotelDIPoint | [38 empty] | START/STOP | STOP
D28 | 鹿耳DS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 581 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 1ABUS | 1ABUS |  | PTE | 1ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1ABUS_PTE | #1ABUS_PTE(非取樣點) | OTHER | [5 empty] | 582 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 583 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 1BBUS | 1BBUS |  | PTE | 1BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1BBUS_PTE | #1BBUS_PTE(非取樣點) | OTHER | [5 empty] | 584 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 585 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 2ABUS | 2ABUS |  | PTE | 2ABUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.2ABUS_PTE | #2ABUS_PTE(非取樣點) | OTHER | [5 empty] | 586 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 587 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
D28 | 鹿耳DS | 0 |  | 2BBUS | 2BBUS |  | PTE | 2BBUS_PTE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.2BBUS_PTE | #2BBUS_PTE(非取樣點) | OTHER | [5 empty] | 588 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  |  |  |  | 1950BE | 1950BE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1950BE | 1950BE(非取樣點) | OTHER | [5 empty] | 589 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
D28 | 鹿耳DS | 0 |  |  |  |  | 1950RE | 1950RE | [24 empty] | ADCS_S | [8 empty] | 鹿耳DS.1950RE | 1950RE(非取樣點) | OTHER | [5 empty] | 590 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo