## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
D29 | 府城DS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 | [10 empty] | B3/D29_A1 | [16 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 | [10 empty] | B3/D29_A1 | [16 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 | [10 empty] | B3/D29_A1 | [16 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 | [10 empty] | B3/D29_A1 | [16 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 | [9 empty] | aaa | B2/D29_A1 | [16 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 | [9 empty] | aab | B2/D29_A1 | [16 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0135 | [9 empty] | ada | B3/D29_A1 | [16 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0101 | [9 empty] | aaa | B3/D29_A1 | [16 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0166 | [9 empty] | aba | B3/D29_A1 | [16 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0197 | [9 empty] | aca | B3/D29_A1 | [16 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 | [10 empty] | B2/D29_A1 | [16 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 | [10 empty] | B2/D29_A1 | [16 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線 (1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 | [10 empty] | B2/D29_A1 | [16 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線 (1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 | [10 empty] | B2/D29_A1 | [16 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0136 | [10 empty] | B2/D29_D1 | [16 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0137 | [10 empty] | B2/D29_D1 | [16 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0138 | [10 empty] | B2/D29_D1 | [16 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0139 | [10 empty] | B2/D29_D1 | [16 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0140 | [10 empty] | B2/D29_D1 | [16 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0141 | [10 empty] | B2/D29_D1 | [16 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0142 | [10 empty] | B2/D29_D1 | [16 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0143 | [10 empty] | B2/D29_D1 | [16 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0144 | [10 empty] | B2/D29_D1 | [16 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0145 | [10 empty] | B2/D29_D1 | [16 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0146 | [10 empty] | B2/D29_D1 | [16 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0147 | [10 empty] | B2/D29_D1 | [16 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0148 | [10 empty] | B2/D29_D1 | [16 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0149 | [10 empty] | B2/D29_D1 | [16 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0150 | [10 empty] | B2/D29_D1 | [16 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0151 | [10 empty] | B2/D29_D1 | [16 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 | [10 empty] | B2/D29_D1 | [16 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 | [10 empty] | B2/D29_D1 | [16 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 | [10 empty] | B2/D29_D1 | [16 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0155 | [10 empty] | B2/D29_D1 | [16 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0156 | [10 empty] | B2/D29_D1 | [16 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0157 | [10 empty] | B2/D29_D1 | [16 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0158 | [10 empty] | B2/D29_D1 | [16 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0159 | [10 empty] | B2/D29_D1 | [16 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0160 | [10 empty] | B2/D29_D1 | [16 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0102 | [10 empty] | B2/D29_D1 | [16 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0103 | [10 empty] | B2/D29_D1 | [16 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0104 | [10 empty] | B2/D29_D1 | [16 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0105 | [10 empty] | B2/D29_D1 | [16 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0106 | [10 empty] | B2/D29_D1 | [16 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0107 | [10 empty] | B2/D29_D1 | [16 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0108 | [10 empty] | B2/D29_D1 | [16 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0109 | [10 empty] | B2/D29_D1 | [16 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0110 | [10 empty] | B2/D29_D1 | [16 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0111 | [10 empty] | B2/D29_D1 | [16 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0112 | [10 empty] | B2/D29_D1 | [16 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0113 | [10 empty] | B2/D29_D1 | [16 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0114 | [10 empty] | B2/D29_D1 | [16 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0115 | [10 empty] | B2/D29_D1 | [16 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0116 | [10 empty] | B2/D29_D1 | [16 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0117 | [10 empty] | B2/D29_D1 | [16 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0118 | [10 empty] | B2/D29_D1 | [16 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0119 | [10 empty] | B2/D29_D1 | [16 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0120 | [10 empty] | B2/D29_D1 | [16 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0121 | [10 empty] | B2/D29_D1 | [16 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0122 | [10 empty] | B2/D29_D1 | [16 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0123 | [10 empty] | B2/D29_D1 | [16 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0124 | [10 empty] | B2/D29_D1 | [16 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0125 | [10 empty] | B2/D29_D1 | [16 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0126 | [10 empty] | B2/D29_D1 | [16 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0167 | [10 empty] | B2/D29_D1 | [16 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0168 | [10 empty] | B2/D29_D1 | [16 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0169 | [10 empty] | B2/D29_D1 | [16 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0170 | [10 empty] | B2/D29_D1 | [16 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0171 | [10 empty] | B2/D29_D1 | [16 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0172 | [10 empty] | B2/D29_D1 | [16 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 | [10 empty] | B2/D29_D1 | [16 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 | [10 empty] | B2/D29_D1 | [16 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 | [10 empty] | B2/D29_D1 | [16 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0176 | [10 empty] | B2/D29_D1 | [16 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0177 | [10 empty] | B2/D29_D1 | [16 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0178 | [10 empty] | B2/D29_D1 | [16 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0179 | [10 empty] | B2/D29_D1 | [16 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0180 | [10 empty] | B2/D29_D1 | [16 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0181 | [10 empty] | B2/D29_D1 | [16 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0182 | [10 empty] | B2/D29_D1 | [16 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0183 | [10 empty] | B2/D29_D1 | [16 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0184 | [10 empty] | B2/D29_D1 | [16 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0185 | [10 empty] | B2/D29_D1 | [16 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0186 | [10 empty] | B2/D29_D1 | [16 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0187 | [10 empty] | B2/D29_D1 | [16 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0188 | [10 empty] | B2/D29_D1 | [16 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0189 | [10 empty] | B2/D29_D1 | [16 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0190 | [10 empty] | B2/D29_D1 | [16 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0191 | [10 empty] | B2/D29_D1 | [16 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0198 | [10 empty] | B2/D29_D1 | [16 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0199 | [10 empty] | B2/D29_D1 | [16 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0200 | [10 empty] | B2/D29_D1 | [16 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0201 | [10 empty] | B2/D29_D1 | [16 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0202 | [10 empty] | B2/D29_D1 | [16 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0203 | [10 empty] | B2/D29_D1 | [16 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0204 | [10 empty] | B2/D29_D1 | [16 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0205 | [10 empty] | B2/D29_D1 | [16 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0206 | [10 empty] | B2/D29_D1 | [16 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0207 | [10 empty] | B2/D29_D1 | [16 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0208 | [10 empty] | B2/D29_D1 | [16 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 | [10 empty] | B2/D29_D1 | [16 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 | [10 empty] | B2/D29_D1 | [16 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 | [10 empty] | B2/D29_D1 | [16 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0212 | [10 empty] | B2/D29_D1 | [16 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0213 | [10 empty] | B2/D29_D1 | [16 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0214 | [10 empty] | B2/D29_D1 | [16 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0215 | [10 empty] | B2/D29_D1 | [16 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0216 | [10 empty] | B2/D29_D1 | [16 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0217 | [10 empty] | B2/D29_D1 | [16 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0218 | [10 empty] | B2/D29_D1 | [16 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0219 | [10 empty] | B2/D29_D1 | [16 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0220 | [10 empty] | B2/D29_D1 | [16 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0221 | [10 empty] | B2/D29_D1 | [16 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0222 | [10 empty] | B2/D29_D1 | [16 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0024 | [10 empty] | B2/D29_A1 | [16 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0025 | [10 empty] | B2/D29_A1 | [16 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0026 | [10 empty] | B2/D29_A1 | [16 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0127 | [10 empty] | B3/D29_A1 | [16 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0128 | [10 empty] | B3/D29_A1 | [16 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0129 | [10 empty] | B3/D29_A1 | [16 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0223 | [10 empty] | B3/D29_A1 | [16 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0224 | [10 empty] | B3/D29_A1 | [16 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0225 | [10 empty] | B3/D29_A1 | [16 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0096 | [10 empty] | B3/D29_A1 | [16 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0097 | [10 empty] | B3/D29_A1 | [16 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0098 | [10 empty] | B3/D29_A1 | [16 empty] | 127 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0099 | [10 empty] | B3/D29_A1 | [16 empty] | 128 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0100 | [10 empty] | B3/D29_A1 | [16 empty] | 129 | [10 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 |  | -652.5 | -725 | -797.5 | -906.2
D29 | 府城DS |  |  | 1DTR | #1DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0032 | [10 empty] | B1/D29_A1 | [16 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0033 | [10 empty] | B1/D29_A1 | [16 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0035 |  | 0115 | [8 empty] | B1/D29_A1 | [16 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0130 | [10 empty] | B3/D29_A1 | [16 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0131 | [10 empty] | B3/D29_A1 | [16 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 | [10 empty] | B3/D29_A1 | [16 empty] | 135 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 | [10 empty] | B3/D29_A1 | [16 empty] | 136 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 | [10 empty] | B3/D29_A1 | [16 empty] | 137 | [10 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 |  | -1305 | -1450 | -1595 | -1812.5
D29 | 府城DS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0034 | [10 empty] | B1/D29_A1 | [16 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0036 |  | 0117 | [8 empty] | B1/D29_A1 | [16 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0037 | [10 empty] | B1/D29_A1 | [16 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0038 | [10 empty] | B1/D29_A1 | [16 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0039 |  | 0119 | [8 empty] | B1/D29_A1 | [16 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0161 | [10 empty] | B3/D29_A1 | [16 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0162 | [10 empty] | B3/D29_A1 | [16 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0163 | [10 empty] | B3/D29_A1 | [16 empty] | 145 | [10 empty] | LG_0 | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0164 | [10 empty] | B3/D29_A1 | [16 empty] | 146 | [10 empty] | LG_0 | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0165 | [10 empty] | B3/D29_A1 | [16 empty] | 147 | [10 empty] | LG_0 | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KW |  |  | MvMoment | KW |  | Y |  | AI | [6 empty] | 0192 | [10 empty] | B3/D29_A1 | [16 empty] | 148 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | KVAR |  |  | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0193 | [10 empty] | B3/D29_A1 | [16 empty] | 149 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0194 | [10 empty] | B3/D29_A1 | [16 empty] | 150 | [10 empty] | LG_0 | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0195 | [10 empty] | B3/D29_A1 | [16 empty] | 151 | [10 empty] | LG_0 | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0196 | [10 empty] | B3/D29_A1 | [16 empty] | 152 | [10 empty] | LG_0 | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0062 | [10 empty] | B3/D29_A1 | [16 empty] | 153 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0061 | [10 empty] | B3/D29_A1 | [16 empty] | 154 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L//T2 |  | 0000 |  | 0001 | [7 empty] | aaca | B2/D29_A1 | [16 empty] | 155 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 | [10 empty] | B2/D29_A1 | [16 empty] | 156 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 | [10 empty] | B2/D29_A1 | [16 empty] | 157 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 | [10 empty] | B2/D29_A1 | [16 empty] | 158 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L//T2 |  | 0004 |  | 0002 | [7 empty] | aada | B2/D29_A1 | [16 empty] | 159 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 | [10 empty] | B2/D29_A1 | [16 empty] | 160 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 | [10 empty] | B2/D29_A1 | [16 empty] | 161 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 | [10 empty] | B2/D29_A1 | [16 empty] | 162 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0040 |  | 0015 | [7 empty] | aafz | B2/D29_A1 | [16 empty] | 163 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 | [10 empty] | B2/D29_A1 | [16 empty] | 164 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 | [10 empty] | B2/D29_A1 | [16 empty] | 165 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 | [10 empty] | B2/D29_A1 | [16 empty] | 166 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0044 | [10 empty] | B3/D29_A1 | [16 empty] | 167 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0045 | [10 empty] | B3/D29_A1 | [16 empty] | 168 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0046 | [10 empty] | ELEM/D29_A1 | [16 empty] | 169 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0047 | [10 empty] | B3/D29_A1 | [16 empty] | 170 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0048 |  | 0011 | [7 empty] | aabb | ELEM/D29_A1 | [16 empty] | 171 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 | [10 empty] | B1/D29_A1 | [16 empty] | 172 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 | [10 empty] | B1/D29_A1 | [16 empty] | 173 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 | [10 empty] | B1/D29_A1 | [16 empty] | 174 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 | [10 empty] | B1/D29_A1 | [16 empty] | 175 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 | [10 empty] | B1/D29_A1 | [16 empty] | 176 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 | [10 empty] | B1/D29_A1 | [16 empty] | 177 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 | [10 empty] | B1/D29_A1 | [16 empty] | 178 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0056 |  | 0016 | [7 empty] | aaca | ELEM/D29_A1 | [16 empty] | 179 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 | [10 empty] | B3/D29_A1 | [16 empty] | 180 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 | [10 empty] | B3/D29_A1 | [16 empty] | 181 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0059 |  | 0017 | [7 empty] | adba | ELEM/D29_A1 | [16 empty] | 182 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 | [10 empty] | B3/D29_A1 | [16 empty] | 183 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 | [10 empty] | B3/D29_A1 | [16 empty] | 184 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0062 |  | 0012 | [7 empty] | aaeb | ELEM/D29_A1 | [16 empty] | 185 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 | [10 empty] | B1/D29_A1 | [16 empty] | 186 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 | [10 empty] | B1/D29_A1 | [16 empty] | 187 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 | [10 empty] | B1/D29_A1 | [16 empty] | 188 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 | [10 empty] | B1/D29_A1 | [16 empty] | 189 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 | [10 empty] | B1/D29_A1 | [16 empty] | 190 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 | [10 empty] | B1/D29_A1 | [16 empty] | 191 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 | [10 empty] | B1/D29_A1 | [16 empty] | 192 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | T/2DTR(A) |  |  | 0070 |  | 0018 | [7 empty] | abba | ELEM/D29_A1 | [16 empty] | 193 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 | [10 empty] | B3/D29_A1 | [16 empty] | 194 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 | [10 empty] | B3/D29_A1 | [16 empty] | 195 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2DTR(B) |  |  | 0073 |  | 0019 | [7 empty] | acga | ELEM/D29_A1 | [16 empty] | 196 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 | [10 empty] | B3/D29_A1 | [16 empty] | 197 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 | [10 empty] | B3/D29_A1 | [16 empty] | 198 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABUS | A/LBS210^C/1SC(A) |  |  | 0192 |  | 0022 | [7 empty] | aaab | B3/D29_A1 | [16 empty] | 199 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0193 | [10 empty] | B3/D29_A1 | [16 empty] | 200 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0194 | [10 empty] | B3/D29_A1 | [16 empty] | 201 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 390 | #1SSTR(390) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0195 |  | 0023 | [7 empty] | aagb | B3/D29_A1 | [16 empty] | 202 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 390 | #1SSTR(390) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 | [10 empty] | B3/D29_A1 | [16 empty] | 203 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 390 | #1SSTR(390) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 | [10 empty] | B3/D29_A1 | [16 empty] | 204 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/4G51/T1 |  |  | 0198 |  | 0024 | [7 empty] | aadb | B2/D29_D1 | [16 empty] | 205 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 | [10 empty] | B2/D29_D1 | [16 empty] | 206 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 | [10 empty] | B2/D29_D1 | [16 empty] | 207 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/4G52/T1 |  |  | 0201 |  | 0025 | [7 empty] | aaeb | B2/D29_D1 | [16 empty] | 208 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 | [10 empty] | B2/D29_D1 | [16 empty] | 209 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 | [10 empty] | B2/D29_D1 | [16 empty] | 210 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/4G53/T1 |  |  | 0204 |  | 0026 | [7 empty] | aafb | B2/D29_D1 | [16 empty] | 211 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 | [10 empty] | B2/D29_D1 | [16 empty] | 212 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 | [10 empty] | B2/D29_D1 | [16 empty] | 213 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/4G54/T1 |  |  | 0207 |  | 0027 | [7 empty] | aahb | B2/D29_D1 | [16 empty] | 214 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0208 | [10 empty] | B2/D29_D1 | [16 empty] | 215 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 | [10 empty] | B2/D29_D1 | [16 empty] | 216 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/4G55/T1 |  |  | 0210 |  | 0028 | [7 empty] | aaib | B2/D29_D1 | [16 empty] | 217 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 | [10 empty] | B2/D29_D1 | [16 empty] | 218 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0212 | [10 empty] | B2/D29_D1 | [16 empty] | 219 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBUS | A/LBS220^C/2SC(A) |  |  | 0213 |  | 0030 | [7 empty] | adab | B3/D29_A1 | [16 empty] | 220 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0214 | [10 empty] | B3/D29_A1 | [16 empty] | 221 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0215 | [10 empty] | B3/D29_A1 | [16 empty] | 222 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/4G11/T1 |  |  | 0216 |  | 0031 | [7 empty] | adgb | B2/D29_D1 | [16 empty] | 223 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 | [10 empty] | B2/D29_D1 | [16 empty] | 224 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 | [10 empty] | B2/D29_D1 | [16 empty] | 225 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/4G12/T1 |  |  | 0219 |  | 0032 | [7 empty] | adfb | B2/D29_D1 | [16 empty] | 226 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 | [10 empty] | B2/D29_D1 | [16 empty] | 227 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 | [10 empty] | B2/D29_D1 | [16 empty] | 228 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/4G13/T1 |  |  | 0222 |  | 0033 | [7 empty] | adeb | B2/D29_D1 | [16 empty] | 229 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 | [10 empty] | B2/D29_D1 | [16 empty] | 230 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0224 | [10 empty] | B2/D29_D1 | [16 empty] | 231 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/4G14/T1 |  |  | 0225 |  | 0034 | [7 empty] | addb | B2/D29_D1 | [16 empty] | 232 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 | [10 empty] | B2/D29_D1 | [16 empty] | 233 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 | [10 empty] | B2/D29_D1 | [16 empty] | 234 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/4G15/T1 |  |  | 0228 |  | 0035 | [7 empty] | adcb | B2/D29_D1 | [16 empty] | 235 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 | [10 empty] | B2/D29_D1 | [16 empty] | 236 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 | [10 empty] | B2/D29_D1 | [16 empty] | 237 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/2ABus |  |  | 0231 |  | 0029 | [7 empty] | aajb | B3/D29_A1 | [16 empty] | 238 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 | [10 empty] | B3/D29_A1 | [16 empty] | 239 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 | [10 empty] | B3/D29_A1 | [16 empty] | 240 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/4G61/T1 |  |  | 0234 |  | 0037 | [7 empty] | abcb | B2/D29_D1 | [16 empty] | 241 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 | [10 empty] | B2/D29_D1 | [16 empty] | 242 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0236 | [10 empty] | B2/D29_D1 | [16 empty] | 243 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/4G62/T1 |  |  | 0237 |  | 0038 | [7 empty] | abdb | B2/D29_D1 | [16 empty] | 244 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 | [10 empty] | B2/D29_D1 | [16 empty] | 245 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 | [10 empty] | B2/D29_D1 | [16 empty] | 246 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/4G63/T1 |  |  | 0240 |  | 0039 | [7 empty] | abfb | B2/D29_D1 | [16 empty] | 247 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 | [10 empty] | B2/D29_D1 | [16 empty] | 248 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0242 | [10 empty] | B2/D29_D1 | [16 empty] | 249 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/4G64/T1 |  |  | 0243 |  | 0040 | [7 empty] | abgb | B2/D29_D1 | [16 empty] | 250 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 | [10 empty] | B2/D29_D1 | [16 empty] | 251 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0245 | [10 empty] | B2/D29_D1 | [16 empty] | 252 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/4G65/T1 |  |  | 0246 |  | 0041 | [7 empty] | abhb | B2/D29_D1 | [16 empty] | 253 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0247 | [10 empty] | B2/D29_D1 | [16 empty] | 254 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0248 | [10 empty] | B2/D29_D1 | [16 empty] | 255 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABUS | A/LBS230^C/3SC(A) |  |  | 0249 |  | 0036 | [7 empty] | abab | B3/D29_A1 | [16 empty] | 256 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0250 | [10 empty] | B3/D29_A1 | [16 empty] | 257 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0251 | [10 empty] | B3/D29_A1 | [16 empty] | 258 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBUS | A/LBS240^C/4SC(A) |  |  | 0252 |  | 0044 | [7 empty] | achb | B3/D29_A1 | [16 empty] | 259 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0253 | [10 empty] | B3/D29_A1 | [16 empty] | 260 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0254 | [10 empty] | B3/D29_A1 | [16 empty] | 261 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 490 | #2SSTR(490) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/2SSTR |  |  | 0255 |  | 0043 | [7 empty] | acib | B3/D29_A1 | [16 empty] | 262 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 490 | #2SSTR(490) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0256 | [10 empty] | B3/D29_A1 | [16 empty] | 263 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 490 | #2SSTR(490) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 | [10 empty] | B3/D29_A1 | [16 empty] | 264 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/100/N1 |  |  | 0258 |  | 0042 | [7 empty] | acjb | B3/D29_A1 | [16 empty] | 265 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 | [10 empty] | B3/D29_A1 | [16 empty] | 266 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 | [10 empty] | B3/D29_A1 | [16 empty] | 267 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/4G66/T1 |  |  | 0261 |  | 0045 | [7 empty] | acab | B2/D29_D1 | [16 empty] | 268 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 | [10 empty] | B2/D29_D1 | [16 empty] | 269 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 | [10 empty] | B2/D29_D1 | [16 empty] | 270 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/4G67/T1 |  |  | 0264 |  | 0046 | [7 empty] | acbb | B2/D29_D1 | [16 empty] | 271 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 | [10 empty] | B2/D29_D1 | [16 empty] | 272 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 | [10 empty] | B2/D29_D1 | [16 empty] | 273 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/4G68/T1 |  |  | 0267 |  | 0047 | [7 empty] | accb | B2/D29_D1 | [16 empty] | 274 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 | [10 empty] | B2/D29_D1 | [16 empty] | 275 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 | [10 empty] | B2/D29_D1 | [16 empty] | 276 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/4G69/T1 |  |  | 0270 |  | 0048 | [7 empty] | aceb | B2/D29_D1 | [16 empty] | 277 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0271 | [10 empty] | B2/D29_D1 | [16 empty] | 278 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 | [10 empty] | B2/D29_D1 | [16 empty] | 279 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/4G70/T1 |  |  | 0273 |  | 0049 | [7 empty] | acfb | B2/D29_D1 | [16 empty] | 280 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 | [10 empty] | B2/D29_D1 | [16 empty] | 281 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 | [10 empty] | B2/D29_D1 | [16 empty] | 282 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 | [10 empty] | ELEM/D29_A1 | [16 empty] | 283 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 | [10 empty] | B2/D29_D1 | [16 empty] | 284 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 | [10 empty] | B2/D29_D1 | [16 empty] | 285 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 | [10 empty] | B2/D29_D1 | [16 empty] | 286 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 | [10 empty] | B2/D29_D1 | [16 empty] | 287 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 | [10 empty] | B2/D29_D1 | [16 empty] | 288 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 | [10 empty] | ELEM/D29_A1 | [16 empty] | 289 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 | [10 empty] | B2/D29_D1 | [16 empty] | 290 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 | [10 empty] | B2/D29_D1 | [16 empty] | 291 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 | [10 empty] | B2/D29_D1 | [16 empty] | 292 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 | [10 empty] | B2/D29_D1 | [16 empty] | 293 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 | [10 empty] | B2/D29_D1 | [16 empty] | 294 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 | [10 empty] | ELEM/D29_A1 | [16 empty] | 295 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 | [10 empty] | B2/D29_D1 | [16 empty] | 296 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 | [10 empty] | B2/D29_D1 | [16 empty] | 297 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 | [10 empty] | B2/D29_D1 | [16 empty] | 298 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 | [10 empty] | B2/D29_D1 | [16 empty] | 299 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 | [10 empty] | B2/D29_D1 | [16 empty] | 300 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 | [10 empty] | ELEM/D29_A1 | [16 empty] | 301 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 | [10 empty] | B2/D29_D1 | [16 empty] | 302 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 | [10 empty] | B2/D29_D1 | [16 empty] | 303 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 | [10 empty] | B2/D29_D1 | [16 empty] | 304 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 | [10 empty] | B2/D29_D1 | [16 empty] | 305 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 | [10 empty] | B2/D29_D1 | [16 empty] | 306 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | RTU | RTU |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP | [6 empty] | 0512 |  | 0000 | [8 empty] | B3/D29_A1 | [16 empty] | 307 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 | [10 empty] | ELEM/D29_A1 | [16 empty] | 308 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0514 | [10 empty] | B2/D29_A1 | [16 empty] | 309 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0515 | [10 empty] | B2/D29_A1 | [16 empty] | 310 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0516 | [10 empty] | B2/D29_A1 | [16 empty] | 311 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0517 | [10 empty] | B2/D29_A1 | [16 empty] | 312 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0160 | [8 empty] | B1/D29_A1 | [16 empty] | 313 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0535 | [9 empty] | c | B1/D29_A1 | [16 empty] | 314 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(A) | #1DTR(A) |  | OLTC_A_M |  |  | Status | OLTC M/A | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0536 |  | 0114 | [8 empty] | B1/D29_A1 | [16 empty] | 315 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0537 | [9 empty] | b | B1/D29_A1 | [16 empty] | 316 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR(B) | #1DTR(B) |  | OLTC_A_M |  |  | Status | OLTC M/A | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0538 |  | 0116 | [8 empty] | B1/D29_A1 | [16 empty] | 317 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0539 | [10 empty] | B1/D29_A1 | [16 empty] | 318 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0540 | [10 empty] | B1/D29_A1 | [16 empty] | 319 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0541 | [10 empty] | B1/D29_A1 | [16 empty] | 320 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0542 | [10 empty] | B1/D29_A1 | [16 empty] | 321 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0543 | [10 empty] | B1/D29_A1 | [16 empty] | 322 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0544 | [10 empty] | B1/D29_A1 | [16 empty] | 323 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0545 | [9 empty] | a | B1/D29_A1 | [16 empty] | 324 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0546 |  | 0164 | [8 empty] | B1/D29_A1 | [16 empty] | 325 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0549 | [10 empty] | B1/D29_A1 | [16 empty] | 326 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | OLTC_A_M |  |  | Status | OLTC M/A | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0550 |  | 0118 | [8 empty] | B1/D29_A1 | [16 empty] | 327 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0551 | [10 empty] | B1/D29_A1 | [16 empty] | 328 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0552 | [10 empty] | B1/D29_A1 | [16 empty] | 329 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0553 | [10 empty] | B1/D29_A1 | [16 empty] | 330 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0554 | [10 empty] | B1/D29_A1 | [16 empty] | 331 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0555 | [10 empty] | B1/D29_A1 | [16 empty] | 332 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0556 | [10 empty] | B1/D29_A1 | [16 empty] | 333 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0557 | [9 empty] | a | B1/D29_A1 | [16 empty] | 334 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0576 | [10 empty] | B3/D29_A1 | [16 empty] | 335 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0577 | [10 empty] | B3/D29_A1 | [16 empty] | 336 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0578 |  | 0158 | [8 empty] | B2/D29_A1 | [16 empty] | 337 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0579 |  | 0159 | [8 empty] | B2/D29_A1 | [16 empty] | 338 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0580 | [10 empty] | B2/D29_A1 | [16 empty] | 339 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | ComPoint |  |  | 12B_CTFA |  |  | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0581 | [10 empty] | B3/D29_A1 | [16 empty] | 340 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0582 | [10 empty] | B3/D29_A1 | [16 empty] | 341 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0583 | [10 empty] | B3/D29_A1 | [16 empty] | 342 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0584 | [10 empty] | B3/D29_A1 | [16 empty] | 343 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Water1 | 地下室第一段水位警報 |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0585 | [10 empty] | B3/D29_A1 | [16 empty] | 344 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Water2 | 地下室第二段水位警報 |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0586 | [10 empty] | B3/D29_A1 | [16 empty] | 345 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0587 | [10 empty] | ELEM/D29_A1 | [16 empty] | 346 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | ComPoint |  |  | 60A |  |  | Status | 電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0588 | [10 empty] | B3/D29_A1 | [16 empty] | 347 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0589 | [10 empty] | B3/D29_A1 | [16 empty] | 348 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0590 | [10 empty] | B3/D29_A1 | [16 empty] | 349 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0591 | [10 empty] | B3/D29_A1 | [16 empty] | 350 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Fire1 | 消防火警(1) |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0592 | [10 empty] | B3/D29_A1 | [16 empty] | 351 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Fire2 | 消防故障(2) |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0593 | [10 empty] | B3/D29_A1 | [16 empty] | 352 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Fire3 | CO2防護區 |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0594 | [10 empty] | B3/D29_A1 | [16 empty] | 353 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Fire4 | CO2控制主機故障 |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0595 | [10 empty] | B3/D29_A1 | [16 empty] | 354 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Fire5 | CO2鋼瓶漏氣 |  | Status | 火災警報5 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0596 | [10 empty] | B3/D29_A1 | [16 empty] | 355 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Door1 | 圍牆大小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0597 | [10 empty] | B3/D29_A1 | [16 empty] | 356 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Burglar | 保全系統 |  | Status | 無人化防盜 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0598 | [10 empty] | B3/D29_A1 | [16 empty] | 357 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0599 | [10 empty] | B3/D29_A1 | [16 empty] | 358 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0600 | [10 empty] | B3/D29_A1 | [16 empty] | 359 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | Door4 |  |  | Status | 無人化門禁4 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0601 | [10 empty] | B3/D29_A1 | [16 empty] | 360 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 通訊室溫度警報 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0602 | [10 empty] | B3/D29_A1 | [16 empty] | 361 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | R_Temp2 | 控制室溫度警報 |  | Status | 溫度警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0603 | [10 empty] | B3/D29_A1 | [16 empty] | 362 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0605 | [10 empty] | B2/D29_A1 | [16 empty] | 363 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0606 | [10 empty] | B2/D29_A1 | [16 empty] | 364 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0607 | [10 empty] | ELEM/D29_A1 | [16 empty] | 365 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0608 | [10 empty] | B3/D29_A1 | [16 empty] | 366 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0609 | [10 empty] | B3/D29_A1 | [16 empty] | 367 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0610 | [10 empty] | ELEM/D29_A1 | [16 empty] | 368 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0611 | [10 empty] | B3/D29_A1 | [16 empty] | 369 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0612 | [10 empty] | B3/D29_A1 | [16 empty] | 370 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0613 | [10 empty] | B1/D29_A1 | [16 empty] | 371 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0614 | [10 empty] | B1/D29_A1 | [16 empty] | 372 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0618 | [10 empty] | B1/D29_A1 | [16 empty] | 373 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0619 |  | 0163 | [8 empty] | B1/D29_A1 | [16 empty] | 374 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0620 |  | 0161 | [8 empty] | B1/D29_A1 | [16 empty] | 375 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 1DTR | #1DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0621 |  | 0162 | [8 empty] | B1/D29_A1 | [16 empty] | 376 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0622 | [10 empty] | B1/D29_A1 | [16 empty] | 377 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0623 |  | 0167 | [8 empty] | B1/D29_A1 | [16 empty] | 378 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0624 |  | 0165 | [8 empty] | B1/D29_A1 | [16 empty] | 379 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS |  |  | 2DTR | #2DTR |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0625 |  | 0166 | [8 empty] | B1/D29_A1 | [16 empty] | 380 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | GPSA | LOCAL GPS故障 |  | Status | GPS故障警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0626 | [10 empty] | B3/D29_A1 | [16 empty] | 381 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | PSF | 變壓器所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0627 | [10 empty] | B3/D29_A1 | [16 empty] | 382 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | PSA | 變壓器所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0628 | [10 empty] | B3/D29_A1 | [16 empty] | 383 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0629 | [10 empty] | B3/D29_A1 | [16 empty] | 384 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0630 | [10 empty] | B3/D29_A1 | [16 empty] | 385 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | AIRCON | 通訊室 |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0631 | [10 empty] | B3/D29_A1 | [16 empty] | 386 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | ComPoint |  |  | TRA_TRF | #1、#2 DTR |  | Status | TRA/TRF UL | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0632 | [10 empty] | B3/D29_A1 | [16 empty] | 387 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 0 |  | StaDev | 所內設施 |  | 1A5Other | 緊急發電機運轉 |  | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0635 | [10 empty] | B3/D29_A1 | [16 empty] | 388 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | ComPoint |  |  | FDR_IRFA | 22KV IED故障 |  | Status | 11/22 kV IED故障監視 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0636 | [10 empty] | ELEM/D29_D1 | [16 empty] | 389 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0637 | [10 empty] | ELEM/D29_A1 | [16 empty] | 390 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0638 | [10 empty] | ELEM/D29_A1 | [16 empty] | 391 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | ComPoint |  |  | LOA |  |  | Status | 復閉失敗 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0639 | [10 empty] | B3/D29_A1 | [16 empty] | 392 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 |  | 0064 | [8 empty] | B2/D29_A1 | [16 empty] | 393 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 |  | 0065 | [8 empty] | B2/D29_A1 | [16 empty] | 394 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 |  | 0066 | [8 empty] | B2/D29_A1 | [16 empty] | 395 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | ES3 | 1513E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0646 |  | 0067 | [8 empty] | B2/D29_A1 | [16 empty] | 396 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 |  | 0068 | [8 empty] | B2/D29_A1 | [16 empty] | 397 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 |  | 0069 | [8 empty] | B2/D29_A1 | [16 empty] | 398 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 |  | 0070 | [8 empty] | B2/D29_A1 | [16 empty] | 399 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | ES3 | 1523E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0654 |  | 0071 | [8 empty] | B2/D29_A1 | [16 empty] | 400 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0720 |  | 0104 | [8 empty] | B2/D29_A1 | [16 empty] | 401 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0722 |  | 0105 | [8 empty] | B2/D29_A1 | [16 empty] | 402 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0724 |  | 0106 | [8 empty] | B2/D29_A1 | [16 empty] | 403 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0726 |  | 0107 | [8 empty] | B2/D29_A1 | [16 empty] | 404 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0728 |  | 0108 | [8 empty] | B2/D29_A1 | [16 empty] | 405 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0730 |  | 0109 | [8 empty] | B2/D29_A1 | [16 empty] | 406 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | LBS210 | #1SC(210) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/210 | C/1SC(B) |  |  | 0740 |  | 0122 | [8 empty] | B3/D29_A1 | [16 empty] | 407 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0742 |  | 0123 | [8 empty] | B3/D29_A1 | [16 empty] | 408 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | LBS230 | #3SC(230) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/230 | C/3SC(B) |  |  | 0744 |  | 0124 | [8 empty] | B3/D29_A1 | [16 empty] | 409 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | LBS240 | #4SC(240) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/240 | C/4SC(B) |  |  | 0746 |  | 0125 | [8 empty] | B3/D29_A1 | [16 empty] | 410 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0768 |  | 0184 | [8 empty] | B2/D29_D1 | [16 empty] | 411 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0769 |  | 0185 | [8 empty] | B2/D29_D1 | [16 empty] | 412 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0186 | [8 empty] | B2/D29_D1 | [16 empty] | 413 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0771 |  | 0187 | [8 empty] | B2/D29_D1 | [16 empty] | 414 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0188 | [8 empty] | B2/D29_D1 | [16 empty] | 415 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0773 |  | 0189 | [8 empty] | B2/D29_D1 | [16 empty] | 416 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  | 0190 | [8 empty] | B2/D29_D1 | [16 empty] | 417 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0775 |  | 0191 | [8 empty] | B2/D29_D1 | [16 empty] | 418 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0192 | [8 empty] | B2/D29_D1 | [16 empty] | 419 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0777 |  | 0193 | [8 empty] | B2/D29_D1 | [16 empty] | 420 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0194 | [8 empty] | B2/D29_D1 | [16 empty] | 421 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0779 |  | 0195 | [8 empty] | B2/D29_D1 | [16 empty] | 422 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  | 0196 | [8 empty] | B2/D29_D1 | [16 empty] | 423 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0781 |  | 0197 | [8 empty] | B2/D29_D1 | [16 empty] | 424 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0198 | [8 empty] | B2/D29_D1 | [16 empty] | 425 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0783 |  | 0199 | [8 empty] | B2/D29_D1 | [16 empty] | 426 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0784 |  | 0200 | [8 empty] | B2/D29_D1 | [16 empty] | 427 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0785 |  | 0201 | [8 empty] | B2/D29_D1 | [16 empty] | 428 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0202 | [8 empty] | B2/D29_D1 | [16 empty] | 429 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0787 |  | 0203 | [8 empty] | B2/D29_D1 | [16 empty] | 430 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  | 0204 | [8 empty] | B2/D29_D1 | [16 empty] | 431 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0789 |  | 0205 | [8 empty] | B2/D29_D1 | [16 empty] | 432 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  | 0206 | [8 empty] | B2/D29_D1 | [16 empty] | 433 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0791 |  | 0207 | [8 empty] | B2/D29_D1 | [16 empty] | 434 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0208 | [8 empty] | B2/D29_D1 | [16 empty] | 435 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0793 |  | 0209 | [8 empty] | B2/D29_D1 | [16 empty] | 436 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0794 |  | 0210 | [8 empty] | B2/D29_D1 | [16 empty] | 437 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0795 |  | 0211 | [8 empty] | B2/D29_D1 | [16 empty] | 438 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0796 |  | 0212 | [8 empty] | B2/D29_D1 | [16 empty] | 439 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0797 |  | 0213 | [8 empty] | B2/D29_D1 | [16 empty] | 440 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0214 | [8 empty] | B2/D29_D1 | [16 empty] | 441 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0799 |  | 0215 | [8 empty] | B2/D29_D1 | [16 empty] | 442 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0216 | [8 empty] | B2/D29_D1 | [16 empty] | 443 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0801 |  | 0217 | [8 empty] | B2/D29_D1 | [16 empty] | 444 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  | 0218 | [8 empty] | B2/D29_D1 | [16 empty] | 445 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0803 |  | 0219 | [8 empty] | B2/D29_D1 | [16 empty] | 446 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0804 |  | 0220 | [8 empty] | B2/D29_D1 | [16 empty] | 447 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0805 |  | 0221 | [8 empty] | B2/D29_D1 | [16 empty] | 448 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0806 |  | 0222 | [8 empty] | B2/D29_D1 | [16 empty] | 449 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0807 |  | 0223 | [8 empty] | B2/D29_D1 | [16 empty] | 450 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0848 |  | 0248 | [8 empty] | B3/D29_A1 | [16 empty] | 451 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0849 |  | 0249 | [8 empty] | B3/D29_A1 | [16 empty] | 452 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0850 |  | 0250 | [8 empty] | B3/D29_A1 | [16 empty] | 453 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0851 |  | 0251 | [8 empty] | B3/D29_A1 | [16 empty] | 454 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0854 |  | 0128 | [8 empty] | B2/D29_A1 | [16 empty] | 455 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0855 |  | 0129 | [8 empty] | B2/D29_A1 | [16 empty] | 456 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0856 |  | 0130 | [8 empty] | B2/D29_A1 | [16 empty] | 457 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | 87UL1 |  |  | Status | 第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0857 |  | 0131 | [8 empty] | B2/D29_A1 | [16 empty] | 458 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | 87UL2 |  |  | Status | 第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0858 |  | 0132 | [8 empty] | B2/D29_A1 | [16 empty] | 459 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0859 |  | 0133 | [8 empty] | B2/D29_A1 | [16 empty] | 460 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G11_DS | 4G11_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線(4G11) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G11_DS | 4G11_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G12_DS | 4G12_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線(4G12) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G12_DS | 4G12_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G13_DS | 4G13_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線(4G13) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G13_DS | 4G13_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G14_DS | 4G14_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線(4G14) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G14_DS | 4G14_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G15_DS | 4G15_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線(4G15) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G15_DS | 4G15_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G51_DS | 4G51_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線(4G51) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G51_DS | 4G51_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G52_DS | 4G52_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線(4G52) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G52_DS | 4G52_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G53_DS | 4G53_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線(4G53) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G53_DS | 4G53_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G54_DS | 4G54_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線(4G54) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G54_DS | 4G54_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G55_DS | 4G55_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線(4G55) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G55_DS | 4G55_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G61_DS | 4G61_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線(4G61) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G61_DS | 4G61_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G62_DS | 4G62_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線(4G62) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G62_DS | 4G62_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G63_DS | 4G63_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線(4G63) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G63_DS | 4G63_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G64_DS | 4G64_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線(4G64) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G64_DS | 4G64_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G65_DS | 4G65_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線(4G65) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G65_DS | 4G65_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G66_DS | 4G66_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線(4G66) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G66_DS | 4G66_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G67_DS | 4G67_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線(4G67) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G67_DS | 4G67_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G68_DS | 4G68_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線(4G68) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G68_DS | 4G68_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G69_DS | 4G69_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線(4G69) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G69_DS | 4G69_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G70_DS | 4G70_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線(4G70) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.4G70_DS | 4G70_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 210 | #1SC(210) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.210_ES | 210_ES(非取樣點) | SC | [5 empty] | 302 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 210 | #1SC(210) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.210_DS | 210_DS(非取樣點) | SC | [5 empty] | 308 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 220 | #2SC(220) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.220_ES | 220_ES(非取樣點) | SC | [5 empty] | 302 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 11 | 11kV | 220 | #2SC(220) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.220_DS | 220_DS(非取樣點) | SC | [5 empty] | 308 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 230 | #3SC(230) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.230_ES | 230_ES(非取樣點) | SC | [5 empty] | 302 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 230 | #3SC(230) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.230_DS | 230_DS(非取樣點) | SC | [5 empty] | 308 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 240 | #4SC(240) |  | E1 | (非取樣點) | ADD | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.240_ES | 240_ES(非取樣點) | SC | [5 empty] | 302 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 240 | #4SC(240) |  | D1 | (非取樣點) | ADD | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.240_DS | 240_DS(非取樣點) | SC | [5 empty] | 308 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  |  | Status | LBS | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0742 |  | 0123 | [8 empty] | B3/D29_A1 | [16 empty] | 408 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.310_DS | 310_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 310 | #1DTR(A)(310) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.310_DS | 310_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.320_DS | 320_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 11 | 11kV | 320 | #1DTR(B)(320) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.320_DS | 320_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.330_DS | 330_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 330 | #2DTR(A)(330) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.330_DS | 330_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | D1 | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.340_DS | 340_DS (非取樣點) | FEEDER | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 340 | #2DTR(B)(340) |  | E1 | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/D29_D1 | [8 empty] | 府城DS.340_DS | 340_ES (非取樣點) | FEEDER | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 390 | #1SSTR(390) |  | D1 | 391(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.391 | 391 (非取樣點) | OTHER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 390 | #1SSTR(390) |  | E1 | 391E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.391E | 391E (非取樣點) | OTHER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 490 | #2SSTR(490) |  | D1 | 491(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.491 | 491 (非取樣點) | OTHER | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 490 | #2SSTR(490) |  | E1 | 491E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.491E | 491E (非取樣點) | OTHER | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 府城DS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D22_A1 | [8 empty] | 府城DS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/D29_A1 | [8 empty] | 府城DS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | D1 | 101(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.101 | 101 (非取樣點) | TIE | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | D2 | 102(非取樣點) |  | Status | DS2 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.102 | 102 (非取樣點) | TIE | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.101E | 101E(非取樣點) | OTHER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.102E | 102E(非取樣點) | OTHER | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | D1 | 201(非取樣點) |  | Status | DS1 | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.201 | 201 (非取樣點) | TIE | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
D29 | 府城DS | 22 | 22kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/D29_A1 | [8 empty] | 府城DS.201E | 201E(非取樣點) | OTHER | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
D29 | 府城DS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/D29_A1 | [17 empty] | v_best_161_12 | OPRD1: D29/161/1BUS/V; OPRD2: D29/161/2BUS/V
D29 | 府城DS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/D29_A1 | [17 empty] | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: D29/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
D29 | 府城DS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/D29_A1 | [17 empty] | p_sum_2 | OPRD1: D29/161/1510/MW; OPRD2: D29/161/1520/MW
D29 | 府城DS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/D29_A1 | [17 empty] | pwr_cnd2 | OPRD1: D29/0/CalcPoint/OPRN2_MW
D29 | 府城DS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/D29_A1 | [17 empty] | none
D29 | 府城DS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/D29_A1 | [17 empty] | pwr_fail | OPRD1: D29/0/CalcPoint/OPRN1; OPRD2: D29/0/CalcPoint/OPRN2; OPRD3: D29/0/CalcPoint/PRFL_UL
D29 | 府城DS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D29_A1 | [17 empty] | dtr_sum_cal | OPRD1: D29/11/310/I_R; OPRD2: D29/22/320/I_R
D29 | 府城DS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D29_A1 | [17 empty] | dtr_sum_cal | OPRD1: D29/11/310/I_S; OPRD2: D29/22/320/I_S
D29 | 府城DS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D29_A1 | [17 empty] | dtr_sum_cal | OPRD1: D29/11/310/I_T; OPRD2: D29/22/320/I_T
D29 | 府城DS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/D29_A1 | [17 empty] | dtr_sum_cal | OPRD1: D29/22/330/I_R; OPRD2: D29/22/340/I_R
D29 | 府城DS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/D29_A1 | [17 empty] | dtr_sum_cal | OPRD1: D29/22/330/I_S; OPRD2: D29/22/340/I_S
D29 | 府城DS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/D29_A1 | [17 empty] | dtr_sum_cal | OPRD1: D29/22/330/I_T; OPRD2: D29/22/340/I_T
D29 | 府城DS | 161 | 161kV | 1510 | 安南府城紅線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D29_A1 | [17 empty] | amp_cal | OPRD1: D29/161/1510/MW; OPRD2: D29/161/1510/MVAR; OPRD3: NULL
D29 | 府城DS | 161 | 161kV | 1520 | 安南府城白線 (1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/D29_A1 | [17 empty] | amp_cal | OPRD1: D29/161/1520/MW; OPRD2: D29/161/1520/MVAR; OPRD3: NULL
D29 | 府城DS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D29_A1 | [17 empty] | bus_uv | OPRD1: D29/11/1BBUS/V
D29 | 府城DS | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D29_A1 | [17 empty] | bus_uv | OPRD1: D29/22/1ABUS/V
D29 | 府城DS | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D29_A1 | [17 empty] | bus_uv | OPRD1: D29/22/2ABUS/V
D29 | 府城DS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/D29_A1 | [17 empty] | bus_uv | OPRD1: D29/22/2BBUS/V
D29 | 府城DS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/D29_A1 | [17 empty] | dtr_perm | OPRD1: D29//1DTR(A)/SupLocal; OPRD2: NULL
D29 | 府城DS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/D29_A1 | [17 empty] | dtr_perm | OPRD1: D29//1DTR(B)/SupLocal; OPRD2: NULL
D29 | 府城DS |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B1/D29_A1 | [17 empty] | dtr_perm | OPRD1: D29//2DTR/SupLocal; OPRD2: NULL
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線 (4G11) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/11/4G11/I_R; OPRD3: D29/11/4G11/I_S; OPRD4: D29/11/4G11/I_T
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線 (4G12) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/11/4G12/I_R; OPRD3: D29/11/4G12/I_S; OPRD4: D29/11/4G12/I_T
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線 (4G13) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/11/4G13/I_R; OPRD3: D29/11/4G13/I_S; OPRD4: D29/11/4G13/I_T
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線 (4G14) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/11/4G14/I_R; OPRD3: D29/11/4G14/I_S; OPRD4: D29/11/4G14/I_T
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線 (4G15) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/11/4G15/I_R; OPRD3: D29/11/4G15/I_S; OPRD4: D29/11/4G15/I_T
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線 (4G51) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G51/I_R; OPRD3: D29/22/4G51/I_S; OPRD4: D29/22/4G51/I_T
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線 (4G52) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G52/I_R; OPRD3: D29/22/4G52/I_S; OPRD4: D29/22/4G52/I_T
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線 (4G53) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G53/I_R; OPRD3: D29/22/4G53/I_S; OPRD4: D29/22/4G53/I_T
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線 (4G54) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G54/I_R; OPRD3: D29/22/4G54/I_S; OPRD4: D29/22/4G54/I_T
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線 (4G55) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G55/I_R; OPRD3: D29/22/4G55/I_S; OPRD4: D29/22/4G55/I_T
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線 (4G61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G61/I_R; OPRD3: D29/22/4G61/I_S; OPRD4: D29/22/4G61/I_T
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線 (4G62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G62/I_R; OPRD3: D29/22/4G62/I_S; OPRD4: D29/22/4G62/I_T
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線 (4G63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G63/I_R; OPRD3: D29/22/4G63/I_S; OPRD4: D29/22/4G63/I_T
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線 (4G64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G64/I_R; OPRD3: D29/22/4G64/I_S; OPRD4: D29/22/4G64/I_T
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線 (4G65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G65/I_R; OPRD3: D29/22/4G65/I_S; OPRD4: D29/22/4G65/I_T
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線 (4G66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G66/I_R; OPRD3: D29/22/4G66/I_S; OPRD4: D29/22/4G66/I_T
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線 (4G67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G67/I_R; OPRD3: D29/22/4G67/I_S; OPRD4: D29/22/4G67/I_T
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線 (4G68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G68/I_R; OPRD3: D29/22/4G68/I_S; OPRD4: D29/22/4G68/I_T
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線 (4G69) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G69/I_R; OPRD3: D29/22/4G69/I_S; OPRD4: D29/22/4G69/I_T
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線 (4G70) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kva_cal | OPRD1: NULL; OPRD2: D29/22/4G70/I_R; OPRD3: D29/22/4G70/I_S; OPRD4: D29/22/4G70/I_T
D29 | 府城DS | 11 | 11kV | 4G11 | 府11線 (4G11) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/11/4G11/kVA; OPRD2: D29/11/4G11/KVAR
D29 | 府城DS | 11 | 11kV | 4G12 | 府12線 (4G12) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/11/4G12/kVA; OPRD2: D29/11/4G12/KVAR
D29 | 府城DS | 11 | 11kV | 4G13 | 府13線 (4G13) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/11/4G13/kVA; OPRD2: D29/11/4G13/KVAR
D29 | 府城DS | 11 | 11kV | 4G14 | 府14線 (4G14) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/11/4G14/kVA; OPRD2: D29/11/4G14/KVAR
D29 | 府城DS | 11 | 11kV | 4G15 | 府15線 (4G15) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/11/4G15/kVA; OPRD2: D29/11/4G15/KVAR
D29 | 府城DS | 22 | 22kV | 4G51 | 府51線 (4G51) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G51/kVA; OPRD2: D29/22/4G51/KVAR
D29 | 府城DS | 22 | 22kV | 4G52 | 府52線 (4G52) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G52/kVA; OPRD2: D29/22/4G52/KVAR
D29 | 府城DS | 22 | 22kV | 4G53 | 府53線 (4G53) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G53/kVA; OPRD2: D29/22/4G53/KVAR
D29 | 府城DS | 22 | 22kV | 4G54 | 府54線 (4G54) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G54/kVA; OPRD2: D29/22/4G54/KVAR
D29 | 府城DS | 22 | 22kV | 4G55 | 府55線 (4G55) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G55/kVA; OPRD2: D29/22/4G55/KVAR
D29 | 府城DS | 22 | 22kV | 4G61 | 府61線 (4G61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G61/kVA; OPRD2: D29/22/4G61/KVAR
D29 | 府城DS | 22 | 22kV | 4G62 | 府62線 (4G62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G62/kVA; OPRD2: D29/22/4G62/KVAR
D29 | 府城DS | 22 | 22kV | 4G63 | 府63線 (4G63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G63/kVA; OPRD2: D29/22/4G63/KVAR
D29 | 府城DS | 22 | 22kV | 4G64 | 府64線 (4G64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G64/kVA; OPRD2: D29/22/4G64/KVAR
D29 | 府城DS | 22 | 22kV | 4G65 | 府65線 (4G65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G65/kVA; OPRD2: D29/22/4G65/KVAR
D29 | 府城DS | 22 | 22kV | 4G66 | 府66線 (4G66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G66/kVA; OPRD2: D29/22/4G66/KVAR
D29 | 府城DS | 22 | 22kV | 4G67 | 府67線 (4G67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G67/kVA; OPRD2: D29/22/4G67/KVAR
D29 | 府城DS | 22 | 22kV | 4G68 | 府68線 (4G68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G68/kVA; OPRD2: D29/22/4G68/KVAR
D29 | 府城DS | 22 | 22kV | 4G69 | 府69線 (4G69) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G69/kVA; OPRD2: D29/22/4G69/KVAR
D29 | 府城DS | 22 | 22kV | 4G70 | 府70線 (4G70) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/D29_D1 | [17 empty] | kw_cal | OPRD1: D29/22/4G70/kVA; OPRD2: D29/22/4G70/KVAR
D29 | 府城DS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D29_A1 | [17 empty] | sc_mvar | OPRD1: D29/11/220/CB; OPRD2: 6.9; OPRD3: 0
D29 | 府城DS | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D29_A1 | [17 empty] | sc_mvar | OPRD1: D29/22/210/CB; OPRD2: 13.8; OPRD3: 0
D29 | 府城DS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D29_A1 | [17 empty] | sc_mvar | OPRD1: D29/22/230/CB; OPRD2: 13.8; OPRD3: 0
D29 | 府城DS | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/D29_A1 | [17 empty] | sc_mvar | OPRD1: D29/22/240/CB; OPRD2: 13.8; OPRD3: 0
D29 | 府城DS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/D29_A1 | [17 empty] | com_alarm_30 | D29//1DTR/51ZA | D29//1DTR/GDA | D29//1DTR/96D | D29//1DTR/TRA | D29//1DTR/63Q | D29//1DTR/96B2 | D29//1DTR/96B1 | D29//1DTR/87A | D29//1DTR/PHA | D29//1DTR/96PA | D29//2DTR/63Q | D29//2DTR/TRA | D29//2DTR/96D | D29//2DTR/96B1 | D29//2DTR/96B2 | D29//2DTR/51ZA | D29//2DTR/PHA | D29//2DTR/GDA | D29//2DTR/87A | D29//2DTR/96PA | D29/11/320/GDA | D29/11/320/PHA | D29/161/1BUS/87A | D29/161/2BUS/87A | D29/22/310/GDA | D29/22/310/PHA | D29/22/330/GDA | D29/22/330/PHA | D29/22/340/PHA | D29/22/340/GDA
D29 | 府城DS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/D29_A1 | [17 empty] | com_alarm_2 | OPRD1: D29//1DTR/TRF; OPRD2: D29//2DTR/TRF
D29 | 府城DS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/0/StaDev/PMA
D29 | 府城DS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/161/1750/CB
D29 | 府城DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/310/CB
D29 | 府城DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/11/320/CB
D29 | 府城DS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/161/1760/CB
D29 | 府城DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/330/CB
D29 | 府城DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/340/CB
D29 | 府城DS | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/310/81A
D29 | 府城DS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/11/320/81A
D29 | 府城DS | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/330/81A
D29 | 府城DS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/340/81A
D29 | 府城DS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/0/RTU/RTU_R_L
D29 | 府城DS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/0/StaDev/STUV
D29 | 府城DS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/0/StaDev/DCA
D29 | 府城DS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/0/StaDev/DCE
D29 | 府城DS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/ComPoint/CBA
D29 | 府城DS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/D29_D1 | [17 empty] | lamp2CC | OPRD1: D29/22/ComPoint/CBF

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo