## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E01 | 南科ES | 345 | 345kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | Locate Empty |  | 345KV #1BUS 電壓 | kV_-450_450(-2000_2000) | aaa | B2/E01_C | [8 empty] | 南科ES.345KV#1BUS_KV | 345KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | Locate Empty |  | 345KV #2BUS 電壓 | kV_-450_450(-2000_2000) | aab | B2/E01_C | [8 empty] | 南科ES.345KV#2BUS_KV | 345KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 1BUS | #1BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | Locate Empty | #1BUS 87B1A | 345KV #1BUS 87B1A |  |  | B2/E01_C | [8 empty] | 南科ES.345#1B_87A1 | 345KV #1BUS 第一組 87RY | BUS |  |  |  |  | CDC | 4 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 1BUS | #1BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | Locate Empty | #1BUS 87B2A | 345KV #1BUS 87B2A |  |  | B2/E01_C | [8 empty] | 南科ES.345#1B_87A2 | 345KV #1BUS 第二組 87RY | BUS |  |  |  |  | CDC | 5 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 2BUS | #2BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | Locate Empty | #2BUS 87B1A | 345KV #2BUS 87B1A |  |  | B2/E01_C | [8 empty] | 南科ES.345#2B_87A1 | 345KV #2BUS 第一組 87RY | BUS |  |  |  |  | CDC | 6 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 2BUS | #2BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | Locate Empty | #2BUS 87B2A | 345KV #2BUS 87B2A |  |  | B2/E01_C | [8 empty] | 南科ES.345#2B_87A2 | 345KV #2BUS 第二組 87RY | BUS |  |  |  |  | CDC | 7 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 3510 | 瓦 | 新嘉民南科二路 3510 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3510_MW | 新嘉民二路 MW | LINE345 |  | CDC_Mon1_DPC,DNP_AI_Mon1_DPC |  |  | CDC | 8 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 3510 | 乏 | 新嘉民南科二路 3510 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3510_MVAR | 新嘉民二路 MVAR | LINE345 |  | CDC_Mon1_DPC,DNP_AI_Mon1_DPC |  |  | CDC | 9 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 3510 | PD | 新嘉民南科二路 3510 PD | kV_-450_450(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.3510LPD_KV | 新嘉民二路(3510) LPD KV | LINE345 |  |  |  |  | CDC | 10 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 3540 | 瓦 | 嘉民二路 3540 瓦(備用) | MW_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3540_MW | 嘉民二路 MW | LINE345 |  |  |  |  | CDC | 11 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 3540 | 乏 | 嘉民二路 3540 乏(備用) | MVAR_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3540_MVAR | 嘉民二路 MVAR | LINE345 |  |  |  |  | CDC | 12 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 3540 | PD | 嘉民二路 3540 PD(備用) | kV_-450_450(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.3540LPD_KV | 嘉民二路(3540) LPD KV | LINE345 |  |  |  |  | CDC | 13 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 3570 | 瓦 | 新嘉民南科一路 3570 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3570_MW | 新嘉民一路 MW | LINE345 |  |  |  |  | CDC | 14 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 3570 | 乏 | 新嘉民南科一路 3570 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3570_MVAR | 新嘉民一路 MVAR | LINE345 |  |  |  |  | CDC | 15 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 3570 | PD | 新嘉民南科一路 3570 PD | kV_-450_450(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.3570LPD_KV | 新嘉民一路(3570) LPD KV | LINE345 |  |  |  |  | CDC | 16 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 3610 | 瓦 | 南科龍崎一路 3610 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3610_MW | 龍崎一路 MW | LINE345 |  |  |  |  | CDC | 17 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 3610 | 乏 | 南科龍崎一路 3610 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3610_MVAR | 龍崎一路 MVAR | LINE345 |  |  |  |  | CDC | 18 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 3610 | PD | 南科龍崎一路 3610 PD | kV_-450_450(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.3610LPD_KV | 龍崎一路(3610) LPD KV | LINE345 |  |  |  |  | CDC | 19 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 3640 | 瓦 | 嘉民二路 3640 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3640_MW | 嘉民一路 MW | LINE345 |  |  |  |  | CDC | 20 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 3640 | 乏 | 嘉民二路 3640 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3640_MVAR | 嘉民一路 MVAR | LINE345 |  |  |  |  | CDC | 21 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 3640 | PD | 嘉民二路 3640 PD | kV_-450_450(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.3640LPD_KV | 嘉民一路(3640) LPD KV | LINE345 |  |  |  |  | CDC | 22 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 3670 | 瓦 | 南科龍崎二路 3670 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3670_MW | 龍崎二路 MW | LINE345 |  |  |  |  | CDC | 23 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 3670 | 乏 | 南科龍崎二路 3670 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E01_C |  |  | 2000 | [5 empty] | 南科ES.3670_MVAR | 龍崎二路 MVAR | LINE345 |  |  |  |  | CDC | 24 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 3670 | PD | 南科龍崎二路 3670 PD | kV_-450_450(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.3670LPD_KV | 龍崎二路(3670) LPD KV | LINE345 |  |  |  |  | CDC | 25 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 3510 | SSA | 新嘉民南科二路 3510 #1SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_SSA1 | 新嘉民二路(3510)#1(87L+21S)RY | LINE345 |  |  |  |  | CDC | 26 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 3540 | PHA | 嘉民南科二路(3640) 相間RY |  |  | B2/E01_C | [8 empty] | 南科ES.3540_PHA | 嘉民南科二路(3540) 相間RY | LINE345 |  |  |  |  | CDC | 27 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 3540 | GDA | 嘉民南科二路(3640) 接地RY |  |  | B2/E01_C | [8 empty] | 南科ES.3540_GDA | 嘉民南科二路(3540) 接地RY | LINE345 |  |  |  |  | CDC | 28 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 3570 | SSA | 新嘉民南科一路 3570 #1SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_SSA1 | 新嘉民一路(3570)#1(87L+21S)RY | LINE345 |  |  |  |  | CDC | 29 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 3610 | SSA | 南科龍崎一路 3610 #1SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3610_SSA1 | 龍崎一路(3610) #1(87L+21S)RY | LINE345 |  |  |  |  | CDC | 30 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 3640 | PHA | 嘉民南科一路(3640) 相間RY |  |  | B2/E01_C | [8 empty] | 南科ES.3640_PHA | 嘉民南科一路(3640) 相間RY | LINE345 |  |  |  |  | CDC | 31 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 3640 | GDA | 嘉民南科一路(3640) 接地RY |  |  | B2/E01_C | [8 empty] | 南科ES.3640_GDA | 嘉民南科一路(3640) 接地RY | LINE345 |  |  |  |  | CDC | 32 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 3670 | SSA | 南科龍崎二路 3670 #1SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3670_SSA1 | 龍崎二路(3670) #1(87L+21S)RY | LINE345 |  |  |  |  | CDC | 33 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 3510 | SSA | 新嘉民南科二路 3510 #2SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_SSA2 | 新嘉民二路(3510)#2測距(21)RY | LINE345 |  |  |  |  | CDC | 34 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0341 |  |  | 1-31-05 |  |  | 3510 | #1RYFA | 新嘉民南科二路 3510 #1RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_RYFA1 | 新嘉民二路(3510)第一套RY故障 | LINE345 |  |  |  |  | CDC | 35 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0343 |  |  | 1-31-07 |  |  | 3510 | #2RYFA | 新嘉民南科二路 3510 #2RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_RYFA2 | 新嘉民二路(3510)第二套RY故障 | LINE345 |  |  |  |  | CDC | 36 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0339 |  | 0033 | 1-31-03 |  | 1-21 | 3510 | 79RY U/L | 新嘉民南科二路 3510 79RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.3510_79UL | 新嘉民二路(3510) 79RY U/L | LINE345 |  |  |  |  | CDC | 37 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 3570 | SSA | 新嘉民南科一路 3570 #2SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_SSA2 | 新嘉民一路(3570)#2測距(21)RY | LINE345 |  |  |  |  | CDC | 38 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0356 |  |  | 1-32-04 |  |  | 3570 | #1RYFA | 新嘉民南科一路 3570 #1RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_RYFA1 | 新嘉民一路(3570)第一套RY故障 | LINE345 |  |  |  |  | CDC | 39 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0358 |  |  | 1-32-06 |  |  | 3570 | #2RYFA | 新嘉民南科一路 3570 #2RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_RYFA2 | 新嘉民一路(3570)第二套RY故障 | LINE345 |  |  |  |  | CDC | 40 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0354 |  | 0035 | 1-32-02 |  | 1-23 | 3570 | 79RY U/L | 新嘉民南科一路 3570 79RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.3570_79UL | 新嘉民一路(3570) 79RY U/L | LINE345 |  |  |  |  | CDC | 41 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 3610 | SSA | 南科龍崎一路 3610 #2SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3610_SSA2 | 龍崎一路(3610) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 42 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0351 |  |  | 1-31-15 |  |  | 3610 | #1RYFA | 南科龍崎一路 3610 #1數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.3610_RYFA1 | 龍崎一路(3610) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 43 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0353 |  |  | 1-32-01 |  |  | 3610 | #2RYFA | 南科龍崎一路 3610 #2數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.3610_RYFA2 | 龍崎一路(3610) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 44 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0349 |  | 0036 | 1-31-13 |  | 1-24 | 3610 | 79RY U/L | 南科龍崎一路 3610 79RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.3610_79UL | 龍崎一路(3610) 79RY U/L | LINE345 |  |  |  |  | CDC | 45 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 3670 | SSA | 南科龍崎二路 3670 #2SSA |  |  | B2/E01_C | [8 empty] | 南科ES.3670_SSA2 | 龍崎二路(3670) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 46 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0361 |  |  | 1-32-09 |  |  | 3670 | #1RYFA | 南科龍崎二路 3670 #1數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.3670_RYFA1 | 龍崎二路(3670) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 47 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0363 |  |  | 1-32-11 |  |  | 3670 | #2RYFA | 南科龍崎二路 3670 #2數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.3670_RYFA2 | 龍崎二路(3670) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 48 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0359 |  | 0038 | 1-32-07 |  | 1-26 | 3670 | 79RY U/L | 南科龍崎二路 3670 79RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.3670_79UL | 龍崎二路(3670) 79RY U/L | LINE345 |  |  |  |  | CDC | 49 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | DS1 | 3511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0480 | 481 | 0063 | 1-34-00 | 1-34-01 | 1-3F | 3511 | ON/OFF | 新嘉民南科二路 3511 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3511_DS | 3511(新嘉民二路) DS | LINE345 |  |  |  |  | CDC | 50 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | DS2 | 3512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0482 | 483 | 0064 | 1-34-02 | 1-34-03 | 1-40 | 3512 | ON/OFF | 新嘉民南科二路 3512 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3512_DS | 3512(新嘉民二路) DS | LINE345 |  |  |  |  | CDC | 51 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | DS1 | 3541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0494 | 495 | 0070 | 1-34-14 | 1-34-15 | 1-46 | 3541 | ON/OFF | 嘉民二路 3541 DS(備用) |  |  | B2/E01_C | [8 empty] | 南科ES.3541_DS | 3541(嘉民二路) DS | LINE345 |  |  |  |  | CDC | 52 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | DS2 | 3542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0496 | 497 | 0071 | 1-35-00 | 1-35-01 | 1-47 | 3542 | ON/OFF | 嘉民二路 3542 DS(備用) |  |  | B2/E01_C | [8 empty] | 南科ES.3542_DS | 3542(嘉民二路) DS | LINE345 |  |  |  |  | CDC | 53 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | DS1 | 3571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0508 | 509 | 0077 | 1-35-12 | 1-35-13 | 1-4D | 3571 | ON/OFF | 新嘉民南科一路 3571 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3571_DS | 3571(新嘉民一路) DS | LINE345 |  |  |  |  | CDC | 54 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | DS2 | 3572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0510 | 511 | 0078 | 1-35-14 | 1-35-15 | 1-4E | 3572 | ON/OFF | 新嘉民南科一路 3572 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3572_DS | 3572(新嘉民一路) DS | LINE345 |  |  |  |  | CDC | 55 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | DS1 | 3611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0522 | 523 | 0084 | 1-36-10 | 1-36-11 | 1-54 | 3611 | ON/OFF | 南科龍崎一路 3611 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3611_DS | 3611(龍崎一路) DS | LINE345 |  |  |  |  | CDC | 56 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | DS2 | 3612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0524 | 525 | 0085 | 1-36-12 | 1-36-13 | 1-55 | 3612 | ON/OFF | 南科龍崎一路 3612 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3612_DS | 3612(龍崎一路) DS | LINE345 |  |  |  |  | CDC | 57 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | DS1 | 3641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0536 | 537 | 0091 | 1-37-08 | 1-37-09 | 1-5B | 3641 | ON/OFF | 嘉民二路 3641 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3641_DS | 3641(嘉民一路) DS | LINE345 |  |  |  |  | CDC | 58 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | DS2 | 3642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0538 | 539 | 0092 | 1-37-10 | 1-37-11 | 1-5C | 3642 | ON/OFF | 嘉民二路 3642 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3642_DS | 3642(嘉民一路) DS | LINE345 |  |  |  |  | CDC | 59 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | DS1 | 3671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0550 | 551 | 0098 | 1-38-06 | 1-38-07 | 1-62 | 3671 | ON/OFF | 南科龍崎二路 3671 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3671_DS | 3671(龍崎二路) DS | LINE345 |  |  |  |  | CDC | 60 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | DS2 | 3672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0552 | 553 | 0099 | 1-38-08 | 1-38-09 | 1-63 | 3672 | ON/OFF | 南科龍崎二路 3672 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3672_DS | 3672(龍崎二路) DS | LINE345 |  |  |  |  | CDC | 61 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E03E012/T2 |  |  | 0000 |  | 0001 | 1-00-00 |  | 1-01 | 3510 | ON/OFF | 新嘉民南科二路 3510 CB |  | aaaa | B2/E01_C | [8 empty] | 南科ES.3510_CB | 3510(新嘉民二路) CB | LINE345 |  |  |  |  | CDC | 62 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | ES2 | 3512E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0484 | 485 | 0065 | 1-34-04 | 1-34-05 | 1-41 | 3512E | ON/OFF | 新嘉民南科二路 3512E DS |  |  | B2/E01_C | [8 empty] | 南科ES.3512E_ES | 3512E(新嘉民二路) ES | LINE345 |  |  |  |  | CDC | 63 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3510LE | 3510LE (非取樣點) | LINE345 | [5 empty] | 64 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3510BE | 3510BE (非取樣點) | LINE345 | [5 empty] | 65 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/嘉民二路/T2 |  |  | 0003 |  | 0004 | 1-00-03 |  | 1-04 | 3540 | ON/OFF | 嘉民二路 3540 CB(備用) |  | aaba | B2/E01_C | [8 empty] | 南科ES.3540_CB | 3540(嘉民二路) CB | LINE345 |  |  |  |  | CDC | 66 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | ES2 | 3542E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0498 | 499 | 0072 | 1-35-02 | 1-35-03 | 1-48 | 3542E | ON/OFF | 嘉民二路 3542E DS(備用) |  |  | B2/E01_C | [8 empty] | 南科ES.3542E_ES | 3542E(嘉民二路) ES | LINE345 |  |  |  |  | CDC | 67 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3540LE | 3540LE (非取樣點) | LINE345 | [5 empty] | 68 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3540BE | 3540BE (非取樣點) | LINE345 | [5 empty] | 69 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E03E011/T2 |  |  | 0006 |  | 0007 | 1-00-06 |  | 1-07 | 3570 | ON/OFF | 新嘉民南科一路 3570 CB |  | aaca | B2/E01_C | [8 empty] | 南科ES.3570_CB | 3570(新嘉民一路) CB | LINE345 |  |  |  |  | CDC | 70 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | ES2 | 3572E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0512 | 513 | 0079 | 1-36-00 | 1-36-01 | 1-4F | 3572E | ON/OFF | 新嘉民南科一路 3572E DS |  |  | B2/E01_C | [8 empty] | 南科ES.3572E_ES | 3572E(新嘉民一路) ES | LINE345 |  |  |  |  | CDC | 71 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3570LE | 3570LE (非取樣點) | LINE345 | [5 empty] | 72 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3570BE | 3570BE (非取樣點) | LINE345 | [5 empty] | 73 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E01E021/T1 |  |  | 0009 |  | 0010 | 1-01-01 |  | 1-0A | 3610 | ON/OFF | 南科龍崎一路 3610 CB |  | aada | B2/E01_C | [8 empty] | 南科ES.3610_CB | 3610(龍崎一路) CB | LINE345 |  |  |  |  | CDC | 74 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | ES2 | 3612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0526 | 527 | 0086 | 1-36-14 | 1-36-15 | 1-56 | 3612E | ON/OFF | 南科龍崎一路 3612E DS |  |  | B2/E01_C | [8 empty] | 南科ES.3612E_ES | 3612E(龍崎一路) ES | LINE345 |  |  |  |  | CDC | 75 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3610LE | 3610LE (非取樣點) | LINE345 | [5 empty] | 76 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3610BE | 3610BE (非取樣點) | LINE345 | [5 empty] | 77 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/嘉民一路/T2 |  |  | 0012 |  | 0013 | 1-01-04 |  | 1-0D | 3640 | ON/OFF | 嘉民二路 3640 CB |  | aaea | B2/E01_C | [8 empty] | 南科ES.3640_CB | 3640(嘉民一路) CB | LINE345 |  |  |  |  | CDC | 78 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | ES2 | 3642E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0540 | 541 | 0093 | 1-37-12 | 1-37-13 | 1-5D | 3642E | ON/OFF | 嘉民二路 3642E DS |  |  | B2/E01_C | [8 empty] | 南科ES.3642E_ES | 3642E(嘉民一路) ES | LINE345 |  |  |  |  | CDC | 79 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3640LE | 3640LE (非取樣點) | LINE345 | [5 empty] | 80 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3640BE | 3640BE (非取樣點) | LINE345 | [5 empty] | 81 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E01E022/T1 |  |  | 0015 |  | 0016 | 1-01-07 |  | 1-10 | 3670 | ON/OFF | 南科龍崎二路 3670 CB |  | aafa | B2/E01_C | [8 empty] | 南科ES.3670_CB | 3670(龍崎二路) CB | LINE345 |  |  |  |  | CDC | 82 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | ES2 | 3672E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0554 | 555 | 0100 | 1-38-10 | 1-38-11 | 1-64 | 3672E | ON/OFF | 南科龍崎二路 3672E DS |  |  | B2/E01_C | [8 empty] | 南科ES.3672E_ES | 3672E(龍崎二路) ES | LINE345 |  |  |  |  | CDC | 83 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3670LE | 3670LE (非取樣點) | LINE345 | [5 empty] | 84 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3670BE | 3670BE (非取樣點) | LINE345 | [5 empty] | 85 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3520 | TIE(3520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3510 | A/3530 |  |  | 0001 |  | 0002 | 1-00-01 |  | 1-02 | 3520 | ON/OFF | 七股紅線 3520 CB |  | aaab | B2/E01_C | [8 empty] | 南科ES.3520_CB | 3520 CB | LINE345 |  |  |  |  | CDC | 86 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3520 | TIE(3520) |  | E1 | 3521E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3521E | 3521E (非取樣點) | LINE345 | [5 empty] | 87 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3520 | TIE(3520) |  | E2 | 3522E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3522E | 3522E (非取樣點) | LINE345 | [5 empty] | 88 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3550 | TIE(3550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3540 | A/3560 |  |  | 0004 |  | 0005 | 1-00-04 |  | 1-05 | 3550 | ON/OFF | 嘉民二路 3550 CB(備用) |  | aabb | B2/E01_C | [8 empty] | 南科ES.3550_CB | 3550 CB | LINE345 |  |  |  |  | CDC | 89 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3550 | TIE(3550) |  | E1 | 3551E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3551E | 3551E (非取樣點) | LINE345 | [5 empty] | 90 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3550 | TIE(3550) |  | E2 | 3552E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3552E | 3552E (非取樣點) | LINE345 | [5 empty] | 91 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3580 | TIE(3580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3570 | A/3590 |  |  | 0007 |  | 0008 | 1-00-07 |  | 1-08 | 3580 | ON/OFF | 七股白線 3580 CB |  | aacb | B2/E01_C | [8 empty] | 南科ES.3580_CB | 3580 CB | LINE345 |  |  |  |  | CDC | 92 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3580 | TIE(3580) |  | E1 | 3581E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3581E | 3581E (非取樣點) | LINE345 | [5 empty] | 93 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3580 | TIE(3580) |  | E2 | 3582E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3582E | 3582E (非取樣點) | LINE345 | [5 empty] | 94 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3620 | TIE(3620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3610 | A/3630 |  |  | 0010 |  | 0011 | 1-01-02 |  | 1-0B | 3620 | ON/OFF | 南科龍崎一路 3620 CB |  | aadb | B2/E01_C | [8 empty] | 南科ES.3620_CB | 3620 CB | LINE345 |  |  |  |  | CDC | 95 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3620 | TIE(3620) |  | E1 | 3621E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3621E | 3621E (非取樣點) | LINE345 | [5 empty] | 96 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3620 | TIE(3620) |  | E2 | 3622E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3622E | 3622E (非取樣點) | LINE345 | [5 empty] | 97 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3650 | TIE(3650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3640 | A/3660 |  |  | 0013 |  | 0014 | 1-01-05 |  | 1-0E | 3650 | ON/OFF | 嘉民一路 3650 CB |  | aaeb | B2/E01_C | [8 empty] | 南科ES.3650_CB | 3650 CB | LINE345 |  |  |  |  | CDC | 98 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3650 | TIE(3650) |  | E1 | 3651E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3651E | 3651E (非取樣點) | LINE345 | [5 empty] | 99 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3650 | TIE(3650) |  | E2 | 3652E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3652E | 3652E (非取樣點) | LINE345 | [5 empty] | 100 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3680 | TIE(3680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3670 | A/3690 |  |  | 0016 |  | 0017 | 1-02-00 |  | 1-11 | 3680 | ON/OFF | 南科龍崎二路 3680 CB |  | aafb | B2/E01_C | [8 empty] | 南科ES.3680_CB | 3680 CB | LINE345 |  |  |  |  | CDC | 101 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3680 | TIE(3680) |  | E1 | 3681E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3681E | 3681E (非取樣點) | LINE345 | [5 empty] | 102 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3680 | TIE(3680) |  | E2 | 3682E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3682E | 3682E (非取樣點) | LINE345 | [5 empty] | 103 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3520 | TIE(3520) |  | DS1 | 3521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0486 | 487 | 0066 | 1-34-06 | 1-34-07 | 1-42 | 3521 | ON/OFF | 七股紅線 3521 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3521_DS | 3521 DS | LINE345 |  |  |  |  | CDC | 104 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3520 | TIE(3520) |  | DS2 | 3522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0488 | 489 | 0067 | 1-34-08 | 1-34-09 | 1-43 | 3522 | ON/OFF | 七股紅線 3522 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3522_DS | 3522 DS | LINE345 |  |  |  |  | CDC | 105 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3550 | TIE(3550) |  | DS1 | 3551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0500 | 501 | 0073 | 1-35-04 | 1-35-05 | 1-49 | 3551 | ON/OFF | 嘉民二路 3551 DS(備用) |  |  | B2/E01_C | [8 empty] | 南科ES.3551_DS | 3551 DS | LINE345 |  |  |  |  | CDC | 106 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3550 | TIE(3550) |  | DS2 | 3552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0502 | 503 | 0074 | 1-35-06 | 1-35-07 | 1-4A | 3552 | ON/OFF | 嘉民二路3552 DS(備用) |  |  | B2/E01_C | [8 empty] | 南科ES.3552_DS | 3552 DS | LINE345 |  |  |  |  | CDC | 107 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3580 | TIE(3580) |  | DS1 | 3581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0514 | 515 | 0080 | 1-36-02 | 1-36-03 | 1-50 | 3581 | ON/OFF | 七股白線 3581 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3581_DS | 3581 DS | LINE345 |  |  |  |  | CDC | 108 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3580 | TIE(3580) |  | DS2 | 3582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0516 | 517 | 0081 | 1-36-04 | 1-36-05 | 1-51 | 3582 | ON/OFF | 七股白線 3582 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3582_DS | 3582 DS | LINE345 |  |  |  |  | CDC | 109 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3620 | TIE(3620) |  | DS1 | 3621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0528 | 529 | 0087 | 1-37-00 | 1-37-01 | 1-57 | 3621 | ON/OFF | 南科龍崎一路 3621 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3621_DS | 3621 DS | LINE345 |  |  |  |  | CDC | 110 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3620 | TIE(3620) |  | DS2 | 3622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0530 | 531 | 0088 | 1-37-02 | 1-37-03 | 1-58 | 3622 | ON/OFF | 南科龍崎一路 3622 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3622_DS | 3622 DS | LINE345 |  |  |  |  | CDC | 111 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3650 | TIE(3650) |  | DS1 | 3651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0542 | 543 | 0094 | 1-37-14 | 1-37-15 | 1-5E | 3651 | ON/OFF | 嘉民一路 3651 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3651_DS | 3651 DS | LINE345 |  |  |  |  | CDC | 112 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3650 | TIE(3650) |  | DS2 | 3652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0544 | 545 | 0095 | 1-38-00 | 1-38-01 | 1-5F | 3652 | ON/OFF | 嘉民一路 3652 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3652_DS | 3652 DS | LINE345 |  |  |  |  | CDC | 113 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3680 | TIE(3680) |  | DS1 | 3681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0556 | 557 | 0101 | 1-38-12 | 1-38-13 | 1-65 | 3681 | ON/OFF | 南科龍崎二路 3681 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3681_DS | 3681 DS | LINE345 |  |  |  |  | CDC | 114 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3680 | TIE(3680) |  | DS2 | 3682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0558 | 559 | 0102 | 1-38-14 | 1-38-15 | 1-66 | 3682 | ON/OFF | 南科龍崎二路 3682 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3682_DS | 3682 DS | LINE345 |  |  |  |  | CDC | 115 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | Locate Empty | 瓦 | #1ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#1ATR_MW | #1ATR二次側 MW | ATR |  |  |  |  | CDC | 116 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | Locate Empty | 乏 | #1ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#1ATR_MVAR | #1ATR二次側 MVAR | ATR |  |  |  |  | CDC | 117 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | Locate Empty | 瓦 | #2ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#2ATR_MW | #2ATR二次側 MW | ATR |  |  |  |  | CDC | 118 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | Locate Empty | 乏 | #2ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#2ATR_MVAR | #2ATR二次側 MVAR | ATR |  |  |  |  | CDC | 119 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | Locate Empty | 瓦 | #3ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#3ATR_MW | #3ATR二次側 MW | ATR |  |  |  |  | CDC | 120 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | Locate Empty | 乏 | #3ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#3ATR_MVAR | #3ATR二次側 MVAR | ATR |  |  |  |  | CDC | 121 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | Locate Empty | 瓦 | #4ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#4ATR_MW | #4ATR二次側 MW | ATR |  |  |  |  | CDC | 122 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | Locate Empty | 乏 | #4ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#4ATR_MVAR | #4ATR二次側 MVAR | ATR |  |  |  |  | CDC | 123 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | Locate Empty | 瓦 | #5ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#5ATR_MW | #5ATR二次側 MW | ATR |  |  |  |  | CDC | 124 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | Locate Empty | 乏 | #5ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#5ATR_MVAR | #5ATR二次側 MVAR | ATR |  |  |  |  | CDC | 125 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | Locate Empty | 瓦 | #6ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#6ATR_MW | #6ATR二次側 MW | ATR |  |  |  |  | CDC | 126 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | Locate Empty | 乏 | #6ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E01_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 南科ES.#6ATR_MVAR | #6ATR二次側 MVAR | ATR |  |  |  |  | CDC | 127 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES |  |  | 1ATR | #1ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0018 |  | 0042 | 1-92 |  | 1-2A | Locate Empty | TAP 位置 | #1ATR TAP 位置 | TAP_-5.5_10.5(0_2000) |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_TAP | #1ATR OLTC TAP | ATR |  |  |  |  | CDC | 128 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES |  |  | 1ATR | #1ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | Locate Empty | 油溫 | #1ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_OIL_R | #1ATR R相油溫 | ATR |  |  |  |  | CDC | 129 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 1ATR | #1ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | Locate Empty | 線溫 | #1ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_COIL_R | #1ATR R相線溫 | ATR |  |  |  |  | CDC | 130 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 2ATR | #2ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0023 |  | 0046 | 1-97 |  | 1-2E | Locate Empty | TAP 位置 | #2ATR TAP 位置 | TAP_-5.5_10.5(0_2000) |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_TAP | #2ATR OLTC TAP | ATR |  |  |  |  | CDC | 131 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES |  |  | 2ATR | #2ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | Locate Empty | 油溫 | #2ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_OIL_R | #2ATR R相油溫 | ATR |  |  |  |  | CDC | 132 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 2ATR | #2ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | Locate Empty | 線溫 | #2ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_COIL_R | #2ATR R相線溫 | ATR |  |  |  |  | CDC | 133 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 3ATR | #3ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0028 |  | 0050 | 1-9C |  | 1-32 | Locate Empty | TAP 位置 | #3ATR TAP 位置 | TAP_-5.5_10.5(0_2000) |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_TAP | #3ATR OLTC TAP | ATR |  |  |  |  | CDC | 134 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES |  |  | 3ATR | #3ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | Locate Empty | 油溫 | #3ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_OIL_R | #3ATR R相油溫 | ATR |  |  |  |  | CDC | 135 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 3ATR | #3ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | Locate Empty | 線溫 | #3ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_COIL_R | #3ATR R相線溫 | ATR |  |  |  |  | CDC | 136 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 4ATR | #4ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0033 |  | 0054 | 1-A1 |  | 1-36 | Locate Empty | TAP 位置 | #4ATR TAP 位置 | TAP_-5.5_10.5(0_2000) |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_TAP | #4ATR OLTC TAP | ATR |  |  |  |  | CDC | 137 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES |  |  | 4ATR | #4ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | Locate Empty | 油溫 | #4ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_OIL_R | #4ATR R相油溫 | ATR |  |  |  |  | CDC | 138 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 4ATR | #4ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | Locate Empty | 線溫 | #4ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_COIL_R | #4ATR R相線溫 | ATR |  |  |  |  | CDC | 139 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 5ATR | #5ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0038 |  | 0058 | 1-A6 |  | 1-3A | Locate Empty | TAP 位置 | #5ATR TAP 位置 | TAP_-5.5_10.5(0_2000) |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_TAP | #5ATR OLTC TAP | ATR |  |  |  |  | CDC | 140 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES |  |  | 5ATR | #5ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | Locate Empty | 油溫 | #5ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_OIL_R | #5ATR R相油溫 | ATR |  |  |  |  | CDC | 141 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 5ATR | #5ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | Locate Empty | 線溫 | #5ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_COIL_R | #5ATR R相線溫 | ATR |  |  |  |  | CDC | 142 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 6ATR | #6ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0043 |  | 0062 | 1-AB |  | 1-3E | Locate Empty | TAP 位置 | #6ATRTAP 位置 | TAP_-5.5_10.5(0_2000) |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_TAP | #6ATR OLTC TAP | ATR |  |  |  |  | CDC | 143 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES |  |  | 6ATR | #6ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | Locate Empty | 油溫 | #6ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_OIL_R | #6ATR R相油溫 | ATR |  |  |  |  | CDC | 144 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES |  |  | 6ATR | #6ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | Locate Empty | 線溫 | #6ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_COIL_R | #6ATR R相線溫 | ATR |  |  |  |  | CDC | 145 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | T/1ATR345 | B/2Bus |  |  | 0002 |  | 0003 | 1-00-02 |  | 1-03 | 3530 | ON/OFF | 七股紅線 3530 CB |  | aaac | B2/E01_C | [8 empty] | 南科ES.3530_CB | 3530(#1ATR) CB | ATR |  |  |  |  | CDC | 146 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3530TE | 3530TE (非取樣點) | ATR | [5 empty] | 147 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3530BE | 3530BE (非取樣點) | ATR | [5 empty] | 148 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | E1 | 3531E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3531E | #1ATR 3531E ES(非取樣點) | ATR | [5 empty] | 149 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1ATR161 |  | 0032 |  | 0019 | 1-04-00 |  | 1-13 | #1ATR | ON/OFF | #1ATR 1810 CB |  | aaea | B3/E01_C | [8 empty] | 南科ES.1810_CB | 1810(#1ATR) CB | ATR |  |  |  |  | CDC | 150 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/2ATR345 | B/2Bus |  |  | 0005 |  | 0006 | 1-00-05 |  | 1-06 | 3560 | ON/OFF | 二號主變3560 CB |  | aabc | B2/E01_C | [8 empty] | 南科ES.3560_CB | 3560(#2ATR) CB | ATR |  |  |  |  | CDC | 151 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3560TE | 3560TE (非取樣點) | ATR | [5 empty] | 152 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3560BE | 3560BE (非取樣點) | ATR | [5 empty] | 153 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2ATR161 |  | 0038 |  | 0021 | 1-04-06 |  | 1-15 | #2ATR | ON/OFF | #2ATR 1820 CB |  | aaja | B3/E01_C | [8 empty] | 南科ES.1820_CB | 1820(#2ATR) CB | ATR |  |  |  |  | CDC | 154 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/3ATR345 | B/2Bus |  |  | 0008 |  | 0009 | 1-01-00 |  | 1-09 | 3590 | ON/OFF | 七股白線 3590 CB |  | aacc | B2/E01_C | [8 empty] | 南科ES.3590_CB | 3590(#3ATR) CB | ATR |  |  |  |  | CDC | 155 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3590TE | 3590TE (非取樣點) | ATR | [5 empty] | 156 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3590BE | 3590BE (非取樣點) | ATR | [5 empty] | 157 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | T/3ATR161 |  |  | 0071 |  | 0020 | 1-08-07 |  | 1-14 | #3ATR | ON/OFF | #3ATR 1830 CB |  | aala | B3/E01_C | [8 empty] | 南科ES.1830_CB | 1830(#3ATR) CB | ATR |  |  |  |  | CDC | 158 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3ATR161 |  | 0044 |  | 0023 | 1-05-04 |  | 1-17 | #3ATR | ON/OFF | #3ATR 1840 CB |  | aama | B3/E01_C | [8 empty] | 南科ES.1840_CB | 1840(#3ATR) CB | ATR |  |  |  |  | CDC | 159 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/4ATR345 | B/2Bus |  |  | 0011 |  | 0012 | 1-01-03 |  | 1-0C | 3630 | ON/OFF | 南科龍崎一路 3630 CB |  | aadc | B2/E01_C | [8 empty] | 南科ES.3630_CB | 3630(#4ATR) CB | ATR |  |  |  |  | CDC | 160 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3630TE | 3630TE (非取樣點) | ATR | [5 empty] | 161 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3630BE | 3630BE (非取樣點) | ATR | [5 empty] | 162 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/3Bus | T/4ATR161 |  |  | 0050 |  | 0025 | 1-06-02 |  | 1-19 | #4ATR | ON/OFF | #4ATR 1850 CB |  | abea | B3/E01_C | [8 empty] | 南科ES.1850_CB | 1850(#4ATR) CB | ATR |  |  |  |  | CDC | 163 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/4ATR161 |  | 0051 |  | 0026 | 1-06-03 |  | 1-1A | #4ATR | ON/OFF | #4ATR 1860 CB |  | abfa | B3/E01_C | [8 empty] | 南科ES.1860_CB | 1860(#4ATR) CB | ATR |  |  |  |  | CDC | 164 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/5ATR345 | B/2Bus |  |  | 0014 |  | 0015 | 1-01-06 |  | 1-0F | 3660 | ON/OFF | 嘉民一路 3660 CB |  | aaec | B2/E01_C | [8 empty] | 南科ES.3660_CB | 3660(#5ATR) CB | ATR |  |  |  |  | CDC | 165 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3660TE | 3660TE (非取樣點) | ATR | [5 empty] | 166 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3660BE | 3660BE (非取樣點) | ATR | [5 empty] | 167 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/3Bus | T/5ATR161 |  |  | 0057 |  | 0027 | 1-07-01 |  | 1-1B | #5ATR | ON/OFF | #5ATR 1870 CB |  | abja | B3/E01_C | [8 empty] | 南科ES.1870_CB | 1870(#5ATR) CB | ATR |  |  |  |  | CDC | 168 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/5ATR161 |  | 0058 |  | 0028 | 1-07-02 |  | 1-1C | #5ATR | ON/OFF | #5ATR 1880 CB |  | abka | B3/E01_C | [8 empty] | 南科ES.1880_CB | 1880(#5ATR) CB | ATR |  |  |  |  | CDC | 169 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | T/6ATR345 | B/2Bus |  |  | 0017 |  | 0018 | 1-02-01 |  | 1-12 | 3690 | ON/OFF | 南科龍崎二路 3690 CB |  | aafc | B2/E01_C | [8 empty] | 南科ES.3690_CB | 3690(#6ATR) CB | ATR |  |  |  |  | CDC | 170 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3690TE | 3690TE (非取樣點) | ATR | [5 empty] | 171 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3690BE | 3690BE (非取樣點) | ATR | [5 empty] | 172 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | E1 | 3691E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E01_C | [8 empty] | 南科ES.3691E | #6ATR 3691E ES(非取樣點) | ATR | [5 empty] | 173 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/3Bus | T/6ATR161 |  |  | 0064 |  | 0030 | 1-08-00 |  | 1-1E | #6ATR | ON/OFF | #6ATR 1910 CB |  | abqa | B3/E01_C | [8 empty] | 南科ES.1910_CB | 1910(#6ATR) CB | ATR |  |  |  |  | CDC | 174 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/6ATR161 |  | 0065 |  | 0031 | 1-08-01 |  | 1-1F | #6ATR | ON/OFF | #6ATR 1920 CB |  | abra | B3/E01_C | [8 empty] | 南科ES.1920_CB | 1920(#6ATR) CB | ATR |  |  |  |  | CDC | 175 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | #1ATR | 871A | #1ATR 871A |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_87A1 | #1ATR 第一組 87RY | ATR |  |  |  |  | CDC | 176 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | #1ATR | 872A | #1ATR 872A |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_87A2 | #1ATR 第二組 87RY | ATR |  |  |  |  | CDC | 177 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | #1ATR | 96PA | #1ATR 機械保護動作(96PA) |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_96PA | #1ATR 機械保護動作 | ATR |  |  |  |  | CDC | 178 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | #1ATR | 51ZA | #1ATR 51ZA |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_51ZA | #1ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 179 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | #1ATR | 59A | #1ATR 59A |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_59A | #1ATR 59RY | ATR |  |  |  |  | CDC | 180 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | #2ATR | 871A | #2ATR 871A |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_87A1 | #2ATR 第一組 87RY | ATR |  |  |  |  | CDC | 181 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | #2ATR | 872A | #2ATR 872A |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_87A2 | #2ATR 第二組 87RY | ATR |  |  |  |  | CDC | 182 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #2ATR | 96PA | #2ATR 機械保護動作(96PA) |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_96PA | #2ATR 機械保護動作 | ATR |  |  |  |  | CDC | 183 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | #2ATR | 51ZA | #2ATR 51ZA |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_51ZA | #2ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 184 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | #2ATR | 59A | #2ATR 59A |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_59A | #2ATR 59RY | ATR |  |  |  |  | CDC | 185 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #3ATR | 871A | #3ATR 871A |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_87A1 | #3ATR 第一組 87RY | ATR |  |  |  |  | CDC | 186 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #3ATR | 872A | #3ATR 872A |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_87A2 | #3ATR 第二組 87RY | ATR |  |  |  |  | CDC | 187 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #3ATR | 96PA | #3ATR 機械保護動作(96PA) |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_96PA | #3ATR 機械保護動作 | ATR |  |  |  |  | CDC | 188 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | #3ATR | 51ZA | #3ATR 51ZA |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_51ZA | #3ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 189 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | #3ATR | 59A | #3ATR 59A |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_59A | #3ATR 59RY | ATR |  |  |  |  | CDC | 190 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #4ATR | 871A | #4ATR 871A |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_87A1 | #4ATR 第一組 87RY | ATR |  |  |  |  | CDC | 191 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #4ATR | 872A | #4ATR 872A |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_87A2 | #4ATR 第二組 87RY | ATR |  |  |  |  | CDC | 192 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #4ATR | 96PA | #4ATR 機械保護動作(96PA) |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_96PA | #4ATR 機械保護動作 | ATR |  |  |  |  | CDC | 193 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #4ATR | 51ZA | #4ATR 51ZA |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_51ZA | #4ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 194 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | #4ATR | 59A | #4ATR 59A |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_59A | #4ATR 59RY | ATR |  |  |  |  | CDC | 195 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #5ATR | 871A | #5ATR 871A |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_87A1 | #5ATR 第一組 87RY | ATR |  |  |  |  | CDC | 196 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | #5ATR | 872A | #5ATR 872A |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_87A2 | #5ATR 第二組 87RY | ATR |  |  |  |  | CDC | 197 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #5ATR | 96PA | #5ATR 機械保護動作(96PA) |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_96PA | #5ATR 機械保護動作 | ATR |  |  |  |  | CDC | 198 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | #5ATR | 51ZA | #5ATR 51ZA |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_51ZA | #5ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 199 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | #5ATR | 59A | #5ATR 59A |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_59A | #5ATR 59RY | ATR |  |  |  |  | CDC | 200 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #6ATR | 871A | #6ATR 871A |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_87A1 | #6ATR 第一組 87RY | ATR |  |  |  |  | CDC | 201 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #6ATR | 872A | #6ATR 872A |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_87A2 | #6ATR 第二組 87RY | ATR |  |  |  |  | CDC | 202 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #6ATR | 96PA | #6ATR 機械保護動作(96PA) |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_96PA | #6ATR 機械保護動作 | ATR |  |  |  |  | CDC | 203 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | #6ATR | 51ZA | #6ATR 51ZA |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_51ZA | #6ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 204 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | #6ATR | 59A | #6ATR 59A |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_59A | #6ATR 59RY | ATR |  |  |  |  | CDC | 205 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0395 |  |  | 2-30-11 |  |  | Locate Empty | 96D | #1ATR 96D |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_96D | #1ATR 96D RY | ATR |  |  |  |  | CDC | 206 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0396 |  |  | 2-30-12 |  |  | Locate Empty | 96P | #1ATR 96P |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_96P | #1ATR 96P RY | ATR |  |  |  |  | CDC | 207 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0397 |  |  | 2-30-13 |  |  | Locate Empty | 63Q | #1ATR 63Q |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_63Q | #1ATR 63Q RY | ATR |  |  |  |  | CDC | 208 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0393 |  |  | 2-30-09 |  |  | Locate Empty | 96B1 | #1ATR 96B1 |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_96B1 | #1ATR 96B1 RY | ATR |  |  |  |  | CDC | 209 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0394 |  |  | 2-30-10 |  |  | Locate Empty | 96B2 | #1ATR 96B2 |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_96B2 | #1ATR 96B2 RY | ATR |  |  |  |  | CDC | 210 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0408 |  |  | 2-31-08 |  |  | Locate Empty | 96D | #2ATR 96D |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_96D | #2ATR 96D RY | ATR |  |  |  |  | CDC | 211 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0409 |  |  | 2-31-09 |  |  | Locate Empty | 96P | #2ATR 96P |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_96P | #2ATR 96P RY | ATR |  |  |  |  | CDC | 212 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0410 |  |  | 2-31-10 |  |  | Locate Empty | 63Q | #2ATR 63Q |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_63Q | #2ATR 63Q RY | ATR |  |  |  |  | CDC | 213 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0406 |  |  | 2-31-06 |  |  | Locate Empty | 96B1 | #2ATR 96B1 |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_96B1 | #2ATR 96B1 RY | ATR |  |  |  |  | CDC | 214 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0407 |  |  | 2-31-07 |  |  | Locate Empty | 96B2 | #2ATR 96B2 |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_96B2 | #2ATR 96B2 RY | ATR |  |  |  |  | CDC | 215 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0417 |  |  | 2-32-01 |  |  | Locate Empty | 96D | #3ATR 96D |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_96D | #3ATR 96D RY | ATR |  |  |  |  | CDC | 216 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0418 |  |  | 2-32-02 |  |  | Locate Empty | 96P | #3ATR 96P |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_96P | #3ATR 96P RY | ATR |  |  |  |  | CDC | 217 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0419 |  |  | 2-32-03 |  |  | Locate Empty | 63Q | #3ATR 63Q |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_63Q | #3ATR 63Q RY | ATR |  |  |  |  | CDC | 218 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0415 |  |  | 2-31-15 |  |  | Locate Empty | 96B1 | #3ATR 96B1 |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_96B1 | #3ATR 96B1 RY | ATR |  |  |  |  | CDC | 219 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0416 |  |  | 2-32-00 |  |  | Locate Empty | 96B2 | #3ATR 96B2 |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_96B2 | #3ATR 96B2 RY | ATR |  |  |  |  | CDC | 220 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0426 |  |  | 2-32-10 |  |  | Locate Empty | 96D | #4ATR 96D |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_96D | #4ATR 96D RY | ATR |  |  |  |  | CDC | 221 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0427 |  |  | 2-32-11 |  |  | Locate Empty | 96P | #4ATR 96P |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_96P | #4ATR 96P RY | ATR |  |  |  |  | CDC | 222 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0428 |  |  | 2-32-12 |  |  | Locate Empty | 63Q | #4ATR 63Q |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_63Q | #4ATR 63Q RY | ATR |  |  |  |  | CDC | 223 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0424 |  |  | 2-32-08 |  |  | Locate Empty | 96B1 | #4ATR 96B1 |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_96B1 | #4ATR 96B1 RY | ATR |  |  |  |  | CDC | 224 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0425 |  |  | 2-32-09 |  |  | Locate Empty | 96B2 | #4ATR 96B2 |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_96B2 | #4ATR 96B2 RY | ATR |  |  |  |  | CDC | 225 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0435 |  |  | 2-33-03 |  |  | Locate Empty | 96D | #5ATR 96D |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_96D | #5ATR 96D RY | ATR |  |  |  |  | CDC | 226 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0436 |  |  | 2-33-04 |  |  | Locate Empty | 96P | #5ATR 96P |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_96P | #5ATR 96P RY | ATR |  |  |  |  | CDC | 227 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0437 |  |  | 2-33-05 |  |  | Locate Empty | 63Q | #5ATR 63Q |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_63Q | #5ATR 63Q RY | ATR |  |  |  |  | CDC | 228 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0433 |  |  | 2-33-01 |  |  | Locate Empty | 96B1 | #5ATR 96B1 |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_96B1 | #5ATR 96B1 RY | ATR |  |  |  |  | CDC | 229 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0434 |  |  | 2-33-02 |  |  | Locate Empty | 96B2 | #5ATR 96B2 |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_96B2 | #5ATR 96B2 RY | ATR |  |  |  |  | CDC | 230 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0444 |  |  | 2-33-12 |  |  | Locate Empty | 96D | #6ATR 96D |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_96D | #6ATR 96D RY | ATR |  |  |  |  | CDC | 231 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0445 |  |  | 2-33-13 |  |  | Locate Empty | 96P | #6ATR 96P |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_96P | #6ATR 96P RY | ATR |  |  |  |  | CDC | 232 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0446 |  |  | 2-33-14 |  |  | Locate Empty | 63Q | #6ATR 63Q |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_63Q | #6ATR 63Q RY | ATR |  |  |  |  | CDC | 233 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0442 |  |  | 2-33-10 |  |  | Locate Empty | 96B1 | #6ATR 96B1 |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_96B1 | #6ATR 96B1 RY | ATR |  |  |  |  | CDC | 234 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0443 |  |  | 2-33-11 |  |  | Locate Empty | 96B2 | #6ATR 96B2 |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_96B2 | #6ATR 96B2 RY | ATR |  |  |  |  | CDC | 235 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0401 |  |  | 2-31-01 |  |  | Locate Empty | TRA 重故障 | #1ATR TRA 重故障 |  | a | B2/E01_C | [8 empty] | 南科ES.#1ATR_TRA | #1ATR 重故障 | ATR |  |  |  |  | CDC | 236 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0400 |  |  | 2-31-00 |  |  | Locate Empty | TRF 輕故障 | #1ATR TRF 輕故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_TRF | #1ATR 輕故障 | ATR |  |  |  |  | CDC | 237 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0398 |  |  | 2-30-14 |  |  | Locate Empty | OLTC S/L | #1ATR OLTC S/L |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_S/L | #1ATR OLTC S/L | ATR |  |  |  |  | CDC | 238 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0399 |  | 0039 | 2-30-15 |  | 1-27 | Locate Empty | OLTC A/M | #1ATR OLTC A/M |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_A/M | #1ATR OLTC A/M | ATR |  |  |  |  | CDC | 239 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E01 | 南科ES |  |  | 1ATR | #1ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0564 | 565 | 0040 | 1-39-04 | 1-39-05 | 1-28 | Locate Empty | M/F/I | #1ATR M/F/I |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_M/F/I | #1ATR M/F/I | ATR |  |  |  |  | CDC | 240 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES |  |  | 2ATR | #2ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0367 |  |  | 1-32-15 |  |  | Locate Empty | TRA 重故障 | #2ATR TRA 重故障 |  | a | B2/E01_C | [8 empty] | 南科ES.#2ATR_TRA | #2ATR 重故障 | ATR |  |  |  |  | CDC | 241 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0366 |  |  | 1-32-14 |  |  | Locate Empty | TRF 輕故障 | #2ATR TRF 輕故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_TRF | #2ATR 輕故障 | ATR |  |  |  |  | CDC | 242 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0364 |  |  | 1-32-12 |  |  | Locate Empty | OLTC S/L | #2ATR OLTC S/L |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_S/L | #2ATR OLTC S/L | ATR |  |  |  |  | CDC | 243 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0365 |  | 0043 | 1-32-13 |  | 1-2B | Locate Empty | OLTC A/M | #2ATR OLTC A/M |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_A/M | #2ATR OLTC A/M | ATR |  |  |  |  | CDC | 244 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E01 | 南科ES |  |  | 2ATR | #2ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0566 | 567 | 0044 | 1-39-06 | 1-39-07 | 1-2C | Locate Empty | M/F/I | #2ATR M/F/I |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_M/F/I | #2ATR M/F/I | ATR |  |  |  |  | CDC | 245 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES |  |  | 3ATR | #3ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0371 |  |  | 1-33-03 |  |  | Locate Empty | TRA 重故障 | #3ATR TRA 重故障 |  | a | B2/E01_C | [8 empty] | 南科ES.#3ATR_TRA | #3ATR 重故障 | ATR |  |  |  |  | CDC | 246 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0370 |  |  | 1-33-02 |  |  | Locate Empty | TRF 輕故障 | #3ATR TRF 輕故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_TRF | #3ATR 輕故障 | ATR |  |  |  |  | CDC | 247 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0368 |  |  | 1-33-00 |  |  | Locate Empty | OLTC S/L | #3ATR OLTC S/L |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_S/L | #3ATR OLTC S/L | ATR |  |  |  |  | CDC | 248 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0369 |  | 0047 | 1-33-01 |  | 1-2F | Locate Empty | OLTC A/M | #3ATR OLTC A/M |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_A/M | #3ATR OLTC A/M | ATR |  |  |  |  | CDC | 249 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E01 | 南科ES |  |  | 3ATR | #3ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0568 | 569 | 0048 | 1-39-08 | 1-39-09 | 1-30 | Locate Empty | M/F/I | #3ATR M/F/I |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_M/F/I | #3ATR M/F/I | ATR |  |  |  |  | CDC | 250 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES |  |  | 4ATR | #4ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0375 |  |  | 1-33-07 |  |  | Locate Empty | TRA 重故障 | #4ATR TRA 重故障 |  | a | B2/E01_C | [8 empty] | 南科ES.#4ATR_TRA | #4ATR 重故障 | ATR |  |  |  |  | CDC | 251 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0374 |  |  | 1-33-06 |  |  | Locate Empty | TRF 輕故障 | #4ATR TRF 輕故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_TRF | #4ATR 輕故障 | ATR |  |  |  |  | CDC | 252 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0372 |  |  | 1-33-04 |  |  | Locate Empty | OLTC S/L | #4ATR OLTC S/L |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_S/L | #4ATR OLTC S/L | ATR |  |  |  |  | CDC | 253 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0373 |  | 0051 | 1-33-05 |  | 1-33 | Locate Empty | OLTC A/M | #4ATR OLTC A/M |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_A/M | #4ATR OLTC A/M | ATR |  |  |  |  | CDC | 254 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E01 | 南科ES |  |  | 4ATR | #4ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0570 | 571 | 0052 | 1-39-10 | 1-39-11 | 1-34 | Locate Empty | M/F/I | #4ATR M/F/I |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_M/F/I | #4ATR M/F/I | ATR |  |  |  |  | CDC | 255 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES |  |  | 5ATR | #5ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0379 |  |  | 1-33-11 |  |  | Locate Empty | TRA 重故障 | #5ATR TRA 重故障 |  | a | B2/E01_C | [8 empty] | 南科ES.#5ATR_TRA | #5ATR 重故障 | ATR |  |  |  |  | CDC | 256 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0378 |  |  | 1-33-10 |  |  | Locate Empty | TRF 輕故障 | #5ATR TRF 輕故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_TRF | #5ATR 輕故障 | ATR |  |  |  |  | CDC | 257 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0376 |  |  | 1-33-08 |  |  | Locate Empty | OLTC S/L | #5ATR OLTC S/L |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_S/L | #5ATR OLTC S/L | ATR |  |  |  |  | CDC | 258 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0377 |  | 0055 | 1-33-09 |  | 1-37 | Locate Empty | OLTC A/M | #5ATR OLTC A/M |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_A/M | #5ATR OLTC A/M | ATR |  |  |  |  | CDC | 259 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E01 | 南科ES |  |  | 5ATR | #5ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0572 | 573 | 0056 | 1-39-12 | 1-39-13 | 1-38 | Locate Empty | M/F/I | #5ATR M/F/I |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_M/F/I | #5ATR M/F/I | ATR |  |  |  |  | CDC | 260 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES |  |  | 6ATR | #6ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0383 |  |  | 1-33-15 |  |  | Locate Empty | TRA 重故障 | #6ATR TRA 重故障 |  | a | B2/E01_C | [8 empty] | 南科ES.#6ATR_TRA | #6ATR 重故障 | ATR |  |  |  |  | CDC | 261 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0382 |  |  | 1-33-14 |  |  | Locate Empty | TRF 輕故障 | #6ATR TRF 輕故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_TRF | #6ATR 輕故障 | ATR |  |  |  |  | CDC | 262 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0380 |  |  | 1-33-12 |  |  | Locate Empty | OLTC S/L | #6ATR OLTC S/L |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_S/L | #6ATR OLTC S/L | ATR |  |  |  |  | CDC | 263 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0381 |  | 0059 | 1-33-13 |  | 1-3B | Locate Empty | OLTC A/M | #6ATR OLTC A/M |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_A/M | #6ATR OLTC A/M | ATR |  |  |  |  | CDC | 264 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E01 | 南科ES |  |  | 6ATR | #6ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0574 | 575 | 0060 | 1-39-14 | 1-39-15 | 1-3C | Locate Empty | M/F/I | #6ATR M/F |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_M/F/I | #6ATR M/F/I | ATR |  |  |  |  | CDC | 265 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | DS1 | 3531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0490 | 491 | 0068 | 1-34-10 | 1-34-11 | 1-44 | 3531 | ON/OFF | 七股紅線 3531 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3531_DS | 3531(#1ATR) DS | ATR |  |  |  |  | CDC | 266 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | DS2 | 3532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0492 | 493 | 0069 | 1-34-12 | 1-34-13 | 1-45 | 3532 | ON/OFF | 七股紅線 3532 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3532_DS | 3532(#1ATR) DS | ATR |  |  |  |  | CDC | 267 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | DS1 | 3561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0504 | 505 | 0075 | 1-35-08 | 1-35-09 | 1-4B | 3561 | ON/OFF | 二號主變3561 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3561_DS | 3561(#2ATR) DS | ATR |  |  |  |  | CDC | 268 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | DS2 | 3562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0506 | 507 | 0076 | 1-35-10 | 1-35-11 | 1-4C | 3562 | ON/OFF | 二號主變3562 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3562_DS | 3562(#2ATR) DS | ATR |  |  |  |  | CDC | 269 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | DS1 | 3591 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0518 | 519 | 0082 | 1-36-06 | 1-36-07 | 1-52 | 3591 | ON/OFF | 七股白線 3591 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3591_DS | 3591(#3ATR) DS | ATR |  |  |  |  | CDC | 270 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | DS2 | 3592 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0520 | 521 | 0083 | 1-36-08 | 1-36-09 | 1-53 | 3592 | ON/OFF | 七股白線 3592 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3592_DS | 3592(#3ATR) DS | ATR |  |  |  |  | CDC | 271 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | DS1 | 3631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0532 | 533 | 0089 | 1-37-04 | 1-37-05 | 1-59 | 3631 | ON/OFF | 南科龍崎一路 3631 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3631_DS | 3631(#4ATR) DS | ATR |  |  |  |  | CDC | 272 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | DS2 | 3632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0534 | 535 | 0090 | 1-37-06 | 1-37-07 | 1-5A | 3632 | ON/OFF | 南科龍崎一路 3632 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3632_DS | 3632(#4ATR) DS | ATR |  |  |  |  | CDC | 273 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | DS1 | 3661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0546 | 547 | 0096 | 1-38-02 | 1-38-03 | 1-60 | 3661 | ON/OFF | 嘉民一路 3661 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3661_DS | 3661(#5ATR) DS | ATR |  |  |  |  | CDC | 274 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | DS2 | 3662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0548 | 549 | 0097 | 1-38-04 | 1-38-05 | 1-61 | 3662 | ON/OFF | 嘉民一路 3662 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3662_DS | 3662(#5ATR) DS | ATR |  |  |  |  | CDC | 275 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | DS1 | 3691 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0560 | 561 | 0103 | 1-39-00 | 1-39-01 | 1-67 | 3691 | ON/OFF | 南科龍崎二路 3691 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3691_DS | 3691(#6ATR) DS | ATR |  |  |  |  | CDC | 276 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | DS2 | 3692 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0562 | 563 | 0104 | 1-39-02 | 1-39-03 | 1-68 | 3692 | ON/OFF | 南科龍崎二路 3692 DS |  |  | B2/E01_C | [8 empty] | 南科ES.3692_DS | 3692(#6ATR) DS | ATR |  |  |  |  | CDC | 277 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS1 | 1811 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0256 | 257 | 0105 | 1-3A-00 | 1-3A-01 | 1-69 | 1811 | ON/OFF | #1ATR 1811 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1811_DS | 1811(#1ATR) DS | ATR |  |  |  |  | CDC | 278 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS2 | 1812 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0258 | 259 | 0106 | 1-3A-02 | 1-3A-03 | 1-6A | 0 | ON/OFF | #1ATR 1812 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1812_DS | 1812(#1ATR) DS | ATR |  |  |  |  | CDC | 279 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | DS1 | 1821 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0262 | 263 | 0108 | 1-3A-06 | 1-3A-07 | 1-6C | 1821 | ON/OFF | #2ATR 1821 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1821_DS | 1821(#2ATR) DS | ATR |  |  |  |  | CDC | 280 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | DS2 | 1822 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0264 | 265 | 0109 | 1-3A-08 | 1-3A-09 | 1-6D | 1822 | ON/OFF | #2ATR 1822 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1822_DS | 1822(#2ATR) DS | ATR |  |  |  |  | CDC | 281 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS1 | 1831 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0192 | 193 | 0128 | 2-36-00 | 2-36-01 | 2-00 | 1831 | ON/OFF | #3ATR 1831 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1831_DS | 1831(#3ATR) DS | ATR |  |  |  |  | CDC | 282 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS2 | 1832 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0194 | 195 | 0129 | 2-36-02 | 2-36-03 | 2-01 | 1832 | ON/OFF | #3ATR 1832 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1832_DS | 1832(#3ATR) DS | ATR |  |  |  |  | CDC | 283 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | DS1 | 1841 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0268 | 269 | 0111 | 1-3A-12 | 1-3A-13 | 1-6F | 1841 | ON/OFF | #3ATR 1841 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1841_DS | 1841(#3ATR) DS | ATR |  |  |  |  | CDC | 284 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | DS2 | 1842 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0270 | 271 | 0112 | 1-3A-14 | 1-3A-15 | 1-70 | 1842 | ON/OFF | #3ATR 1842 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1842_DS | 1842(#3ATR) DS | ATR |  |  |  |  | CDC | 285 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | DS1 | 1851 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0274 | 275 | 0114 | 1-3B-02 | 1-3B-03 | 1-72 | 1851 | ON/OFF | #4ATR 1851 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1851_DS | 1851(#4ATR) DS | ATR |  |  |  |  | CDC | 286 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | DS2 | 1852 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0276 | 277 | 0115 | 1-3B-04 | 1-3B-05 | 1-73 | 1852 | ON/OFF | #4ATR 1852 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1852_DS | 1852(#4ATR) DS | ATR |  |  |  |  | CDC | 287 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | DS1 | 1861 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0278 | 279 | 0116 | 1-3B-06 | 1-3B-07 | 1-74 | 1861 | ON/OFF | #4ATR 1861 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1861_DS | 1861(#4ATR) DS | ATR |  |  |  |  | CDC | 288 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | DS2 | 1862 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0280 | 281 | 0117 | 1-3B-08 | 1-3B-09 | 1-75 | 1862 | ON/OFF | #4ATR 1862 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1862_DS | 1862(#4ATR) DS | ATR |  |  |  |  | CDC | 289 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | DS1 | 1871 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0282 | 283 | 0118 | 1-3B-10 | 1-3B-11 | 1-76 | 1871 | ON/OFF | #5ATR 1871 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1871_DS | 1871(#5ATR) DS | ATR |  |  |  |  | CDC | 290 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | DS2 | 1872 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0284 | 285 | 0119 | 1-3B-12 | 1-3B-13 | 1-77 | 1872 | ON/OFF | #5ATR 1872 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1872_DS | 1872(#5ATR) DS | ATR |  |  |  |  | CDC | 291 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | DS1 | 1881 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0286 | 287 | 0120 | 1-3B-14 | 1-3B-15 | 1-78 | 1881 | ON/OFF | #5ATR 1881 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1881_DS | 1881(#5ATR) DS | ATR |  |  |  |  | CDC | 292 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | DS2 | 1882 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0288 | 289 | 0121 | 1-3C-00 | 1-3C-01 | 1-79 | 1882 | ON/OFF | #5ATR 1882 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1882_DS | 1882(#5ATR) DS | ATR |  |  |  |  | CDC | 293 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | DS1 | 1911 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0292 | 293 | 0123 | 1-3C-04 | 1-3C-05 | 1-7B | 1911 | ON/OFF | #6ATR 1911 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1911_DS | 1911(#6ATR) DS | ATR |  |  |  |  | CDC | 294 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | DS2 | 1912 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0294 | 295 | 0124 | 1-3C-06 | 1-3C-07 | 1-7C | 1912 | ON/OFF | #6ATR 1912 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1912_DS | 1912(#6ATR) DS | ATR |  |  |  |  | CDC | 295 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | DS1 | 1921 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0296 | 297 | 0125 | 1-3C-08 | 1-3C-09 | 1-7D | 1921 | ON/OFF | #6ATR 1921 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1921_DS | 1921(#6ATR) DS | ATR |  |  |  |  | CDC | 296 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | DS2 | 1922 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0298 | 299 | 0126 | 1-3C-10 | 1-3C-11 | 1-7E | 1922 | ON/OFF | #6ATR 1922 DS |  |  | B3/E01_C | [8 empty] | 南科ES.1922_DS | 1922(#6ATR) DS | ATR |  |  |  |  | CDC | 297 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/2ATR33 | R/2SHR |  |  | 0161 |  | 0022 | 1-10-01 |  | 1-16 | 520 | ON/OFF | #2ATR THI 520 CB |  | aaab | B3/E01_C | [8 empty] | 南科ES.520_CB | 520 CB | OTHER |  |  |  |  | CDC | 298 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/3ATR33 | R/3SHR |  |  | 0162 |  | 0024 | 1-10-02 |  | 1-18 | 530 | ON/OFF | #3ATR THI 530 CB |  | aabb | B3/E01_C | [8 empty] | 南科ES.530_CB | 530 CB | OTHER |  |  |  |  | CDC | 299 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/5ATR33 | R/4SHR |  |  | 0163 |  | 0029 | 1-10-03 |  | 1-1D | 550 | ON/OFF | #5ATR THI 550 CB |  | aacb | B3/E01_C | [8 empty] | 南科ES.550_CB | 550 CB | OTHER |  |  |  |  | CDC | 300 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | DS1 | 521 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0266 | 267 | 0110 | 1-3A-10 | 1-3A-11 | 1-6E | 521 | ON/OFF | #2ATR THI 521 DS |  |  | B3/E01_C | [8 empty] | 南科ES.521_DS | 521 DS | OTHER |  |  |  |  | CDC | 301 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | DS1 | 531 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0272 | 273 | 0113 | 1-3B-00 | 1-3B-01 | 1-71 | 531 | ON/OFF | #3ATR THI 531 DS |  |  | B3/E01_C | [8 empty] | 南科ES.531_DS | 531 DS | OTHER |  |  |  |  | CDC | 302 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | DS1 | 551 | B3 | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0290 | 291 | 0122 | 1-3C-02 | 1-3C-03 | 1-7A | 551 | ON/OFF | #5ATR THI 551 DS |  |  | B3/E01_C | [8 empty] | 南科ES.551_DS | 551 DS | OTHER |  |  |  |  | CDC | 303 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | Locate Empty |  | Card 1 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南超ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 304 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | Locate Empty |  | Card 1 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南超ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 305 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | Locate Empty |  | Card 2 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南超ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 306 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | Locate Empty |  | Card 2 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南超ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 307 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 1_DCV_P | #1直流P電源 | Element | MvMoment | #1 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | Locate Empty |  | #1DC – P 電壓 | kV_-150_150(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南科ES.#1直流P電源 | #1直流P電源電壓 | OTHER |  |  |  |  | CDC | 308 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 1_DCV_N | #1直流N電源 | Element | MvMoment | #1 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | Locate Empty |  | #1DC – N 電壓 | kV_-150_150(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南科ES.#1直流N電源 | #1直流N電源電壓 | OTHER |  |  |  |  | CDC | 309 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 2_DCV_P | #2直流P電源 | Element | MvMoment | #2 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | Locate Empty |  | #2DC – P 電壓 | kV_-150_150(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南科ES.#2直流P電源 | #2直流P電源電壓 | OTHER |  |  |  |  | CDC | 310 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 2_DCV_N | #2直流N電源 | Element | MvMoment | #2 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | Locate Empty |  | #2DC – N 電壓 | kV_-150_150(-2000_2000) |  | B3/E01_A1 | [8 empty] | 南科ES.#2直流N電源 | #2直流N電源電壓 | OTHER |  |  |  |  | CDC | 311 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0251 |  |  | 1-1B-03 |  |  | Locate Empty | CHG2 | CHG2 通訊用充電機 |  |  | B3/E01_A1 | [8 empty] | 南科ES.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 312 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0252 |  |  | 1-1B-04 |  |  | Locate Empty |  | 通訊設備 AC故障 |  |  | B3/E01_A1 | [8 empty] | 南科ES.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 313 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | RTU | RTU |  | Test_CB1 |  |  | Status | TEST CB1 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0320 |  | 0000 | 1-30-00 |  | 1-00 | Locate Empty | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 南科ES.TEST_CB(1) | 345KV TEST CB | OTHER |  |  |  |  | CDC | 314 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | RTU | RTU |  | RTU_R_L |  | Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0321 |  |  | 1-30-01 |  |  | Locate Empty | ON/OFF | L/R STATUS |  |  | ELEM/E01_A1 | [8 empty] | 南科ES.RTU_S/L(1) | 345KV RTU S/L | OTHER |  |  |  |  | CDC | 315 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | OSCA | OSCA | OSCA 345KV 示波器 |  |  | B2/E01_C | [8 empty] | 南科ES.345KV_OSCA | 345KV 示波器啟動警報 | OTHER |  |  |  |  | CDC | 316 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 1A5Other | COF | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0447 |  |  | 2-33-15 |  |  | Locate Empty |  | COF 消防 |  |  | B3/E01_A1 | [8 empty] | 南科ES.COF | 消防警報 | OTHER |  |  |  |  | CDC | 317 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | ES2 | 1832E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0314 | 315 |  | 1-3D-10 | 1-3D-11 |  | 1832E | ON/OFF | #3ATR 1832E DS |  |  | B3/E01_C | [8 empty] | 南科ES.1832E_ES | #3ATR1832E ES | OTHER |  |  |  |  | CDC | 318 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | ES2 | 1852E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0308 | 309 |  | 1-3D-04 | 1-3D-05 |  | 1852E | ON/OFF | #4ATR 1852E DS |  |  | B3/E01_C | [8 empty] | 南科ES.1852E_ES | #4ATR1852E ES | OTHER |  |  |  |  | CDC | 319 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | ES2 | 1872E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0310 | 311 |  | 1-3D-06 | 1-3D-07 |  | 1872E | ON/OFF | #5ATR 1872E DS |  |  | B3/E01_C | [8 empty] | 南科ES.1872E_ES | #5ATR1872E ES | OTHER |  |  |  |  | CDC | 320 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | ES2 | 1912E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0312 | 313 |  | 1-3D-08 | 1-3D-09 |  | 1912E | ON/OFF | #6ATR 1912E DS |  |  | B3/E01_C | [8 empty] | 南科ES.1912E_ES | #6ATR1912E ES | OTHER |  |  |  |  | CDC | 321 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | ES1 | 3561E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0300 | 301 |  | 1-3C-12 | 1-3C-13 |  | 3561 | ON/OFF | 二號主變3561 ES |  |  | B2/E01_C | [8 empty] | 南科ES.3561E_ES | #2ATR 3561E ES | OTHER |  |  |  |  | CDC | 322 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | ES1 | 3591E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0302 | 303 |  | 1-3C-14 | 1-3C-15 |  | 3591 | ON/OFF | 七股白線 3591 ES |  |  | B2/E01_C | [8 empty] | 南科ES.3591E_ES | #3ATR 3591E ES | OTHER |  |  |  |  | CDC | 323 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | ES1 | 3631E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0304 | 305 |  | 1-3D-00 | 1-3D-01 |  | 3631 | ON/OFF | 南科龍崎一路 3631 ES |  |  | B2/E01_C | [8 empty] | 南科ES.3631E_ES | #4ATR 3631E ES | OTHER |  |  |  |  | CDC | 324 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | ES1 | 3661E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0306 | 307 |  | 1-3D-02 | 1-3D-03 |  | 3661 | ON/OFF | 嘉民一路 3661 ES |  |  | B2/E01_C | [8 empty] | 南科ES.3661E_ES | #5ATR 3661E ES | OTHER |  |  |  |  | CDC | 325 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | 87C_CFA | Cable 87CFA | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0224 |  |  | 1-18-00 |  |  | 3640 | RYFA | 嘉民一路 CABLE RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3640_RY1A | 嘉民一路(3640) 電纜電驛故障 | OTHER |  |  |  |  | CDC | 326 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | 87C_CFA | Cable 87CFA | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0226 |  |  | 1-18-02 |  |  | 3540 | RYFA | 嘉民二路 CABLE RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3540_RY1A | 嘉民二路(3540) 電纜電驛故障 | OTHER |  |  |  |  | CDC | 327 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 87C_CFA | Cable 87CFA | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0228 |  |  | 1-18-04 |  |  | 3610 | RYFA | 南科龍崎一路 CABLE RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3610_RY1A | 龍崎一路(3610) 電纜電驛故障 | OTHER |  |  |  |  | CDC | 328 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 87C_CFA | Cable 87CFA | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0230 |  |  | 1-18-06 |  |  | 3670 | RYFA | 南科龍崎二路 CABLE RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3670_RY1A | 龍崎二路(3670) 電纜電驛故障 | OTHER |  |  |  |  | CDC | 329 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0389 |  |  | 2-30-05 |  |  | Locate Empty | SR96B1 | #1ATR SR96B1 |  |  | B3/E01_C | [8 empty] | 南科ES.#1ATR_SR96B1 | #1ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 330 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0390 |  |  | 2-30-06 |  |  | Locate Empty | SR96B2 | #1ATR SR96B2 |  |  | B3/E01_C | [8 empty] | 南科ES.#1ATR_SR96B2 | #1ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 510 | #1SHR(510) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0391 |  |  | 2-30-07 |  |  | Locate Empty | SR96D | #1ATR SR96D |  |  | B3/E01_C | [8 empty] | 南科ES.#1ATR_SR96D | #1ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 510 | #1SHR(510) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0392 |  |  | 2-30-08 |  |  | Locate Empty | SR96P | #1ATR SR96P |  |  | B3/E01_C | [8 empty] | 南科ES.#1ATR_SR96P | #1ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0404 |  |  | 2-31-04 |  |  | Locate Empty | SR96D | #2ATR SR96D |  |  | B3/E01_C | [8 empty] | 南科ES.#2ATR_SR96D | #2ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 334 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0405 |  |  | 2-31-05 |  |  | Locate Empty | SR96P | #2ATR SR96P |  |  | B3/E01_C | [8 empty] | 南科ES.#2ATR_SR96P | #2ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 335 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0402 |  |  | 2-31-02 |  |  | Locate Empty | SR96B1 | #2ATR SR96B1 |  |  | B3/E01_C | [8 empty] | 南科ES.#2ATR_SR96B1 | #2ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 336 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0403 |  |  | 2-31-03 |  |  | Locate Empty | SR96B2 | #2ATR SR96B2 |  |  | B3/E01_C | [8 empty] | 南科ES.#2ATR_SR96B2 | #2ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 337 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0411 |  |  | 2-31-11 |  |  | Locate Empty | SR96B1 | #3ATR SR96B1 |  |  | B3/E01_C | [8 empty] | 南科ES.#3ATR_SR96B1 | #3ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 338 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0412 |  |  | 2-31-12 |  |  | Locate Empty | SR96B2 | #3ATR SR96B2 |  |  | B3/E01_C | [8 empty] | 南科ES.#3ATR_SR96B2 | #3ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 339 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0413 |  |  | 2-31-13 |  |  | Locate Empty | SR96D | #3ATR SR96D |  |  | B3/E01_C | [8 empty] | 南科ES.#3ATR_SR96D | #3ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 340 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0414 |  |  | 2-31-14 |  |  | Locate Empty | SR96P | #3ATR SR96P |  |  | B3/E01_C | [8 empty] | 南科ES.#3ATR_SR96P | #3ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 341 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 540 | #4SHR(540) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0422 |  |  | 2-32-06 |  |  | Locate Empty | SR96D | #4ATR SR96D |  |  | B3/E01_C | [8 empty] | 南科ES.#4ATR_SR96D | #4ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 342 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 540 | #4SHR(540) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0423 |  |  | 2-32-07 |  |  | Locate Empty | SR96P | #4ATR SR96P |  |  | B3/E01_C | [8 empty] | 南科ES.#4ATR_SR96P | #4ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 343 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 540 | #4SHR(540) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0420 |  |  | 2-32-04 |  |  | Locate Empty | SR96B1 | #4ATR SR96B1 |  |  | B3/E01_C | [8 empty] | 南科ES.#4ATR_SR96B1 | #4ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 344 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 540 | #4SHR(540) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0421 |  |  | 2-32-05 |  |  | Locate Empty | SR96B2 | #4ATR SR96B2 |  |  | B3/E01_C | [8 empty] | 南科ES.#4ATR_SR96B2 | #4ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 345 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0429 |  |  | 2-32-13 |  |  | Locate Empty | SR96B1 | #5ATR SR96B1 |  |  | B3/E01_C | [8 empty] | 南科ES.#5ATR_SR96B1 | #5ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 346 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0430 |  |  | 2-32-14 |  |  | Locate Empty | SR96B2 | #5ATR SR96B2 |  |  | B3/E01_C | [8 empty] | 南科ES.#5ATR_SR96B2 | #5ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 347 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0431 |  |  | 2-32-15 |  |  | Locate Empty | SR96D | #5ATR SR96D |  |  | B3/E01_C | [8 empty] | 南科ES.#5ATR_SR96D | #5ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 348 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0432 |  |  | 2-33-00 |  |  | Locate Empty | SR96P | #5ATR SR96P |  |  | B3/E01_C | [8 empty] | 南科ES.#5ATR_SR96P | #5ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 349 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 560 | #6SHR(560) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0440 |  |  | 2-33-08 |  |  | Locate Empty | SR96D | #6ATR SR96D |  |  | B3/E01_C | [8 empty] | 南科ES.#6ATR_SR96D | #6ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 350 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 560 | #6SHR(560) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0441 |  |  | 2-33-09 |  |  | Locate Empty | SR96P | #6ATR SR96P |  |  | B3/E01_C | [8 empty] | 南科ES.#6ATR_SR96P | #6ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 351 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 560 | #6SHR(560) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0438 |  |  | 2-33-06 |  |  | Locate Empty | SR96B1 | #6ATR SR96B1 |  |  | B3/E01_C | [8 empty] | 南科ES.#6ATR_SR96B1 | #6ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 352 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 560 | #6SHR(560) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0439 |  |  | 2-33-07 |  |  | Locate Empty | SR96B2 | #6ATR SR96B2 |  |  | B3/E01_C | [8 empty] | 南科ES.#6ATR_SR96B2 | #6ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 353 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | CHG1_1 | #1充電機故障 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0452 |  |  | 2-34-04 |  |  | Locate Empty |  | CHG1-1 變電用充電機 |  |  | B3/E01_A1 | [8 empty] | 南科ES.#1充電機故障 | 變電所#1直流充電機故障 | OTHER |  |  |  |  | CDC | 354 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | CHG1_2 | #2充電機故障 | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0461 |  |  | 2-34-13 |  |  | Locate Empty |  | CHG1-2 變電用充電機 |  |  | B3/E01_A1 | [8 empty] | 南科ES.#2充電機故障 | 變電所#2直流充電機故障 | OTHER |  |  |  |  | CDC | 355 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 5A5Other | #3充電機故障 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0462 |  |  | 2-34-14 |  |  | Locate Empty |  | CHG1-3 變電用充電機 |  |  | B3/E01_A1 | [8 empty] | 南科ES.#3充電機故障 | 變電所#3直流充電機故障 | OTHER |  |  |  |  | CDC | 356 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | STUV | A | Element | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0448 |  |  | 2-34-00 |  |  | Locate Empty |  | STUV 所內欠壓 |  |  | ELEM/E01_A1 | [8 empty] | 南科ES.A所內電源欠壓 | 345KV 所內電源欠壓 | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | DCA |  | Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0450 |  |  | 2-34-02 |  |  | Locate Empty |  | DCA 直流警報 |  |  | ELEM/E01_A1 | [8 empty] | 南科ES.A棟直流電源DCA | 345KV 直流電源DCA | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | DCE |  | Element | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0449 |  |  | 2-34-01 |  |  | Locate Empty |  | DCE 直流接地 |  |  | ELEM/E01_A1 | [8 empty] | 南科ES.A棟直流電源DCE | 345KV 直流電源DCE | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | OilLeak | A洩油池水位 | Element | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0451 |  |  | 2-34-03 |  |  | Locate Empty |  | WSF 洩油池警報 |  |  | B3/E01_A1 | [8 empty] | 南科ES.A洩油池水位 | 345KV 洩油池水位警報 | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0340 |  |  | 1-31-04 |  |  | 3510 | #187CFA | 新嘉民南科二路 3510 #187CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_87CFA | 新嘉民二路(3510)87RY通訊故障 | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0342 |  |  | 1-31-06 |  |  | 3510 | #285CFA | 新嘉民南科二路 3510 #285CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_85CFA | 新嘉民二路(3510)85RY通訊故障 | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 87CFA1 |  | B2,B3,Element | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0236 |  |  | 1-19-04 |  |  | 3510 | 87CFA | 新嘉民南科二路 Cable 87CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_87CFA1 | 新嘉民二路(3510) 電纜通訊故障 | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 87C_CFA | Cable 87CFA | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0232 |  |  | 1-19-00 |  |  | 3510 | RYFA | 新嘉民南科二路 Cable RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3510_RY1A | 新嘉民二路(3510) 電纜電驛故障 | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0355 |  |  | 1-32-03 |  |  | 3570 | #187CFA | 新嘉民南科一路 3570 #187CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_87CFA | 新嘉民一路(3570)87RY通訊故障 | OTHER |  |  |  |  | CDC | 365 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0357 |  |  | 1-32-05 |  |  | 3570 | #285CFA | 新嘉民南科一路 3570 #285FA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_85CFA | 新嘉民一路(3570)85RY通訊故障 | OTHER |  |  |  |  | CDC | 366 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 87CFA1 |  | B2,B3,Element | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0238 |  |  | 1-19-06 |  |  | 3570 | 87CFA | 新嘉民南科一路 Cable 87CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_87CFA1 | 新嘉民一路(3570) 電纜通訊故障 | OTHER |  |  |  |  | CDC | 367 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 87C_CFA | Cable 87CFA | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0234 |  |  | 1-19-02 |  |  | 3570 | RYFA | 新嘉民南科一路 Cable RYFA |  |  | B2/E01_C | [8 empty] | 南科ES.3570_RY1A | 新嘉民一路(3570) 電纜電驛故障 | OTHER |  |  |  |  | CDC | 368 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0350 |  |  | 1-31-14 |  |  | 3610 | #187CFA | 南科龍崎一路 3610 #187CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3610_87CFA | 龍崎一路(3610) #187RY通訊故障 | OTHER |  |  |  |  | CDC | 369 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0352 |  |  | 1-32-00 |  |  | 3610 | #285CFA | 南科龍崎一路 3610 #285CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3610_85CFA | 龍崎一路(3610) #285RY通訊故障 | OTHER |  |  |  |  | CDC | 370 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0360 |  |  | 1-32-08 |  |  | 3670 | #187CFA | 南科龍崎二路 3670 #187CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3670_87CFA | 龍崎二路(3670) #187RY通訊故障 | OTHER |  |  |  |  | CDC | 371 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0362 |  |  | 1-32-10 |  |  | 3670 | #2R85CFA | 南科龍崎二路 3670 #285CFA |  |  | B2/E01_C | [8 empty] | 南科ES.3670_85CFA | 龍崎二路(3670) #285RY通訊故障 | OTHER |  |  |  |  | CDC | 372 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | Water |  |  | Status | 地下室淹水 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0476 |  |  | 2-35-12 |  |  | 地下室 | A/N | A.C.D棟地下室水位警報 |  |  | B3/E01_A1 | [8 empty] | 南科ES.水位警報 | A,C,D棟地下室水位警報 | OTHER |  |  |  |  | CDC | 373 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 6A5Other | 電壓驟降 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0479 |  |  | 2-35-15 |  |  | Locate Empty | 系統電壓 | 電壓驟降 |  |  | B3/E01_A1 | [8 empty] | 南科ES.電壓驟降 | 電壓驟降警報 | OTHER |  |  |  |  | CDC | 374 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | R_Temp | 通信機房溫度 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0255 |  |  | 1-1B-07 |  |  | Locate Empty |  | 通訊室溫度警報 |  |  | B3/E01_A1 | [8 empty] | 南科ES.通信機房溫度 | 通信機房溫度警報 | OTHER |  |  |  |  | CDC | 375 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1810TE | 1810TE(非取樣點) | OTHER | [5 empty] | 376 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1810BE | 1810BE(非取樣點) | OTHER | [5 empty] | 377 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1820TE | 1820TE(非取樣點) | OTHER | [5 empty] | 378 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1820BE | 1820BE(非取樣點) | OTHER | [5 empty] | 379 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1830TE | 1830TE(非取樣點) | OTHER | [5 empty] | 380 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1830BE | 1830BE(非取樣點) | OTHER | [5 empty] | 381 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1840TE | 1840TE(非取樣點) | OTHER | [5 empty] | 382 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1840BE | 1840BE(非取樣點) | OTHER | [5 empty] | 383 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1850TE | 1850TE(非取樣點) | OTHER | [5 empty] | 384 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1850BE | 1850BE(非取樣點) | OTHER | [5 empty] | 385 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1860TE | 1860TE(非取樣點) | OTHER | [5 empty] | 386 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1860BE | 1860BE(非取樣點) | OTHER | [5 empty] | 387 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1870TE | 1870TE(非取樣點) | OTHER | [5 empty] | 388 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1870BE | 1870BE(非取樣點) | OTHER | [5 empty] | 389 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1880TE | 1880TE(非取樣點) | OTHER | [5 empty] | 390 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1880BE | 1880BE(非取樣點) | OTHER | [5 empty] | 391 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1910TE | 1910TE(非取樣點) | OTHER | [5 empty] | 392 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1910BE | 1910BE(非取樣點) | OTHER | [5 empty] | 393 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1920TE | 1920TE(非取樣點) | OTHER | [5 empty] | 394 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.1920BE | 1920BE(非取樣點) | OTHER | [5 empty] | 395 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.520TE | 520TE(非取樣點) | OTHER | [5 empty] | 396 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | RE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.520RE | 520RE(非取樣點) | OTHER | [5 empty] | 397 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.530TE | 530TE(非取樣點) | OTHER | [5 empty] | 398 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | RE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.530RE | 530RE(非取樣點) | OTHER | [5 empty] | 399 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.550TE | 550TE(非取樣點) | OTHER | [5 empty] | 400 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | RE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E01_C | [8 empty] | 南科ES.550RE | 550RE(非取樣點) | OTHER | [5 empty] | 401 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | StaDev | 所內設施 |  | 8A5Other | SOE_SYN | Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | Locate Empty |  |  |  |  | B3/E01_A1 | [15 empty] | CDC | 402 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E01 | 南科ES | 345 | 345kV | 1BUS | #1BUS |  | 1_87UL1 | 345#1B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0384 |  | 0130 | 2-30-00 |  | 2-02 | Locate Empty | #1BUS 87B1S | 345KV #1BUS 87B1S #1set |  |  | B2/E01_C | [8 empty] | 南科ES.345#1B_87UL1 | 345KV #1BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 403 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 1BUS | #1BUS |  | 1_87UL2 | 345#1B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0386 |  | 0132 | 2-30-02 |  | 2-04 | Locate Empty | #1BUS 87B2S | 345KV #1BUS 87B2S #2set |  |  | B2/E01_C | [8 empty] | 南科ES.345#1B_87UL2 | 345KV #1BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 404 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 2BUS | #2BUS |  | 1_87UL1 | 345#2B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0385 |  | 0131 | 2-30-01 |  | 2-03 | Locate Empty | #2BUS 87B1S | 345KV#2BUS 87B1S #1set |  |  | B2/E01_C | [8 empty] | 南科ES.345#2B_87UL1 | 345KV #2BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 405 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 2BUS | #2BUS |  | 1_87UL2 | 345#2B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0387 |  | 0133 | 2-30-03 |  | 2-05 | Locate Empty | #2BUS 87B2S | 345KV #2BUS 87B2S #2set |  |  | B2/E01_C | [8 empty] | 南科ES.345#2B_87UL2 | 345KV #2BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 406 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0316 |  |  | 1-3D-12 |  |  | 345kV #1,2Bus | #1RYFA | 345kV #1,2Bus #1 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.345KVBUS_RYFA1 | 345KV #1,2BUS 第一套數位RY故障 | OTHER |  |  |  |  | CDC | 407 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | 87CTFA1 | CTFA1 | Element | Status | 第1具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0317 |  |  | 1-3D-13 |  |  | 345kV #1,2Bus | #CTFA | 345kV #1,2Bus #1 CT迴路故障警報 |  |  | B2/E01_C | [8 empty] | 南科ES.345KVBUS_CTFA1 | 345KV #1,2BUS 第一套CT回路故障 | OTHER |  |  |  |  | CDC | 408 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0318 |  |  | 1-3D-14 |  |  | 345kV #1,2Bus | #2RYFA | 345kV #1,2Bus #2 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.345KVBUS_RYFA2 | 345KV #1,2BUS 第二套數位RY故障 | OTHER |  |  |  |  | CDC | 409 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | 87CTFA2 | CTFA2 | Element | Status | 第2具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0319 |  |  | 1-3D-15 |  |  | 345kV #1,2Bus | #2CTFA | 345kV #1,2Bus #2 CT迴路故障警報 |  |  | B2/E01_C | [8 empty] | 南科ES.345KVBUS_CTFA2 | 345KV #1,2BUS 第二套CT回路故障 | OTHER |  | CDC_Mon1_DPC,DNP_DI_Mon1_DPC |  |  | CDC | 410 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0330 |  | 0134 | 1-30-10 |  | 2-06 | Locate Empty | ON/OFF | #1ATR 第一套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_87UL1 | #1ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 411 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0331 |  | 0135 | 1-30-11 |  | 2-07 | Locate Empty | ON/OFF | #1ATR 第二套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_87UL2 | #1ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 412 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 1ATR | #1ATR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0576 |  | 0136 | 1-3E-00 |  | 2-08 | #1ATR | 51Z U/L | #1ATR 51Z RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_51Z | #1ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 413 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0322 |  | 0137 | 1-30-02 |  | 2-09 | Locate Empty | ON/OFF | #2ATR 第一套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_87UL1 | #2ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 414 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0323 |  | 0138 | 1-30-03 |  | 2-0A | Locate Empty | ON/OFF | #2ATR 第二套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_87UL2 | #2ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 415 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0578 |  | 0139 | 1-3E-02 |  | 2-0B | #2ATR | 51Z U/L | #2ATR 51Z RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_51Z | #2ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 416 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 2ATR | #2ATR |  | 2_87UL1 |  | B2 | Status | 第2套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0580 |  | 0140 | 1-3E-04 |  | 2-0C | #2ATR | 87U/L | #2ATR三次側電抗器用 87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_87UL3 | #2ATR三次側電抗器用 87RY U/L | OTHER |  |  |  |  | CDC | 417 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | 87A |  | B2,B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0167 |  |  | 1-10-07 |  |  | 520 | 87A | #2ATR THI 520 87RY |  |  | B3/E01_C | [8 empty] | 南科ES.#2ATR(520)_87A | #2ATR(520) 87RY | OTHER |  |  |  |  | CDC | 418 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 520 | #2SHR(520) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-11-00 |  |  | 520 | 51A | #2ATR THI 520 51RY |  |  | B3/E01_C | [8 empty] | 南科ES.#2ATR(520)_51A | #2ATR(520) 51RY | OTHER |  |  |  |  | CDC | 419 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 1ATR | #1ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0577 |  |  | 1-3E-01 |  |  | #1ATR | RYFA | #1ATR 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_RYFA | #1ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 420 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0579 |  |  | 1-3E-03 |  |  | #2ATR | RYFA | #2ATR 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_RYFA | #2ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 421 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 510 | #1SHR(510) |  | 87A |  | B2,B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0165 |  |  | 1-10-05 |  |  | 510 | 87A | #1ATR THI 510 87RY |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR(510)_87A | #1ATR(510) 87RY | OTHER |  |  |  |  | CDC | 422 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 510 | #1SHR(510) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-10-06 |  |  | 510 | 51A | #1ATR THI 510 51RY |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR(510)_51A | #1ATR(510) 51RY | OTHER |  |  |  |  | CDC | 423 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | 87A |  | B2,B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-11-01 |  |  | 530 | 87A | #3ATR THI 530 87RY |  |  | B3/E01_C | [8 empty] | 南科ES.#3ATR(530)_87A | #3ATR(530) 87RY | OTHER |  |  |  |  | CDC | 424 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 530 | #3SHR(530) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-11-02 |  |  | 530 | 51A | #3ATR THI 530 51RY |  |  | B3/E01_C | [8 empty] | 南科ES.#3ATR(530)_51A | #3ATR(530) 51RY | OTHER |  |  |  |  | CDC | 425 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | 87A |  | B2,B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-11-03 |  |  | 550 | 87A | #5ATR THI 550 87RY |  |  | B3/E01_C | [8 empty] | 南科ES.#5ATR(550)_87A | #5ATR(550) 87RY | OTHER |  |  |  |  | CDC | 426 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 550 | #5SHR(550) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-11-04 |  |  | 550 | 51A | #5ATR THI 550 51RY |  |  | B3/E01_C | [8 empty] | 南科ES.#5ATR(550)_51A | #5ATR(550) 51RY | OTHER |  |  |  |  | CDC | 427 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 560 | #6SHR(560) |  | 87A |  | B2,B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 1-11-05 |  |  | 560 | 87A | #6ATR THI 560 87RY |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR(560)_87A | #6ATR(560) 87RY | OTHER |  |  |  |  | CDC | 428 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES | 33 | 33kV | 560 | #6SHR(560) |  | 51A |  | B2,B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 1-11-06 |  |  | 560 | 51A | #6ATR THI 560 51RY |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR(560)_51A | #6ATR(560) 51RY | OTHER |  |  |  |  | CDC | 429 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0324 |  | 0141 | 1-30-04 |  | 2-0D | Locate Empty | ON/OFF | #3ATR 第一套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_87UL1 | #3ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 430 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0325 |  | 0142 | 1-30-05 |  | 2-0E | Locate Empty | ON/OFF | #3ATR 第二套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_87UL2 | #3ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 431 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0326 |  | 0145 | 1-30-06 |  | 2-11 | Locate Empty | ON/OFF | #4ATR 第一套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_87UL1 | #4ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 432 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0327 |  | 0146 | 1-30-07 |  | 2-12 | Locate Empty | ON/OFF | #4ATR 第二套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_87UL2 | #4ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0328 |  | 0148 | 1-30-08 |  | 2-14 | Locate Empty | ON/OFF | #5ATR 第一套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_87UL1 | #5ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0329 |  | 0149 | 1-30-09 |  | 2-15 | Locate Empty | ON/OFF | #5ATR 第二套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_87UL2 | #5ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0332 |  | 0152 | 1-30-12 |  | 2-18 | Locate Empty | ON/OFF | #6ATR 第一套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_87UL1 | #6ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 436 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0333 |  | 0153 | 1-30-13 |  | 2-19 | Locate Empty | ON/OFF | #6ATR 第二套87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_87UL2 | #6ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 437 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 1ATR | #1ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0581 |  |  | 1-3E-05 |  |  | #1ATR | 86A | #1ATR 86(51Z/87/96) RY |  |  | B2/E01_C | [8 empty] | 南科ES.#1ATR_86A | #1ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 438 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 2ATR | #2ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0582 |  |  | 1-3E-06 |  |  | #2ATR | 86A | #2ATR 86(51Z/87/96) RY |  |  | B2/E01_C | [8 empty] | 南科ES.#2ATR_86A | #2ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 439 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0583 |  |  | 1-3E-07 |  |  | #3ATR | 86A | #3ATR 86(51Z/87/96) RY |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_86A | #3ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 440 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0584 |  | 0143 | 1-3E-08 |  | 2-0F | #3ATR | 51Z U/L | #3ATR 51Z RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_51Z | #3ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 441 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 3ATR | #3ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 1-3E-09 |  |  | #3ATR | RYFA | #3ATR 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_RYFA | #3ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 442 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 3ATR | #3ATR |  | 2_87UL1 |  | B2 | Status | 第2套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0586 |  | 0144 | 1-3E-10 |  | 2-10 | #3ATR | 87U/L | #3ATR 電抗器(530) 87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#3ATR_87UL3 | #3ATR三次側電抗器用 87RY U/L | OTHER |  |  |  |  | CDC | 443 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 4ATR | #4ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0587 |  |  | 1-3E-11 |  |  | #4ATR | 86A | #4ATR 86(51Z/87/96) RY |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_86A | #4ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 444 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 4ATR | #4ATR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0588 |  | 0147 | 1-3E-12 |  | 2-13 | #4ATR | 51Z U/L | #4ATR 51Z RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_51Z | #4ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 4ATR | #4ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0589 |  |  | 1-3E-13 |  |  | #4ATR | RYFA | #4ATR 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#4ATR_RYFA | #4ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0590 |  |  | 1-3E-14 |  |  | #5ATR | 86A | #5ATR 86(51Z/87/96) RY |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_86A | #5ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 447 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0591 |  | 0150 | 1-3E-15 |  | 2-16 | #5ATR | 51Z U/L | #5ATR 51Z RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_51Z | #5ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 448 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 5ATR | #5ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0592 |  |  | 1-3F-00 |  |  | #5ATR | RYFA | #5ATR 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_RYFA | #5ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 449 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 5ATR | #5ATR |  | 2_87UL1 |  | B2 | Status | 第2套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0593 |  | 0151 | 1-3F-01 |  | 2-17 | #5ATR | 87U/L | #5ATR 電抗器(550) 87RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#5ATR_87UL3 | #5ATR三次側電抗器用 87RY U/L | OTHER |  |  |  |  | CDC | 450 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 6ATR | #6ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0594 |  |  | 1-3F-02 |  |  | #6ATR | 86A | #6ATR 86(51Z/87/96) RY |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_86A | #6ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES |  |  | 6ATR | #6ATR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0595 |  | 0154 | 1-3F-03 |  | 2-1A | #6ATR | 51Z U/L | #6ATR 51Z RY U/L |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_51Z | #6ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E01 | 南科ES |  |  | 6ATR | #6ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0596 |  |  | 1-3F-04 |  |  | #6ATR | RYFA | #6ATR 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.#6ATR_RYFA | #6ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | BFA | BF_RYFA | Element | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0597 |  |  | 1-3F-05 |  |  | B.F. RY | RYFA | 345KV斷路器失靈電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.345KV_BF_RYFA | 345KV斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 3640 | 87LA | 嘉民一路 Cable 87LA |  |  | B2/E01_C | [8 empty] | 南科ES.3640_87LA | 嘉民一路(3640)電纜87RY | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 3540 | 87LA | 嘉民二路 Cable 87LA |  |  | B2/E01_C | [8 empty] | 南科ES.3540_87LA | 嘉民二路(3540)電纜87RY | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 3610 | 87LA | 南科龍崎一路 Cable 87LA |  |  | B2/E01_C | [8 empty] | 南科ES.3610_87LA | 龍崎一路(3610)電纜87RY | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | 87A |  | B2,B3,Element | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 3670 | 87LA | 南科龍崎二路 Cable 87LA |  |  | B2/E01_C | [8 empty] | 南科ES.3670_87LA | 龍崎二路(3670)電纜87RY | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 3510 | 87LA1 | 新嘉民南科二路 Cable 87LA1 |  |  | B2/E01_C | [8 empty] | 南科ES.3510_87LA1 | 新嘉民二路(3510)電纜87A1 | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 3510 | 87LA2 | 新嘉民南科二路 Cable 87LA2 |  |  | B2/E01_C | [8 empty] | 南科ES.3510_87LA2 | 新嘉民二路(3510)電纜87A2 | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | 3570 | 87LA1 | 新嘉民南科一路 Cable 87LA1 |  |  | B2/E01_C | [8 empty] | 南科ES.3570_87LA1 | 新嘉民一路(3570)電纜87A1 | OTHER |  |  |  |  | CDC | 461 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 3570 | 87LA2 | 新嘉民南科一路 Cable 87LA2 |  |  | B2/E01_C | [8 empty] | 南科ES.3570_87LA2 | 新嘉民一路(3570)電纜87A2 | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | ComPoint |  |  | RTU_MCT | MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 345RTU | MCT_ SOE | 345 RTU MASTER RY SOE |  |  | B2/E01_C | [15 empty] | CDC | 463 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0598 |  |  | 1-3F-06 |  |  | 3640 | RYFA | 嘉民南科一路 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.3640_RYFA | 嘉民ㄧ路(3640)數位電驛故障 | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0599 |  |  | 1-3F-07 |  |  | 3540 | RYFA | 嘉民南科二路 數位電驛故障 |  |  | B2/E01_C | [8 empty] | 南科ES.3540_RYFA | 嘉民二路(3540)數位電驛故障 | OTHER |  |  |  |  | CDC | 465 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
E01 | 南科ES | 0 |  | CalcPoint |  |  | Vbs8 | [9 empty] | B1/E01_C | [15 empty] | BEST_SOURCE_35KV_1 |  | v_best_345_12 | OPRD1: E01/345/1BUS/V; OPRD2: E01/345/2BUS/V
E01 | 南科ES | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/E01_C | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: E01/0/CalcPoint/Vbs8; OPRD9: NULL
E01 | 南科ES | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/E01_C | [15 empty] | TOT_1MTR_CAL |  | p_sum_12 | OPRD1: E01/345/3510/MW; OPRD2: E01/345/3530/MW; OPRD3: E01/345/3540/MW; OPRD4: E01/345/3560/MW; OPRD5: E01/345/3570/MW; OPRD6: E01/345/3590/MW; OPRD7: E01/345/3610/MW; OPRD8: E01/345/3630/MW; OPRD9: E01/345/3640/MW; OPRD10: E01/345/3660/MW; OPRD11: E01/345/3670/MW; OPRD12: E01/345/3690/MW
E01 | 南科ES | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/E01_C | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: E01/0/CalcPoint/OPRN2_MW
E01 | 南科ES | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/E01_C | [17 empty] | none
E01 | 南科ES | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/E01_C | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: E01/0/CalcPoint/OPRN1; OPRD2: E01/0/CalcPoint/OPRN2; OPRD3: E01/0/CalcPoint/PRFL_UL
E01 | 南科ES |  |  | 1ATR | 1ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.#1ATR_AMP | #1ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E01/345/3530/MW; OPRD2: E01/345/3530/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES |  |  | 2ATR | 2ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.#2ATR_AMP | #2ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E01/345/3560/MW; OPRD2: E01/345/3560/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES |  |  | 3ATR | 3ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.#3ATR_AMP | #3ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E01/345/3590/MW; OPRD2: E01/345/3590/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES |  |  | 4ATR | 4ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.#4ATR_AMP | #4ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E01/345/3630/MW; OPRD2: E01/345/3630/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES |  |  | 5ATR | 5ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.#5ATR_AMP | #5ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E01/345/3660/MW; OPRD2: E01/345/3660/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES |  |  | 6ATR | 6ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.#6ATR_AMP | #6ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E01/345/3690/MW; OPRD2: E01/345/3690/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民～南科二路(3510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.3510_AMP | 新嘉民二路 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E01/345/3510/MW; OPRD2: E01/345/3510/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民～南科二路(3540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.3540_AMP | 嘉民二路 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E01/345/3540/MW; OPRD2: E01/345/3540/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民～南科一路(3570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.3570_AMP | 新嘉民一路 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E01/345/3570/MW; OPRD2: E01/345/3570/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES | 345 | 345kV | 3610 | 南科～龍崎一路(3610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.3610_AMP | 龍崎一路 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E01/345/3610/MW; OPRD2: E01/345/3610/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民～南科一路(3640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.3640_AMP | 嘉民一路 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E01/345/3640/MW; OPRD2: E01/345/3640/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES | 345 | 345kV | 3670 | 南科～龍崎二路(3670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E01_C | [12 empty] | 南科ES.3670_AMP | 龍崎二路 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E01/345/3670/MW; OPRD2: E01/345/3670/MVAR; OPRD3: E01/0/CalcPoint/Vbs8
E01 | 南科ES |  |  | 1ATR | #1ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E01_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 南科ES.#1ATR_MVA | #1ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E01/345/3530/MW; OPRD2: E01/345/3530/MVAR
E01 | 南科ES |  |  | 2ATR | #2ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E01_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 南科ES.#2ATR_MVA | #2ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E01/345/3560/MW; OPRD2: E01/345/3560/MVAR
E01 | 南科ES |  |  | 3ATR | #3ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E01_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 南科ES.#3ATR_MVA | #3ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E01/345/3590/MW; OPRD2: E01/345/3590/MVAR
E01 | 南科ES |  |  | 4ATR | #4ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E01_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 南科ES.#4ATR_MVA | #4ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E01/345/3630/MW; OPRD2: E01/345/3630/MVAR
E01 | 南科ES |  |  | 5ATR | #5ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E01_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 南科ES.#5ATR_MVA | #5ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E01/345/3660/MW; OPRD2: E01/345/3660/MVAR
E01 | 南科ES |  |  | 6ATR | #6ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E01_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 南科ES.#6ATR_MVA | #6ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E01/345/3690/MW; OPRD2: E01/345/3690/MVAR
E01 | 南科ES |  |  | 1ATR | #1ATR |  | LOAD | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#1ATR_LOAD | #1ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E01//1ATR/MVA; OPRD2: 500
E01 | 南科ES |  |  | 2ATR | #2ATR |  | LOAD | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#2ATR_LOAD | #2ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E01//2ATR/MVA; OPRD2: 500
E01 | 南科ES |  |  | 3ATR | #3ATR |  | LOAD | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#3ATR_LOAD | #3ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E01//3ATR/MVA; OPRD2: 500
E01 | 南科ES |  |  | 4ATR | #4ATR |  | LOAD | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#4ATR_LOAD | #4ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E01//4ATR/MVA; OPRD2: 500
E01 | 南科ES |  |  | 5ATR | #5ATR |  | LOAD | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#5ATR_LOAD | #5ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E01//5ATR/MVA; OPRD2: 500
E01 | 南科ES |  |  | 6ATR | #6ATR |  | LOAD | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#6ATR_LOAD | #6ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E01//6ATR/MVA; OPRD2: 500
E01 | 南科ES |  |  | 1ATR | #1ATR |  | PF | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#1ATR_PF | #1ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E01/345/3530/MW; OPRD2: E01/345/3530/MVAR
E01 | 南科ES |  |  | 2ATR | #2ATR |  | PF | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#2ATR_PF | #2ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E01/345/3560/MW; OPRD2: E01/345/3560/MVAR
E01 | 南科ES |  |  | 3ATR | #3ATR |  | PF | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#3ATR_PF | #3ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E01/345/3590/MW; OPRD2: E01/345/3590/MVAR
E01 | 南科ES |  |  | 4ATR | #4ATR |  | PF | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#4ATR_PF | #4ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E01/345/3630/MW; OPRD2: E01/345/3630/MVAR
E01 | 南科ES |  |  | 5ATR | #5ATR |  | PF | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#5ATR_PF | #5ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E01/345/3660/MW; OPRD2: E01/345/3660/MVAR
E01 | 南科ES |  |  | 6ATR | #6ATR |  | PF | [9 empty] | B2/E01_C | [12 empty] | 南科ES.#6ATR_PF | #6ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E01/345/3690/MW; OPRD2: E01/345/3690/MVAR
E01 | 南科ES | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/E01_C | [12 empty] | 南科ES.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_20 |  | com_alarm_47 | E01//1ATR/96B2 | E01//1ATR/TRA | E01//1ATR/96B1 | E01//1ATR/63Q | E01//1ATR/96D | E01//1ATR/51ZA | E01//1ATR/96PA | E01//2ATR/96PA | E01//2ATR/96B2 | E01//2ATR/51ZA | E01//2ATR/96B1 | E01//2ATR/TRA | E01//2ATR/96D | E01//2ATR/63Q | E01//3ATR/96B2 | E01//3ATR/TRA | E01//3ATR/96B1 | E01//3ATR/96D | E01//3ATR/63Q | E01//3ATR/96PA | E01//3ATR/51ZA | E01//4ATR/96B2 | E01//4ATR/96B1 | E01//4ATR/96PA | E01//4ATR/TRA | E01//4ATR/63Q | E01//4ATR/51ZA | E01//4ATR/96D | E01//5ATR/96PA | E01//5ATR/51ZA | E01//5ATR/TRA | E01//5ATR/96B2 | E01//5ATR/96D | E01//5ATR/63Q | E01//5ATR/96B1 | E01//6ATR/TRA | E01//6ATR/96D | E01//6ATR/96PA | E01//6ATR/51ZA | E01//6ATR/96B2 | E01//6ATR/96B1 | E01//6ATR/63Q | E01/33/510/87A | E01/33/520/87A | E01/33/530/87A | E01/33/550/87A | E01/33/560/87A
E01 | 南科ES | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/E01_C | [12 empty] | 南科ES.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_4 |  | com_alarm_6 | OPRD1: E01//1ATR/TRF; OPRD2: E01//2ATR/TRF; OPRD3: E01//3ATR/TRF; OPRD4: E01//4ATR/TRF; OPRD5: E01//5ATR/TRF; OPRD6: E01//6ATR/TRF
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 1_DCV_P | #1直流P電源 |  | MvMoment | #1 直流P電源電壓 |  | Y |  | AI |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/1_DCV_P
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 1_DCV_N | #1直流N電源 |  | MvMoment | #1 直流N電源電壓 |  | Y |  | AI |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/1_DCV_N
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 2_DCV_P | #2直流P電源 |  | MvMoment | #2 直流P電源電壓 |  | Y |  | AI |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/2_DCV_P
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 2_DCV_N | #2直流N電源 |  | MvMoment | #2 直流N電源電壓 |  | Y |  | AI |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/2_DCV_N
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/CHG2
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/CommACF
E01 | 南科ES | 0 |  | RTU_C | RTU |  | RTU_R_L | RTU_S/L(1) |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/RTU/RTU_R_L
E01 | 南科ES | 0 |  | RTU_D1 | RTU |  | RTU_R_L | RTU_S/L(1) |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/E01_D1 | [17 empty] | lamp2CC | OPRD1: E01/0/RTU/RTU_R_L
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 1A5Other | COF |  | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/1A5Other
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 3A5Other | #1充電機故障 |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/3A5Other
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 4A5Other | #2充電機故障 |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/4A5Other
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 5A5Other | #3充電機故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/5A5Other
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | STUV | A所內電源欠壓 |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/STUV
E01 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | STUV | A所內電源欠壓 |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E01_D1 | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/STUV
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | DCA | A棟直流電源DCA |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/DCA
E01 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | DCA | A棟直流電源DCA |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E01_D1 | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/DCA
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | DCE | A棟直流電源DCE |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/DCE
E01 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | DCE | A棟直流電源DCE |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E01_D1 | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/DCE
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | OilLeak | A洩油池水位 |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/OilLeak
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Water |  |  | Status | 地下室淹水 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/Water
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 6A5Other | 電壓驟降 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/6A5Other
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 7A5Other | 通信機房溫度 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/7A5Other
E01 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 8A5Other | SOE_SYN |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E01_C | [17 empty] | lamp2CC | OPRD1: E01/0/StaDev/8A5Other

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E01 | 南科ES | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 南科ES.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_161KV_4 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
E01 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1510_AMP | 南科道爺ㄧ路 AMP | LINE161 |  |  | AMP_CAL |  |  | 3 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1520_AMP | 南科道爺二路 AMP | LINE161 |  |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1550_AMP | 三福科線 AMP | LINE161 |  |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1610_AMP | 麻工ㄧ路 AMP | LINE161 |  |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1620_AMP | 麻工二路 AMP | LINE161 |  |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1630_AMP | 南科豐華紅線 AMP | LINE161 |  |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1640_AMP | 南科豐華白線 AMP | LINE161 |  |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1650_AMP | 三竹ㄧ路 AMP | LINE161 |  |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1660_AMP | 三竹二路 AMP | LINE161 |  |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1670_AMP | 積六線 AMP | LINE161 |  |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1680_AMP | 康寧線 AMP | LINE161 |  |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C20R0964 | 867.599976 | 867.599976 | 964.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1710_AMP | 南科和鑫二線 AMP | LINE161 |  |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1720_AMP | 南科積P3線 AMP | LINE161 |  |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1730_AMP | 積十八線 AMP | LINE161 |  |  | AMP_CAL |  |  | 16 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1740_AMP | 積十九線 AMP | LINE161 |  |  | AMP_CAL |  |  | 17 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 0 |  |  |  |  | 科二十線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科二十線KVA | 11KV科二十線KVA | FEEDER |  |  | KVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科二十線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科二十線KW | 11KV科二十線KW | FEEDER |  |  | KW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十七線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十七線KVA | 11KV科十七線KVA | FEEDER |  |  | KVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十七線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十七線KW | 11KV科十七線KW | FEEDER |  |  | KW_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十九線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十九線KVA | 11KV科十九線KVA | FEEDER |  |  | KVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十九線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十九線KW | 11KV科十九線KW | FEEDER |  |  | KW_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十八線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十八線KVA | 11KV科十八線KVA | FEEDER |  |  | KVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十八線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十八線KW | 11KV科十八線KW | FEEDER |  |  | KW_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十六線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十六線KVA | 11KV科十六線KVA | FEEDER |  |  | KVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科十六線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科十六線KW | 11KV科十六線KW | FEEDER |  |  | KW_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七一線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七一線KVA | 23KV科七一線KVA | FEEDER |  |  | KVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七一線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七一線KW | 23KV科七一線KW | FEEDER |  |  | KW_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七七線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七七線KVA | 23KV科七七線KVA | FEEDER |  |  | KVA_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七七線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七七線KW | 23KV科七七線KW | FEEDER |  |  | KW_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七二線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七二線KVA | 23KV科七二線KVA | FEEDER |  |  | KVA_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七二線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七二線KW | 23KV科七二線KW | FEEDER |  |  | KW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七八線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七八線KVA | 23KV科七八線KVA | FEEDER |  |  | KVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七八線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七八線KW | 23KV科七八線KW | FEEDER |  |  | KW_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七三線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七三線KVA | 23KV科七三線KVA | FEEDER |  |  | KVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七三線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七三線KW | 23KV科七三線KW | FEEDER |  |  | KW_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七五線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七五線KVA | 23KV科七五線KVA | FEEDER |  |  | KVA_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七五線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七五線KW | 23KV科七五線KW | FEEDER |  |  | KW_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七六線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七六線KVA | 23KV科七六線KVA | FEEDER |  |  | KVA_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七六線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七六線KW | 23KV科七六線KW | FEEDER |  |  | KW_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七四線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七四線KVA | 23KV科七四線KVA | FEEDER |  |  | KVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科七四線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科七四線KW | 23KV科七四線KW | FEEDER |  |  | KW_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六一線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六一線KVA | 23KV科六一線KVA | FEEDER |  |  | KVA_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六一線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六一線KW | 23KV科六一線KW | FEEDER |  |  | KW_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六七線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六七線KVA | 23KV科六七線KVA | FEEDER |  |  | KVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六七線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六七線KW | 23KV科六七線KW | FEEDER |  |  | KW_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六二線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六二線KVA | 23KV科六二線KVA | FEEDER |  |  | KVA_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六二線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六二線KW | 23KV科六二線KW | FEEDER |  |  | KW_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六八線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六八線KVA | 23KV科六八線KVA | FEEDER |  |  | KVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六八線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六八線KW | 23KV科六八線KW | FEEDER |  |  | KW_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六三線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六三線KVA | 23KV科六三線KVA | FEEDER |  |  | KVA_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六三線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六三線KW | 23KV科六三線KW | FEEDER |  |  | KW_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六五線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六五線KVA | 23KV科六五線KVA | FEEDER |  |  | KVA_CAL |  |  | 54 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六五線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六五線KW | 23KV科六五線KW | FEEDER |  |  | KW_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六六線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六六線KVA | 23KV科六六線KVA | FEEDER |  |  | KVA_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六六線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六六線KW | 23KV科六六線KW | FEEDER |  |  | KW_CAL |  |  | 57 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六四線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六四線KVA | 23KV科六四線KVA | FEEDER |  |  | KVA_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科六四線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科六四線KW | 23KV科六四線KW | FEEDER |  |  | KW_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 61 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_MVA | #4DTR二次側(A) MVA | MTR |  |  | MVA_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_LOAD | #4DTR(A) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 67 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_PF | #4DTR(A) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_MVA | #4DTR二次側(B) MVA | MTR |  |  | MVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4DTR(B) | #4DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_LOAD | #4DTR(B) 負載率 | MTR |  |  | TR_LOAD_30 |  |  | 70 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4DTR(B) | #4DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_PF | #4DTR(B) 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_MW | #1DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_MVAR | #1DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_MVA | #1DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_LOAD | #1DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 75 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_MVA | #2DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 2DTR | #2DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_PF | #2DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_LOAD | #2DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 78 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_MVA | #3DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 3DTR | #3DTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_PF | #3DTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_LOAD | #3DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 81 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4DTR | #4DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_MW | #4DTR MW | MTR |  |  | MTR_PQ_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | 4DTR | #4DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_MVAR | #4DTR MVAR | MTR |  |  | MTR_PQ_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | 4DTR | #4DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_MVA | #4DTR二次側 MVA | MTR |  |  | MVA_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4DTR | #4DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_LOAD | #4DTR 負載率 | MTR |  |  | TR_LOAD_60 |  |  | 85 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 22 | 22kV | 210_SC | #1SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.210_SC_MVAR | 23KV#1SC MVAR | SC |  |  | SC_CAL_23 |  |  | 86 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.220_SC_MVAR | 11KV#2SC MVAR | SC |  |  | SC_LBS_11 |  |  | 87 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.230_SC_MVAR | 23KV#3SC MVAR | SC |  |  | SC_CAL_23 |  |  | 88 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 240_SC | #4SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.240_SC_MVAR | 23KV#4SC MVAR | SC |  |  | SC_CAL_23 |  |  | 89 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.250_SC_MVAR | 23KV#5SC MVAR | SC |  |  | SC_CAL_23 |  |  | 90 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.260_SC_MVAR | 23KV#6SC MVAR | SC |  |  | SC_CAL_23 |  |  | 91 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | ETOTAL | 南科東轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.ETOTAL_MW | 南科東轄區瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 92 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | ETOTAL | 南科東轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 南科ES.ETOTAL_MVAR | 南科東轄區瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_12 |  |  | 93 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | WTOTAL | 南科西轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.WTOTAL_MW | 南科西轄區瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 94 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | WTOTAL | 南科西轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 南科ES.WTOTAL_MVAR | 南科西轄區瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_9 |  |  | 95 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | TOTAL | 南科轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.TOTAL_MW | 南科轄區瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | TOTAL | 南科轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 南科ES.TOTAL_MVAR | 南科轄區瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1570_AMP | 南科道爺三路 AMP | LINE161 |  |  | AMP_CAL |  |  | 98 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 0 |  | DTR_TOT | 南科DTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.DTR_TOT_MW | 南科DTR瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 99 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 345 | 345kV | _BUS | BUS |  | V | [25 empty] | CDCS_S | [8 empty] | 南科ES.345KV_BUS_KV | 345KV BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_345KV_2 |  |  | 100 | CalcAIPoint | [21 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | I | [25 empty] | CDCS_S | [8 empty] | 南科ES.3510_AMP | 新嘉民二路 AMP | LINE345 | E01/345/3510/I |  | AMP_CAL |  |  | 101 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | I | [25 empty] | CDCS_S | [8 empty] | 南科ES.3540_AMP | 嘉民二路 AMP | LINE345 | E01/345/3540/I |  | AMP_CAL |  |  | 102 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | I | [25 empty] | CDCS_S | [8 empty] | 南科ES.3570_AMP | 新嘉民一路 AMP | LINE345 | E01/345/3570/I |  | AMP_CAL |  |  | 103 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | I | [25 empty] | CDCS_S | [8 empty] | 南科ES.3610_AMP | 龍崎一路 AMP | LINE345 | E01/345/3610/I |  | AMP_CAL |  |  | 104 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | I | [25 empty] | CDCS_S | [8 empty] | 南科ES.3640_AMP | 嘉民一路 AMP | LINE345 | E01/345/3640/I |  | AMP_CAL |  |  | 105 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | I | [25 empty] | CDCS_S | [8 empty] | 南科ES.3670_AMP | 龍崎二路 AMP | LINE345 | E01/345/3670/I |  | AMP_CAL |  |  | 106 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E01 | 南科ES | 0 |  | 1ATR | #1ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_MVA | #1ATR二次側 MVA | ATR | E01//1ATR/MVA |  | MVA_CAL |  |  | 107 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_LOAD | #1ATR 負載率 | ATR | E01//1ATR/Loading |  | TR_LOAD_500 |  |  | 108 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_PF | #1ATR 功率因素 | ATR | E01//1ATR/PF |  | RPDC_PF_CAL |  |  | 109 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_AMP | #1ATR 二次側 AMP | ATR | E01//1ATR/I |  | AMP_CAL |  |  | 110 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E01 | 南科ES | 0 |  | 2ATR | #2ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_MVA | #2ATR二次側 MVA | ATR | E01//2ATR/MVA |  | MVA_CAL |  |  | 111 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_LOAD | #2ATR 負載率 | ATR | E01//2ATR/Loading |  | TR_LOAD_500 |  |  | 112 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_PF | #2ATR 功率因素 | ATR | E01//2ATR/PF |  | RPDC_PF_CAL |  |  | 113 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_AMP | #2ATR 二次側 AMP | ATR | E01//2ATR/I |  | AMP_CAL |  |  | 114 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E01 | 南科ES | 0 |  | 3ATR | #3ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_MVA | #3ATR二次側 MVA | ATR | E01//3ATR/MVA |  | MVA_CAL |  |  | 115 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_LOAD | #3ATR 負載率 | ATR | E01//3ATR/Loading |  | TR_LOAD_500 |  |  | 116 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_PF | #3ATR 功率因素 | ATR | E01//3ATR/PF |  | RPDC_PF_CAL |  |  | 117 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_AMP | #3ATR 二次側 AMP | ATR | E01//3ATR/I |  | AMP_CAL |  |  | 118 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E01 | 南科ES | 0 |  | 4ATR | #4ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_MVA | #4ATR二次側 MVA | ATR | E01//4ATR/MVA |  | MVA_CAL |  |  | 119 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_LOAD | #4ATR 負載率 | ATR | E01//4ATR/Loading |  | TR_LOAD_500 |  |  | 120 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_PF | #4ATR 功率因素 | ATR | E01//4ATR/PF |  | RPDC_PF_CAL |  |  | 121 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_AMP | #4ATR 二次側 AMP | ATR | E01//4ATR/I |  | AMP_CAL |  |  | 122 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E01 | 南科ES | 0 |  | 5ATR | #5ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_MVA | #5ATR二次側 MVA | ATR | E01//5ATR/MVA |  | MVA_CAL |  |  | 123 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_LOAD | #5ATR 負載率 | ATR | E01//5ATR/Loading |  | TR_LOAD_500 |  |  | 124 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_PF | #5ATR 功率因素 | ATR | E01//5ATR/PF |  | RPDC_PF_CAL |  |  | 125 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_AMP | #5ATR 二次側 AMP | ATR | E01//5ATR/I |  | AMP_CAL |  |  | 126 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E01 | 南科ES | 0 |  | 6ATR | #6ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_MVA | #6ATR二次側 MVA | ATR | E01//6ATR/MVA |  | MVA_CAL |  |  | 127 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_LOAD | #6ATR 負載率 | ATR | E01//6ATR/Loading |  | TR_LOAD_500 |  |  | 128 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_PF | #6ATR 功率因素 | ATR | E01//6ATR/PF |  | RPDC_PF_CAL |  |  | 129 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_AMP | #6ATR 二次側 AMP | ATR | E01//6ATR/I |  | AMP_CAL |  |  | 130 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E01 | 南科ES | 0 |  | TRTOT | 南科主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.TRTOT_MW | 南科主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_6 |  |  | 131 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 2BUS | #2BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 南科ES.23KV#2BUS_KV | 23KV #2BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 132 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 22 | 22kV | 3BUS | #3BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 南科ES.23KV#3BUS_KV | 23KV #3BUS BEST SOURCE | BUS |  |  | BEST_1W2CB |  |  | 133 | CalcAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1540_AMP | 南科積E六線 AMP | LINE161 |  |  | AMP_CAL |  |  | 134 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 0 |  |  |  |  | 科21線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科21線KVA | 11KV科21線KVA | FEEDER |  |  | KVA_CAL |  |  | 135 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科21線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科21線KW | 11KV科21線KW | FEEDER |  |  | KW_CAL |  |  | 136 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科22線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科22線KVA | 11KV科22線KVA | FEEDER |  |  | KVA_CAL |  |  | 137 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科22線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科22線KW | 11KV科22線KW | FEEDER |  |  | KW_CAL |  |  | 138 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科23線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科23線KVA | 11KV科23線KVA | FEEDER |  |  | KVA_CAL |  |  | 139 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科23線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科23線KW | 11KV科23線KW | FEEDER |  |  | KW_CAL |  |  | 140 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科24線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科24線KVA | 11KV科24線KVA | FEEDER |  |  | KVA_CAL |  |  | 141 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科24線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科24線KW | 11KV科24線KW | FEEDER |  |  | KW_CAL |  |  | 142 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科25線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科25線KVA | 11KV科25線KVA | FEEDER |  |  | KVA_CAL |  |  | 143 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科25線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科25線KW | 11KV科25線KW | FEEDER |  |  | KW_CAL |  |  | 144 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7A線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7A線KVA | 23KV科7A線KVA | FEEDER |  |  | KVA_CAL |  |  | 145 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7A線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7A線KW | 23KV科7A線KW | FEEDER |  |  | KW_CAL |  |  | 146 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7B線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7B線KVA | 23KV科7B線KVA | FEEDER |  |  | KVA_CAL |  |  | 147 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7B線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7B線KW | 23KV科7B線KW | FEEDER |  |  | KW_CAL |  |  | 148 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7C線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7C線KVA | 23KV科7C線KVA | FEEDER |  |  | KVA_CAL |  |  | 149 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7C線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7C線KW | 23KV科7C線KW | FEEDER |  |  | KW_CAL |  |  | 150 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7D線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7D線KVA | 23KV科7D線KVA | FEEDER |  |  | KVA_CAL |  |  | 151 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科7D線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科7D線KW | 23KV科7D線KW | FEEDER |  |  | KW_CAL |  |  | 152 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 11 | 11kV | 280_SC | #8SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.280_SC_MVAR | 11KV#8SC MVAR | SC |  |  | SC_LBS_11 |  |  | 153 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 270_SC | #7SC | 9 | MVAR | [25 empty] | ADCS_S | [8 empty] | 南科ES.270_SC_MVAR | 23KV#7SC MVAR | SC |  |  | SC_CAL_23 |  |  | 154 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科51線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科51線KVA | 23KV科51線KVA | FEEDER |  |  | KVA_CAL |  |  | 155 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科51線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科51線KW | 23KV科51線KW | FEEDER |  |  | KW_CAL |  |  | 156 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科52線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科52線KVA | 23KV科52線KVA | FEEDER |  |  | KVA_CAL |  |  | 157 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科52線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科52線KW | 23KV科52線KW | FEEDER |  |  | KW_CAL |  |  | 158 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科53線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科53線KVA | 23KV科53線KVA | FEEDER |  |  | KVA_CAL |  |  | 159 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科53線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科53線KW | 23KV科53線KW | FEEDER |  |  | KW_CAL |  |  | 160 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科54線KVA | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科54線KVA | 23KV科54線KVA | FEEDER |  |  | KVA_CAL |  |  | 161 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  |  |  |  | 科54線KW | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.科54線KW | 23KV科54線KW | FEEDER |  |  | KW_CAL |  |  | 162 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | TEN_DAYS17 | (1710+1720 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.TEN_DAYS17_MW | (1710+1720 MW) |  |  |  | MTR_PQ_CAL |  |  | 163 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | TEN_DAYS07 | (1670+1680 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 南科ES.TEN_DAYS07_MW | (1670+1680 MW) |  |  |  | MTR_PQ_CAL |  |  | 164 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1580_AMP | 南科道爺四路 AMP | LINE161 |  |  | AMP_CAL |  |  | 165 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 南科ES.1530_AMP | 南科三福一線 AMP | LINE161 |  |  | AMP_CAL |  |  | 166 | CalcAIPoint | [21 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E01 | 南科ES | 33 | 33kV | 520_SHR | #2SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 南科ES.520_SHR_MVAR | 33KV#2SHR MVAR | SC |  |  | SHR_CAL_33KV_5 |  |  | 167 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 33 | 33kV | 530_SHR | #3SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 南科ES.530_SHR_MVAR | 33KV#3SHR MVAR | SC |  |  | SHR_CAL_33KV_5 |  |  | 168 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 33 | 33kV | 550_SHR | #5SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 南科ES.550_SHR_MVAR | 33KV#5SHR MVAR | SC |  |  | SHR_CAL_33KV_5 |  |  | 169 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 170 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 171 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 172 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 400_CB | 400(400_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.400_CB_4 | 400 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 173 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 174 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 175 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 320_CB | #1DTR(320_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.320_CB_4 | 320(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 176 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 177 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 178 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 179 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 180 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 181 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 360_CB | #3DTR(360_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.360_CB_4 | 360(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 182 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 1780_CB | #4DTR(1780_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.1780_CB_4 | 1780(#4DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 183 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 370_CB | #4DTR(370_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.370_CB_4 | 370(#4DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 184 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 380_CB | #4DTR(380_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.380_CB_4 | 380(#4DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 185 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 22 | 22kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.210_CB_4 | 210(23KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 186 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 187 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.230_CB_4 | 230(23KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 188 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 22 | 22kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.240_CB_4 | 240(23KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 189 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.250_CB_4 | 250(23KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 190 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.260_CB_4 | 260(23KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 191 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.RTU_S/L_4 | RTU SUPY/LOCAL點燈 (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 192 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E01 | 南科ES | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 南科ES.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | E01/0/CalcPoint/SUBA |  | STATION_FAULT_20 |  |  | 193 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 南科ES.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | E01/0/CalcPoint/SUBF |  | STATION_FAULT_4 |  |  | 194 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 195 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 196 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 161 | 161kV | 1510_AMP | 南科道爺ㄧ路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1510_AMP_A | 南科道爺ㄧ路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 197 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1520_AMP | 南科道爺二路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1520_AMP_A | 南科道爺二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 198 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1550_AMP | 三福科線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1550_AMP_A | 三福科線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 199 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1610_AMP | 麻工ㄧ路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1610_AMP_A | 麻工ㄧ路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 200 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1620_AMP | 麻工二路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1620_AMP_A | 麻工二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 201 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1630_AMP | 南科豐華紅線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1630_AMP_A | 南科豐華紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 202 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1640_AMP | 南科豐華白線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1640_AMP_A | 南科豐華白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 203 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1650_AMP | 三竹ㄧ路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1650_AMP_A | 三竹ㄧ路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 204 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1660_AMP | 三竹二路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1660_AMP_A | 三竹二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 205 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1670_AMP | 積六線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1670_AMP_A | 積六線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 206 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1680_AMP | 康寧線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1680_AMP_A | 康寧線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 207 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1710_AMP | 南科和鑫二線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1710_AMP_A | 南科和鑫二線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 208 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1720_AMP | 南科積P3線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1720_AMP_A | 南科積P3線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 209 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR |  |  | DTR_PERM |  |  | 210 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR |  |  | DTR_PERM |  |  | 211 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2DTR | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_PERM | #2DTR TAP PERMISSION POINT | MTR |  |  | DTR_PERM |  |  | 212 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3DTR | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_PERM | #3DTR TAP PERMISSION POINT | MTR |  |  | DTR_PERM |  |  | 213 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_PERM | #4DTR(A) TAP PERMISSION POINT | MTR |  |  | DTR_PERM |  |  | 214 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4DTR(B) | #4DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_PERM | #4DTR TAP PERMISSION POINT | MTR |  |  | DTR_PERM |  |  | 215 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 216 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1DTR_MVA | #1DTR(A) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.#1DTR_MVA_4 | #1DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 217 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1DTR_MVA | #1DTR(B) |  | 5 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.#1DTR_MVA_5 | #1DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 218 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 219 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2DTR_MVA | #2DTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.#2DTR_MVA_4 | #2DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 220 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 221 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3DTR_MVA | #3DTR |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.#3DTR_MVA_4 | #3DTR MVA 點燈 (D4) | MTR |  |  | AD_LAMP_DD_2 |  |  | 222 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 22 | 22kV | 11__CBA | 11/斷路器重故障(11__CBA) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.11/23KV_CBA_4 | 11/23KV斷路器重故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 223 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 11__CBF | 11/斷路器輕故障(11__CBF) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.11/23KV_CBF_4 | 11/23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 224 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4DTR_MVA | #4DTR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_MVA_A | #4DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 225 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4DTR_MVA | #4DTR(A) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.#4DTR_MVA_4 | #4DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 226 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4DTR_MVA | #4DTR(B) |  | 5 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.#4DTR_MVA_5 | #4DTR(B) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 227 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1570_AMP | 南科道爺三路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1570_AMP_A | 南科道爺三路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 228 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 南科ES.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_ES_6 |  |  | 229 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510_AMP | 新嘉民二路 | [27 empty] | CDCS_S | [8 empty] | 南科ES.3510_AMP_A | 新嘉民二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 230 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 345 | 345kV | 3540_AMP | 嘉民二路 | [27 empty] | CDCS_S | [8 empty] | 南科ES.3540_AMP_A | 嘉民二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 231 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 345 | 345kV | 3570_AMP | 新嘉民一路 | [27 empty] | CDCS_S | [8 empty] | 南科ES.3570_AMP_A | 新嘉民一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 232 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 345 | 345kV | 3610_AMP | 龍崎一路 | [27 empty] | CDCS_S | [8 empty] | 南科ES.3610_AMP_A | 龍崎一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 233 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 345 | 345kV | 3640_AMP | 嘉民一路 | [27 empty] | CDCS_S | [8 empty] | 南科ES.3640_AMP_A | 嘉民一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 234 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 345 | 345kV | 3670_AMP | 龍崎二路 | [27 empty] | CDCS_S | [8 empty] | 南科ES.3670_AMP_A | 龍崎二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 235 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1ATR_MVA | #1ATR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_MVA_A | #1ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 236 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_PERM | #1ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 237 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2ATR_MVA | #2ATR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_MVA_A | #2ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 238 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_PERM | #2ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 239 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3ATR_MVA | #3ATR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_MVA_A | #3ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 240 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_PERM | #3ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 241 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4ATR_MVA | #4ATR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_MVA_A | #4ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 242 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_PERM | #4ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 243 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 5ATR_MVA | #5ATR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_MVA_A | #5ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 244 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_PERM | #5ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 245 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 6ATR_MVA | #6ATR | [27 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_MVA_A | #6ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 246 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_PERM | #6ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 247 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 161 | 161kV | 1540_AMP | 南科積E六線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1540_AMP_A | 南科積E六線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 248 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 11 | 11kV | 280_CB | #8SC(280_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.280_CB_4 | 280(11KV #8SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 249 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.270_CB_4 | 270(23KV #7SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 250 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | PMA | 電力量測表計故障(#4DTR) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.PMA_4 | 電力量測表計故障(#4DTR) (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 251 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 161 | 161kV | 1580_AMP | 南科道爺四路 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1580_AMP_A | 南科道爺四路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 252 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1ABUS | #1ABUS |  | 23KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 南科ES.23KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 253 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 南科ES.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 254 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2ABUS | #2ABUS |  | 23KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 南科ES.23KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 255 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 南科ES.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 256 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 南科ES.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 257 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 南科ES.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 258 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4ABUS | #4ABUS |  | 23KV#4ABUSC | [25 empty] | CDCS | [8 empty] | 南科ES.23KV#4ABUSC | #4ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 259 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 4BBUS | #4BBUS |  | 11KV#4BBUSC | [25 empty] | CDCS | [8 empty] | 南科ES.11KV#4BBUSC | #4BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 260 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 南科ES.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T6 |  |  | 261 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 南科ES.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B8 |  |  | 262 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 南科ES.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 263 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1530_AMP | 南科三福一線 | [27 empty] | ADCS_S | [8 empty] | 南科ES.1530_AMP_A | 南科三福一線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 264 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E01 | 南科ES | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 南科ES.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_2 |  |  | 265 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 11__RYFA | 11/ IED |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 南科ES.11/23KV_RYFA_4 | 11/23KV IED 故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 266 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池 |  | 遠勁右池KVAR | [14 empty] | 0017 | [8 empty] | KVAR_-12000_12000(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池KVAR | 23KV遠勁右池 KVAR | FEEDER |  |  |  |  | DNP | 267 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池 |  | 遠勁右池A1 | [14 empty] | 0018 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池A1 | 23KV遠勁右池 R相AMP | FEEDER |  |  |  |  | DNP | 268 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池 |  | 遠勁右池A2 | [14 empty] | 0019 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池A2 | 23KV遠勁右池 S相AMP | FEEDER |  |  |  |  | DNP | 269 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池 |  | 遠勁右池A3 | [14 empty] | 0020 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池A3 | 23KV遠勁右池 T相AMP | FEEDER |  |  |  |  | DNP | 270 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池 |  | 遠勁左池KVAR | [14 empty] | 0009 | [8 empty] | KVAR_-12000_12000(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池KVAR | 23KV遠勁左池 KVAR | FEEDER |  |  |  |  | DNP | 271 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 7.200000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池 |  | 遠勁左池A1 | [14 empty] | 0010 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池A1 | 23KV遠勁左池 R相AMP | FEEDER |  |  |  |  | DNP | 272 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池 |  | 遠勁左池A2 | [14 empty] | 0011 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池A2 | 23KV遠勁左池 S相AMP | FEEDER |  |  |  |  | DNP | 273 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池 |  | 遠勁左池A3 | [14 empty] | 0012 | [8 empty] | A_-200_200(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池A3 | 23KV遠勁左池 T相AMP | FEEDER |  |  |  |  | DNP | 274 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | KV1 | [14 empty] | 0021 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_KV1 | 22KV遠勁右池(K252) VR | OTHER |  |  |  |  | DNP | 275 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | KV2 | [14 empty] | 0022 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_KV2 | 22KV遠勁右池(K252) VS | OTHER |  |  |  |  | DNP | 276 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | KV3 | [14 empty] | 0023 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_KV3 | 22KV遠勁右池(K252) VT | OTHER |  |  |  |  | DNP | 277 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | KW | [14 empty] | 0016 | [8 empty] | KW_-12000_12000(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_KW | 22KV遠勁右池(K252) KW | OTHER |  |  |  |  | DNP | 278 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | KV1 | [14 empty] | 0013 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_KV1 | 22KV遠勁左池(K27B) VR | OTHER |  |  |  |  | DNP | 279 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | KV2 | [14 empty] | 0014 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_KV2 | 22KV遠勁左池(K27B) VS | OTHER |  |  |  |  | DNP | 280 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | KV3 | [14 empty] | 0015 | [8 empty] | kV_-18_18(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_KV3 | 22KV遠勁左池(K27B) VT | OTHER |  |  |  |  | DNP | 281 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | KW | [14 empty] | 0008 | [8 empty] | KW_-12000_12000(-2000_2000) |  | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_KW | 22KV遠勁左池(K27B) KW | OTHER |  |  |  |  | DNP | 282 | DNPAIPoint | PV004 |  |  | AI | [17 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 3.600000 | 0.010000
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | CB | [14 empty] | 0016 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_CB | 23KV遠勁右池(K252) CB | OTHER |  |  |  |  | DNP | 283 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 遠勁右池 | 遠勁右池 |  | CFA | [14 empty] | 1047 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_CFA | 23KV遠勁右池(K252)通訊警報 | OTHER |  |  |  |  | DNP | 284 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 遠勁右池 | 遠勁右池 |  | PHA | [14 empty] | 0018 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_PHA | 23KV遠勁右池(K252)PHA/GDA | OTHER |  |  |  |  | DNP | 285 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | PTDS | [14 empty] | 1042 | 1043 | [9 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_PTDS | 23KV遠勁右池(K252) PTDS | OTHER |  |  |  |  | DNP | 286 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 0 |  | 遠勁右池 | 遠勁右池 |  | UVA | [14 empty] | 0017 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_UVA | 23KV遠勁右池(K252)UVA+81A | OTHER |  |  |  |  | DNP | 287 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | CB | [14 empty] | 0008 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_CB | 23KV遠勁左池(K27B) CB | OTHER |  |  |  |  | DNP | 288 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 遠勁左池 | 遠勁左池 |  | CFA | [14 empty] | 1039 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_CFA | 23KV遠勁左池(K27B)通訊警報 | OTHER |  |  |  |  | DNP | 289 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 遠勁左池 | 遠勁左池 |  | PHA | [14 empty] | 0010 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_PHA | 23KV遠勁左池(K27B)PHA/GDA | OTHER |  |  |  |  | DNP | 290 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | PTDS | [14 empty] | 1034 | 1035 | [9 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_PTDS | 23KV遠勁左池(K27B) PTDS | OTHER |  |  |  |  | DNP | 291 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 0 |  | 遠勁左池 | 遠勁左池 |  | UVA | [14 empty] | 0009 | [10 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_UVA | 23KV遠勁左池(K252)UVA+81A | OTHER |  |  |  |  | DNP | 292 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | DS1 | 遠勁右池 | [13 empty] | 1040 | 1041 | [9 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_DS | 23KV遠勁右池(K252) DS | OTHER |  |  |  |  | DNP | 293 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | DS1 | 遠勁左池 | [13 empty] | 1032 | 1033 | [9 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_DS | 23KV遠勁左池(K27B) DS | OTHER |  |  |  |  | DNP | 294 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 22 | 22kV | 遠勁右池 | 遠勁右池(K252) |  | LE0 | 遠勁右池 | [13 empty] | 1044 | 1045 | [9 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁右池_ES | 23KV遠勁右池(K252) ES | OTHER |  |  |  |  | DNP | 295 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 22 | 22kV | 遠勁左池 | 遠勁左池(K27B) |  | LE0 | 遠勁左池 | [13 empty] | 1036 | 1037 | [9 empty] | DDCS4_1 | [8 empty] | 南科ES.遠勁左池_ES | 23KV遠勁左池(K27B) ES | OTHER |  |  |  |  | DNP | 296 | DNPDIPoint | PV004 |  |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南超ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | E01/0/RTU/ADCH1 |  |  |  | CDC | 297 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南超ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | E01/0/RTU/ADCH2 |  |  |  | CDC | 298 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南超ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 299 | GENERICAIPoint | ES001_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南超ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | E01/0/RTU/ADCL1 |  |  |  | CDC | 300 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南超ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | E01/0/RTU/ADCL2 |  |  |  | CDC | 301 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E01 | 南科ES | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南超ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 302 | GENERICAIPoint | ES001_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.345KV#1BUS_KV | 345KV #1BUS KV | BUS | E01/345/1BUS/V |  |  |  | CDC | 303 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.345KV#2BUS_KV | 345KV #2BUS KV | BUS | E01/345/2BUS/V |  |  |  | CDC | 304 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3510_MW | 新嘉民二路 MW | LINE345 | E01/345/3510/MW |  |  |  | CDC | 305 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3510_MVAR | 新嘉民二路 MVAR | LINE345 | E01/345/3510/MVAR |  |  |  | CDC | 306 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3510LPD | 新嘉民二路(3510) |  | V | [17 empty] | 1-B8 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3510LPD_KV | 新嘉民二路(3510) LPD KV | LINE345 | E01/345/3510/V |  |  |  | CDC | 307 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3540_MW | 嘉民二路 MW | LINE345 | E01/345/3540/MW |  |  |  | CDC | 308 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3540_MVAR | 嘉民二路 MVAR | LINE345 | E01/345/3540/MVAR |  |  |  | CDC | 309 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3540LPD | 嘉民二路(3540) |  | V | [17 empty] | 1-B9 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3540LPD_KV | 嘉民二路(3540) LPD KV | LINE345 | E01/345/3540/V |  |  |  | CDC | 310 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3570_MW | 新嘉民一路 MW | LINE345 | E01/345/3570/MW |  |  |  | CDC | 311 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3570_MVAR | 新嘉民一路 MVAR | LINE345 | E01/345/3570/MVAR |  |  |  | CDC | 312 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3570LPD | 新嘉民一路(3570) |  | V | [17 empty] | 1-BA | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3570LPD_KV | 新嘉民一路(3570) LPD KV | LINE345 | E01/345/3570/V |  |  |  | CDC | 313 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3610_MW | 龍崎一路 MW | LINE345 | E01/345/3610/MW |  |  |  | CDC | 314 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3610_MVAR | 龍崎一路 MVAR | LINE345 | E01/345/3610/MVAR |  |  |  | CDC | 315 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3610LPD | 龍崎一路(3610) |  | V | [17 empty] | 1-BB | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3610LPD_KV | 龍崎一路(3610) LPD KV | LINE345 | E01/345/3610/V |  |  |  | CDC | 316 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3640_MW | 嘉民一路 MW | LINE345 | E01/345/3640/MW |  |  |  | CDC | 317 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3640_MVAR | 嘉民一路 MVAR | LINE345 | E01/345/3640/MVAR |  |  |  | CDC | 318 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3640LPD | 嘉民一路(3640) |  | V | [17 empty] | 1-BC | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3640LPD_KV | 嘉民一路(3640) LPD KV | LINE345 | E01/345/3640/V |  |  |  | CDC | 319 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3670_MW | 龍崎二路 MW | LINE345 | E01/345/3670/MW |  |  |  | CDC | 320 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3670_MVAR | 龍崎二路 MVAR | LINE345 | E01/345/3670/MVAR |  |  |  | CDC | 321 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E01 | 南科ES | 345 | 345kV | 3670LPD | 龍崎二路(3670) |  | V | [17 empty] | 1-BD | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.3670LPD_KV | 龍崎二路(3670) LPD KV | LINE345 | E01/345/3670/V |  |  |  | CDC | 322 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E01 | 南科ES | 0 |  | 1ATR | #1ATR二次側 |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1ATR_MW | #1ATR二次側 MW | ATR | E01/345/3530/MW |  |  |  | CDC | 323 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 0 |  | 1ATR | #1ATR二次側 |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1ATR_MVAR | #1ATR二次側 MVAR | ATR | E01/345/3530/MVAR |  |  |  | CDC | 324 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | TapPosMv | [17 empty] | 1-92 |  | 1-2A |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_S | [8 empty] | 南科ES.#1ATR_TAP | #1ATR OLTC TAP | ATR | E01//1ATR/TapPosMv |  |  |  | CDC | 325 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES | 0 |  | 1ATR_OIL | #1ATR |  | R | [17 empty] | 1-94 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#1ATR_OIL_R | #1ATR R相油溫 | ATR | E01//1ATR/Oil_R |  |  |  | CDC | 326 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 1ATR_COIL | #1ATR |  | R | [17 empty] | 1-93 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#1ATR_COIL_R | #1ATR R相線溫 | ATR | E01//1ATR/Coil_R |  |  |  | CDC | 327 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 2ATR | #2ATR二次側 |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2ATR_MW | #2ATR二次側 MW | ATR | E01/345/3560/MW |  |  |  | CDC | 328 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 0 |  | 2ATR | #2ATR二次側 |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2ATR_MVAR | #2ATR二次側 MVAR | ATR | E01/345/3560/MVAR |  |  |  | CDC | 329 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | TapPosMv | [17 empty] | 1-97 |  | 1-2E |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_S | [8 empty] | 南科ES.#2ATR_TAP | #2ATR OLTC TAP | ATR | E01//2ATR/TapPosMv |  |  |  | CDC | 330 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES | 0 |  | 2ATR_OIL | #2ATR |  | R | [17 empty] | 1-99 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#2ATR_OIL_R | #2ATR R相油溫 | ATR | E01//2ATR/Oil_R |  |  |  | CDC | 331 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 2ATR_COIL | #2ATR |  | R | [17 empty] | 1-98 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#2ATR_COIL_R | #2ATR R相線溫 | ATR | E01//2ATR/Coil_R |  |  |  | CDC | 332 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 3ATR | #3ATR二次側 |  | MW | [17 empty] | 1-9A | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3ATR_MW | #3ATR二次側 MW | ATR | E01/345/3590/MW |  |  |  | CDC | 333 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 0 |  | 3ATR | #3ATR二次側 |  | MVAR | [17 empty] | 1-9B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3ATR_MVAR | #3ATR二次側 MVAR | ATR | E01/345/3590/MVAR |  |  |  | CDC | 334 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | TapPosMv | [17 empty] | 1-9C |  | 1-32 |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_S | [8 empty] | 南科ES.#3ATR_TAP | #3ATR OLTC TAP | ATR | E01//3ATR/TapPosMv |  |  |  | CDC | 335 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES | 0 |  | 3ATR_OIL | #3ATR |  | R | [17 empty] | 1-9E | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#3ATR_OIL_R | #3ATR R相油溫 | ATR | E01//3ATR/Oil_R |  |  |  | CDC | 336 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 3ATR_COIL | #3ATR |  | R | [17 empty] | 1-9D | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#3ATR_COIL_R | #3ATR R相線溫 | ATR | E01//3ATR/Coil_R |  |  |  | CDC | 337 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 4ATR | #4ATR二次側 |  | MW | [17 empty] | 1-9F | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4ATR_MW | #4ATR二次側 MW | ATR | E01/345/3630/MW |  |  |  | CDC | 338 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 0 |  | 4ATR | #4ATR二次側 |  | MVAR | [17 empty] | 1-A0 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4ATR_MVAR | #4ATR二次側 MVAR | ATR | E01/345/3630/MVAR |  |  |  | CDC | 339 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | TapPosMv | [17 empty] | 1-A1 |  | 1-36 |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_S | [8 empty] | 南科ES.#4ATR_TAP | #4ATR OLTC TAP | ATR | E01//4ATR/TapPosMv |  |  |  | CDC | 340 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES | 0 |  | 4ATR_OIL | #4ATR |  | R | [17 empty] | 1-A3 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#4ATR_OIL_R | #4ATR R相油溫 | ATR | E01//4ATR/Oil_R |  |  |  | CDC | 341 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 4ATR_COIL | #4ATR |  | R | [17 empty] | 1-A2 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#4ATR_COIL_R | #4ATR R相線溫 | ATR | E01//4ATR/Coil_R |  |  |  | CDC | 342 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 5ATR | #5ATR二次側 |  | MW | [17 empty] | 1-A4 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#5ATR_MW | #5ATR二次側 MW | ATR | E01/345/3660/MW |  |  |  | CDC | 343 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 0 |  | 5ATR | #5ATR二次側 |  | MVAR | [17 empty] | 1-A5 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#5ATR_MVAR | #5ATR二次側 MVAR | ATR | E01/345/3660/MVAR |  |  |  | CDC | 344 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | TapPosMv | [17 empty] | 1-A6 |  | 1-3A |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_S | [8 empty] | 南科ES.#5ATR_TAP | #5ATR OLTC TAP | ATR | E01//5ATR/TapPosMv |  |  |  | CDC | 345 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES | 0 |  | 5ATR_OIL | #5ATR |  | R | [17 empty] | 1-A8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#5ATR_OIL_R | #5ATR R相油溫 | ATR | E01//5ATR/Oil_R |  |  |  | CDC | 346 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 5ATR_COIL | #5ATR |  | R | [17 empty] | 1-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#5ATR_COIL_R | #5ATR R相線溫 | ATR | E01//5ATR/Coil_R |  |  |  | CDC | 347 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 6ATR | #6ATR二次側 |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#6ATR_MW | #6ATR二次側 MW | ATR | E01/345/3690/MW |  |  |  | CDC | 348 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E01 | 南科ES | 0 |  | 6ATR | #6ATR二次側 |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#6ATR_MVAR | #6ATR二次側 MVAR | ATR | E01/345/3690/MVAR |  |  |  | CDC | 349 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | TapPosMv | [17 empty] | 1-AB |  | 1-3E |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_S | [8 empty] | 南科ES.#6ATR_TAP | #6ATR OLTC TAP | ATR | E01//6ATR/TapPosMv |  |  |  | CDC | 350 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E01 | 南科ES | 0 |  | 6ATR_OIL | #6ATR |  | R | [17 empty] | 1-AD | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#6ATR_OIL_R | #6ATR R相油溫 | ATR | E01//6ATR/Oil_R |  |  |  | CDC | 351 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  | 6ATR_COIL | #6ATR |  | R | [17 empty] | 1-AC | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 南科ES.#6ATR_COIL_R | #6ATR R相線溫 | ATR | E01//6ATR/Coil_R |  |  |  | CDC | 352 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E01 | 南科ES | 0 |  |  |  |  | #1直流N電源 | [17 empty] | 1-C3 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1直流N電源 | #1直流N電源電壓 | OTHER | E01/0/StaDev/1_DCV_N |  |  |  | CDC | 353 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  |  |  |  | #1直流P電源 | [17 empty] | 1-C2 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1直流P電源 | #1直流P電源電壓 | OTHER | E01/0/StaDev/1_DCV_P |  |  |  | CDC | 354 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  |  |  |  | #2直流N電源 | [17 empty] | 1-C5 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2直流N電源 | #2直流N電源電壓 | OTHER | E01/0/StaDev/2_DCV_N |  |  |  | CDC | 355 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  |  |  |  | #2直流P電源 | [17 empty] | 1-C4 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2直流P電源 | #2直流P電源電壓 | OTHER | E01/0/StaDev/2_DCV_P |  |  |  | CDC | 356 | GENERICAIPoint | ES001_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E01 | 南科ES | 0 |  |  |  |  | CHG2 | [17 empty] | 1-1B-03 | [7 empty] | CDCS_S | [8 empty] | 南科ES.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | E01/0/StaDev/CHG2 |  |  |  | CDC | 357 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | CommACF | [17 empty] | 1-1B-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.通訊設備AC故障 | 通訊設備AC故障 | OTHER | E01/0/StaDev/CommACF |  |  |  | CDC | 358 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 1-1B-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.通信機房溫度 | 通信機房溫度警報 | OTHER | E01/0/StaDev/7A5Other |  |  |  | CDC | 359 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 3510 |  | SSA1 | [17 empty] | 1-02-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3510_SSA1 | 新嘉民二路(3510)#1(87L+21S)RY | LINE345 | E01/345/3510/1SSA1 |  |  |  | CDC | 360 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 3510 |  | SSA2 | [17 empty] | 1-02-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3510_SSA2 | 新嘉民二路(3510)#2測距(21)RY | LINE345 | E01/345/3510/2SSA |  |  |  | CDC | 361 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 3510 |  | RYFA1 | [17 empty] | 1-31-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3510_RYFA1 | 新嘉民二路(3510)第一套RY故障 | LINE345 | E01/345/3510/RYFA1 |  |  |  | CDC | 362 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 3510 |  | RYFA2 | [17 empty] | 1-31-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3510_RYFA2 | 新嘉民二路(3510)第二套RY故障 | LINE345 | E01/345/3510/RYFA2 |  |  |  | CDC | 363 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | 79UL | [17 empty] | 1-31-03 |  | 1-21 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3510_79UL | 新嘉民二路(3510) 79RY U/L | LINE345 | E01/345/3510/79UL |  |  |  | CDC | 364 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | DS1 | 3511 | [16 empty] | 1-34-00 | 1-34-01 | 1-3F | [5 empty] | CDCS_S | [8 empty] | 南科ES.3511_DS | 3511(新嘉民二路) DS | LINE345 | E01/345/3510/DS1 |  |  |  | CDC | 365 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | DS2 | 3512 | [16 empty] | 1-34-02 | 1-34-03 | 1-40 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3512_DS | 3512(新嘉民二路) DS | LINE345 | E01/345/3510/DS2 |  |  |  | CDC | 366 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | CB | [17 empty] | 1-00-00 |  | 1-01 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3510_CB | 3510(新嘉民二路) CB | LINE345 | E01/345/3510/CB |  |  |  | CDC | 367 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | E2 | 3512E | [16 empty] | 1-34-04 | 1-34-05 | 1-41 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3512E_ES | 3512E(新嘉民二路) ES | LINE345 | E01/345/3510/ES2 |  |  |  | CDC | 368 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | DS1 | 3541 | [16 empty] | 1-34-14 | 1-34-15 | 1-46 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3541_DS | 3541(嘉民二路) DS | LINE345 | E01/345/3540/DS1 |  |  |  | CDC | 369 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | DS2 | 3542 | [16 empty] | 1-35-00 | 1-35-01 | 1-47 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3542_DS | 3542(嘉民二路) DS | LINE345 | E01/345/3540/DS2 |  |  |  | CDC | 370 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | CB | [17 empty] | 1-00-03 |  | 1-04 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3540_CB | 3540(嘉民二路) CB | LINE345 | E01/345/3540/CB |  |  |  | CDC | 371 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | E2 | 3542E | [16 empty] | 1-35-02 | 1-35-03 | 1-48 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3542E_ES | 3542E(嘉民二路) ES | LINE345 | E01/345/3540/ES2 |  |  |  | CDC | 372 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3570 | 3570 |  | SSA1 | [17 empty] | 1-03-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3570_SSA1 | 新嘉民一路(3570)#1(87L+21S)RY | LINE345 | E01/345/3570/1SSA1 |  |  |  | CDC | 373 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 3570 |  | SSA2 | [17 empty] | 1-03-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3570_SSA2 | 新嘉民一路(3570)#2測距(21)RY | LINE345 | E01/345/3570/2SSA |  |  |  | CDC | 374 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 3570 |  | RYFA1 | [17 empty] | 1-32-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3570_RYFA1 | 新嘉民一路(3570)第一套RY故障 | LINE345 | E01/345/3570/RYFA1 |  |  |  | CDC | 375 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 3570 |  | RYFA2 | [17 empty] | 1-32-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3570_RYFA2 | 新嘉民一路(3570)第二套RY故障 | LINE345 | E01/345/3570/RYFA2 |  |  |  | CDC | 376 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | 79UL | [17 empty] | 1-32-02 |  | 1-23 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3570_79UL | 新嘉民一路(3570) 79RY U/L | LINE345 | E01/345/3570/79UL |  |  |  | CDC | 377 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | DS1 | 3571 | [16 empty] | 1-35-12 | 1-35-13 | 1-4D | [5 empty] | CDCS_S | [8 empty] | 南科ES.3571_DS | 3571(新嘉民一路) DS | LINE345 | E01/345/3570/DS1 |  |  |  | CDC | 378 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | DS2 | 3572 | [16 empty] | 1-35-14 | 1-35-15 | 1-4E | [5 empty] | CDCS_S | [8 empty] | 南科ES.3572_DS | 3572(新嘉民一路) DS | LINE345 | E01/345/3570/DS2 |  |  |  | CDC | 379 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | CB | [17 empty] | 1-00-06 |  | 1-07 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3570_CB | 3570(新嘉民一路) CB | LINE345 | E01/345/3570/CB |  |  |  | CDC | 380 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | E2 | 3572E | [16 empty] | 1-36-00 | 1-36-01 | 1-4F | [5 empty] | CDCS_S | [8 empty] | 南科ES.3572E_ES | 3572E(新嘉民一路) ES | LINE345 | E01/345/3570/ES2 |  |  |  | CDC | 381 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | SSA1 | [17 empty] | 1-03-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3610_SSA1 | 龍崎一路(3610) #1(87L+21S)RY | LINE345 | E01/345/3610/1SSA1 |  |  |  | CDC | 382 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | SSA2 | [17 empty] | 1-03-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3610_SSA2 | 龍崎一路(3610) #2測距(21)RY | LINE345 | E01/345/3610/2SSA |  |  |  | CDC | 383 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | RYFA1 | [17 empty] | 1-31-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3610_RYFA1 | 龍崎一路(3610) 第一套RY故障 | LINE345 | E01/345/3610/RYFA1 |  |  |  | CDC | 384 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | RYFA2 | [17 empty] | 1-32-01 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3610_RYFA2 | 龍崎一路(3610) 第二套RY故障 | LINE345 | E01/345/3610/RYFA2 |  |  |  | CDC | 385 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | 79UL | [17 empty] | 1-31-13 |  | 1-24 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3610_79UL | 龍崎一路(3610) 79RY U/L | LINE345 | E01/345/3610/79UL |  |  |  | CDC | 386 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | DS1 | 3611 | [16 empty] | 1-36-10 | 1-36-11 | 1-54 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3611_DS | 3611(龍崎一路) DS | LINE345 | E01/345/3610/DS1 |  |  |  | CDC | 387 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | DS2 | 3612 | [16 empty] | 1-36-12 | 1-36-13 | 1-55 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3612_DS | 3612(龍崎一路) DS | LINE345 | E01/345/3610/DS2 |  |  |  | CDC | 388 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | CB | [17 empty] | 1-01-01 |  | 1-0A | [5 empty] | 345KV_S | [8 empty] | 南科ES.3610_CB | 3610(龍崎一路) CB | LINE345 | E01/345/3610/CB |  |  |  | CDC | 389 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | E2 | 3612E | [16 empty] | 1-36-14 | 1-36-15 | 1-56 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3612E_ES | 3612E(龍崎一路) ES | LINE345 | E01/345/3610/ES2 |  |  |  | CDC | 390 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | DS1 | 3641 | [16 empty] | 1-37-08 | 1-37-09 | 1-5B | [5 empty] | CDCS_S | [8 empty] | 南科ES.3641_DS | 3641(嘉民一路) DS | LINE345 | E01/345/3640/DS1 |  |  |  | CDC | 391 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | DS2 | 3642 | [16 empty] | 1-37-10 | 1-37-11 | 1-5C | [5 empty] | CDCS_S | [8 empty] | 南科ES.3642_DS | 3642(嘉民一路) DS | LINE345 | E01/345/3640/DS2 |  |  |  | CDC | 392 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | CB | [17 empty] | 1-01-04 |  | 1-0D | [5 empty] | 345KV_S | [8 empty] | 南科ES.3640_CB | 3640(嘉民一路) CB | LINE345 | E01/345/3640/CB |  |  |  | CDC | 393 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | E2 | 3642E | [16 empty] | 1-37-12 | 1-37-13 | 1-5D | [5 empty] | CDCS_S | [8 empty] | 南科ES.3642E_ES | 3642E(嘉民一路) ES | LINE345 | E01/345/3640/ES2 |  |  |  | CDC | 394 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | SSA1 | [17 empty] | 1-03-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3670_SSA1 | 龍崎二路(3670) #1(87L+21S)RY | LINE345 | E01/345/3670/1SSA1 |  |  |  | CDC | 395 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | SSA2 | [17 empty] | 1-03-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3670_SSA2 | 龍崎二路(3670) #2測距(21)RY | LINE345 | E01/345/3670/2SSA |  |  |  | CDC | 396 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | RYFA1 | [17 empty] | 1-32-09 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3670_RYFA1 | 龍崎二路(3670) 第一套RY故障 | LINE345 | E01/345/3670/RYFA1 |  |  |  | CDC | 397 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | RYFA2 | [17 empty] | 1-32-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3670_RYFA2 | 龍崎二路(3670) 第二套RY故障 | LINE345 | E01/345/3670/RYFA2 |  |  |  | CDC | 398 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | 79UL | [17 empty] | 1-32-07 |  | 1-26 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3670_79UL | 龍崎二路(3670) 79RY U/L | LINE345 | E01/345/3670/79UL |  |  |  | CDC | 399 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | DS1 | 3671 | [16 empty] | 1-38-06 | 1-38-07 | 1-62 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3671_DS | 3671(龍崎二路) DS | LINE345 | E01/345/3670/DS1 |  |  |  | CDC | 400 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | DS2 | 3672 | [16 empty] | 1-38-08 | 1-38-09 | 1-63 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3672_DS | 3672(龍崎二路) DS | LINE345 | E01/345/3670/DS2 |  |  |  | CDC | 401 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | CB | [17 empty] | 1-01-07 |  | 1-10 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3670_CB | 3670(龍崎二路) CB | LINE345 | E01/345/3670/CB |  |  |  | CDC | 402 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | E2 | 3672E | [16 empty] | 1-38-10 | 1-38-11 | 1-64 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3672E_ES | 3672E(龍崎二路) ES | LINE345 | E01/345/3670/ES2 |  |  |  | CDC | 403 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | 3520 | 3520 |  | CB | [17 empty] | 1-00-01 |  | 1-02 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3520_CB | 3520 CB | LINE345 | E01/345/3520/CB |  |  |  | CDC | 404 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3520 | 3520 |  | DS1 | 3521 | [16 empty] | 1-34-06 | 1-34-07 | 1-42 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3521_DS | 3521 DS | LINE345 | E01/345/3520/DS1 |  |  |  | CDC | 405 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3520 | 3520 |  | DS2 | 3522 | [16 empty] | 1-34-08 | 1-34-09 | 1-43 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3522_DS | 3522 DS | LINE345 | E01/345/3520/DS2 |  |  |  | CDC | 406 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3550 | 3550 |  | CB | [17 empty] | 1-00-04 |  | 1-05 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3550_CB | 3550 CB | LINE345 | E01/345/3550/CB |  |  |  | CDC | 407 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3550 | 3550 |  | DS1 | 3551 | [16 empty] | 1-35-04 | 1-35-05 | 1-49 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3551_DS | 3551 DS | LINE345 | E01/345/3550/DS1 |  |  |  | CDC | 408 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3550 | 3550 |  | DS2 | 3552 | [16 empty] | 1-35-06 | 1-35-07 | 1-4A | [5 empty] | CDCS_S | [8 empty] | 南科ES.3552_DS | 3552 DS | LINE345 | E01/345/3550/DS2 |  |  |  | CDC | 409 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3580 | 3580 |  | CB | [17 empty] | 1-00-07 |  | 1-08 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3580_CB | 3580 CB | LINE345 | E01/345/3580/CB |  |  |  | CDC | 410 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3580 | 3580 |  | DS1 | 3581 | [16 empty] | 1-36-02 | 1-36-03 | 1-50 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3581_DS | 3581 DS | LINE345 | E01/345/3580/DS1 |  |  |  | CDC | 411 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3580 | 3580 |  | DS2 | 3582 | [16 empty] | 1-36-04 | 1-36-05 | 1-51 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3582_DS | 3582 DS | LINE345 | E01/345/3580/DS2 |  |  |  | CDC | 412 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3620 | 3620 |  | CB | [17 empty] | 1-01-02 |  | 1-0B | [5 empty] | 345KV_S | [8 empty] | 南科ES.3620_CB | 3620 CB | LINE345 | E01/345/3620/CB |  |  |  | CDC | 413 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3620 | 3620 |  | DS1 | 3621 | [16 empty] | 1-37-00 | 1-37-01 | 1-57 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3621_DS | 3621 DS | LINE345 | E01/345/3620/DS1 |  |  |  | CDC | 414 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3620 | 3620 |  | DS2 | 3622 | [16 empty] | 1-37-02 | 1-37-03 | 1-58 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3622_DS | 3622 DS | LINE345 | E01/345/3620/DS2 |  |  |  | CDC | 415 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3650 | 3650 |  | CB | [17 empty] | 1-01-05 |  | 1-0E | [5 empty] | 345KV_S | [8 empty] | 南科ES.3650_CB | 3650 CB | LINE345 | E01/345/3650/CB |  |  |  | CDC | 416 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3650 | 3650 |  | DS1 | 3651 | [16 empty] | 1-37-14 | 1-37-15 | 1-5E | [5 empty] | CDCS_S | [8 empty] | 南科ES.3651_DS | 3651 DS | LINE345 | E01/345/3650/DS1 |  |  |  | CDC | 417 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3650 | 3650 |  | DS2 | 3652 | [16 empty] | 1-38-00 | 1-38-01 | 1-5F | [5 empty] | CDCS_S | [8 empty] | 南科ES.3652_DS | 3652 DS | LINE345 | E01/345/3650/DS2 |  |  |  | CDC | 418 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3680 | 3680 |  | CB | [17 empty] | 1-02-00 |  | 1-11 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3680_CB | 3680 CB | LINE345 | E01/345/3680/CB |  |  |  | CDC | 419 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 345 | 345kV | 3680 | 3680 |  | DS1 | 3681 | [16 empty] | 1-38-12 | 1-38-13 | 1-65 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3681_DS | 3681 DS | LINE345 | E01/345/3680/DS1 |  |  |  | CDC | 420 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3680 | 3680 |  | DS2 | 3682 | [16 empty] | 1-38-14 | 1-38-15 | 1-66 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3682_DS | 3682 DS | LINE345 | E01/345/3680/DS2 |  |  |  | CDC | 421 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | CB | [17 empty] | 1-00-02 |  | 1-03 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3530_CB | 3530(#1ATR) CB | ATR | E01/345/3530/CB |  |  |  | CDC | 422 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | CB | [17 empty] | 1-04-00 |  | 1-13 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1810_CB | 1810(#1ATR) CB | ATR | E01/161/1810/CB |  |  |  | CDC | 423 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 87A1 | [17 empty] | 1-04-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#1ATR_87A1 | #1ATR 第一組 87RY | ATR | E01//1ATR/87A1 |  |  |  | CDC | 424 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 87A2 | [17 empty] | 1-04-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#1ATR_87A2 | #1ATR 第二組 87RY | ATR | E01//1ATR/87A2 |  |  |  | CDC | 425 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 96PA | [17 empty] | 1-04-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#1ATR_96PA | #1ATR 機械保護動作 | ATR | E01//1ATR/96PA |  |  |  | CDC | 426 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 51ZA | [17 empty] | 1-04-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#1ATR_51ZA | #1ATR 51Z(21+50,59-2,51Z) | ATR | E01//1ATR/51ZA |  |  |  | CDC | 427 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 59A | [17 empty] | 1-04-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#1ATR_59A | #1ATR 59RY | ATR | E01//1ATR/59A |  |  |  | CDC | 428 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 1_87UL1 | [17 empty] | 1-30-10 |  | 2-06 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_87UL1 | #1ATR 第一套 87RY U/L | OTHER | E01//1ATR/1_87UL1 |  |  |  | CDC | 429 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 1_87UL2 | [17 empty] | 1-30-11 |  | 2-07 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_87UL2 | #1ATR 第二套 87RY U/L | OTHER | E01//1ATR/1_87UL2 |  |  |  | CDC | 430 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 96D | [17 empty] | 2-30-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_96D | #1ATR 96D RY | ATR | E01//1ATR/96D |  |  |  | CDC | 431 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 96P | [17 empty] | 2-30-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_96P | #1ATR 96P RY | ATR | E01//1ATR/96P |  |  |  | CDC | 432 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 63Q | [17 empty] | 2-30-13 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_63Q | #1ATR 63Q RY | ATR | E01//1ATR/63Q |  |  |  | CDC | 433 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 96B1 | [17 empty] | 2-30-09 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_96B1 | #1ATR 96B1 RY | ATR | E01//1ATR/96B1 |  |  |  | CDC | 434 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 96B2 | [17 empty] | 2-30-10 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_96B2 | #1ATR 96B2 RY | ATR | E01//1ATR/96B2 |  |  |  | CDC | 435 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | TRA | [17 empty] | 2-31-01 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_TRA | #1ATR 重故障 | ATR | E01//1ATR/TRA |  |  |  | CDC | 436 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | TRF | [17 empty] | 2-31-00 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_TRF | #1ATR 輕故障 | ATR | E01//1ATR/TRF |  |  |  | CDC | 437 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | SupLocal | [17 empty] | 2-30-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_S/L | #1ATR OLTC S/L | ATR | E01//1ATR/SupLocal |  |  |  | CDC | 438 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | A_M | [17 empty] | 2-30-15 |  | 1-27 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_A/M | #1ATR OLTC A/M | ATR | E01/345/3530/Tap Chan |  |  |  | CDC | 439 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | M/F/I | [17 empty] | 1-39-04 | 1-39-05 | 1-28 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_M/F/I | #1ATR M/F/I | ATR | E01//1ATR/M_F_I |  |  |  | CDC | 440 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | DS1 | 3531 | [16 empty] | 1-34-10 | 1-34-11 | 1-44 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3531_DS | 3531(#1ATR) DS | ATR | E01/345/3530/DS1 |  |  |  | CDC | 441 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | DS2 | 3532 | [16 empty] | 1-34-12 | 1-34-13 | 1-45 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3532_DS | 3532(#1ATR) DS | ATR | E01/345/3530/DS2 |  |  |  | CDC | 442 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS1 | 1811 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-69 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1811_DS | 1811(#1ATR) DS | ATR | E01/161/1810/DS1 |  |  |  | CDC | 443 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS2 | 1812 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-6A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1812_DS | 1812(#1ATR) DS | ATR | E01/161/1810/DS2 |  |  |  | CDC | 444 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | CB | [17 empty] | 1-00-05 |  | 1-06 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3560_CB | 3560(#2ATR) CB | ATR | E01/345/3560/CB |  |  |  | CDC | 445 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | CB | [17 empty] | 1-04-06 |  | 1-15 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1820_CB | 1820(#2ATR) CB | ATR | E01/161/1820/CB |  |  |  | CDC | 446 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 87A1 | [17 empty] | 1-05-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#2ATR_87A1 | #2ATR 第一組 87RY | ATR | E01//2ATR/87A1 |  |  |  | CDC | 447 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 87A2 | [17 empty] | 1-05-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#2ATR_87A2 | #2ATR 第二組 87RY | ATR | E01//2ATR/87A2 |  |  |  | CDC | 448 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 96PA | [17 empty] | 1-04-07 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#2ATR_96PA | #2ATR 機械保護動作 | ATR | E01//2ATR/96PA |  |  |  | CDC | 449 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 51ZA | [17 empty] | 1-05-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#2ATR_51ZA | #2ATR 51Z(21+50,59-2,51Z) | ATR | E01//2ATR/51ZA |  |  |  | CDC | 450 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 59A | [17 empty] | 1-05-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#2ATR_59A | #2ATR 59RY | ATR | E01//2ATR/59A |  |  |  | CDC | 451 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 1_87UL1 | [17 empty] | 1-30-02 |  | 2-09 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_87UL1 | #2ATR 第一套 87RY U/L | OTHER | E01//2ATR/1_87UL1 |  |  |  | CDC | 452 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 1_87UL2 | [17 empty] | 1-30-03 |  | 2-0A | [5 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_87UL2 | #2ATR 第二套 87RY U/L | OTHER | E01//2ATR/1_87UL2 |  |  |  | CDC | 453 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 96D | [17 empty] | 2-31-08 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_96D | #2ATR 96D RY | ATR | E01//2ATR/96D |  |  |  | CDC | 454 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 96P | [17 empty] | 2-31-09 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_96P | #2ATR 96P RY | ATR | E01//2ATR/96P |  |  |  | CDC | 455 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 63Q | [17 empty] | 2-31-10 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_63Q | #2ATR 63Q RY | ATR | E01//2ATR/63Q |  |  |  | CDC | 456 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 96B1 | [17 empty] | 2-31-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_96B1 | #2ATR 96B1 RY | ATR | E01//2ATR/96B1 |  |  |  | CDC | 457 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 96B2 | [17 empty] | 2-31-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_96B2 | #2ATR 96B2 RY | ATR | E01//2ATR/96B2 |  |  |  | CDC | 458 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | TRA | [17 empty] | 1-32-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_TRA | #2ATR 重故障 | ATR | E01//2ATR/TRA |  |  |  | CDC | 459 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | TRF | [17 empty] | 1-32-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_TRF | #2ATR 輕故障 | ATR | E01//2ATR/TRF |  |  |  | CDC | 460 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | SupLocal | [17 empty] | 1-32-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_S/L | #2ATR OLTC S/L | ATR | E01//2ATR/SupLocal |  |  |  | CDC | 461 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | A_M | [17 empty] | 1-32-13 |  | 1-2B | [5 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_A/M | #2ATR OLTC A/M | ATR | E01/345/3560/Tap Chan |  |  |  | CDC | 462 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | M/F/I | [17 empty] | 1-39-06 | 1-39-07 | 1-2C | [5 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_M/F/I | #2ATR M/F/I | ATR | E01//2ATR/M_F_I |  |  |  | CDC | 463 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | DS1 | 3561 | [16 empty] | 1-35-08 | 1-35-09 | 1-4B | [5 empty] | CDCS_S | [8 empty] | 南科ES.3561_DS | 3561(#2ATR) DS | ATR | E01/345/3560/DS1 |  |  |  | CDC | 464 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | DS2 | 3562 | [16 empty] | 1-35-10 | 1-35-11 | 1-4C | [5 empty] | CDCS_S | [8 empty] | 南科ES.3562_DS | 3562(#2ATR) DS | ATR | E01/345/3560/DS2 |  |  |  | CDC | 465 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | DS1 | 1821 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-6C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1821_DS | 1821(#2ATR) DS | ATR | E01/161/1820/DS1 |  |  |  | CDC | 466 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1820 | #2ATR(1820) |  | DS2 | 1822 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-6D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1822_DS | 1822(#2ATR) DS | ATR | E01/161/1820/DS2 |  |  |  | CDC | 467 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | CB | [17 empty] | 1-01-00 |  | 1-09 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3590_CB | 3590(#3ATR) CB | ATR | E01/345/3590/CB |  |  |  | CDC | 468 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | CB | [17 empty] | 1-08-07 |  | 1-14 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1830_CB | 1830(#3ATR) CB | ATR | E01/161/1830/CB |  |  |  | CDC | 469 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 87A1 | [17 empty] | 1-05-06 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#3ATR_87A1 | #3ATR 第一組 87RY | ATR | E01//3ATR/87A1 |  |  |  | CDC | 470 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 87A2 | [17 empty] | 1-05-07 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#3ATR_87A2 | #3ATR 第二組 87RY | ATR | E01//3ATR/87A2 |  |  |  | CDC | 471 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 96PA | [17 empty] | 1-05-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#3ATR_96PA | #3ATR 機械保護動作 | ATR | E01//3ATR/96PA |  |  |  | CDC | 472 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 51ZA | [17 empty] | 1-06-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#3ATR_51ZA | #3ATR 51Z(21+50,59-2,51Z) | ATR | E01//3ATR/51ZA |  |  |  | CDC | 473 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 59A | [17 empty] | 1-06-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#3ATR_59A | #3ATR 59RY | ATR | E01//3ATR/59A |  |  |  | CDC | 474 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 1_87UL1 | [17 empty] | 1-30-04 |  | 2-0D | [5 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_87UL1 | #3ATR 第一套 87RY U/L | OTHER | E01//3ATR/1_87UL1 |  |  |  | CDC | 475 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 1_87UL2 | [17 empty] | 1-30-05 |  | 2-0E | [5 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_87UL2 | #3ATR 第二套 87RY U/L | OTHER | E01//3ATR/1_87UL2 |  |  |  | CDC | 476 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 96D | [17 empty] | 2-32-01 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_96D | #3ATR 96D RY | ATR | E01//3ATR/96D |  |  |  | CDC | 477 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 96P | [17 empty] | 2-32-02 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_96P | #3ATR 96P RY | ATR | E01//3ATR/96P |  |  |  | CDC | 478 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 63Q | [17 empty] | 2-32-03 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_63Q | #3ATR 63Q RY | ATR | E01//3ATR/63Q |  |  |  | CDC | 479 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 96B1 | [17 empty] | 2-31-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_96B1 | #3ATR 96B1 RY | ATR | E01//3ATR/96B1 |  |  |  | CDC | 480 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 96B2 | [17 empty] | 2-32-00 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_96B2 | #3ATR 96B2 RY | ATR | E01//3ATR/96B2 |  |  |  | CDC | 481 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | TRA | [17 empty] | 1-33-03 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_TRA | #3ATR 重故障 | ATR | E01//3ATR/TRA |  |  |  | CDC | 482 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | TRF | [17 empty] | 1-33-02 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_TRF | #3ATR 輕故障 | ATR | E01//3ATR/TRF |  |  |  | CDC | 483 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | SupLocal | [17 empty] | 1-33-00 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_S/L | #3ATR OLTC S/L | ATR | E01//3ATR/SupLocal |  |  |  | CDC | 484 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | A_M | [17 empty] | 1-33-01 |  | 1-2F | [5 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_A/M | #3ATR OLTC A/M | ATR | E01/345/3590/Tap Chan |  |  |  | CDC | 485 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | M/F/I | [17 empty] | 1-39-08 | 1-39-09 | 1-30 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_M/F/I | #3ATR M/F/I | ATR | E01//3ATR/M_F_I |  |  |  | CDC | 486 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | DS1 | 3591 | [16 empty] | 1-36-06 | 1-36-07 | 1-52 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3591_DS | 3591(#3ATR) DS | ATR | E01/345/3590/DS1 |  |  |  | CDC | 487 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | DS2 | 3592 | [16 empty] | 1-36-08 | 1-36-09 | 1-53 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3592_DS | 3592(#3ATR) DS | ATR | E01/345/3590/DS2 |  |  |  | CDC | 488 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS1 | 1831 | [16 empty] | 2-36-00 | 2-36-01 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1831_DS | 1831(#3ATR) DS | ATR | E01/161/1830/DS1 |  |  |  | CDC | 489 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS2 | 1832 | [16 empty] | 2-36-02 | 2-36-03 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1832_DS | 1832(#3ATR) DS | ATR | E01/161/1830/DS2 |  |  |  | CDC | 490 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | CB | [17 empty] | 1-01-03 |  | 1-0C | [5 empty] | 345KV_S | [8 empty] | 南科ES.3630_CB | 3630(#4ATR) CB | ATR | E01/345/3630/CB |  |  |  | CDC | 491 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | CB | [17 empty] | 1-06-02 |  | 1-19 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1850_CB | 1850(#4ATR) CB | ATR | E01/161/1850/CB |  |  |  | CDC | 492 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 87A1 | [17 empty] | 1-06-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#4ATR_87A1 | #4ATR 第一組 87RY | ATR | E01//4ATR/87A1 |  |  |  | CDC | 493 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 87A2 | [17 empty] | 1-06-06 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#4ATR_87A2 | #4ATR 第二組 87RY | ATR | E01//4ATR/87A2 |  |  |  | CDC | 494 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 96PA | [17 empty] | 1-06-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#4ATR_96PA | #4ATR 機械保護動作 | ATR | E01//4ATR/96PA |  |  |  | CDC | 495 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 51ZA | [17 empty] | 1-06-07 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#4ATR_51ZA | #4ATR 51Z(21+50,59-2,51Z) | ATR | E01//4ATR/51ZA |  |  |  | CDC | 496 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 59A | [17 empty] | 1-07-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#4ATR_59A | #4ATR 59RY | ATR | E01//4ATR/59A |  |  |  | CDC | 497 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 1_87UL1 | [17 empty] | 1-30-06 |  | 2-11 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_87UL1 | #4ATR 第一套 87RY U/L | OTHER | E01//4ATR/1_87UL1 |  |  |  | CDC | 498 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 1_87UL2 | [17 empty] | 1-30-07 |  | 2-12 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_87UL2 | #4ATR 第二套 87RY U/L | OTHER | E01//4ATR/1_87UL2 |  |  |  | CDC | 499 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 96D | [17 empty] | 2-32-10 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_96D | #4ATR 96D RY | ATR | E01//4ATR/96D |  |  |  | CDC | 500 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 96P | [17 empty] | 2-32-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_96P | #4ATR 96P RY | ATR | E01//4ATR/96P |  |  |  | CDC | 501 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 63Q | [17 empty] | 2-32-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_63Q | #4ATR 63Q RY | ATR | E01//4ATR/63Q |  |  |  | CDC | 502 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 96B1 | [17 empty] | 2-32-08 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_96B1 | #4ATR 96B1 RY | ATR | E01//4ATR/96B1 |  |  |  | CDC | 503 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 96B2 | [17 empty] | 2-32-09 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_96B2 | #4ATR 96B2 RY | ATR | E01//4ATR/96B2 |  |  |  | CDC | 504 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | TRA | [17 empty] | 1-33-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_TRA | #4ATR 重故障 | ATR | E01//4ATR/TRA |  |  |  | CDC | 505 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | TRF | [17 empty] | 1-33-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_TRF | #4ATR 輕故障 | ATR | E01//4ATR/TRF |  |  |  | CDC | 506 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | SupLocal | [17 empty] | 1-33-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_S/L | #4ATR OLTC S/L | ATR | E01//4ATR/SupLocal |  |  |  | CDC | 507 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | A_M | [17 empty] | 1-33-05 |  | 1-33 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_A/M | #4ATR OLTC A/M | ATR | E01/345/3630/Tap Chan |  |  |  | CDC | 508 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | M/F/I | [17 empty] | 1-39-10 | 1-39-11 | 1-34 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_M/F/I | #4ATR M/F/I | ATR | E01//4ATR/M_F_I |  |  |  | CDC | 509 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | DS1 | 3631 | [16 empty] | 1-37-04 | 1-37-05 | 1-59 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3631_DS | 3631(#4ATR) DS | ATR | E01/345/3630/DS1 |  |  |  | CDC | 510 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | DS2 | 3632 | [16 empty] | 1-37-06 | 1-37-07 | 1-5A | [5 empty] | CDCS_S | [8 empty] | 南科ES.3632_DS | 3632(#4ATR) DS | ATR | E01/345/3630/DS2 |  |  |  | CDC | 511 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | DS1 | 1851 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-72 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1851_DS | 1851(#4ATR) DS | ATR | E01/161/1850/DS1 |  |  |  | CDC | 512 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | DS2 | 1852 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-73 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1852_DS | 1852(#4ATR) DS | ATR | E01/161/1850/DS2 |  |  |  | CDC | 513 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | CB | [17 empty] | 1-01-06 |  | 1-0F | [5 empty] | 345KV_S | [8 empty] | 南科ES.3660_CB | 3660(#5ATR) CB | ATR | E01/345/3660/CB |  |  |  | CDC | 514 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | CB | [17 empty] | 1-07-01 |  | 1-1B | [5 empty] | 161KV_S | [8 empty] | 南科ES.1870_CB | 1870(#5ATR) CB | ATR | E01/161/1870/CB |  |  |  | CDC | 515 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 87A1 | [17 empty] | 1-07-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#5ATR_87A1 | #5ATR 第一組 87RY | ATR | E01//5ATR/87A1 |  |  |  | CDC | 516 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 87A2 | [17 empty] | 1-07-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#5ATR_87A2 | #5ATR 第二組 87RY | ATR | E01//5ATR/87A2 |  |  |  | CDC | 517 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 96PA | [17 empty] | 1-07-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#5ATR_96PA | #5ATR 機械保護動作 | ATR | E01//5ATR/96PA |  |  |  | CDC | 518 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 51ZA | [17 empty] | 1-07-06 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#5ATR_51ZA | #5ATR 51Z(21+50,59-2,51Z) | ATR | E01//5ATR/51ZA |  |  |  | CDC | 519 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 59A | [17 empty] | 1-07-07 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#5ATR_59A | #5ATR 59RY | ATR | E01//5ATR/59A |  |  |  | CDC | 520 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 1_87UL1 | [17 empty] | 1-30-08 |  | 2-14 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_87UL1 | #5ATR 第一套 87RY U/L | OTHER | E01//5ATR/1_87UL1 |  |  |  | CDC | 521 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 1_87UL2 | [17 empty] | 1-30-09 |  | 2-15 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_87UL2 | #5ATR 第二套 87RY U/L | OTHER | E01//5ATR/1_87UL2 |  |  |  | CDC | 522 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 96D | [17 empty] | 2-33-03 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_96D | #5ATR 96D RY | ATR | E01//5ATR/96D |  |  |  | CDC | 523 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 96P | [17 empty] | 2-33-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_96P | #5ATR 96P RY | ATR | E01//5ATR/96P |  |  |  | CDC | 524 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 63Q | [17 empty] | 2-33-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_63Q | #5ATR 63Q RY | ATR | E01//5ATR/63Q |  |  |  | CDC | 525 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 96B1 | [17 empty] | 2-33-01 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_96B1 | #5ATR 96B1 RY | ATR | E01//5ATR/96B1 |  |  |  | CDC | 526 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 96B2 | [17 empty] | 2-33-02 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_96B2 | #5ATR 96B2 RY | ATR | E01//5ATR/96B2 |  |  |  | CDC | 527 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | TRA | [17 empty] | 1-33-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_TRA | #5ATR 重故障 | ATR | E01//5ATR/TRA |  |  |  | CDC | 528 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | TRF | [17 empty] | 1-33-10 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_TRF | #5ATR 輕故障 | ATR | E01//5ATR/TRF |  |  |  | CDC | 529 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | SupLocal | [17 empty] | 1-33-08 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_S/L | #5ATR OLTC S/L | ATR | E01//5ATR/SupLocal |  |  |  | CDC | 530 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | A_M | [17 empty] | 1-33-09 |  | 1-37 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_A/M | #5ATR OLTC A/M | ATR | E01/345/3660/Tap Chan |  |  |  | CDC | 531 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | M/F/I | [17 empty] | 1-39-12 | 1-39-13 | 1-38 | [5 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_M/F/I | #5ATR M/F/I | ATR | E01//5ATR/M_F_I |  |  |  | CDC | 532 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | DS1 | 3661 | [16 empty] | 1-38-02 | 1-38-03 | 1-60 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3661_DS | 3661(#5ATR) DS | ATR | E01/345/3660/DS1 |  |  |  | CDC | 533 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | DS2 | 3662 | [16 empty] | 1-38-04 | 1-38-05 | 1-61 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3662_DS | 3662(#5ATR) DS | ATR | E01/345/3660/DS2 |  |  |  | CDC | 534 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | DS1 | 1871 | [16 empty] | 1-3B-10 | 1-3B-11 | 1-76 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1871_DS | 1871(#5ATR) DS | ATR | E01/161/1870/DS1 |  |  |  | CDC | 535 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | DS2 | 1872 | [16 empty] | 1-3B-12 | 1-3B-13 | 1-77 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1872_DS | 1872(#5ATR) DS | ATR | E01/161/1870/DS2 |  |  |  | CDC | 536 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | CB | [17 empty] | 1-02-01 |  | 1-12 | [5 empty] | 345KV_S | [8 empty] | 南科ES.3690_CB | 3690(#6ATR) CB | ATR | E01/345/3690/CB |  |  |  | CDC | 537 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | CB | [17 empty] | 1-08-00 |  | 1-1E | [5 empty] | 161KV_S | [8 empty] | 南科ES.1910_CB | 1910(#6ATR) CB | ATR | E01/161/1910/CB |  |  |  | CDC | 538 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 87A1 | [17 empty] | 1-08-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#6ATR_87A1 | #6ATR 第一組 87RY | ATR | E01//6ATR/87A1 |  |  |  | CDC | 539 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 87A2 | [17 empty] | 1-08-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#6ATR_87A2 | #6ATR 第二組 87RY | ATR | E01//6ATR/87A2 |  |  |  | CDC | 540 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 96PA | [17 empty] | 1-08-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#6ATR_96PA | #6ATR 機械保護動作 | ATR | E01//6ATR/96PA |  |  |  | CDC | 541 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 51ZA | [17 empty] | 1-08-05 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#6ATR_51ZA | #6ATR 51Z(21+50,59-2,51Z) | ATR | E01//6ATR/51ZA |  |  |  | CDC | 542 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 59A | [17 empty] | 1-08-06 | [7 empty] | 345KV_S | [8 empty] | 南科ES.#6ATR_59A | #6ATR 59RY | ATR | E01//6ATR/59A |  |  |  | CDC | 543 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 1_87UL1 | [17 empty] | 1-30-12 |  | 2-18 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_87UL1 | #6ATR 第一套 87RY U/L | OTHER | E01//6ATR/1_87UL1 |  |  |  | CDC | 544 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 1_87UL2 | [17 empty] | 1-30-13 |  | 2-19 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_87UL2 | #6ATR 第二套 87RY U/L | OTHER | E01//6ATR/1_87UL2 |  |  |  | CDC | 545 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 96D | [17 empty] | 2-33-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_96D | #6ATR 96D RY | ATR | E01//6ATR/96D |  |  |  | CDC | 546 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 96P | [17 empty] | 2-33-13 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_96P | #6ATR 96P RY | ATR | E01//6ATR/96P |  |  |  | CDC | 547 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 63Q | [17 empty] | 2-33-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_63Q | #6ATR 63Q RY | ATR | E01//6ATR/63Q |  |  |  | CDC | 548 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 96B1 | [17 empty] | 2-33-10 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_96B1 | #6ATR 96B1 RY | ATR | E01//6ATR/96B1 |  |  |  | CDC | 549 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 96B2 | [17 empty] | 2-33-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_96B2 | #6ATR 96B2 RY | ATR | E01//6ATR/96B2 |  |  |  | CDC | 550 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | TRA | [17 empty] | 1-33-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_TRA | #6ATR 重故障 | ATR | E01//6ATR/TRA |  |  |  | CDC | 551 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | TRF | [17 empty] | 1-33-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_TRF | #6ATR 輕故障 | ATR | E01//6ATR/TRF |  |  |  | CDC | 552 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | SupLocal | [17 empty] | 1-33-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_S/L | #6ATR OLTC S/L | ATR | E01//6ATR/SupLocal |  |  |  | CDC | 553 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | A_M | [17 empty] | 1-33-13 |  | 1-3B | [5 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_A/M | #6ATR OLTC A/M | ATR | E01/345/3690/Tap Chan |  |  |  | CDC | 554 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | M/F/I | [17 empty] | 1-39-14 | 1-39-15 | 1-3C | [5 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_M/F/I | #6ATR M/F/I | ATR | E01//6ATR/M_F_I |  |  |  | CDC | 555 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | DS1 | 3691 | [16 empty] | 1-39-00 | 1-39-01 | 1-67 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3691_DS | 3691(#6ATR) DS | ATR | E01/345/3690/DS1 |  |  |  | CDC | 556 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | DS2 | 3692 | [16 empty] | 1-39-02 | 1-39-03 | 1-68 | [5 empty] | CDCS_S | [8 empty] | 南科ES.3692_DS | 3692(#6ATR) DS | ATR | E01/345/3690/DS2 |  |  |  | CDC | 557 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | DS1 | 1911 | [16 empty] | 1-3C-04 | 1-3C-05 | 1-7B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1911_DS | 1911(#6ATR) DS | ATR | E01/161/1910/DS1 |  |  |  | CDC | 558 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | DS2 | 1912 | [16 empty] | 1-3C-06 | 1-3C-07 | 1-7C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1912_DS | 1912(#6ATR) DS | ATR | E01/161/1910/DS2 |  |  |  | CDC | 559 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | CB | [17 empty] | 1-06-03 |  | 1-1A | [5 empty] | 161KV_S | [8 empty] | 南科ES.1860_CB | 1860(#4ATR) CB | ATR | E01/161/1860/CB |  |  |  | CDC | 560 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | DS1 | 1861 | [16 empty] | 1-3B-06 | 1-3B-07 | 1-74 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1861_DS | 1861(#4ATR) DS | ATR | E01/161/1860/DS1 |  |  |  | CDC | 561 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1860 | #4ATR(1860) |  | DS2 | 1862 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-75 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1862_DS | 1862(#4ATR) DS | ATR | E01/161/1860/DS2 |  |  |  | CDC | 562 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | CB | [17 empty] | 1-07-02 |  | 1-1C | [5 empty] | 161KV_S | [8 empty] | 南科ES.1880_CB | 1880(#5ATR) CB | ATR | E01/161/1880/CB |  |  |  | CDC | 563 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | DS1 | 1881 | [16 empty] | 1-3B-14 | 1-3B-15 | 1-78 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1881_DS | 1881(#5ATR) DS | ATR | E01/161/1880/DS1 |  |  |  | CDC | 564 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1880 | #5ATR(1880) |  | DS2 | 1882 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-79 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1882_DS | 1882(#5ATR) DS | ATR | E01/161/1880/DS2 |  |  |  | CDC | 565 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | CB | [17 empty] | 1-08-01 |  | 1-1F | [5 empty] | 161KV_S | [8 empty] | 南科ES.1920_CB | 1920(#6ATR) CB | ATR | E01/161/1920/CB |  |  |  | CDC | 566 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | DS1 | 1921 | [16 empty] | 1-3C-08 | 1-3C-09 | 1-7D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1921_DS | 1921(#6ATR) DS | ATR | E01/161/1920/DS1 |  |  |  | CDC | 567 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1920 | #6ATR(1920) |  | DS2 | 1922 | [16 empty] | 1-3C-10 | 1-3C-11 | 1-7E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1922_DS | 1922(#6ATR) DS | ATR | E01/161/1920/DS2 |  |  |  | CDC | 568 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 345 | 345kV | 3451B | #1BUS |  | 87A1 | [17 empty] | 1-09-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.345#1B_87A1 | 345KV #1BUS 第一組 87RY | BUS | E01/345/1BUS/87A1 |  |  |  | CDC | 569 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3451B | #1BUS |  | 87A2 | [17 empty] | 1-09-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.345#1B_87A2 | 345KV #1BUS 第二組 87RY | BUS | E01/345/1BUS/87A2 |  |  |  | CDC | 570 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3451B | #1BUS |  | 1_87UL1 | [17 empty] | 2-30-00 |  | 2-02 | [5 empty] | CDCS_S | [8 empty] | 南科ES.345#1B_87UL1 | 345KV #1BUS 第一組 87RY U/L | OTHER | E01/345/1BUS/1_87UL1 |  |  |  | CDC | 571 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3451B | #1BUS |  | 1_87UL2 | [17 empty] | 2-30-02 |  | 2-04 | [5 empty] | CDCS_S | [8 empty] | 南科ES.345#1B_87UL2 | 345KV #1BUS 第二組 87RY U/L | OTHER | E01/345/1BUS/1_87UL2 |  |  |  | CDC | 572 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3452B | #2BUS |  | 87A1 | [17 empty] | 1-09-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.345#2B_87A1 | 345KV #2BUS 第一組 87RY | BUS | E01/345/2BUS/87A1 |  |  |  | CDC | 573 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3452B | #2BUS |  | 87A2 | [17 empty] | 1-09-04 | [7 empty] | 345KV_S | [8 empty] | 南科ES.345#2B_87A2 | 345KV #2BUS 第二組 87RY | BUS | E01/345/2BUS/87A2 |  |  |  | CDC | 574 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3452B | #2BUS |  | 1_87UL1 | [17 empty] | 2-30-01 |  | 2-03 | [5 empty] | CDCS_S | [8 empty] | 南科ES.345#2B_87UL1 | 345KV #2BUS 第一組 87RY U/L | OTHER | E01/345/2BUS/1_87UL1 |  |  |  | CDC | 575 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV | 3452B | #2BUS |  | 1_87UL2 | [17 empty] | 2-30-03 |  | 2-05 | [5 empty] | CDCS_S | [8 empty] | 南科ES.345#2B_87UL2 | 345KV #2BUS 第二組 87RY U/L | OTHER | E01/345/2BUS/1_87UL2 |  |  |  | CDC | 576 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 345 | 345kV |  |  |  | BFA | [17 empty] | 1-09-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_BFA | 345KV斷路器失靈(BF)警報 | OTHER |  |  |  |  | CDC | 577 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 斷路器失靈RY | 斷路器失靈RY |  | BFS | [17 empty] | 2-30-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_BFS | 345KV 斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 578 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E01 | 南科ES | 345 | 345kV |  |  |  | CBA | [17 empty] | 2-34-10 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_CBA | 345KV 斷路器重故障 | OTHER |  |  |  |  | CDC | 579 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | CBF | [17 empty] | 2-34-09 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_CBF | 345KV 斷路器輕故障 | OTHER |  |  |  |  | CDC | 580 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | COMT | [17 empty] | 2-34-08 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_COMT | 345KV 空壓機運轉超時警報 | OTHER |  |  |  |  | CDC | 581 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 25RY | 25RY |  | 25TA | [17 empty] | 2-34-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_25TA | 345KV 25RY 超時動作警報 | OTHER |  |  |  |  | CDC | 582 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 25RY | 25RY |  | 25PFA | [17 empty] | 2-34-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_25PFA | 345KV 25RY 電源故障警報 | OTHER |  |  |  |  | CDC | 583 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 520 | 520 |  | CB | [17 empty] | 1-10-01 |  | 1-16 | [5 empty] | 161KV_S | [8 empty] | 南科ES.520_CB | 520 CB | OTHER | E01/33/520/CB |  |  |  | CDC | 584 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 520 | 520 |  | DS1 | 521 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-6E | [5 empty] | CDCS_S | [8 empty] | 南科ES.521_DS | 521 DS | OTHER | E01/33/520/DS1 |  |  |  | CDC | 585 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 0 |  | 530 | 530 |  | CB | [17 empty] | 1-10-02 |  | 1-18 | [5 empty] | 161KV_S | [8 empty] | 南科ES.530_CB | 530 CB | OTHER | E01/33/530/CB |  |  |  | CDC | 586 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 530 | 530 |  | DS1 | 531 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-71 | [5 empty] | CDCS_S | [8 empty] | 南科ES.531_DS | 531 DS | OTHER | E01/33/530/DS1 |  |  |  | CDC | 587 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 0 |  | 550 | 550 |  | CB | [17 empty] | 1-10-03 |  | 1-1D | [5 empty] | 161KV_S | [8 empty] | 南科ES.550_CB | 550 CB | OTHER | E01/33/550/CB |  |  |  | CDC | 588 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 550 | 550 |  | DS1 | 551 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-7A | [5 empty] | CDCS_S | [8 empty] | 南科ES.551_DS | 551 DS | OTHER | E01/33/550/DS1 |  |  |  | CDC | 589 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 0 |  | 560 | 560 |  | CB | [17 empty] | 1-10-04 |  | 1-20 | [5 empty] | 161KV_S | [8 empty] | 南科ES.560_CB | 560 CB | OTHER |  |  |  |  | CDC | 590 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | SR96B1 | [17 empty] | 2-30-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_SR96B1 | #1ATR 33KV 電抗器96B1 RY | OTHER | E01/33/1SHR/96B1 |  |  |  | CDC | 591 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | SR96B2 | [17 empty] | 2-30-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_SR96B2 | #1ATR 33KV 電抗器96B2 RY | OTHER | E01/33/1SHR/96B2 |  |  |  | CDC | 592 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | SR96D | [17 empty] | 2-30-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_SR96D | #1ATR 33KV 電抗器96D RY | OTHER | E01/33/1SHR/96D |  |  |  | CDC | 593 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | SR96P | [17 empty] | 2-30-08 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1ATR_SR96P | #1ATR 33KV 電抗器96P RY | OTHER | E01/33/1SHR/96P |  |  |  | CDC | 594 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | #1充電機故障 | [17 empty] | 2-34-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#1充電機故障 | 變電所#1直流充電機故障 | OTHER | E01/0/StaDev/3A5Other |  |  |  | CDC | 595 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | SR96B1 | [17 empty] | 2-31-02 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_SR96B1 | #2ATR 33KV 電抗器96B1 RY | OTHER | E01/33/2SHR/96B1 |  |  |  | CDC | 596 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | SR96B2 | [17 empty] | 2-31-03 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_SR96B2 | #2ATR 33KV 電抗器96B2 RY | OTHER | E01/33/2SHR/96B2 |  |  |  | CDC | 597 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | SR96D | [17 empty] | 2-31-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_SR96D | #2ATR 33KV 電抗器96D RY | OTHER | E01/33/2SHR/96D |  |  |  | CDC | 598 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | SR96P | [17 empty] | 2-31-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2ATR_SR96P | #2ATR 33KV 電抗器96P RY | OTHER | E01/33/2SHR/96P |  |  |  | CDC | 599 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | #2充電機故障 | [17 empty] | 2-34-13 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#2充電機故障 | 變電所#2直流充電機故障 | OTHER | E01/0/StaDev/4A5Other |  |  |  | CDC | 600 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | SR96B1 | [17 empty] | 2-31-11 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_SR96B1 | #3ATR 33KV 電抗器96B1 RY | OTHER | E01/33/3SHR/96B1 |  |  |  | CDC | 601 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | SR96B2 | [17 empty] | 2-31-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_SR96B2 | #3ATR 33KV 電抗器96B2 RY | OTHER | E01/33/3SHR/96B2 |  |  |  | CDC | 602 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | SR96D | [17 empty] | 2-31-13 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_SR96D | #3ATR 33KV 電抗器96D RY | OTHER | E01/33/3SHR/96D |  |  |  | CDC | 603 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | SR96P | [17 empty] | 2-31-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3ATR_SR96P | #3ATR 33KV 電抗器96P RY | OTHER | E01/33/3SHR/96P |  |  |  | CDC | 604 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | #3充電機故障 | [17 empty] | 2-34-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#3充電機故障 | 變電所#3直流充電機故障 | OTHER | E01/0/StaDev/5A5Other |  |  |  | CDC | 605 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | SR96B1 | [17 empty] | 2-32-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_SR96B1 | #4ATR 33KV 電抗器96B1 RY | OTHER | E01/33/4SHR/96B1 |  |  |  | CDC | 606 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | SR96B2 | [17 empty] | 2-32-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_SR96B2 | #4ATR 33KV 電抗器96B2 RY | OTHER | E01/33/4SHR/96B2 |  |  |  | CDC | 607 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | SR96D | [17 empty] | 2-32-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_SR96D | #4ATR 33KV 電抗器96D RY | OTHER | E01/33/4SHR/96D |  |  |  | CDC | 608 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | SR96P | [17 empty] | 2-32-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#4ATR_SR96P | #4ATR 33KV 電抗器96P RY | OTHER | E01/33/4SHR/96P |  |  |  | CDC | 609 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | SR96B1 | [17 empty] | 2-32-13 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_SR96B1 | #5ATR 33KV 電抗器96B1 RY | OTHER | E01/33/5SHR/96B1 |  |  |  | CDC | 610 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | SR96B2 | [17 empty] | 2-32-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_SR96B2 | #5ATR 33KV 電抗器96B2 RY | OTHER | E01/33/5SHR/96B2 |  |  |  | CDC | 611 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | SR96D | [17 empty] | 2-32-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_SR96D | #5ATR 33KV 電抗器96D RY | OTHER | E01/33/5SHR/96D |  |  |  | CDC | 612 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | SR96P | [17 empty] | 2-33-00 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#5ATR_SR96P | #5ATR 33KV 電抗器96P RY | OTHER | E01/33/5SHR/96P |  |  |  | CDC | 613 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | SR96B1 | [17 empty] | 2-33-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_SR96B1 | #6ATR 33KV 電抗器96B1 RY | OTHER | E01/33/6SHR/96B1 |  |  |  | CDC | 614 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | SR96B2 | [17 empty] | 2-33-07 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_SR96B2 | #6ATR 33KV 電抗器96B2 RY | OTHER | E01/33/6SHR/96B2 |  |  |  | CDC | 615 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | SR96D | [17 empty] | 2-33-08 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_SR96D | #6ATR 33KV 電抗器96D RY | OTHER | E01/33/6SHR/96D |  |  |  | CDC | 616 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | SR96P | [17 empty] | 2-33-09 | [7 empty] | CDCS_S | [8 empty] | 南科ES.#6ATR_SR96P | #6ATR 33KV 電抗器96P RY | OTHER | E01/33/6SHR/96P |  |  |  | CDC | 617 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | OSCA | [17 empty] | 1-03-07 | [7 empty] | 345KV_S | [8 empty] | 南科ES.345KV_OSCA | 345KV 示波器啟動警報 | OTHER | E01/345/ComPoint/OSCA |  |  |  | CDC | 618 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3510 | 新嘉民二路(3510) |  | 85CFA | [17 empty] | 1-31-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3510_85CFA | 新嘉民二路(3510)85RY通訊故障 | OTHER | E01/345/3510/85CFA |  |  |  | CDC | 619 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3510 | 新嘉民二路(3510) |  | 87CFA | [17 empty] | 1-31-04 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3510_87CFA | 新嘉民二路(3510)87RY通訊故障 | OTHER | E01/345/3510/87CFA |  |  |  | CDC | 620 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3540 | 嘉民二路(3540) |  | RY1A | [17 empty] | 1-18-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3540_RY1A | 嘉民二路(3540) 電纜電驛故障 | OTHER | E01/345/3540/2A5Other |  |  |  | CDC | 621 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | E1 | 3561E | [16 empty] | 1-3C-12 | 1-3C-13 | [6 empty] | 345KV_S | [8 empty] | 南科ES.3561E_ES | #2ATR 3561E ES | OTHER | E01/345/3560/ES1 |  |  |  | CDC | 622 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 0 |  | 3570 | 新嘉民一路(3570) |  | 85CFA | [17 empty] | 1-32-05 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3570_85CFA | 新嘉民一路(3570)85RY通訊故障 | OTHER | E01/345/3570/85CFA |  |  |  | CDC | 623 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3570 | 新嘉民一路(3570) |  | 87CFA | [17 empty] | 1-32-03 | [7 empty] | CDCS_S | [8 empty] | 南科ES.3570_87CFA | 新嘉民一路(3570)87RY通訊故障 | OTHER | E01/345/3570/87CFA |  |  |  | CDC | 624 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | E1 | 3591E | [16 empty] | 1-3C-14 | 1-3C-15 | [6 empty] | 345KV_S | [8 empty] | 南科ES.3591E_ES | #3ATR 3591E ES | OTHER | E01/345/3690/ES1 |  |  |  | CDC | 625 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 0 |  | 3610 | 龍崎一路(3610) |  | 85CFA | [17 empty] | 1-32-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3610_85CFA | 龍崎一路(3610) #285RY通訊故障 | OTHER | E01/345/3610/85CFA |  |  |  | CDC | 626 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3610 | 龍崎一路(3610) |  | 87CFA | [17 empty] | 1-31-14 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3610_87CFA | 龍崎一路(3610) #187RY通訊故障 | OTHER | E01/345/3610/87CFA |  |  |  | CDC | 627 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3610 | 龍崎一路(3610) |  | RY1A | [17 empty] | 1-18-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3610_RY1A | 龍崎一路(3610) 電纜電驛故障 | OTHER | E01/345/3610/2A5Other |  |  |  | CDC | 628 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | E1 | 3631E | [16 empty] | 1-3D-00 | 1-3D-01 | [6 empty] | 345KV_S | [8 empty] | 南科ES.3631E_ES | #4ATR 3631E ES | OTHER | E01/345/3630/ES1 |  |  |  | CDC | 629 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 0 |  | 3640 | 嘉民一路(3640) |  | RY1A | [17 empty] | 1-18-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3640_RY1A | 嘉民一路(3640) 電纜電驛故障 | OTHER | E01/345/3640/2A5Other |  |  |  | CDC | 630 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | E1 | 3661E | [16 empty] | 1-3D-02 | 1-3D-03 | [6 empty] | 345KV_S | [8 empty] | 南科ES.3661E_ES | #5ATR 3661E ES | OTHER | E01/345/3660/ES1 |  |  |  | CDC | 631 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 0 |  | 3670 | 龍崎二路(3670) |  | 85CFA | [17 empty] | 1-32-10 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3670_85CFA | 龍崎二路(3670) #285RY通訊故障 | OTHER | E01/345/3670/85CFA |  |  |  | CDC | 632 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3670 | 龍崎二路(3670) |  | 87CFA | [17 empty] | 1-32-08 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3670_87CFA | 龍崎二路(3670) #187RY通訊故障 | OTHER | E01/345/3670/87CFA |  |  |  | CDC | 633 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3670 | 龍崎二路(3670) |  | RY1A | [17 empty] | 1-18-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3670_RY1A | 龍崎二路(3670) 電纜電驛故障 | OTHER | E01/345/3670/2A5Other |  |  |  | CDC | 634 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | A所內電源欠壓 | [17 empty] | 2-34-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.A所內電源欠壓 | 345KV 所內電源欠壓 | OTHER | E01/0/StaDev/STUV |  |  |  | CDC | 635 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | A洩油池水位 | [17 empty] | 2-34-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.A洩油池水位 | 345KV 洩油池水位警報 | OTHER | E01/0/StaDev/OilLeak |  |  |  | CDC | 636 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | A棟直流電源DCA | [17 empty] | 2-34-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.A棟直流電源DCA | 345KV 直流電源DCA | OTHER | E01/0/StaDev/DCA |  |  |  | CDC | 637 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV |  |  |  | A棟直流電源DCE | [17 empty] | 2-34-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.A棟直流電源DCE | 345KV 直流電源DCE | OTHER | E01/0/StaDev/DCE |  |  |  | CDC | 638 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | COF | [17 empty] | 2-33-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.COF | 消防警報 | OTHER | E01/0/StaDev/1A5Other |  |  |  | CDC | 639 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | RTU | RTU |  | S/L(1) | [17 empty] | 1-30-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.RTU_S/L(1) | 345KV RTU S/L | OTHER | E01/0/RTU/RTU_R_L |  |  |  | CDC | 640 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E01 | 南科ES | 345 | 345kV | TEST | TEST |  | CB(1) | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | 345KV_S | [8 empty] | 南科ES.TEST_CB(1) | 345KV TEST CB | OTHER | E01/0/RTU/Test_CB1 |  |  |  | CDC | 641 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | Water | [17 empty] | 2-35-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.水位警報 | A,C,D棟地下室水位警報 | OTHER | E01/0/StaDev/Water |  |  |  | CDC | 642 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  |  |  |  | 電壓驟降 | [17 empty] | 2-35-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.電壓驟降 | 電壓驟降警報 | OTHER | E01/0/StaDev/6A5Other |  |  |  | CDC | 643 | GENERICDIPoint | ES001_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 復閉 | 復閉 |  | RCA | [17 empty] | 1-03-06 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KV_RCA | 345KV 79RY(復閉) 動作 | OTHER |  |  |  |  | CDC | 644 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3510 | 新嘉民二路(3510) |  | 87CFA1 | [17 empty] | 1-19-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3510_87CFA1 | 新嘉民二路(3510) 電纜通訊故障 | OTHER | E01/345/3510/87CFA1 |  |  |  | CDC | 645 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3510 | 新嘉民二路(3510) |  | RY1A | [17 empty] | 1-19-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3510_RY1A | 新嘉民二路(3510) 電纜電驛故障 | OTHER | E01/345/3510/2A5Other |  |  |  | CDC | 646 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3570 | 新嘉民一路(3570) |  | 87CFA1 | [17 empty] | 1-19-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3570_87CFA1 | 新嘉民一路(3570) 電纜通訊故障 | OTHER | E01/345/3570/87CFA1 |  |  |  | CDC | 647 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3570 | 新嘉民一路(3570) |  | RY1A | [17 empty] | 1-19-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3570_RY1A | 新嘉民一路(3570) 電纜電驛故障 | OTHER | E01/345/3570/2A5Other |  |  |  | CDC | 648 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | CB | [17 empty] | 1-05-04 |  | 1-17 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1840_CB | 1840(#3ATR) CB | ATR | E01/161/1840/CB |  |  |  | CDC | 649 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | DS1 | 1841 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-6F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1841_DS | 1841(#3ATR) DS | ATR | E01/161/1840/DS1 |  |  |  | CDC | 650 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1840 | #3ATR(1840) |  | DS2 | 1842 | [16 empty] | 1-3A-14 | 1-3A-15 | 1-70 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1842_DS | 1842(#3ATR) DS | ATR | E01/161/1840/DS2 |  |  |  | CDC | 651 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E01 | 南科ES | 161 | 161kV | 1830 | #3ATR(1830) |  | E2 | 1832E | [16 empty] | 1-3D-10 | 1-3D-11 | [6 empty] | ADCS_S | [8 empty] | 南科ES.1832E_ES | #3ATR1832E ES | OTHER | E01/161/1830/ES2 |  |  |  | CDC | 652 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 161 | 161kV | 1850 | #4ATR(1850) |  | E2 | 1852E | [16 empty] | 1-3D-04 | 1-3D-05 | [6 empty] | ADCS_S | [8 empty] | 南科ES.1852E_ES | #4ATR1852E ES | OTHER | E01/161/1850/ES2 |  |  |  | CDC | 653 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 161 | 161kV | 1870 | #5ATR(1870) |  | E2 | 1872E | [16 empty] | 1-3D-06 | 1-3D-07 | [6 empty] | ADCS_S | [8 empty] | 南科ES.1872E_ES | #5ATR1872E ES | OTHER | E01/161/1870/ES2 |  |  |  | CDC | 654 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 161 | 161kV | 1910 | #6ATR(1910) |  | E2 | 1912E | [16 empty] | 1-3D-08 | 1-3D-09 | [6 empty] | ADCS_S | [8 empty] | 南科ES.1912E_ES | #6ATR1912E ES | OTHER | E01/161/1910/ES2 |  |  |  | CDC | 655 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E01 | 南科ES | 345 | 345kV | BUS | #1,2BUS |  | CTFA1 | [17 empty] | 1-3D-13 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KVBUS_CTFA1 | 345KV #1,2BUS 第一套CT回路故障 | OTHER | E01/345/ComPoint/87CTFA1 |  |  |  | CDC | 656 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | BUS | #1,2BUS |  | CTFA2 | [17 empty] | 1-3D-15 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KVBUS_CTFA2 | 345KV #1,2BUS 第二套CT回路故障 | OTHER | E01/345/ComPoint/87CTFA2 |  |  |  | CDC | 657 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | BUS | #1,2BUS |  | RYFA1 | [17 empty] | 1-3D-12 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KVBUS_RYFA1 | 345KV #1,2BUS 第一套數位RY故障 | OTHER | E01/345/ComPoint/RYFA1 |  |  |  | CDC | 658 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | BUS | #1,2BUS |  | RYFA2 | [17 empty] | 1-3D-14 | [7 empty] | CDCS_S | [8 empty] | 南科ES.345KVBUS_RYFA2 | 345KV #1,2BUS 第二套數位RY故障 | OTHER | E01/345/ComPoint/RYFA2 |  |  |  | CDC | 659 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | 51ZA | [17 empty] | 1-3E-00 |  | 2-08 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_51Z | #1ATR 51ZRY U/L | OTHER | E01//1ATR/51Z_UL |  |  |  | CDC | 660 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | ATR_86A | [17 empty] | 1-3E-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_86A | #1ATR 86(51Z/87/96)RY | OTHER | E01//1ATR/ATR_86A |  |  |  | CDC | 661 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR | #1ATR |  | RYFA | [17 empty] | 1-3E-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR_RYFA | #1ATR 數位電驛故障 | OTHER | E01//1ATR/RYFA |  |  |  | CDC | 662 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR(520) | #2ATR(520) |  | 87A | [17 empty] | 1-10-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR(520)_87A | #2ATR(520) 87RY | OTHER | E01/33/520/87A |  |  |  | CDC | 663 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | 51ZA | [17 empty] | 1-3E-02 |  | 2-0B | [5 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_51Z | #2ATR 51ZRY U/L | OTHER | E01//2ATR/51Z_UL |  |  |  | CDC | 664 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | ATR_86A | [17 empty] | 1-3E-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_86A | #2ATR 86(51Z/87/96)RY | OTHER | E01//2ATR/ATR_86A |  |  |  | CDC | 665 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR | #2ATR三次側電抗器用 |  | 2_87UL1 | [17 empty] | 1-3E-04 |  | 2-0C | [5 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_87UL3 | #2ATR三次側電抗器用 87RY U/L | OTHER | E01//2ATR/2_87UL1 |  |  |  | CDC | 666 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 2ATR | #2ATR |  | RYFA | [17 empty] | 1-3E-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR_RYFA | #2ATR 數位電驛故障 | OTHER | E01//2ATR/RYFA |  |  |  | CDC | 667 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR(510) | #1ATR(510) |  | 51A | [17 empty] | 1-10-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR(510)_51A | #1ATR(510) 51RY | OTHER | E01/33/510/51A |  |  |  | CDC | 668 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 1ATR(510) | #1ATR(510) |  | 87A | [17 empty] | 1-10-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1ATR(510)_87A | #1ATR(510) 87RY | OTHER | E01/33/510/87A |  |  |  | CDC | 669 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 2ATR(520) | #2ATR(520) |  | 51A | [17 empty] | 1-11-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2ATR(520)_51A | #2ATR(520) 51RY | OTHER | E01/33/520/51A |  |  |  | CDC | 670 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR(530) | #3ATR(530) |  | 51A | [17 empty] | 1-11-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR(530)_51A | #3ATR(530) 51RY | OTHER | E01/33/530/51A |  |  |  | CDC | 671 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR(530) | #3ATR(530) |  | 87A | [17 empty] | 1-11-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR(530)_87A | #3ATR(530) 87RY | OTHER | E01/33/530/87A |  |  |  | CDC | 672 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | 51ZA | [17 empty] | 1-3E-08 |  | 2-0F | [5 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_51Z | #3ATR 51ZRY U/L | OTHER | E01//3ATR/51Z_UL |  |  |  | CDC | 673 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | ATR_86A | [17 empty] | 1-3E-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_86A | #3ATR 86(51Z/87/96)RY | OTHER | E01//3ATR/ATR_86A |  |  |  | CDC | 674 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3ATR | #3ATR三次側電抗器用 |  | 2_87UL1 | [17 empty] | 1-3E-10 |  | 2-10 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_87UL3 | #3ATR三次側電抗器用 87RY U/L | OTHER | E01//3ATR/2_87UL1 |  |  |  | CDC | 675 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 3ATR | #3ATR |  | RYFA | [17 empty] | 1-3E-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3ATR_RYFA | #3ATR 數位電驛故障 | OTHER | E01//3ATR/RYFA |  |  |  | CDC | 676 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | 51ZA | [17 empty] | 1-3E-12 |  | 2-13 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_51Z | #4ATR 51ZRY U/L | OTHER | E01//4ATR/51Z_UL |  |  |  | CDC | 677 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | ATR_86A | [17 empty] | 1-3E-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_86A | #4ATR 86(51Z/87/96)RY | OTHER | E01//4ATR/ATR_86A |  |  |  | CDC | 678 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 4ATR | #4ATR |  | RYFA | [17 empty] | 1-3E-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4ATR_RYFA | #4ATR 數位電驛故障 | OTHER | E01//4ATR/RYFA |  |  |  | CDC | 679 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR(550) | #5ATR(550) |  | 51A | [17 empty] | 1-11-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR(550)_51A | #5ATR(550) 51RY | OTHER | E01/33/550/51A |  |  |  | CDC | 680 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR(550) | #5ATR(550) |  | 87A | [17 empty] | 1-11-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR(550)_87A | #5ATR(550) 87RY | OTHER | E01/33/550/87A |  |  |  | CDC | 681 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | 51ZA | [17 empty] | 1-3E-15 |  | 2-16 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_51Z | #5ATR 51ZRY U/L | OTHER | E01//5ATR/51Z_UL |  |  |  | CDC | 682 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | ATR_86A | [17 empty] | 1-3E-14 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_86A | #5ATR 86(51Z/87/96)RY | OTHER | E01//5ATR/ATR_86A |  |  |  | CDC | 683 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 5ATR | #5ATR三次側電抗器用 |  | 2_87UL1 | [17 empty] | 1-3F-01 |  | 2-17 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_87UL3 | #5ATR三次側電抗器用 87RY U/L | OTHER | E01//5ATR/2_87UL1 |  |  |  | CDC | 684 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 5ATR | #5ATR |  | RYFA | [17 empty] | 1-3F-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#5ATR_RYFA | #5ATR 數位電驛故障 | OTHER | E01//5ATR/RYFA |  |  |  | CDC | 685 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR(560) | #6ATR(560) |  | 51A | [17 empty] | 1-11-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR(560)_51A | #6ATR(560) 51RY | OTHER | E01/33/560/51A |  |  |  | CDC | 686 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR(560) | #6ATR(560) |  | 87A | [17 empty] | 1-11-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR(560)_87A | #6ATR(560) 87RY | OTHER | E01/33/560/87A |  |  |  | CDC | 687 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | 51ZA | [17 empty] | 1-3F-03 |  | 2-1A | [5 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_51Z | #6ATR 51ZRY U/L | OTHER | E01//6ATR/51Z_UL |  |  |  | CDC | 688 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | USE/LOCK | USE
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | ATR_86A | [17 empty] | 1-3F-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_86A | #6ATR 86(51Z/87/96)RY | OTHER | E01//6ATR/ATR_86A |  |  |  | CDC | 689 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 6ATR | #6ATR |  | RYFA | [17 empty] | 1-3F-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#6ATR_RYFA | #6ATR 數位電驛故障 | OTHER | E01//6ATR/RYFA |  |  |  | CDC | 690 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | _BF | _BF |  | RYFA | [17 empty] | 1-3F-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.345KV_BF_RYFA | 345KV斷路器失靈電驛故障 | OTHER | E01/345/ComPoint/BFA |  |  |  | CDC | 691 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3640 | 嘉民一路(3640) |  | 87LA | [17 empty] | 1-0A-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3640_87LA | 嘉民一路(3640)電纜87RY | OTHER | E01/345/3640/87A |  |  |  | CDC | 692 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3540 | 嘉民二路(3540) |  | 87LA | [17 empty] | 1-0A-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3540_87LA | 嘉民二路(3540)電纜87RY | OTHER | E01/345/3540/87A |  |  |  | CDC | 693 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3610 | 龍崎一路(3610) |  | 87LA | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3610_87LA | 龍崎一路(3610)電纜87RY | OTHER | E01/345/3610/87A |  |  |  | CDC | 694 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3670 | 龍崎二路(3670) |  | 87LA | [17 empty] | 1-0A-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3670_87LA | 龍崎二路(3670)電纜87RY | OTHER | E01/345/3670/87A |  |  |  | CDC | 695 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3510 | 新嘉民二路(3510) |  | 87LA1 | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3510_87LA1 | 新嘉民二路(3510)電纜87A1 | OTHER | E01/345/3510/87A1 |  |  |  | CDC | 696 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3510 | 新嘉民二路(3510) |  | 87LA2 | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3510_87LA2 | 新嘉民二路(3510)電纜87A2 | OTHER | E01/345/3510/87A2 |  |  |  | CDC | 697 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3570 | 新嘉民一路(3570) |  | 87LA1 | [17 empty] | 1-0A-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3570_87LA1 | 新嘉民一路(3570)電纜87A1 | OTHER | E01/345/3570/87A1 |  |  |  | CDC | 698 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3570 | 新嘉民一路(3570) |  | 87LA2 | [17 empty] | 1-0A-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3570_87LA2 | 新嘉民一路(3570)電纜87A2 | OTHER | E01/345/3570/87A2 |  |  |  | CDC | 699 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3540 | 嘉民二路(3540) |  | RYFA | [17 empty] | 1-3F-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3540_RYFA | 嘉民二路(3540)數位電驛故障 | OTHER | E01/345/3540/RYFA |  |  |  | CDC | 700 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 0 |  | 3640 | 嘉民一路(3640) |  | RYFA | [17 empty] | 1-3F-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.3640_RYFA | 嘉民ㄧ路(3640)數位電驛故障 | OTHER | E01/345/3640/RYFA |  |  |  | CDC | 701 | GENERICDIPoint | ES001_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | PHA | [17 empty] | 1-0B-02 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3540_PHA | 嘉民南科二路(3540) 相間RY | LINE345 | E01/345/3540/PHA |  |  |  | CDC | 702 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | GDA | [17 empty] | 1-0B-03 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3540_GDA | 嘉民南科二路(3540) 接地RY | LINE345 | E01/345/3540/GDA |  |  |  | CDC | 703 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | PHA | [17 empty] | 1-0B-00 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3640_PHA | 嘉民南科一路(3640) 相間RY | LINE345 | E01/345/3640/PHA |  |  |  | CDC | 704 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | GDA | [17 empty] | 1-0B-01 | [7 empty] | 345KV_S | [8 empty] | 南科ES.3640_GDA | 嘉民南科一路(3640) 接地RY | LINE345 | E01/345/3640/GDA |  |  |  | CDC | 705 | GENERICDIPoint | ES001_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E01 | 南科ES | 22 | 22kV | 210_SC | #1SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.210_SC_CAP | 23KV#1SC 容量 | SC | [5 empty] | 706 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 707 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 708 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 240_SC | #4SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.240_SC_CAP | 23KV#4SC 容量 | SC | [5 empty] | 709 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 710 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 711 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 117 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_117 | 南科ES NT #1ADTR 11KV_Hi_Limit | [6 empty] | 712 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 118 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_118 | 南科ES NT #1ADTR 11KV_Lo_Limit | [6 empty] | 713 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 119 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_119 | 南科ES NT #1BDTR 11KV_Hi_Limit | [6 empty] | 714 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 120 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_120 | 南科ES NT #1BDTR 11KV_Lo_Limit | [6 empty] | 715 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 121 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_121 | 南科ES NT #2ADTR 23KV_Hi_Limit | [6 empty] | 716 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 122 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_122 | 南科ES NT #2ADTR 23KV_Lo_Limit | [6 empty] | 717 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 123 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_123 | 南科ES NT #2BDTR 23KV_Hi_Limit | [6 empty] | 718 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 124 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_124 | 南科ES NT #2BDTR 23KV_Lo_Limit | [6 empty] | 719 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 125 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_125 | 南科ES NT #3ADTR 23KV_Hi_Limit | [6 empty] | 720 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 126 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_126 | 南科ES NT #3ADTR 23KV_Lo_Limit | [6 empty] | 721 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 127 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_127 | 南科ES NT #3BDTR 23KV_Hi_Limit | [6 empty] | 722 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 0 |  | TRD | 南科ES |  | 128 | [25 empty] | TRAIN_AD | [8 empty] | 南科ES.TRD_128 | 南科ES NT #3BDTR 23KV_Lo_Limit | [6 empty] | 723 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
E01 | 南科ES | 11 | 11kV | 280_SC | #8SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.280_SC_CAP | 11KV#8SC 容量 | SC | [5 empty] | 724 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 22 | 22kV | 270_SC | #7SC | 9 | CAP | [25 empty] | ADCS_S | [8 empty] | 南科ES.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 725 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 0 |  | NA | NA |  | 01 | [25 empty] | CDCS | [8 empty] | 南科ES.NA_01 | 南科ES裝置容量 | [6 empty] | 726 | NotelAIPoint | [21 empty] | MW | 10000.000000 | 10000.000000 | 10000.000000 | 10000.000000 | 0.100000 | -10000.000000 | -10000.000000 | -10000.000000 | -10000.000000
E01 | 南科ES | 33 | 33kV | _SHR | _SHR |  | XL | [25 empty] | ADCS_N | [8 empty] | 南科ES.33KV_SHR_XL | 33KV_SHR_感抗值 | SC | [5 empty] | 727 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E01 | 南科ES | 161 | 161kV | 1510 | 1510 |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1510 | 1510 |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1520 | 1520 |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1520 | 1520 |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1550 | 1550 |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1550 | 1550 |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1610 | 1610 |  | LE0 | 1610LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1610 | 1610 |  | BE0 | 1610BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1620 | 1620 |  | LE0 | 1620LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1620 | 1620 |  | BE0 | 1620BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1630 | 1630 |  | LE0 | 1630LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1630LE | 1630LE (非取樣點) | LINE161 | [5 empty] | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1630 | 1630 |  | BE0 | 1630BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1630BE | 1630BE (非取樣點) | LINE161 | [5 empty] | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1640 | 1640 |  | LE0 | 1640LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1640LE | 1640LE (非取樣點) | LINE161 | [5 empty] | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1640 | 1640 |  | BE0 | 1640BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1640BE | 1640BE (非取樣點) | LINE161 | [5 empty] | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1650 | 1650 |  | LE0 | 1650LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1650LE | 1650LE (非取樣點) | LINE161 | [5 empty] | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1650 | 1650 |  | BE0 | 1650BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1650BE | 1650BE (非取樣點) | LINE161 | [5 empty] | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1660 | 1660 |  | LE0 | 1660LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1660LE | 1660LE (非取樣點) | LINE161 | [5 empty] | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1660 | 1660 |  | BE0 | 1660BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1660BE | 1660BE (非取樣點) | LINE161 | [5 empty] | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1670 | 1670 |  | LE0 | 1670LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1670LE | 1670LE (非取樣點) | LINE161 | [5 empty] | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1670 | 1670 |  | BE0 | 1670BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1670BE | 1670BE (非取樣點) | LINE161 | [5 empty] | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1680 | 1680 |  | LE0 | 1680LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1680LE | 1680LE (非取樣點) | LINE161 | [5 empty] | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1680 | 1680 |  | BE0 | 1680BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1680BE | 1680BE (非取樣點) | LINE161 | [5 empty] | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1710 | 1710 |  | LE0 | 1710LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1710LE | 1710LE (非取樣點) | LINE161 | [5 empty] | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1710 | 1710 |  | BE0 | 1710BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1710BE | 1710BE (非取樣點) | LINE161 | [5 empty] | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1720 | 1720 |  | LE0 | 1720LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1720LE | 1720LE (非取樣點) | LINE161 | [5 empty] | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1720 | 1720 |  | BE0 | 1720BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1720BE | 1720BE (非取樣點) | LINE161 | [5 empty] | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1730 | 1730 |  | LE0 | 1730LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1730LE | 1730LE (非取樣點) | LINE161 | [5 empty] | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1730 | 1730 |  | BE0 | 1730BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1730BE | 1730BE (非取樣點) | LINE161 | [5 empty] | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1740 | 1740 |  | LE0 | 1740LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1740LE | 1740LE (非取樣點) | LINE161 | [5 empty] | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1740 | 1740 |  | BE0 | 1740BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1740BE | 1740BE (非取樣點) | LINE161 | [5 empty] | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K216 | K216_DS |  | DS1 | K216_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_DS | K216_DS (非取樣點) | FEEDER | [5 empty] | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K216 | K216_ES |  | LE0 | K216_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_ES | K216_ES (非取樣點) | FEEDER | [5 empty] | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K217 | K217_DS |  | DS1 | K217_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_DS | K217_DS (非取樣點) | FEEDER | [5 empty] | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K217 | K217_ES |  | LE0 | K217_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_ES | K217_ES (非取樣點) | FEEDER | [5 empty] | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K218 | K218_DS |  | DS1 | K218_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_DS | K218_DS (非取樣點) | FEEDER | [5 empty] | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K218 | K218_ES |  | LE0 | K218_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_ES | K218_ES (非取樣點) | FEEDER | [5 empty] | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K219 | K219_DS |  | DS1 | K219_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_DS | K219_DS (非取樣點) | FEEDER | [5 empty] | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K219 | K219_ES |  | LE0 | K219_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_ES | K219_ES (非取樣點) | FEEDER | [5 empty] | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K220 | K220_DS |  | DS1 | K220_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_DS | K220_DS (非取樣點) | FEEDER | [5 empty] | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K220 | K220_ES |  | LE0 | K220_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_ES | K220_ES (非取樣點) | FEEDER | [5 empty] | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K261 | K261_DS |  | DS1 | K261_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_DS | K261_DS (非取樣點) | FEEDER | [5 empty] | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K261 | K261_ES |  | LE0 | K261_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_ES | K261_ES (非取樣點) | FEEDER | [5 empty] | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K262 | K262_DS |  | DS1 | K262_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_DS | K262_DS (非取樣點) | FEEDER | [5 empty] | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K262 | K262_ES |  | LE0 | K262_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_ES | K262_ES (非取樣點) | FEEDER | [5 empty] | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K263 | K263_DS |  | DS1 | K263_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_DS | K263_DS (非取樣點) | FEEDER | [5 empty] | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K263 | K263_ES |  | LE0 | K263_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_ES | K263_ES (非取樣點) | FEEDER | [5 empty] | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K264 | K264_DS |  | DS1 | K264_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_DS | K264_DS (非取樣點) | FEEDER | [5 empty] | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K264 | K264_ES |  | LE0 | K264_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_ES | K264_ES (非取樣點) | FEEDER | [5 empty] | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K265 | K265_DS |  | DS1 | K265_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_DS | K265_DS (非取樣點) | FEEDER | [5 empty] | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K265 | K265_ES |  | LE0 | K265_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_ES | K265_ES (非取樣點) | FEEDER | [5 empty] | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K266 | K266_DS |  | DS1 | K266_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_DS | K266_DS (非取樣點) | FEEDER | [5 empty] | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K266 | K266_ES |  | LE0 | K266_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_ES | K266_ES (非取樣點) | FEEDER | [5 empty] | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K267 | K267_DS |  | DS1 | K267_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_DS | K267_DS (非取樣點) | FEEDER | [5 empty] | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K267 | K267_ES |  | LE0 | K267_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_ES | K267_ES (非取樣點) | FEEDER | [5 empty] | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K268 | K268_DS |  | DS1 | K268_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_DS | K268_DS (非取樣點) | FEEDER | [5 empty] | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K268 | K268_ES |  | LE0 | K268_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_ES | K268_ES (非取樣點) | FEEDER | [5 empty] | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K271 | K271_DS |  | DS1 | K271_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_DS | K271_DS (非取樣點) | FEEDER | [5 empty] | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K271 | K271_ES |  | LE0 | K271_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_ES | K271_ES (非取樣點) | FEEDER | [5 empty] | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K272 | K272_DS |  | DS1 | K272_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_DS | K272_DS (非取樣點) | FEEDER | [5 empty] | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K272 | K272_ES |  | LE0 | K272_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_ES | K272_ES (非取樣點) | FEEDER | [5 empty] | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K273 | K273_DS |  | DS1 | K273_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_DS | K273_DS (非取樣點) | FEEDER | [5 empty] | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K273 | K273_ES |  | LE0 | K273_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_ES | K273_ES (非取樣點) | FEEDER | [5 empty] | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K274 | K274_DS |  | DS1 | K274_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_DS | K274_DS (非取樣點) | FEEDER | [5 empty] | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K274 | K274_ES |  | LE0 | K274_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_ES | K274_ES (非取樣點) | FEEDER | [5 empty] | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K275 | K275_DS |  | DS1 | K275_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_DS | K275_DS (非取樣點) | FEEDER | [5 empty] | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K275 | K275_ES |  | LE0 | K275_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_ES | K275_ES (非取樣點) | FEEDER | [5 empty] | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K276 | K276_DS |  | DS1 | K276_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_DS | K276_DS (非取樣點) | FEEDER | [5 empty] | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K276 | K276_ES |  | LE0 | K276_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_ES | K276_ES (非取樣點) | FEEDER | [5 empty] | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K277 | K277_DS |  | DS1 | K277_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_DS | K277_DS (非取樣點) | FEEDER | [5 empty] | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K277 | K277_ES |  | LE0 | K277_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_ES | K277_ES (非取樣點) | FEEDER | [5 empty] | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K278 | K278_DS |  | DS1 | K278_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_DS | K278_DS (非取樣點) | FEEDER | [5 empty] | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K278 | K278_ES |  | LE0 | K278_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_ES | K278_ES (非取樣點) | FEEDER | [5 empty] | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 101 | 101 |  | 101 | 101 | [24 empty] | ADCS_S | [8 empty] | 南科ES.101 | 101 (非取樣點) | TIE | [5 empty] | 800 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 100 | 100 |  | E1 | 101E | [24 empty] | ADCS_S | [8 empty] | 南科ES.101E | 101E (非取樣點) | TIE | [5 empty] | 801 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1500 | 1500 |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 南科ES.1501E | 1501E (非取樣點) | TIE | [5 empty] | 802 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1500 | 1500 |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 南科ES.1502E | 1502E (非取樣點) | TIE | [5 empty] | 803 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1700 | 1700 |  | E1 | 1701E | [24 empty] | ADCS_S | [8 empty] | 南科ES.1701E | 1701E (非取樣點) | TIE | [5 empty] | 804 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1700 | 1700 |  | E3 | 1703E | [24 empty] | ADCS_S | [8 empty] | 南科ES.1703E | 1703E (非取樣點) | TIE | [5 empty] | 805 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1800 | 1800 |  | E2 | 1802E | [24 empty] | ADCS_S | [8 empty] | 南科ES.1802E | 1802E (非取樣點) | TIE | [5 empty] | 806 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1800 | 1800 |  | E4 | 1804E | [24 empty] | ADCS_S | [8 empty] | 南科ES.1804E | 1804E (非取樣點) | TIE | [5 empty] | 807 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 201 | 201 |  | 201 | 201 | [24 empty] | ADCS_S | [8 empty] | 南科ES.201 | 201 (非取樣點) | TIE | [5 empty] | 808 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 200 | 200 |  | E1 | 201E | [24 empty] | ADCS_S | [8 empty] | 南科ES.201E | 201E (非取樣點) | TIE | [5 empty] | 809 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 301 | 301 |  | 301 | 301 | [24 empty] | ADCS_S | [8 empty] | 南科ES.301 | 301 (非取樣點) | TIE | [5 empty] | 810 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 300 | 300 |  | E1 | 301E | [24 empty] | ADCS_S | [8 empty] | 南科ES.301E | 301E (非取樣點) | TIE | [5 empty] | 811 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 401 | 401 |  | 401 | 401 | [24 empty] | ADCS_S | [8 empty] | 南科ES.401 | 401 (非取樣點) | TIE | [5 empty] | 812 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 400 | 400 |  | E1 | 401E | [24 empty] | ADCS_S | [8 empty] | 南科ES.401E | 401E (非取樣點) | TIE | [5 empty] | 813 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 191 | 191 |  | 191 | 191 | [24 empty] | ADCS_S | [8 empty] | 南科ES.191 | 191 (非取樣點) | OTHER | [5 empty] | 814 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 291 | 291 |  | 291 | 291 | [24 empty] | ADCS_S | [8 empty] | 南科ES.291 | 291 (非取樣點) | OTHER | [5 empty] | 815 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 391 | 391 |  | 391 | 391 | [24 empty] | ADCS_S | [8 empty] | 南科ES.391 | 391 (非取樣點) | OTHER | [5 empty] | 816 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 491 | 491 |  | 491 | 491 | [24 empty] | ADCS_S | [8 empty] | 南科ES.491 | 491 (非取樣點) | OTHER | [5 empty] | 817 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 161 | 161kV | 1750 | 1750 |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 818 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1750 | 1750 |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 819 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 311 | 311 |  | 311 | 311 | [24 empty] | ADCS_S | [8 empty] | 南科ES.311 | 311 (非取樣點) | MTR | [5 empty] | 820 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 310 | 310 |  | E1 | 311E | [24 empty] | ADCS_S | [8 empty] | 南科ES.311E | 311E (非取樣點) | MTR | [5 empty] | 821 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 321 | 321 |  | 321 | 321 | [24 empty] | ADCS_S | [8 empty] | 南科ES.321 | 321 (非取樣點) | MTR | [5 empty] | 822 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 320 | 320 |  | E1 | 321E | [24 empty] | ADCS_S | [8 empty] | 南科ES.321E | 321E (非取樣點) | MTR | [5 empty] | 823 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1760 | 1760 |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 824 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1760 | 1760 |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 825 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 331 | 331 |  | 331 | 331 | [24 empty] | ADCS_S | [8 empty] | 南科ES.331 | 331 (非取樣點) | MTR | [5 empty] | 826 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 330 | 330 |  | E1 | 331E | [24 empty] | ADCS_S | [8 empty] | 南科ES.331E | 331E (非取樣點) | MTR | [5 empty] | 827 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 341 | 341 |  | 341 | 341 | [24 empty] | ADCS_S | [8 empty] | 南科ES.341 | 341 (非取樣點) | MTR | [5 empty] | 828 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 340 | 340 |  | E1 | 341E | [24 empty] | ADCS_S | [8 empty] | 南科ES.341E | 341E (非取樣點) | MTR | [5 empty] | 829 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1770 | 1770 |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 830 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1770 | 1770 |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 831 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 351 | 351 |  | 351 | 351 | [24 empty] | ADCS_S | [8 empty] | 南科ES.351 | 351 (非取樣點) | MTR | [5 empty] | 832 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 350 | 350 |  | E1 | 351E | [24 empty] | ADCS_S | [8 empty] | 南科ES.351E | 351E (非取樣點) | MTR | [5 empty] | 833 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 361 | 361 |  | 361 | 361 | [24 empty] | ADCS_S | [8 empty] | 南科ES.361 | 361 (非取樣點) | MTR | [5 empty] | 834 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 360 | 360 |  | E1 | 361E | [24 empty] | ADCS_S | [8 empty] | 南科ES.361E | 361E (非取樣點) | MTR | [5 empty] | 835 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1780 | 1780 |  | TE0 | 1780TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1780TE | 1780TE (非取樣點) | MTR | [5 empty] | 836 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1780 | 1780 |  | BE0 | 1780BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1780BE | 1780BE (非取樣點) | MTR | [5 empty] | 837 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 371 | 371 |  | 371 | 371 | [24 empty] | ADCS_S | [8 empty] | 南科ES.371 | 371 (非取樣點) | MTR | [5 empty] | 838 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 370 | 370 |  | E1 | 371E | [24 empty] | ADCS_S | [8 empty] | 南科ES.371E | 371E (非取樣點) | MTR | [5 empty] | 839 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 381 | 381 |  | 381 | 381 | [24 empty] | ADCS_S | [8 empty] | 南科ES.381 | 381 (非取樣點) | MTR | [5 empty] | 840 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 380 | 380 |  | E1 | 381E | [24 empty] | ADCS_S | [8 empty] | 南科ES.381E | 381E (非取樣點) | MTR | [5 empty] | 841 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 211E | 211E |  | 211E | 211E | [24 empty] | ADCS_S | [8 empty] | 南科ES.211E | 211E (非取樣點) | SC | [5 empty] | 842 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 211 | 211 |  | 211 | 211 | [24 empty] | ADCS_S | [8 empty] | 南科ES.211 | 211 (非取樣點) | SC | [5 empty] | 843 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 221E | 221E |  | 221E | 221E | [24 empty] | ADCS_S | [8 empty] | 南科ES.221E | 221E (非取樣點) | SC | [5 empty] | 844 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 220 | 220SC1_ES |  | SC10 | 220SC1 | [24 empty] | ADCS_S | [8 empty] | 南科ES.220SC1_ES | 220SC1_ES (非取樣點) | SC | [5 empty] | 845 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 221 | 221 |  | 221 | 221 | [24 empty] | ADCS_S | [8 empty] | 南科ES.221 | 221 (非取樣點) | SC | [5 empty] | 846 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 220 | 220SC2_ES |  | SC20 | 220SC2 | [24 empty] | ADCS_S | [8 empty] | 南科ES.220SC2_ES | 220SC2_ES (非取樣點) | SC | [5 empty] | 847 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 231E | 231E |  | 231E | 231E | [24 empty] | ADCS_S | [8 empty] | 南科ES.231E | 231E (非取樣點) | SC | [5 empty] | 848 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 230 | 230SC_ES |  | SC0 | 230SC | [24 empty] | ADCS_S | [8 empty] | 南科ES.230SC_ES | 230SC_ES (非取樣點) | SC | [5 empty] | 849 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 231 | 231 |  | 231 | 231 | [24 empty] | ADCS_S | [8 empty] | 南科ES.231 | 231 (非取樣點) | SC | [5 empty] | 850 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 241E | 241E |  | 241E | 241E | [24 empty] | ADCS_S | [8 empty] | 南科ES.241E | 241E (非取樣點) | SC | [5 empty] | 851 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 240 | 240SC_ES |  | SC0 | 240SC | [24 empty] | ADCS_S | [8 empty] | 南科ES.240SC_ES | 240SC_ES (非取樣點) | SC | [5 empty] | 852 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 241 | 241 |  | 241 | 241 | [24 empty] | ADCS_S | [8 empty] | 南科ES.241 | 241 (非取樣點) | SC | [5 empty] | 853 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 251E | 251E |  | 251E | 251E | [24 empty] | ADCS_S | [8 empty] | 南科ES.251E | 251E (非取樣點) | SC | [5 empty] | 854 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 250 | 250SC_ES |  | SC0 | 250SC | [24 empty] | ADCS_S | [8 empty] | 南科ES.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 855 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 251 | 251 |  | 251 | 251 | [24 empty] | ADCS_S | [8 empty] | 南科ES.251 | 251 (非取樣點) | SC | [5 empty] | 856 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 261E | 261E |  | 261E | 261E | [24 empty] | ADCS_S | [8 empty] | 南科ES.261E | 261E (非取樣點) | SC | [5 empty] | 857 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 260 | 260SC_ES |  | SC0 | 260SC | [24 empty] | ADCS_S | [8 empty] | 南科ES.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 858 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 261 | 261 |  | 261 | 261 | [24 empty] | ADCS_S | [8 empty] | 南科ES.261 | 261 (非取樣點) | SC | [5 empty] | 859 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_S | [8 empty] | 南科ES.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 860 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_S | [8 empty] | 南科ES.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 861 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 160 | 160 |  | BE3 | 161B3E | [24 empty] | ADCS_S | [8 empty] | 南科ES.161B3E | 161B3E (非取樣點) | BUS | [5 empty] | 862 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 160 | 160 |  | BE4 | 161B4E | [24 empty] | ADCS_S | [8 empty] | 南科ES.161B4E | 161B4E (非取樣點) | BUS | [5 empty] | 863 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 南科ES.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 864 | NotelDIPoint | [38 empty] | START/STOP | STOP
E01 | 南科ES | 0 |  |  |  |  | 102 | 102 | [24 empty] | ADCS_S | [8 empty] | 南科ES.102 | 102(非取樣點) | OTHER | [5 empty] | 865 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 102E | 102E | [24 empty] | ADCS_S | [8 empty] | 南科ES.102E | 102E(非取樣點) | OTHER | [5 empty] | 866 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 191E | 191E |  | 191E | 191E | [24 empty] | ADCS_S | [8 empty] | 南科ES.191E | 191E (非取樣點) | OTHER | [5 empty] | 867 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 202 | 202 | [24 empty] | ADCS_S | [8 empty] | 南科ES.202 | 202(非取樣點) | OTHER | [5 empty] | 868 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 202E | 202E | [24 empty] | ADCS_S | [8 empty] | 南科ES.202E | 202E(非取樣點) | OTHER | [5 empty] | 869 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 291E | 291E |  | 291E | 291E | [24 empty] | ADCS_S | [8 empty] | 南科ES.291E | 291E (非取樣點) | OTHER | [5 empty] | 870 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 302 | 302 | [24 empty] | ADCS_S | [8 empty] | 南科ES.302 | 302(非取樣點) | OTHER | [5 empty] | 871 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 302E | 302E | [24 empty] | ADCS_S | [8 empty] | 南科ES.302E | 302E(非取樣點) | OTHER | [5 empty] | 872 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 391E | 391E |  | 391E | 391E | [24 empty] | ADCS_S | [8 empty] | 南科ES.391E | 391E (非取樣點) | OTHER | [5 empty] | 873 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 402 | 402 | [24 empty] | ADCS_S | [8 empty] | 南科ES.402 | 402(非取樣點) | OTHER | [5 empty] | 874 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 402E | 402E | [24 empty] | ADCS_S | [8 empty] | 南科ES.402E | 402E(非取樣點) | OTHER | [5 empty] | 875 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 491E | 491E |  | 491E | 491E | [24 empty] | ADCS_S | [8 empty] | 南科ES.491E | 491E (非取樣點) | OTHER | [5 empty] | 876 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1570 | 1570 |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 877 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1570 | 1570 |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 878 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | LE0 | 3510LE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3510LE | 3510LE (非取樣點) | LINE345 | E01/345/3510/LE0 |  |  |  |  | 879 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3510 | 新嘉民二路(3510) |  | BE0 | 3510BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3510BE | 3510BE (非取樣點) | LINE345 | E01/345/3510/BE0 |  |  |  |  | 880 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | LE0 | 3540LE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3540LE | 3540LE (非取樣點) | LINE345 | E01/345/3540/LE0 |  |  |  |  | 881 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3540 | 嘉民二路(3540) |  | BE0 | 3540BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3540BE | 3540BE (非取樣點) | LINE345 | E01/345/3540/BE0 |  |  |  |  | 882 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | LE0 | 3570LE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3570LE | 3570LE (非取樣點) | LINE345 | E01/345/3570/LE0 |  |  |  |  | 883 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3570 | 新嘉民一路(3570) |  | BE0 | 3570BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3570BE | 3570BE (非取樣點) | LINE345 | E01/345/3570/BE0 |  |  |  |  | 884 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | LE0 | 3610LE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3610LE | 3610LE (非取樣點) | LINE345 | E01/345/3610/LE0 |  |  |  |  | 885 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3610 | 龍崎一路(3610) |  | BE0 | 3610BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3610BE | 3610BE (非取樣點) | LINE345 | E01/345/3610/BE0 |  |  |  |  | 886 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | LE0 | 3640LE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3640LE | 3640LE (非取樣點) | LINE345 | E01/345/3640/LE0 |  |  |  |  | 887 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3640 | 嘉民一路(3640) |  | BE0 | 3640BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3640BE | 3640BE (非取樣點) | LINE345 | E01/345/3640/BE0 |  |  |  |  | 888 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | LE0 | 3670LE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3670LE | 3670LE (非取樣點) | LINE345 | E01/345/3670/LE0 |  |  |  |  | 889 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3670 | 龍崎二路(3670) |  | BE0 | 3670BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3670BE | 3670BE (非取樣點) | LINE345 | E01/345/3670/BE0 |  |  |  |  | 890 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3520 | 3520 |  | E1 | 3521E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3521E | 3521E (非取樣點) | LINE345 | E01/345/3520/E1 |  |  |  |  | 891 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3520 | 3520 |  | E2 | 3522E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3522E | 3522E (非取樣點) | LINE345 | E01/345/3520/E2 |  |  |  |  | 892 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3550 | 3550 |  | E1 | 3551E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3551E | 3551E (非取樣點) | LINE345 | E01/345/3550/E1 |  |  |  |  | 893 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3550 | 3550 |  | E2 | 3552E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3552E | 3552E (非取樣點) | LINE345 | E01/345/3550/E2 |  |  |  |  | 894 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3580 | 3580 |  | E1 | 3581E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3581E | 3581E (非取樣點) | LINE345 | E01/345/3580/E1 |  |  |  |  | 895 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3580 | 3580 |  | E2 | 3582E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3582E | 3582E (非取樣點) | LINE345 | E01/345/3580/E2 |  |  |  |  | 896 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3620 | 3620 |  | E1 | 3621E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3621E | 3621E (非取樣點) | LINE345 | E01/345/3620/E1 |  |  |  |  | 897 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3620 | 3620 |  | E2 | 3622E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3622E | 3622E (非取樣點) | LINE345 | E01/345/3620/E2 |  |  |  |  | 898 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3650 | 3650 |  | E1 | 3651E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3651E | 3651E (非取樣點) | LINE345 | E01/345/3650/E1 |  |  |  |  | 899 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3650 | 3650 |  | E2 | 3652E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3652E | 3652E (非取樣點) | LINE345 | E01/345/3650/E2 |  |  |  |  | 900 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3680 | 3680 |  | E1 | 3681E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3681E | 3681E (非取樣點) | LINE345 | E01/345/3680/E1 |  |  |  |  | 901 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3680 | 3680 |  | E2 | 3682E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3682E | 3682E (非取樣點) | LINE345 | E01/345/3680/E2 |  |  |  |  | 902 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | TE0 | 3530TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3530TE | 3530TE (非取樣點) | ATR | E01/345/3530/TE0 |  |  |  |  | 903 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | BE0 | 3530BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3530BE | 3530BE (非取樣點) | ATR | E01/345/3530/BE0 |  |  |  |  | 904 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3530 | #1ATR(3530) |  | E1 | 3531E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3531E | #1ATR 3531E ES(非取樣點) | ATR | E01/345/3530/E1 |  |  |  |  | 905 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | TE0 | 3560TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3560TE | 3560TE (非取樣點) | ATR | E01/345/3560/TE0 |  |  |  |  | 906 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3560 | #2ATR(3560) |  | BE0 | 3560BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3560BE | 3560BE (非取樣點) | ATR | E01/345/3560/BE0 |  |  |  |  | 907 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | TE0 | 3590TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3590TE | 3590TE (非取樣點) | ATR | E01/345/3590/TE0 |  |  |  |  | 908 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3590 | #3ATR(3590) |  | BE0 | 3590BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3590BE | 3590BE (非取樣點) | ATR | E01/345/3590/BE0 |  |  |  |  | 909 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | TE0 | 3630TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3630TE | 3630TE (非取樣點) | ATR | E01/345/3630/TE0 |  |  |  |  | 910 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3630 | #4ATR(3630) |  | BE0 | 3630BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3630BE | 3630BE (非取樣點) | ATR | E01/345/3630/BE0 |  |  |  |  | 911 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | TE0 | 3660TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3660TE | 3660TE (非取樣點) | ATR | E01/345/3660/TE0 |  |  |  |  | 912 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3660 | #5ATR(3660) |  | BE0 | 3660BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3660BE | 3660BE (非取樣點) | ATR | E01/345/3660/BE0 |  |  |  |  | 913 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | TE0 | 3690TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3690TE | 3690TE (非取樣點) | ATR | E01/345/3690/TE0 |  |  |  |  | 914 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | BE0 | 3690BE | [24 empty] | CDCS_S | [8 empty] | 南科ES.3690BE | 3690BE (非取樣點) | ATR | E01/345/3690/BE0 |  |  |  |  | 915 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 345 | 345kV | 3690 | #6ATR(3690) |  | E1 | 3691E | [24 empty] | CDCS_S | [8 empty] | 南科ES.3691E | #6ATR 3691E ES(非取樣點) | ATR | E01/345/3690/E1 |  |  |  |  | 916 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1810BE | 1810BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1810BE | 1810BE(非取樣點) | OTHER | E01/161/1810/BE0 |  |  |  |  | 917 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1810TE | 1810TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1810TE | 1810TE(非取樣點) | OTHER | E01/161/1810/TE0 |  |  |  |  | 918 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1820BE | 1820BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1820BE | 1820BE(非取樣點) | OTHER | E01/161/1820/BE0 |  |  |  |  | 919 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1820TE | 1820TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1820TE | 1820TE(非取樣點) | OTHER | E01/161/1820/TE0 |  |  |  |  | 920 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1830BE | 1830BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1830BE | 1830BE(非取樣點) | OTHER | E01/161/1830/BE0 |  |  |  |  | 921 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1830TE | 1830TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1830TE | 1830TE(非取樣點) | OTHER | E01/161/1830/TE0 |  |  |  |  | 922 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1850BE | 1850BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1850BE | 1850BE(非取樣點) | OTHER | E01/161/1850/BE0 |  |  |  |  | 923 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1850TE | 1850TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1850TE | 1850TE(非取樣點) | OTHER | E01/161/1850/TE0 |  |  |  |  | 924 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1860BE | 1860BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1860BE | 1860BE(非取樣點) | OTHER | E01/161/1860/BE0 |  |  |  |  | 925 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1860TE | 1860TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1860TE | 1860TE(非取樣點) | OTHER | E01/161/1860/TE0 |  |  |  |  | 926 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1870BE | 1870BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1870BE | 1870BE(非取樣點) | OTHER | E01/161/1870/BE0 |  |  |  |  | 927 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1870TE | 1870TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1870TE | 1870TE(非取樣點) | OTHER | E01/161/1870/TE0 |  |  |  |  | 928 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1880BE | 1880BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1880BE | 1880BE(非取樣點) | OTHER | E01/161/1880/BE0 |  |  |  |  | 929 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1880TE | 1880TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1880TE | 1880TE(非取樣點) | OTHER | E01/161/1880/TE0 |  |  |  |  | 930 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1910BE | 1910BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1910BE | 1910BE(非取樣點) | OTHER | E01/161/1910/BE0 |  |  |  |  | 931 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1910TE | 1910TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1910TE | 1910TE(非取樣點) | OTHER | E01/161/1910/TE0 |  |  |  |  | 932 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1920BE | 1920BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1920BE | 1920BE(非取樣點) | OTHER | E01/161/1920/BE0 |  |  |  |  | 933 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1920TE | 1920TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1920TE | 1920TE(非取樣點) | OTHER | E01/161/1920/TE0 |  |  |  |  | 934 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 520RE | 520RE | [24 empty] | CDCS_S | [8 empty] | 南科ES.520RE | 520RE(非取樣點) | OTHER | E01/33/520/RE0 |  |  |  |  | 935 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 520TE | 520TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.520TE | 520TE(非取樣點) | OTHER | E01/33/520/TE0 |  |  |  |  | 936 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 530RE | 530RE | [24 empty] | CDCS_S | [8 empty] | 南科ES.530RE | 530RE(非取樣點) | OTHER | E01/33/530/RE0 |  |  |  |  | 937 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 530TE | 530TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.530TE | 530TE(非取樣點) | OTHER | E01/33/530/TE0 |  |  |  |  | 938 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 550RE | 550RE | [24 empty] | CDCS_S | [8 empty] | 南科ES.550RE | 550RE(非取樣點) | OTHER | E01/33/550/RE0 |  |  |  |  | 939 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 550TE | 550TE | [24 empty] | CDCS_S | [8 empty] | 南科ES.550TE | 550TE(非取樣點) | OTHER | E01/33/550/TE0 |  |  |  |  | 940 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1540 | 1540 |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 941 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1540 | 1540 |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 942 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K221 | K221_DS |  | DS1 | K221_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_DS | K221_DS (非取樣點) | FEEDER | [5 empty] | 943 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K221 | K221_ES |  | LE0 | K221_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_ES | K221_ES (非取樣點) | FEEDER | [5 empty] | 944 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K222 | K222_DS |  | DS1 | K222_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_DS | K222_DS (非取樣點) | FEEDER | [5 empty] | 945 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K222 | K222_ES |  | LE0 | K222_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_ES | K222_ES (非取樣點) | FEEDER | [5 empty] | 946 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K223 | K223_DS |  | DS1 | K223_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_DS | K223_DS (非取樣點) | FEEDER | [5 empty] | 947 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K223 | K223_ES |  | LE0 | K223_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_ES | K223_ES (非取樣點) | FEEDER | [5 empty] | 948 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K224 | K224_DS |  | DS1 | K224_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_DS | K224_DS (非取樣點) | FEEDER | [5 empty] | 949 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K224 | K224_ES |  | LE0 | K224_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_ES | K224_ES (非取樣點) | FEEDER | [5 empty] | 950 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K225 | K225_DS |  | DS1 | K225_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_DS | K225_DS (非取樣點) | FEEDER | [5 empty] | 951 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K225 | K225_ES |  | LE0 | K225_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_ES | K225_ES (非取樣點) | FEEDER | [5 empty] | 952 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K27A | K27A_DS |  | DS1 | K27A_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_DS | K27A_DS (非取樣點) | FEEDER | [5 empty] | 953 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K27A | K27A_ES |  | LE0 | K27A_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_ES | K27A_ES (非取樣點) | FEEDER | [5 empty] | 954 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K27B | K27B_DS |  | DS1 | K27B_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_DS | K27B_DS (非取樣點) | FEEDER | [5 empty] | 955 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K27B | K27B_ES |  | LE0 | K27B_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_ES | K27B_ES (非取樣點) | FEEDER | [5 empty] | 956 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K27C | K27C_DS |  | DS1 | K27C_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_DS | K27C_DS (非取樣點) | FEEDER | [5 empty] | 957 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K27C | K27C_ES |  | LE0 | K27C_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_ES | K27C_ES (非取樣點) | FEEDER | [5 empty] | 958 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K27D | K27D_DS |  | DS1 | K27D_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_DS | K27D_DS (非取樣點) | FEEDER | [5 empty] | 959 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K27D | K27D_ES |  | LE0 | K27D_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_ES | K27D_ES (非取樣點) | FEEDER | [5 empty] | 960 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 281E | 281E |  | 281E | 281E | [24 empty] | ADCS_S | [8 empty] | 南科ES.281E | 281E (非取樣點) | SC | [5 empty] | 961 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 281 | 281 |  | 281 | 281 | [24 empty] | ADCS_S | [8 empty] | 南科ES.281 | 281 (非取樣點) | SC | [5 empty] | 962 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 271E | 271E |  | 271E | 271E | [24 empty] | ADCS_S | [8 empty] | 南科ES.271E | 271E (非取樣點) | SC | [5 empty] | 963 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 271 | 271 |  | 271 | 271 | [24 empty] | ADCS_S | [8 empty] | 南科ES.271 | 271 (非取樣點) | SC | [5 empty] | 964 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K251 | K251_DS |  | DS1 | K251_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_DS | K251_DS (非取樣點) | FEEDER | [5 empty] | 965 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K251 | K251_ES |  | LE0 | K251_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_ES | K251_ES (非取樣點) | FEEDER | [5 empty] | 966 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K252 | K252_DS |  | DS1 | K252_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_DS | K252_DS (非取樣點) | FEEDER | [5 empty] | 967 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K252 | K252_ES |  | LE0 | K252_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_ES | K252_ES (非取樣點) | FEEDER | [5 empty] | 968 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K253 | K253_DS |  | DS1 | K253_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_DS | K253_DS (非取樣點) | FEEDER | [5 empty] | 969 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K253 | K253_ES |  | LE0 | K253_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_ES | K253_ES (非取樣點) | FEEDER | [5 empty] | 970 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | K254 | K254_DS |  | DS1 | K254_DS | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_DS | K254_DS (非取樣點) | FEEDER | [5 empty] | 971 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | K254 | K254_ES |  | LE0 | K254_ES | [24 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_ES | K254_ES (非取樣點) | FEEDER | [5 empty] | 972 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 210 | 210SC_ES |  | SC0 | 210SC | [24 empty] | ADCS_S | [8 empty] | 南科ES.210SC_ES | 210SC_ES (非取樣點) | SC | [5 empty] | 973 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1840BE | 1840BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1840BE | 1840BE(非取樣點) | OTHER | E01/161/1840/BE0 |  |  |  |  | 974 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  |  |  |  | 1840TE | 1840TE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1840TE | 1840TE(非取樣點) | OTHER | E01/161/1840/TE0 |  |  |  |  | 975 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1580 | 1580 |  | LE0 | 1580LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 976 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1580 | 1580 |  | BE0 | 1580BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 977 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1530 | 1530 |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 978 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 161 | 161kV | 1530 | 1530 |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 979 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 1ABUS | 1ABUS |  | BE | 1ABUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1ABUS_BE | #1ABUS_BE(非取樣點) | FEEDER | [5 empty] | 980 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 1BBUS | 1BBUS |  | BE | 1BBUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.1BBUS_BE | #1BBUS_BE(非取樣點) | FEEDER | [5 empty] | 981 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 2ABUS | 2ABUS |  | BE | 2ABUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.2ABUS_BE | #2ABUS_BE(非取樣點) | FEEDER | [5 empty] | 982 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 2BBUS | 2BBUS |  | BE | 2BBUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.2BBUS_BE | #2BBUS_BE(非取樣點) | FEEDER | [5 empty] | 983 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 3ABUS | 3ABUS |  | BE | 3ABUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.3ABUS_BE | #3ABUS_BE(非取樣點) | FEEDER | [5 empty] | 984 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 3BBUS | 3BBUS |  | BE | 3BBUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.3BBUS_BE | #3BBUS_BE(非取樣點) | FEEDER | [5 empty] | 985 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 4ABUS | 4ABUS |  | BE | 4ABUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.4ABUS_BE | #4ABUS_BE(非取樣點) | FEEDER | [5 empty] | 986 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 4BBUS | 4BBUS |  | BE | 4BBUS_BE | [24 empty] | ADCS_S | [8 empty] | 南科ES.4BBUS_BE | #4BBUS_BE(非取樣點) | FEEDER | [5 empty] | 987 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E01 | 南科ES | 0 |  | 480 | 480 |  | CB | 480_CB | [24 empty] | ADCS_S | [8 empty] | 南科ES.480_CB | 480CB_#4SSTR(非取樣點) | FEEDER | [5 empty] | 988 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 470 | 470 |  | CB | 470_CB | [24 empty] | ADCS_S | [8 empty] | 南科ES.470_CB | 470CB_#3SSTR(非取樣點) | FEEDER | [5 empty] | 989 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  |  |  |  | ACB3 | 所內電源ACB3 | [24 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACB3 | 所內電源開關ACB3(非取樣點) | FEEDER | [5 empty] | 990 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  |  |  |  | ACB4 | 所內電源ACB4 | [24 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACB4 | 所內電源開關ACB4(非取樣點) | FEEDER | [5 empty] | 991 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E01 | 南科ES | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT2 | 所內電源ACBT2 | [24 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACBT2 | 所內電源開關ACB TIE2(非取樣點) | FEEDER | [5 empty] | 992 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo