## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E02 | 南科ES | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | Locate Empty |  | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/E02_A1 | [8 empty] | 南科ES.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | Locate Empty |  | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/E02_A1 | [8 empty] | 南科ES.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0027 |  |  | 1-9B |  |  | Locate Empty |  | 161KV #3BUS 電壓 | kV_-210_210(-2000_2000) | aba | B2/E02_A1 | [8 empty] | 南科ES.161KV#3BUS_KV | 161KV #3BUS KV | BUS |  |  |  |  | CDC | 4 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0028 |  |  | 1-9C |  |  | Locate Empty |  | 161KV #4BUS 電壓 | kV_-210_210(-2000_2000) | abb | B2/E02_A1 | [8 empty] | 南科ES.161KV#4BUS_KV | 161KV #4BUS KV | BUS |  |  |  |  | CDC | 5 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 22 | 22kV | 1ABUS | #1ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0074 |  |  | 1-CA |  |  | Locate Empty |  | 23KV #1APT 電壓 | kV_-18_18(-2000_2000) | aaa | B3/E02_A1 | [8 empty] | 南科ES.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS |  |  |  |  | CDC | 6 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 11 | 11kV | 1BBUS | #1BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0105 |  |  | 1-E9 |  |  | Locate Empty |  | 23KV #1BPT 電壓 | kV_-9_9(-2000_2000) | aba | B3/E02_A1 | [8 empty] | 南科ES.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS |  |  |  |  | CDC | 7 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
E02 | 南科ES | 22 | 22kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0143 |  |  | 2-8F |  |  | Locate Empty |  | 23KV #2APT 電壓 | kV_-18_18(-2000_2000) | baa | B3/E02_A1 | [8 empty] | 南科ES.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS |  |  |  |  | CDC | 8 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0169 |  |  | 2-A9 |  |  | Locate Empty |  | 23KV #2BPT 電壓 | kV_-18_18(-2000_2000) | bba | B3/E02_A1 | [8 empty] | 南科ES.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS |  |  |  |  | CDC | 9 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0200 |  |  | 2-C8 |  |  | Locate Empty |  | 23KV #3APT 電壓 | kV_-18_18(-2000_2000) | bca | B3/E02_A1 | [8 empty] | 南科ES.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS |  |  |  |  | CDC | 10 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0226 |  |  | 2-E2 |  |  | Locate Empty |  | 23KV #3BPT 電壓 | kV_-18_18(-2000_2000) | bda | B3/E02_A1 | [8 empty] | 南科ES.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS |  |  |  |  | CDC | 11 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 4ABUS | #4ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0263 |  |  | 3-87 |  |  | Locate Empty |  | 23KV #4APT 電壓 | kV_-18_18(-2000_2000) | aca | B3/E02_A1 | [8 empty] | 南科ES.23KV#4ABUS_KV | 23KV #4ABUS KV | BUS |  |  |  |  | CDC | 12 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 11 | 11kV | 4BBUS | #4BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0294 |  |  | 3-A6 |  |  | Locate Empty |  | 23KV #4BPT 電壓 | kV_-9_9(-2000_2000) | ada | B3/E02_A1 | [8 empty] | 南科ES.11KV#4BBUS_KV | 11KV #4BBUS KV | BUS |  |  |  |  | CDC | 13 | AI_23/11KV_BUS_PT |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
E02 | 南科ES | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aafz | B2/E02_A1 | [16 empty] | 14 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0615 |  |  | 1-36-07 |  |  | Locate Empty | UVA1 | 161KV #1BUS UVA1 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 15 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | Locate Empty | 87B1A | 161KB #1BUS 87B1A |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#1BUS_87A | 161KV #1BUS 87RY | BUS |  |  |  |  | CDC | 16 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aafz | B2/E02_A1 | [16 empty] | 17 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0616 |  |  | 1-36-08 |  |  | Locate Empty | UVA2 | 161KV #2BUS UVA2 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 18 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | Locate Empty | 87B2A | 161KB #2BUS 87B2A |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#2BUS_87A | 161KV #2BUS 87RY | BUS |  |  |  |  | CDC | 19 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161B3E | #3BUS(161B3E) |  | BE1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/3Bus | [13 empty] | abaz | B2/E02_A1 | [16 empty] | 20 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 3BUS | #3BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0617 |  |  | 1-36-09 |  |  | Locate Empty | UVA3 | 161KV #3BUS UVA3 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS |  |  |  |  | CDC | 21 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 3BUS | #3BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | Locate Empty | 87B3A | 161KB #3BUS 87B3A |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#3BUS_87A | 161KV #3BUS 87RY | BUS |  |  |  |  | CDC | 22 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161B4E | #4BUS(161B4E) |  | BE2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/4Bus | [13 empty] | abaz | B2/E02_A1 | [16 empty] | 23 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 4BUS | #4BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0618 |  |  | 1-36-10 |  |  | Locate Empty | UVA4 | 161KV #4BUS UVA4 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS |  |  |  |  | CDC | 24 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 4BUS | #4BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | Locate Empty | 87B4A | 161KB #4BUS 87B4A |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#4BUS_87A | 161KV #4BUS 87RY | BUS |  |  |  |  | CDC | 25 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1530 | 瓦 | 南科~三福一線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1530_MW | 南科三福一線 MW | LINE161 |  |  |  |  | CDC | 26 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1530 | 乏 | 南科~三福一線 1530 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1530_MVAR | 南科三福一線 MVAR | LINE161 |  |  |  |  | CDC | 27 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0346 |  |  | 3-DA |  |  | 1530 | PD | 南科~三福一線 1530 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1530LPD_KV | 南科三福一線(1530) LPD KV | LINE161 |  |  |  |  | CDC | 28 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1510 | 瓦 | 南科道爺一路 1510 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1510_MW | 南科道爺ㄧ路 MW | LINE161 |  |  |  |  | CDC | 29 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1510 | 乏 | 南科道爺一路 1510 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1510_MVAR | 南科道爺ㄧ路 MVAR | LINE161 |  |  |  |  | CDC | 30 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0324 |  |  | 3-C4 |  |  | 1510 | PD | 南科道爺一路 1510 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1510LPD_KV | 南科道爺ㄧ路(1510) LPD KV | LINE161 |  |  |  |  | CDC | 31 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1520 | 瓦 | 南科道爺二路 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1520_MW | 南科道爺二路 MW | LINE161 |  |  |  |  | CDC | 32 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1520 | 乏 | 南科道爺二路 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1520_MVAR | 南科道爺二路 MVAR | LINE161 |  |  |  |  | CDC | 33 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0325 |  |  | 3-C5 |  |  | 1520 | PD | 南科道爺二路 1520 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1520LPD_KV | 南科道爺二路(1520) LPD KV | LINE161 |  |  |  |  | CDC | 34 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1540 | 瓦 | 南科~積E六線 1540 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1540_MW | 南科積E六線 MW | LINE161 |  |  |  |  | CDC | 35 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1540 | 乏 | 南科~積E六線 1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1540_MVAR | 南科積E六線 MVAR | LINE161 |  |  |  |  | CDC | 36 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0347 |  |  | 3-DB |  |  | 1540 | PD | 南科~積E六線 1540 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1540LPD_KV | 南科積E六線(1540) LPD KV | LINE161 |  |  |  |  | CDC | 37 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1550 | 瓦 | 三福線 1550 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1550_MW | 三福科線 MW | LINE161 |  |  |  |  | CDC | 38 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1550 | 乏 | 三福線 1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1550_MVAR | 三福科線 MVAR | LINE161 |  |  |  |  | CDC | 39 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0345 |  |  | 3-D9 |  |  | 1550 | PD | 南科三福線 1550 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1550LPD_KV | 三福科線(1550) LPD KV | LINE161 |  |  |  |  | CDC | 40 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1570 | 瓦 | 南科道爺三路 1570 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1570_MW | 南科道爺三路 MW | LINE161 |  |  |  |  | CDC | 41 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1570 | 乏 | 南科道爺三路 1570 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1570_MVAR | 南科道爺三路 MVAR | LINE161 |  |  |  |  | CDC | 42 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0323 |  |  | 3-C3 |  |  | 1570 | PD | 南科道爺三路 1570 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1570LPD_KV | 南科道爺三路(1570) LPD KV | LINE161 |  |  |  |  | CDC | 43 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1580 | 瓦 | 南科道爺四路 1580 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1580_MW | 南科道爺四路 MW | LINE161 |  |  |  |  | CDC | 44 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1580 | 乏 | 南科道爺四路 1580 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1580_MVAR | 南科道爺四路 MVAR | LINE161 |  |  |  |  | CDC | 45 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0344 |  |  | 3-D8 |  |  | 1580 | PD | 南科道爺四路 1580 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1580LPD_KV | 南科道爺四路(1580) LPD KV | LINE161 |  |  |  |  | CDC | 46 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 1610 | 瓦 | 南科麻工一路 1610 瓦(備用) | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1610_MW | 麻工ㄧ路 MW | LINE161 |  |  |  |  | CDC | 47 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 1610 | 乏 | 南科麻工一路 1610 乏(備用) | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1610_MVAR | 麻工ㄧ路 MVAR | LINE161 |  |  |  |  | CDC | 48 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0326 |  |  | 3-C6 |  |  | 1610 | PD | 南科麻工一路 1610 PD(備用) | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1610LPD_KV | 麻工ㄧ路(1610) LPD KV | LINE161 |  |  |  |  | CDC | 49 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 1620 | 瓦 | 南科麻工二路 1620 瓦(備用) | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1620_MW | 麻工二路 MW | LINE161 |  |  |  |  | CDC | 50 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 1620 | 乏 | 南科麻工二路 1620 乏(備用) | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1620_MVAR | 麻工二路 MVAR | LINE161 |  |  |  |  | CDC | 51 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0327 |  |  | 3-C7 |  |  | 1620 | PD | 南科麻工二路 1620 PD(備用) | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1620LPD_KV | 麻工二路(1620) LPD KV | LINE161 |  |  |  |  | CDC | 52 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 1630 | 瓦 | 南科豐華紅線 1630 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1630_MW | 南科豐華紅線 MW | LINE161 |  |  |  |  | CDC | 53 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 1630 | 乏 | 南科豐華紅線 1630 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1630_MVAR | 南科豐華紅線 MVAR | LINE161 |  |  |  |  | CDC | 54 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0328 |  |  | 3-C8 |  |  | 1630 | PD | 南科豐華紅線 1630 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1630LPD_KV | 南科豐華紅線(1630) LPD KV | LINE161 |  |  |  |  | CDC | 55 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 1640 | 瓦 | 南科豐華白線(1640) 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1640_MW | 南科豐華白線 MW | LINE161 |  |  |  |  | CDC | 56 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 1640 | 乏 | 南科豐華白線(1640) 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1640_MVAR | 南科豐華白線 MVAR | LINE161 |  |  |  |  | CDC | 57 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0329 |  |  | 3-C9 |  |  | 1640 | PD | 三竹三路 1640 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1640LPD_KV | 南科豐華白線(1640) LPD KV | LINE161 |  |  |  |  | CDC | 58 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 1660 | 瓦 | 南科三竹二路 1660 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1660_MW | 三竹二路 MW | LINE161 |  |  |  |  | CDC | 59 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 1660 | 乏 | 南科三竹二路 1660 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1660_MVAR | 三竹二路 MVAR | LINE161 |  |  |  |  | CDC | 60 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0330 |  |  | 3-CA |  |  | 1660 | PD | 南科三竹二路 1660 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1660LPD_KV | 三竹二路(1660) LPD KV | LINE161 |  |  |  |  | CDC | 61 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 1650 | 瓦 | 南科三竹一路 1650 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1650_MW | 三竹ㄧ路 MW | LINE161 |  |  |  |  | CDC | 62 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 1650 | 乏 | 南科三竹一路 1650 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1650_MVAR | 三竹ㄧ路 MVAR | LINE161 |  |  |  |  | CDC | 63 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0331 |  |  | 3-CB |  |  | 1650 | PD | 南科三竹一路 1650 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1650LPD_KV | 三竹ㄧ路(1650) LPD KV | LINE161 |  |  |  |  | CDC | 64 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 1670 | 瓦 | 積六線 1670 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1670_MW | 積六線 MW | LINE161 |  |  |  |  | CDC | 65 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 1670 | 乏 | 積六線 1670 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1670_MVAR | 積六線 MVAR | LINE161 |  |  |  |  | CDC | 66 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0332 |  |  | 3-CC |  |  | 1670 | PD | 積六線 1670 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1670LPD_KV | 積六線(1670) LPD KV | LINE161 |  |  |  |  | CDC | 67 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 1680 | 瓦 | 康寧線 1680 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1680_MW | 康寧線 MW | LINE161 |  |  |  |  | CDC | 68 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 1680 | 乏 | 康寧線 1680 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1680_MVAR | 康寧線 MVAR | LINE161 |  |  |  |  | CDC | 69 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0337 |  |  | 3-D1 |  |  | 1680 | PD | 康寧線 1680 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1680LPD_KV | 康寧線(1680) LPD KV | LINE161 |  |  |  |  | CDC | 70 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 1710 | 瓦 | 南科~和鑫二線 1710 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1710_MW | 南科和鑫二線 MW | LINE161 |  |  |  |  | CDC | 71 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 1710 | 乏 | 南科~和鑫二線 1710 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1710_MVAR | 南科和鑫二線 MVAR | LINE161 |  |  |  |  | CDC | 72 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0333 |  |  | 3-CD |  |  | 1710 | PD | 南科~和鑫二線 1710 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1710LPD_KV | 南科和鑫二線(1710) LPD KV | LINE161 |  |  |  |  | CDC | 73 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 1720 | 瓦 | 南科積P3白線 1720 瓦 | MW_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1720_MW | 南科積P3線 MW | LINE161 |  |  |  |  | CDC | 74 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 1720 | 乏 | 南科積P3白線 1720 乏 | MVAR_-560_560(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1720_MVAR | 南科積P3線 MVAR | LINE161 |  |  |  |  | CDC | 75 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0343 |  |  | 3-D7 |  |  | 1720 | PD | 南科積P3白線 1720 PD | kV_-210_210(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.1720LPD_KV | 南科積P3線(1720) LPD KV | LINE161 |  |  |  |  | CDC | 76 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1530 | PHA | 南科~三福一線 1530 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_PHA | 南科三福一線(1530) 相間RY | LINE161 |  |  |  |  | CDC | 77 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1530 | GDA | 南科~三福一線 1530 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_GDA | 南科三福一線(1530) 接地RY | LINE161 |  |  |  |  | CDC | 78 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 1510 | PHA | 南科道爺一路 1510 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_PHA | 南科道爺ㄧ路(1510) 相間RY | LINE161 |  |  |  |  | CDC | 79 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1510 | GDA | 南科道爺一路 1510 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_GDA | 南科道爺ㄧ路(1510) 接地RY | LINE161 |  |  |  |  | CDC | 80 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1510 | 87A | 南科道爺一路 1510 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_87A | 南科道爺ㄧ路(1510) 87RY | LINE161 |  |  |  |  | CDC | 81 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1520 | PHA | 南科道爺二路 1520 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_PHA | 南科道爺二路(1520) 相間RY | LINE161 |  |  |  |  | CDC | 82 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | 1520 | GDA | 南科道爺二路 1520 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_GDA | 南科道爺二路(1520) 接地RY | LINE161 |  |  |  |  | CDC | 83 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1520 | 87A | 南科道爺二路 1520 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_87A | 南科道爺二路(1520) 87RY | LINE161 |  |  |  |  | CDC | 84 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1540 | PHA | 南科~積E六線 1540 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_PHA | 南科積E六線(1540) 相間RY | LINE161 |  |  |  |  | CDC | 85 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1540 | GDA | 南科~積E六線 1540 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_GDA | 南科積E六線(1540) 接地RY | LINE161 |  |  |  |  | CDC | 86 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 1550 | PHA | 三福線 1550 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1550_PHA | 三福科線(1550) 相間RY | LINE161 |  |  |  |  | CDC | 87 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1550 | GDA | 三福線 1550 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1550_GDA | 三福科線(1550) 接地RY | LINE161 |  |  |  |  | CDC | 88 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1550 | 85A | 三福線 1550 85A(無設備) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1550_85A | 三福科線(1550) 85RY | LINE161 |  |  |  |  | CDC | 89 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1570 | PHA | 南科道爺三路 1570 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_PHA | 南科道爺三路(1570) 相間RY | LINE161 |  |  |  |  | CDC | 90 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 1570 | GDA | 南科道爺三路 1570 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_GDA | 南科道爺三路(1570) 接地RY | LINE161 |  |  |  |  | CDC | 91 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 1570 | 87A | 南科道爺三路 1570 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_87A | 南科道爺三路(1570) 87RY | LINE161 |  |  |  |  | CDC | 92 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | 1580 | PHA | 南科道爺四路 1580 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_PHA | 南科道爺四路(1580) 相間RY | LINE161 |  |  |  |  | CDC | 93 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 1580 | GDA | 南科道爺四路 1580 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_GDA | 南科道爺四路(1580) 接地RY | LINE161 |  |  |  |  | CDC | 94 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1580 | 87A | 南科道爺四路 1580 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_87A | 南科道爺四路(1580) 87RY | LINE161 |  |  |  |  | CDC | 95 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 1610 | PHA | 南科麻工一路 1610 PHA(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_PHA | 麻工ㄧ路(1610) 相間RY | LINE161 |  |  |  |  | CDC | 96 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 1610 | GDA | 南科麻工一路 1610 GDA(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_GDA | 麻工ㄧ路(1610) 接地RY | LINE161 |  |  |  |  | CDC | 97 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 1610 | 85A | 南科麻工一路 1610 85A(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_85A | 麻工ㄧ路(1610) 85RY | LINE161 |  |  |  |  | CDC | 98 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 1620 | PHA | 南科麻工二路 1620 PHA(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_PHA | 麻工二路(1620) 相間RY | LINE161 |  |  |  |  | CDC | 99 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 1620 | GDA | 南科麻工二路 1620 GDA(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_GDA | 麻工二路(1620) 接地RY | LINE161 |  |  |  |  | CDC | 100 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1620 | 85A | 南科麻工二路 1620 85A(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_85A | 麻工二路(1620) 85RY | LINE161 |  |  |  |  | CDC | 101 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 1630 | PHA | 南科豐華紅線 1630 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_PHA | 南科豐華紅線(1630) 相間RY | LINE161 |  |  |  |  | CDC | 102 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 1630 | GDA | 南科豐華紅線 1630 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_GDA | 南科豐華紅線(1630) 接地RY | LINE161 |  |  |  |  | CDC | 103 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 1630 | 87A | 南科豐華紅線 1630 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_87A | 南科豐華紅線(1630) 87RY | LINE161 |  |  |  |  | CDC | 104 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 1640 | PHA | 南科豐華白線(1640) PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_PHA | 南科豐華白線(1640) 相間RY | LINE161 |  |  |  |  | CDC | 105 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 1640 | GDA | 南科豐華白線(1640) GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_GDA | 南科豐華白線(1640) 接地RY | LINE161 |  |  |  |  | CDC | 106 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 3-00-02 |  |  | 1660 | PHA | 南科三竹二路 1660 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_PHA | 三竹二路(1660) 相間RY | LINE161 |  |  |  |  | CDC | 107 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 3-00-03 |  |  | 1660 | GDA | 南科三竹二路 1660 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_GDA | 三竹二路(1660) 接地RY | LINE161 |  |  |  |  | CDC | 108 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 3-00-06 |  |  | 1650 | PHA | 南科三竹一路 1650 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_PHA | 三竹ㄧ路(1650) 相間RY | LINE161 |  |  |  |  | CDC | 109 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 3-00-07 |  |  | 1650 | GDA | 南科三竹一路 1650 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_GDA | 三竹ㄧ路(1650) 接地RY | LINE161 |  |  |  |  | CDC | 110 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 |  |  | 3-01-02 |  |  | 1670 | PHA | 積六線 1670 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_PHA | 積六線(1670) 相間RY | LINE161 |  |  |  |  | CDC | 111 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 3-01-03 |  |  | 1670 | GDA | 積六線 1670 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_GDA | 積六線(1670) 接地RY | LINE161 |  |  |  |  | CDC | 112 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 3-01-01 |  |  | 1670 | 85A | 積六線 1670 85A(無設備) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_85A | 積六線(1670) 85RY | LINE161 |  |  |  |  | CDC | 113 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0144 |  |  | 3-02-00 |  |  | 1680 | PHA | 康寧線 1680 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1680_PHA | 康寧線(1680) 相間RY | LINE161 |  |  |  |  | CDC | 114 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 3-02-01 |  |  | 1680 | GDA | 康寧線 1680 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1680_GDA | 康寧線(1680) 接地RY | LINE161 |  |  |  |  | CDC | 115 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 3-02-06 |  |  | 1710 | PHA | 南科~和鑫二線 1710 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_PHA | 南科和鑫二線(1710) 相間RY | LINE161 |  |  |  |  | CDC | 116 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 3-02-07 |  |  | 1710 | GDA | 南科~和鑫二線 1710 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_GDA | 南科和鑫二線(1710) 接地RY | LINE161 |  |  |  |  | CDC | 117 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 3-02-05 |  |  | 1710 | 85A | 南科~和鑫二線 1710 85A(無設備) |  |  | B2/E02_A1 | [15 empty] | CDC | 118 | DI_LINE161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 3-03-04 |  |  | 1720 | PHA | 南科積P3白線 1720 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_PHA | 南科積P3線(1720) 相間RY | LINE161 |  |  |  |  | CDC | 119 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 3-03-05 |  |  | 1720 | GDA | 南科積P3白線 1720 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_GDA | 南科積P3線(1720) 接地RY | LINE161 |  |  |  |  | CDC | 120 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  | 0106 | 1-30-06 |  | 1-6A | 1510 | 87RY /UL | 南科道爺一路 1510 87RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_87UL | 南科道爺ㄧ路(1510) 87RY U/L | LINE161 |  |  |  |  | CDC | 121 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  | 0108 | 1-30-10 |  | 1-6C | 1520 | 87RY /UL | 南科道爺二路 1520 87RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_87UL | 南科道爺二路(1520) 87RY U/L | LINE161 |  |  |  |  | CDC | 122 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0112 | 1-31-06 |  | 1-70 | 1570 | 87RY /UL | 南科道爺三路 1570 87RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_87UL | 南科道爺三路(1570) 87RY U/L | LINE161 |  |  |  |  | CDC | 123 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0114 | 1-31-10 |  | 1-72 | 1580 | 87RY /UL | 南科道爺四路 1580 87RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_87UL | 南科道爺四路(1580) 87RY U/L | LINE161 |  |  |  |  | CDC | 124 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0546 |  | 0120 | 1-32-02 |  | 1-78 | 1610 | 85RY /UL | 南科麻工一路 1610 85RY /UL(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_85UL | 麻工ㄧ路(1610) 85RY U/L | LINE161 |  |  |  |  | CDC | 125 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0550 |  | 0122 | 1-32-06 |  | 1-7A | 1620 | 85RY /UL | 南科麻工二路 1620 85RY /UL(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_85UL | 麻工二路(1620) 85RY U/L | LINE161 |  |  |  |  | CDC | 126 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  | 0124 | 1-32-10 |  | 1-7C | 1630 | 87RY /UL | 南科豐華紅線 1630 87RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_87UL | 南科豐華紅線(1630) 87RY U/L | LINE161 |  |  |  |  | CDC | 127 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0456 |  | 0244 | 3-38-08 |  | 2-74 | 1670 | 85RY U/L | 積六線 1670 85RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_87UL1 | 南科積六線(1670) 87RY1 U/L | OTHER |  |  |  |  | CDC | 128 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0140 |  |  | 3-01-04 |  |  | 1670 | RY | 積六線 1670 87L1A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_87A1 | 南科積六線(1670) 87A1 | OTHER |  |  |  |  | CDC | 129 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | 87A2 | 第2具87RY | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0141 |  |  | 3-01-05 |  |  | 1670 | RY | 積六線 1670 87L2A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_87A2 | 南科積六線(1670) 87A2 | OTHER |  |  |  |  | CDC | 130 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 3-02-02 |  |  | 1680 | RY | 康寧線 1680 87L1A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1680_87L1TA | 康寧線(1680) 87L1TA RY | LINE161 |  |  |  |  | CDC | 131 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | 87A2 | 第2具87RY | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0147 |  |  | 3-02-03 |  |  | 1680 | RY | 康寧線 1680 87L2A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1680_87L2TA | 康寧線(1680) 87L2TA | LINE161 |  |  |  |  | CDC | 132 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0464 |  | 0248 | 3-39-00 |  | 2-78 | 1710 | 87RY1 U/L | 南科~和鑫二線 1710 87RY1 U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_87UL1 | 南科和鑫二線(1710) #1_87RY U/L | LINE161 |  |  |  |  | CDC | 133 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 3-03-00 |  |  | 1710 | RY | 南科~和鑫二線 1710 87L1A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_87L1TA | 南科和鑫二線(1710) 87L1TA RY | LINE161 |  |  |  |  | CDC | 134 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | 87A2 | 第2具87RY | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0153 |  |  | 3-03-01 |  |  | 1710 | RY | 南科~和鑫二線 1710 87L2A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_87L2TA | 南科和鑫二線(1710) 87L2TA | LINE161 |  |  |  |  | CDC | 135 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0468 |  | 0250 | 3-39-04 |  | 2-7A | 1720 | 87RY1 U/L | 南科積P3白線 1720 87RY1 U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_87UL1 | 南科積P3線(1720) #1_87RY U/L | LINE161 |  |  |  |  | CDC | 136 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0158 |  |  | 3-03-06 |  |  | 1720 | RY | 南科積P3白線 1720 87L1A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_87L1TA | 南科積P3線(1720) 87L1TA RY | LINE161 |  |  |  |  | CDC | 137 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | 87A2 | 第2具87RY | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0159 |  |  | 3-03-07 |  |  | 1720 | RY | 南科積P3白線 1720 87L2A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_87L2TA | 南科積P3線(1720) 87L2TA | LINE161 |  |  |  |  | CDC | 138 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01C06/T1 |  | 0004 |  | 0001 | 1-00-04 |  | 1-01 | 1530 | ON/OFF | 南科~三福一線 1530 CB |  | abbb | B2/E02_A1 | [8 empty] | 南科ES.1530_CB | 1530(南科三福一線) CB | LINE161 |  |  |  |  | CDC | 139 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0233 | 1-30-03 |  | 2-69 | 1530 | 79UL | 南科~三福一線 1530 79RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_79UL | 南科三福一線(1530) 79RY U/L | LINE161 |  |  |  |  | CDC | 140 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E01D051/T1 |  | 0008 |  | 0002 | 1-01-00 |  | 1-02 | 1510 | ON/OFF | 南科道爺一路 1510 CB |  | aaab | B2/E02_A1 | [8 empty] | 南科ES.1510_CB | 1510(南科道爺ㄧ路) CB | LINE161 |  |  |  |  | CDC | 141 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  | 0107 | 1-30-07 |  | 1-6B | 1510 | 79RY /UL | 南科道爺一路 1510 79RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_79UL | 南科道爺ㄧ路(1510) 79RY U/L | LINE161 |  |  |  |  | CDC | 142 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E01D052/T1 |  | 0012 |  | 0003 | 1-01-04 |  | 1-03 | 1520 | ON/OFF | 南科道爺二路 1520 CB |  | aabb | B2/E02_A1 | [8 empty] | 南科ES.1520_CB | 1520(南科道爺二路) CB | LINE161 |  |  |  |  | CDC | 143 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  | 0109 | 1-30-11 |  | 1-6D | 1520 | 79RY /UL | 南科道爺二路 1520 79RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_79UL | 南科道爺二路(1520) 79RY U/L | LINE161 |  |  |  |  | CDC | 144 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01C09/T1 |  | 0016 |  | 0004 | 1-02-00 |  | 1-04 | 1540 | ON/OFF | 南科~積E六線 1540 CB |  | abob | B2/E02_A1 | [8 empty] | 南科ES.1540_CB | 1540(南科積E六線) CB | LINE161 |  |  |  |  | CDC | 145 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0527 |  | 0236 | 1-30-15 |  | 2-6C | 1540 | 79UL | 南科~積E六線 1540 79RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_79UL | 南科積E六線(1540) 79RY U/L | LINE161 |  |  |  |  | CDC | 146 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E01C22/T1 |  | 0020 |  | 0006 | 1-02-04 |  | 1-06 | 1550 | ON/OFF | 三福線 1550 CB |  | aahb | B2/E02_A1 | [8 empty] | 南科ES.1550_CB | 1550(三福科線) CB | LINE161 |  |  |  |  | CDC | 147 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E01D053/T1 |  | 0024 |  | 0007 | 1-03-00 |  | 1-07 | 1570 | ON/OFF | 南科道爺三路 1570 CB |  | aaib | B2/E02_A1 | [8 empty] | 南科ES.1570_CB | 1570(南科道爺三路) CB | LINE161 |  |  |  |  | CDC | 148 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  | 0113 | 1-31-07 |  | 1-71 | 1570 | 79RY /UL | 南科道爺三路 1570 79RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_79UL | 南科道爺三路(1570) 79RY U/L | LINE161 |  |  |  |  | CDC | 149 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E01D054/T1 |  | 0028 |  | 0008 | 1-03-04 |  | 1-08 | 1580 | ON/OFF | 南科道爺四路 1580 CB |  | aakb | B2/E02_A1 | [8 empty] | 南科ES.1580_CB | 1580(南科道爺四路) CB | LINE161 |  |  |  |  | CDC | 150 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0115 | 1-31-11 |  | 1-73 | 1580 | 79RY /UL | 南科道爺四路 1580 79RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_79UL | 南科道爺四路(1580) 79RY U/L | LINE161 |  |  |  |  | CDC | 151 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/麻工ㄧ路/T1 |  | 0036 |  | 0010 | 1-04-04 |  | 1-0A | 1610 | ON/OFF | 南科麻工一路 1610 CB(備用) |  | aanb | B2/E02_A1 | [8 empty] | 南科ES.1610_CB | 1610(麻工ㄧ路) CB | LINE161 |  |  |  |  | CDC | 152 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0547 |  | 0121 | 1-32-03 |  | 1-79 | 1610 | 79RY /UL | 南科麻工一路 1610 79RY /UL(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_79UL | 麻工ㄧ路(1610) 79RY U/L | LINE161 |  |  |  |  | CDC | 153 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/麻工二路/T1 |  | 0040 |  | 0011 | 1-05-00 |  | 1-0B | 1620 | ON/OFF | 南科麻工二路 1620 CB(備用) |  | aaob | B2/E02_A1 | [8 empty] | 南科ES.1620_CB | 1620(麻工二路) CB | LINE161 |  |  |  |  | CDC | 154 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0551 |  | 0123 | 1-32-07 |  | 1-7B | 1620 | 79RY /UL | 南科麻工二路 1620 79RY /UL(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_79UL | 麻工二路(1620) 79RY U/L | LINE161 |  |  |  |  | CDC | 155 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01D04R/T1 |  | 0050 |  | 0014 | 1-06-02 |  | 1-0E | 1630 | ON/OFF | 南科豐華紅線 1630 CB |  | abfb | B2/E02_A1 | [8 empty] | 南科ES.1630_CB | 1630(南科豐華紅線) CB | LINE161 |  |  |  |  | CDC | 156 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0555 |  | 0125 | 1-32-11 |  | 1-7D | 1630 | 79RY /UL | 南科豐華紅線 1630 79RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_79UL | 南科豐華紅線(1630) 79RY U/L | LINE161 |  |  |  |  | CDC | 157 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01D04W/T1 |  | 0054 |  | 0015 | 1-06-06 |  | 1-0F | 1640 | ON/OFF | 南科豐華白線(1640) CB |  | abgb | B2/E02_A1 | [8 empty] | 南科ES.1640_CB | 1640(南科豐華白線) CB | LINE161 |  |  |  |  | CDC | 158 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0559 |  | 0127 | 1-32-15 |  | 1-7F | 1640 | 79RY /UL | 南科豐華白線(1640) 79RY /UL |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_79UL | 南科豐華白線(1640) 79RY U/L | LINE161 |  |  |  |  | CDC | 159 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01D022/T1 |  | 0128 |  | 0256 | 3-00-00 |  | 3-00 | 1660 | ON/OFF | 南科三竹二路 1660 CB |  | abkb | B2/E02_A1 | [8 empty] | 南科ES.1660_CB | 1660(三竹二路) CB | LINE161 |  |  |  |  | CDC | 160 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0449 |  | 0241 | 3-38-01 |  | 2-71 | 1660 | 79RY U/L | 南科三竹二路 1660 79RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_79UL | 三竹二路(1660) 79RY U/L | LINE161 |  |  |  |  | CDC | 161 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01D021/T1 |  | 0132 |  | 0257 | 3-00-04 |  | 3-01 | 1650 | ON/OFF | 南科三竹一路 1650 CB |  | ablb | B2/E02_A1 | [8 empty] | 南科ES.1650_CB | 1650(三竹ㄧ路) CB | LINE161 |  |  |  |  | CDC | 162 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0453 |  | 0243 | 3-38-05 |  | 2-73 | 1650 | 79RY U/L | 南科三竹一路 1650 79RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_79UL | 三竹ㄧ路(1650) 79RY U/L | LINE161 |  |  |  |  | CDC | 163 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01C05/T1 |  | 0136 |  | 0258 | 3-01-00 |  | 3-02 | 1670 | ON/OFF | 積六線 1670 CB |  | abmb | B2/E02_A1 | [8 empty] | 南科ES.1670_CB | 1670(積六線) CB | LINE161 |  |  |  |  | CDC | 164 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0457 |  | 0245 | 3-38-09 |  | 2-75 | 1670 | 79RY U/L | 積六線 1670 79RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_79UL | 積六線(1670) 79RY U/L | LINE161 |  |  |  |  | CDC | 165 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01C02/T1 |  | 0142 |  | 0259 | 3-01-06 |  | 3-03 | 1680 | ON/OFF | 康寧線 1680 CB |  | abnb | B2/E02_A1 | [8 empty] | 南科ES.1680_CB | 1680(康寧線) CB | LINE161 |  |  |  |  | CDC | 166 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01C01/T1 |  | 0148 |  | 0260 | 3-02-04 |  | 3-04 | 1710 | ON/OFF | 南科~和鑫二線 1710 CB |  | abrb | B2/E02_A1 | [8 empty] | 南科ES.1710_CB | 1710(南科和鑫二線) CB | LINE161 |  |  |  |  | CDC | 167 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0465 |  | 0249 | 3-39-01 |  | 2-79 | 1710 | 87RY2 U/L | 南科~和鑫二線 1710 87RY2 U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_87UL2 | 南科和鑫二線(1710) #2_87RY U/L | LINE161 |  |  |  |  | CDC | 168 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E01C03/T1 |  | 0154 |  | 0261 | 3-03-02 |  | 3-05 | 1720 | ON/OFF | 南科積P3白線 1720 CB |  | absb | B2/E02_A1 | [8 empty] | 南科ES.1720_CB | 1720(南科積P3線) CB | LINE161 |  |  |  |  | CDC | 169 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0469 |  | 0251 | 3-39-05 |  | 2-7B | 1720 | 87RY2 U/L | 南科積P3白線 1720 87RY2 U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_87UL2 | 南科積P3線(1720)#2_87RY U/L | LINE161 |  |  |  |  | CDC | 170 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DS1 | 1531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 641 | 0040 | 1-38-00 | 1-38-01 | 1-28 | 1531 |  | 南科~三福一線 1531 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1531_DS | 1531(南科三福一線) DS | LINE161 |  |  |  |  | CDC | 171 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DS2 | 1532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 643 | 0041 | 1-38-02 | 1-38-03 | 1-29 | 1532 |  | 南科~三福一線 1532 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1532_DS | 1532(南科三福一線) DS | LINE161 |  |  |  |  | CDC | 172 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DS1 | 1511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 | 0044 | 1-38-08 | 1-38-09 | 1-2C | 1511 |  | 南科道爺一路 1511 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1511_DS | 1511(南科道爺ㄧ路) DS | LINE161 |  |  |  |  | CDC | 173 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DS2 | 1512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 651 | 0045 | 1-38-10 | 1-38-11 | 1-2D | 1512 |  | 南科道爺一路 1512 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1512_DS | 1512(南科道爺ㄧ路) DS | LINE161 |  |  |  |  | CDC | 174 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DS1 | 1521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 657 | 0048 | 1-39-00 | 1-39-01 | 1-30 | 1521 |  | 南科道爺二路 1521 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1521_DS | 1521(南科道爺二路) DS | LINE161 |  |  |  |  | CDC | 175 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DS2 | 1522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0658 | 659 | 0049 | 1-39-02 | 1-39-03 | 1-31 | 1522 |  | 南科道爺二路 1522 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1522_DS | 1522(南科道爺二路) DS | LINE161 |  |  |  |  | CDC | 176 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DS1 | 1541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0664 | 665 | 0052 | 1-39-08 | 1-39-09 | 1-34 | 1541 |  | 南科~積E六線 1541 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1541_DS | 1541(南科積E六線) DS | LINE161 |  |  |  |  | CDC | 177 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DS2 | 1542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0666 | 667 | 0053 | 1-39-10 | 1-39-11 | 1-35 | 1542 |  | 南科~積E六線 1542 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1542_DS | 1542(南科積E六線) DS | LINE161 |  |  |  |  | CDC | 178 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | DS1 | 1551 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 677 | 0058 | 1-3A-04 | 1-3A-05 | 1-3A | 1551 |  | 三福線 1551 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1551_DS | 1551(三福科線) DS | LINE161 |  |  |  |  | CDC | 179 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | DS2 | 1552 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 679 | 0059 | 1-3A-06 | 1-3A-07 | 1-3B | 1552 |  | 三福線 1552 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1552_DS | 1552(三福科線) DS | LINE161 |  |  |  |  | CDC | 180 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | DS1 | 1571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 685 | 0062 | 1-3A-12 | 1-3A-13 | 1-3E | 1571 |  | 南科道爺三路 1571 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1571_DS | 1571(南科道爺三路) DS | LINE161 |  |  |  |  | CDC | 181 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | DS2 | 1572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0686 | 687 | 0063 | 1-3A-14 | 1-3A-15 | 1-3F | 1572 |  | 南科道爺三路 1572 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1572_DS | 1572(南科道爺三路) DS | LINE161 |  |  |  |  | CDC | 182 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | DS1 | 1581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 693 | 0066 | 1-3B-04 | 1-3B-05 | 1-42 | 1581 |  | 南科道爺四路 1581 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1581_DS | 1581(南科道爺四路) DS | LINE161 |  |  |  |  | CDC | 183 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | DS2 | 1582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0694 | 695 | 0067 | 1-3B-06 | 1-3B-07 | 1-43 | 1582 |  | 南科道爺四路 1582 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1582_DS | 1582(南科道爺四路) DS | LINE161 |  |  |  |  | CDC | 184 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | DS1 | 1611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0708 | 709 | 0074 | 1-3C-04 | 1-3C-05 | 1-4A | 1611 |  | 南科麻工一路 1611 DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1611_DS | 1611(麻工ㄧ路) DS | LINE161 |  |  |  |  | CDC | 185 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | DS2 | 1612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0710 | 711 | 0075 | 1-3C-06 | 1-3C-07 | 1-4B | 1612 |  | 南科麻工一路 1612 DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1612_DS | 1612(麻工ㄧ路) DS | LINE161 |  |  |  |  | CDC | 186 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | DS1 | 1621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0716 | 717 | 0078 | 1-3C-12 | 1-3C-13 | 1-4E | 1621 |  | 南科麻工二路 1621 DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1621_DS | 1621(麻工二路) DS | LINE161 |  |  |  |  | CDC | 187 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | DS2 | 1622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0718 | 719 | 0079 | 1-3C-14 | 1-3C-15 | 1-4F | 1622 |  | 南科麻工二路 1622 DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1622_DS | 1622(麻工二路) DS | LINE161 |  |  |  |  | CDC | 188 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | DS1 | 1631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0732 | 733 | 0086 | 1-3D-12 | 1-3D-13 | 1-56 | 1631 |  | 南科豐華紅線 1631 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1631_DS | 1631(南科豐華紅線) DS | LINE161 |  |  |  |  | CDC | 189 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | DS2 | 1632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0734 | 735 | 0087 | 1-3D-14 | 1-3D-15 | 1-57 | 1632 |  | 南科豐華紅線 1632 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1632_DS | 1632(南科豐華紅線) DS | LINE161 |  |  |  |  | CDC | 190 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | DS1 | 1641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0740 | 741 | 0090 | 1-3E-04 | 1-3E-05 | 1-5A | 1641 |  | 南科豐華白線(1641) DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1641_DS | 1641(南科豐華白線) DS | LINE161 |  |  |  |  | CDC | 191 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | DS2 | 1642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0742 | 743 | 0091 | 1-3E-06 | 1-3E-07 | 1-5B | 1642 |  | 南科豐華白線(1642) DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1642_DS | 1642(南科豐華白線) DS | LINE161 |  |  |  |  | CDC | 192 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | DS1 | 1661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0768 | 769 | 0264 | 3-30-00 | 3-30-01 | 3-08 | 1661 |  | 南科三竹二路 1661 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1661_DS | 1661(三竹二路) DS | LINE161 |  |  |  |  | CDC | 193 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | DS2 | 1662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0770 | 771 | 0265 | 3-30-02 | 3-30-03 | 3-09 | 1662 |  | 南科三竹二路 1662 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1662_DS | 1662(三竹二路) DS | LINE161 |  |  |  |  | CDC | 194 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | DS1 | 1651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0776 | 777 | 0268 | 3-30-08 | 3-30-09 | 3-0C | 1651 |  | 南科三竹一路 1651 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1651_DS | 1651(三竹ㄧ路) DS | LINE161 |  |  |  |  | CDC | 195 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | DS2 | 1652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0778 | 779 | 0269 | 3-30-10 | 3-30-11 | 3-0D | 1652 |  | 南科三竹一路 1652 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1652_DS | 1652(三竹ㄧ路) DS | LINE161 |  |  |  |  | CDC | 196 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | DS1 | 1671 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 | 0272 | 3-31-00 | 3-31-01 | 3-10 | 1671 |  | 積六線 1671 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1671_DS | 1671(積六線) DS | LINE161 |  |  |  |  | CDC | 197 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | DS2 | 1672 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0786 | 787 | 0273 | 3-31-02 | 3-31-03 | 3-11 | 1672 |  | 積六線 1672 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1672_DS | 1672(積六線) DS | LINE161 |  |  |  |  | CDC | 198 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | DS1 | 1681 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0792 | 793 | 0276 | 3-31-08 | 3-31-09 | 3-14 | 1681 |  | 康寧線 1681 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1681_DS | 1681(康寧線) DS | LINE161 |  |  |  |  | CDC | 199 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | DS2 | 1682 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0794 | 795 | 0277 | 3-31-10 | 3-31-11 | 3-15 | 1682 |  | 康寧線 1682 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1682_DS | 1682(康寧線) DS | LINE161 |  |  |  |  | CDC | 200 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | DS1 | 1711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0800 | 801 | 0280 | 3-32-00 | 3-32-01 | 3-18 | 1711 |  | 南科~和鑫二線 1711 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1711_DS | 1711(南科和鑫二線) DS | LINE161 |  |  |  |  | CDC | 201 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | DS2 | 1712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0802 | 803 | 0281 | 3-32-02 | 3-32-03 | 3-19 | 1712 |  | 南科~和鑫二線 1712 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1712_DS | 1712(南科和鑫二線) DS | LINE161 |  |  |  |  | CDC | 202 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | DS1 | 1721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0808 | 809 | 0284 | 3-32-08 | 3-32-09 | 3-1C | 1721 |  | 南科積P3白線 1721 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1721_DS | 1721(南科積P3線) DS | LINE161 |  |  |  |  | CDC | 203 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | DS2 | 1722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0810 | 811 | 0285 | 3-32-10 | 3-32-11 | 3-1D | 1722 |  | 南科積P3白線 1722 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1722_DS | 1722(南科積P3線) DS | LINE161 |  |  |  |  | CDC | 204 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DS3 | 1533 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 | 0042 | 1-38-04 | 1-38-05 | 1-2A | 1533 |  | 南科~三福一線 1533 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1533_DS | 1533(南科三福一線) DS | LINE161 |  |  |  |  | CDC | 205 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | E3 | 1533E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0646 | 647 | 0043 | 1-38-06 | 1-38-07 | 1-2B | 1533E |  | 南科~三福一線 1533E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1533E_ES | 1533E(南科三福一線) ES | LINE161 |  |  |  |  | CDC | 206 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 207 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 208 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | DS3 | 1513 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 653 | 0046 | 1-38-12 | 1-38-13 | 1-2E | 1513 |  | 南科道爺一路 1513 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1513_DS | 1513(南科道爺ㄧ路) DS | LINE161 |  |  |  |  | CDC | 209 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | E3 | 1513E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0654 | 655 | 0047 | 1-38-14 | 1-38-15 | 1-2F | 1513E |  | 南科道爺一路 1513E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1513E_ES | 1513E(南科道爺ㄧ路) ES | LINE161 |  |  |  |  | CDC | 210 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 211 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 212 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | DS3 | 1523 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0660 | 661 | 0050 | 1-39-04 | 1-39-05 | 1-32 | 1523 |  | 南科道爺二路 1523 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1523_DS | 1523(南科道爺二路) DS | LINE161 |  |  |  |  | CDC | 213 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | E3 | 1523E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0662 | 663 | 0051 | 1-39-06 | 1-39-07 | 1-33 | 1523E |  | 南科道爺二路 1523E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1523E_ES | 1523E(南科道爺二路) ES | LINE161 |  |  |  |  | CDC | 214 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 215 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 216 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DS3 | 1543 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 | 0054 | 1-39-12 | 1-39-13 | 1-36 | 1543 |  | 南科~積E六線 1543 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1543_DS | 1543(南科積E六線) DS | LINE161 |  |  |  |  | CDC | 217 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | E3 | 1543E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0670 | 671 | 0055 | 1-39-14 | 1-39-15 | 1-37 | 1543E |  | 南科~積E六線 1543E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1543E_ES | 1543E(南科積E六線) ES | LINE161 |  |  |  |  | CDC | 218 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 219 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 220 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | DS3 | 1553 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 | 0060 | 1-3A-08 | 1-3A-09 | 1-3C | 1553 |  | 三福線 1553 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1553_DS | 1553(三福科線) DS | LINE161 |  |  |  |  | CDC | 221 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | E3 | 1553E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0682 | 683 | 0061 | 1-3A-10 | 1-3A-11 | 1-3D | 1553E |  | 三福線 1553E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1553E_ES | 1553E(三福科線) ES | LINE161 |  |  |  |  | CDC | 222 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 223 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 224 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | DS3 | 1573 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 689 | 0064 | 1-3B-00 | 1-3B-01 | 1-40 | 1573 |  | 南科道爺三路 1573 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1573_DS | 1573(南科道爺三路) DS | LINE161 |  |  |  |  | CDC | 225 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | E3 | 1573E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0690 | 691 | 0065 | 1-3B-02 | 1-3B-03 | 1-41 | 1573E |  | 南科道爺三路 1573E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1573E_ES | 1573E(南科道爺三路) ES | LINE161 |  |  |  |  | CDC | 226 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 227 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 228 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | DS3 | 1583 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 697 | 0068 | 1-3B-08 | 1-3B-09 | 1-44 | 1583 |  | 南科道爺四路 1583 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1583_DS | 1583(南科道爺四路) DS | LINE161 |  |  |  |  | CDC | 229 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | E3 | 1583E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0698 | 699 | 0069 | 1-3B-10 | 1-3B-11 | 1-45 | 1583E |  | 南科道爺四路 1583E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1583E_ES | 1583E(南科道爺四路) ES | LINE161 |  |  |  |  | CDC | 230 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 231 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 232 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | DS3 | 1613 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0712 | 713 | 0076 | 1-3C-08 | 1-3C-09 | 1-4C | 1613 |  | 南科麻工一路 1613 DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1613_DS | 1613(麻工ㄧ路) DS | LINE161 |  |  |  |  | CDC | 233 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | E3 | 1613E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0714 | 715 | 0077 | 1-3C-10 | 1-3C-11 | 1-4D | 1613E |  | 南科麻工一路 1613E DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1613E_ES | 1613E(麻工ㄧ路) ES | LINE161 |  |  |  |  | CDC | 234 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 235 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 236 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | DS3 | 1623 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0720 | 721 | 0080 | 1-3D-00 | 1-3D-01 | 1-50 | 1623 |  | 南科麻工二路 1623 DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1623_DS | 1623(麻工二路) DS | LINE161 |  |  |  |  | CDC | 237 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | E3 | 1623E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0722 | 723 | 0081 | 1-3D-02 | 1-3D-03 | 1-51 | 1623E |  | 南科麻工二路 1623E DS(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1623E_ES | 1623E(麻工二路) ES | LINE161 |  |  |  |  | CDC | 238 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 239 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 240 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | DS3 | 1633 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0736 | 737 | 0088 | 1-3E-00 | 1-3E-01 | 1-58 | 1633 |  | 南科豐華紅線 1633 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1633_DS | 1633(南科豐華紅線) DS | LINE161 |  |  |  |  | CDC | 241 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | E3 | 1633E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0738 | 739 | 0089 | 1-3E-02 | 1-3E-03 | 1-59 | 1633E |  | 南科豐華紅線 1633E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1633E_ES | 1633E(南科豐華紅線) ES | LINE161 |  |  |  |  | CDC | 242 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 243 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 244 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | DS3 | 1643 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0744 | 745 | 0092 | 1-3E-08 | 1-3E-09 | 1-5C | 1643 |  | 南科豐華白線(1643) DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1643_DS | 1643(南科豐華白線) DS | LINE161 |  |  |  |  | CDC | 245 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | E3 | 1643E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0746 | 747 | 0093 | 1-3E-10 | 1-3E-11 | 1-5D | 1643E |  | 南科豐華白線(1643E) DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1643E_ES | 1643E(南科豐華白線) ES | LINE161 |  |  |  |  | CDC | 246 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 247 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 248 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | DS3 | 1663 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0772 | 773 | 0266 | 3-30-04 | 3-30-05 | 3-0A | 1663 |  | 南科三竹二路 1663 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1663_DS | 1663(三竹二路) DS | LINE161 |  |  |  |  | CDC | 249 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | E3 | 1663E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0774 | 775 | 0267 | 3-30-06 | 3-30-07 | 3-0B | 1663E |  | 南科三竹二路 1663E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1663E_ES | 1663E(三竹二路) ES | LINE161 |  |  |  |  | CDC | 250 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 251 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 252 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | DS3 | 1653 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0780 | 781 | 0270 | 3-30-12 | 3-30-13 | 3-0E | 1653 |  | 南科三竹一路 1653 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1653_DS | 1653(三竹ㄧ路) DS | LINE161 |  |  |  |  | CDC | 253 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | E3 | 1653E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0782 | 783 | 0271 | 3-30-14 | 3-30-15 | 3-0F | 1653E |  | 南科三竹一路 1653E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1653E_ES | 1653E(三竹ㄧ路) ES | LINE161 |  |  |  |  | CDC | 254 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 255 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 256 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | DS3 | 1673 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0788 | 789 | 0274 | 3-31-04 | 3-31-05 | 3-12 | 1673 |  | 積六線 1673 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1673_DS | 1673(積六線) DS | LINE161 |  |  |  |  | CDC | 257 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | E3 | 1673E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0790 | 791 | 0275 | 3-31-06 | 3-31-07 | 3-13 | 1673E |  | 積六線 1673E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1673E_ES | 1673E(積六線) ES | LINE161 |  |  |  |  | CDC | 258 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 259 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 260 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | DS3 | 1683 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0796 | 797 | 0278 | 3-31-12 | 3-31-13 | 3-16 | 1683 |  | 康寧線 1683 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1683_DS | 1683(康寧線) DS | LINE161 |  |  |  |  | CDC | 261 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | E3 | 1683E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0798 | 799 | 0279 | 3-31-14 | 3-31-15 | 3-17 | 1683E |  | 康寧線 1683E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1683E_ES | 1683E(康寧線) ES | LINE161 |  |  |  |  | CDC | 262 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 263 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 264 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | DS3 | 1713 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0804 | 805 | 0282 | 3-32-04 | 3-32-05 | 3-1A | 1713 |  | 南科~和鑫二線 1713 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1713_DS | 1713(南科和鑫二線) DS | LINE161 |  |  |  |  | CDC | 265 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | E3 | 1713E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0806 | 807 | 0283 | 3-32-06 | 3-32-07 | 3-1B | 1713E |  | 南科~和鑫二線 1713E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1713E_ES | 1713E(南科和鑫二線) ES | LINE161 |  |  |  |  | CDC | 266 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 267 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 268 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | DS3 | 1723 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0812 | 813 | 0286 | 3-32-12 | 3-32-13 | 3-1E | 1723 |  | 南科積P3白線 1723 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1723_DS | 1723(南科積P3線) DS | LINE161 |  |  |  |  | CDC | 269 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | E3 | 1723E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0814 | 815 | 0287 | 3-32-14 | 3-32-15 | 3-1F | 1723E |  | 南科積P3白線 1723E DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1723E_ES | 1723E(南科積P3線) ES | LINE161 |  |  |  |  | CDC | 270 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 271 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 272 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | 85CFA | 85FA | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0548 |  |  | 1-32-04 |  |  | 1610 | 87CFA | 南科麻工一路 1610 85CFA(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_85FA | 麻工ㄧ路(1610) 85FA | LINE161 |  |  |  |  | CDC | 273 | DI_LINE161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0549 |  |  | 1-32-05 |  |  | 1610 | RYFA | 南科麻工一路 1610 數位電驛故障(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1610_85UA | 麻工ㄧ路(1610) 85uA | LINE161 |  |  |  |  | CDC | 274 | DI_LINE161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | 85CFA | 85FA | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | 1620 | 87CFA | 南科麻工二路 1620 85CFA(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_85FA | 麻工二路(1620) 85FA | LINE161 |  |  |  |  | CDC | 275 | DI_LINE161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | 1620 | RYFA | 南科麻工二路 1620 數位電驛故障(備用) |  |  | B2/E02_A1 | [8 empty] | 南科ES.1620_85UA | 麻工二路(1620) 85uA | LINE161 |  |  |  |  | CDC | 276 | DI_LINE161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | KVAR | 科51線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 251 | 乏 | 科51線 K251 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科51線KVAR | 23KV科51線 KVAR | FEEDER |  |  |  |  | CDC | 277 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | I_R | 科51線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 251 | R相電流 | 科51線 K251 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科51線A1 | 23KV科51線 R相AMP | FEEDER |  |  |  |  | CDC | 278 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | I_S | 科51線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 251 | S相電流 | 科51線 K251 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科51線A2 | 23KV科51線 S相AMP | FEEDER |  |  |  |  | CDC | 279 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | I_T | 科51線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 251 | T相電流 | 科51線 K251 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科51線A3 | 23KV科51線 T相AMP | FEEDER |  |  |  |  | CDC | 280 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | I_N | 科51線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 251 | N相電流 | 科51線 K251 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科51線A0 | 23KV科51線 N相AMP | FEEDER |  |  |  |  | CDC | 281 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | KVAR | 科52線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 252 | 乏 | 科52線 K252 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科52線KVAR | 23KV科52線 KVAR | FEEDER |  |  |  |  | CDC | 282 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | I_R | 科52線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 252 | R相電流 | 科52線 K252 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科52線A1 | 23KV科52線 R相AMP | FEEDER |  |  |  |  | CDC | 283 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | I_S | 科52線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 252 | S相電流 | 科52線 K252 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科52線A2 | 23KV科52線 S相AMP | FEEDER |  |  |  |  | CDC | 284 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | I_T | 科52線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 252 | T相電流 | 科52線 K252 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科52線A3 | 23KV科52線 T相AMP | FEEDER |  |  |  |  | CDC | 285 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | I_N | 科52線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 252 | N相電流 | 科52線 K252 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科52線A0 | 23KV科52線 N相AMP | FEEDER |  |  |  |  | CDC | 286 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | KVAR | 科53線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 253 | 乏 | 科53線 K253 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科53線KVAR | 23KV科53線 KVAR | FEEDER |  |  |  |  | CDC | 287 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | I_R | 科53線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 253 | R相電流 | 科53線 K253 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科53線A1 | 23KV科53線 R相AMP | FEEDER |  |  |  |  | CDC | 288 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | I_S | 科53線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 253 | S相電流 | 科53線 K253 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科53線A2 | 23KV科53線 S相AMP | FEEDER |  |  |  |  | CDC | 289 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | I_T | 科53線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 253 | T相電流 | 科53線 K253 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科53線A3 | 23KV科53線 T相AMP | FEEDER |  |  |  |  | CDC | 290 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | I_N | 科53線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 253 | N相電流 | 科53線 K253 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科53線A0 | 23KV科53線 N相AMP | FEEDER |  |  |  |  | CDC | 291 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | KVAR | 科54線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 254 | 乏 | 科54線 K254 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科54線KVAR | 23KV科54線 KVAR | FEEDER |  |  |  |  | CDC | 292 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | I_R | 科54線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 254 | R相電流 | 科54線 K254 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科54線A1 | 23KV科54線 R相AMP | FEEDER |  |  |  |  | CDC | 293 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | I_S | 科54線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 254 | S相電流 | 科54線 K254 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科54線A2 | 23KV科54線 S相AMP | FEEDER |  |  |  |  | CDC | 294 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | I_T | 科54線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 254 | T相電流 | 科54線 K254 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科54線A3 | 23KV科54線 T相AMP | FEEDER |  |  |  |  | CDC | 295 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | I_N | 科54線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 254 | N相電流 | 科54線 K254 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科54線A0 | 23KV科54線 N相AMP | FEEDER |  |  |  |  | CDC | 296 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | KVAR | 科十六線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 216 | 乏 | 科十六 K216 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十六線KVAR | 11KV科十六線 KVAR | FEEDER |  |  |  |  | CDC | 297 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | I_R | 科十六線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 216 | R相電流 | 科十六 K216 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十六線A1 | 11KV科十六線 R相AMP | FEEDER |  |  |  |  | CDC | 298 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | I_S | 科十六線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 216 | S相電流 | 科十六 K216 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十六線A2 | 11KV科十六線 S相AMP | FEEDER |  |  |  |  | CDC | 299 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | I_T | 科十六線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 216 | T相電流 | 科十六 K216 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十六線A3 | 11KV科十六線 T相AMP | FEEDER |  |  |  |  | CDC | 300 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | I_N | 科十六線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 216 | N相電流 | 科十六 K216 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十六線A0 | 11KV科十六線 N相AMP | FEEDER |  |  |  |  | CDC | 301 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | KVAR | 科十七線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 217 | 乏 | 科十七 K217 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十七線KVAR | 11KV科十七線 KVAR | FEEDER |  |  |  |  | CDC | 302 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | I_R | 科十七線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 217 | R相電流 | 科十七 K217 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十七線A1 | 11KV科十七線 R相AMP | FEEDER |  |  |  |  | CDC | 303 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | I_S | 科十七線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 217 | S相電流 | 科十七 K217 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十七線A2 | 11KV科十七線 S相AMP | FEEDER |  |  |  |  | CDC | 304 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | I_T | 科十七線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 217 | T相電流 | 科十七 K217 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十七線A3 | 11KV科十七線 T相AMP | FEEDER |  |  |  |  | CDC | 305 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | I_N | 科十七線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 217 | N相電流 | 科十七 K217 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十七線A0 | 11KV科十七線 N相AMP | FEEDER |  |  |  |  | CDC | 306 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | KVAR | 科十八線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 218 | 乏 | 科十八 K218 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十八線KVAR | 11KV科十八線 KVAR | FEEDER |  |  |  |  | CDC | 307 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | I_R | 科十八線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 218 | R相電流 | 科十八 K218 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十八線A1 | 11KV科十八線 R相AMP | FEEDER |  |  |  |  | CDC | 308 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | I_S | 科十八線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 218 | S相電流 | 科十八 K218 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十八線A2 | 11KV科十八線 S相AMP | FEEDER |  |  |  |  | CDC | 309 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | I_T | 科十八線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 218 | T相電流 | 科十八 K218 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十八線A3 | 11KV科十八線 T相AMP | FEEDER |  |  |  |  | CDC | 310 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | I_N | 科十八線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 218 | N相電流 | 科十八 K218 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十八線A0 | 11KV科十八線 N相AMP | FEEDER |  |  |  |  | CDC | 311 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | KVAR | 科十九線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 219 | 乏 | 科十九 K219 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十九線KVAR | 11KV科十九線 KVAR | FEEDER |  |  |  |  | CDC | 312 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | I_R | 科十九線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 219 | R相電流 | 科十九 K219 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十九線A1 | 11KV科十九線 R相AMP | FEEDER |  |  |  |  | CDC | 313 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | I_S | 科十九線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 219 | S相電流 | 科十九 K219 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十九線A2 | 11KV科十九線 S相AMP | FEEDER |  |  |  |  | CDC | 314 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | I_T | 科十九線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 219 | T相電流 | 科十九 K219 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十九線A3 | 11KV科十九線 T相AMP | FEEDER |  |  |  |  | CDC | 315 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | I_N | 科十九線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 219 | N相電流 | 科十九 K219 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科十九線A0 | 11KV科十九線 N相AMP | FEEDER |  |  |  |  | CDC | 316 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | KVAR | 科二十線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 220 | 乏 | 科二十 K220 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科二十線KVAR | 11KV科二十線 KVAR | FEEDER |  |  |  |  | CDC | 317 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | I_R | 科二十線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 220 | R相電流 | 科二十 K220 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科二十線A1 | 11KV科二十線 R相AMP | FEEDER |  |  |  |  | CDC | 318 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | I_S | 科二十線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 220 | S相電流 | 科二十 K220 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科二十線A2 | 11KV科二十線 S相AMP | FEEDER |  |  |  |  | CDC | 319 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | I_T | 科二十線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 220 | T相電流 | 科二十 K220 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科二十線A3 | 11KV科二十線 T相AMP | FEEDER |  |  |  |  | CDC | 320 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | I_N | 科二十線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 220 | N相電流 | 科二十 K220 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科二十線A0 | 11KV科二十線 N相AMP | FEEDER |  |  |  |  | CDC | 321 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | KVAR | 科六一線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 261 | 乏 | 科六十一 K261 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六一線KVAR | 23KV科六一線 KVAR | FEEDER |  |  |  |  | CDC | 322 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | I_R | 科六一線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 261 | R相電流 | 科六十一 K261 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六一線A1 | 23KV科六一線 R相AMP | FEEDER |  |  |  |  | CDC | 323 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | I_S | 科六一線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 261 | S相電流 | 科六十一 K261 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六一線A2 | 23KV科六一線 S相AMP | FEEDER |  |  |  |  | CDC | 324 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | I_T | 科六一線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 261 | T相電流 | 科六十一 K261 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六一線A3 | 23KV科六一線 T相AMP | FEEDER |  |  |  |  | CDC | 325 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | I_N | 科六一線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 261 | N相電流 | 科六十一 K261 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六一線A0 | 23KV科六一線 N相AMP | FEEDER |  |  |  |  | CDC | 326 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | KVAR | 科六二線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 262 | 乏 | 科六十二 K262 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六二線KVAR | 23KV科六二線 KVAR | FEEDER |  |  |  |  | CDC | 327 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | I_R | 科六二線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 262 | R相電流 | 科六十二 K262 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六二線A1 | 23KV科六二線 R相AMP | FEEDER |  |  |  |  | CDC | 328 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | I_S | 科六二線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 262 | S相電流 | 科六十二 K262 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六二線A2 | 23KV科六二線 S相AMP | FEEDER |  |  |  |  | CDC | 329 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | I_T | 科六二線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 262 | T相電流 | 科六十二 K262 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六二線A3 | 23KV科六二線 T相AMP | FEEDER |  |  |  |  | CDC | 330 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | I_N | 科六二線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 262 | N相電流 | 科六十二 K262 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六二線A0 | 23KV科六二線 N相AMP | FEEDER |  |  |  |  | CDC | 331 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | KVAR | 科六三線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 263 | 乏 | 科六十三 K263 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六三線KVAR | 23KV科六三線 KVAR | FEEDER |  |  |  |  | CDC | 332 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | I_R | 科六三線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 263 | R相電流 | 科六十三 K263 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六三線A1 | 23KV科六三線 R相AMP | FEEDER |  |  |  |  | CDC | 333 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | I_S | 科六三線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 263 | S相電流 | 科六十三 K263 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六三線A2 | 23KV科六三線 S相AMP | FEEDER |  |  |  |  | CDC | 334 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | I_T | 科六三線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 263 | T相電流 | 科六十三 K263 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六三線A3 | 23KV科六三線 T相AMP | FEEDER |  |  |  |  | CDC | 335 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | I_N | 科六三線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 263 | N相電流 | 科六十三 K263 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六三線A0 | 23KV科六三線 N相AMP | FEEDER |  |  |  |  | CDC | 336 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | KVAR | 科六四線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 264 | 乏 | 科六十四 K264 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六四線KVAR | 23KV科六四線 KVAR | FEEDER |  |  |  |  | CDC | 337 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | I_R | 科六四線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 264 | R相電流 | 科六十四 K264 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六四線A1 | 23KV科六四線 R相AMP | FEEDER |  |  |  |  | CDC | 338 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | I_S | 科六四線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 264 | S相電流 | 科六十四 K264 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六四線A2 | 23KV科六四線 S相AMP | FEEDER |  |  |  |  | CDC | 339 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | I_T | 科六四線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 264 | T相電流 | 科六十四 K264 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六四線A3 | 23KV科六四線 T相AMP | FEEDER |  |  |  |  | CDC | 340 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | I_N | 科六四線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 264 | N相電流 | 科六十四 K264 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六四線A0 | 23KV科六四線 N相AMP | FEEDER |  |  |  |  | CDC | 341 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | KVAR | 科六五線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | 265 | 乏 | 科六十五 K265 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六五線KVAR | 23KV科六五線 KVAR | FEEDER |  |  |  |  | CDC | 342 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | I_R | 科六五線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | 265 | R相電流 | 科六十五 K265 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六五線A1 | 23KV科六五線 R相AMP | FEEDER |  |  |  |  | CDC | 343 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | I_S | 科六五線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | 265 | S相電流 | 科六十五 K265 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六五線A2 | 23KV科六五線 S相AMP | FEEDER |  |  |  |  | CDC | 344 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | I_T | 科六五線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | 265 | T相電流 | 科六十五 K265 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六五線A3 | 23KV科六五線 T相AMP | FEEDER |  |  |  |  | CDC | 345 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | I_N | 科六五線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 265 | N相電流 | 科六十五 K265 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六五線A0 | 23KV科六五線 N相AMP | FEEDER |  |  |  |  | CDC | 346 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | KVAR | 科六六線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | 266 | 乏 | 科六十六 K266 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六六線KVAR | 23KV科六六線 KVAR | FEEDER |  |  |  |  | CDC | 347 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | I_R | 科六六線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | 266 | R相電流 | 科六十六 K266 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六六線A1 | 23KV科六六線 R相AMP | FEEDER |  |  |  |  | CDC | 348 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | I_S | 科六六線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | 266 | S相電流 | 科六十六 K266 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六六線A2 | 23KV科六六線 S相AMP | FEEDER |  |  |  |  | CDC | 349 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | I_T | 科六六線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | 266 | T相電流 | 科六十六 K266 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六六線A3 | 23KV科六六線 T相AMP | FEEDER |  |  |  |  | CDC | 350 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | I_N | 科六六線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | 266 | N相電流 | 科六十六 K266 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六六線A0 | 23KV科六六線 N相AMP | FEEDER |  |  |  |  | CDC | 351 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | KVAR | 科六七線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 267 | 乏 | 科六十七 K267 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六七線KVAR | 23KV科六七線 KVAR | FEEDER |  |  |  |  | CDC | 352 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | I_R | 科六七線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | 267 | R相電流 | 科六十七 K267 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六七線A1 | 23KV科六七線 R相AMP | FEEDER |  |  |  |  | CDC | 353 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | I_S | 科六七線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 267 | S相電流 | 科六十七 K267 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六七線A2 | 23KV科六七線 S相AMP | FEEDER |  |  |  |  | CDC | 354 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | I_T | 科六七線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 267 | T相電流 | 科六十七 K267 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六七線A3 | 23KV科六七線 T相AMP | FEEDER |  |  |  |  | CDC | 355 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | I_N | 科六七線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 267 | N相電流 | 科六十七 K267 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六七線A0 | 23KV科六七線 N相AMP | FEEDER |  |  |  |  | CDC | 356 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | KVAR | 科六八線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 268 | 乏 | 科六十八 K268 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六八線KVAR | 23KV科六八線 KVAR | FEEDER |  |  |  |  | CDC | 357 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | I_R | 科六八線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 268 | R相電流 | 科六十八 K268 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六八線A1 | 23KV科六八線 R相AMP | FEEDER |  |  |  |  | CDC | 358 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | I_S | 科六八線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 268 | S相電流 | 科六十八 K268 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六八線A2 | 23KV科六八線 S相AMP | FEEDER |  |  |  |  | CDC | 359 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | I_T | 科六八線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 268 | T相電流 | 科六十八 K268 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六八線A3 | 23KV科六八線 T相AMP | FEEDER |  |  |  |  | CDC | 360 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | I_N | 科六八線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 268 | N相電流 | 科六十八 K268 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科六八線A0 | 23KV科六八線 N相AMP | FEEDER |  |  |  |  | CDC | 361 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | KVAR | 科七一線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 271 | 乏 | 科七十一 K271 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七一線KVAR | 23KV科七一線 KVAR | FEEDER |  |  |  |  | CDC | 362 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | I_R | 科七一線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 271 | R相電流 | 科七十一 K271 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七一線A1 | 23KV科七一線 R相AMP | FEEDER |  |  |  |  | CDC | 363 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | I_S | 科七一線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 271 | S相電流 | 科七十一 K271 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七一線A2 | 23KV科七一線 S相AMP | FEEDER |  |  |  |  | CDC | 364 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | I_T | 科七一線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | 271 | T相電流 | 科七十一 K271 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七一線A3 | 23KV科七一線 T相AMP | FEEDER |  |  |  |  | CDC | 365 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | I_N | 科七一線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | 271 | N相電流 | 科七十一 K271 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七一線A0 | 23KV科七一線 N相AMP | FEEDER |  |  |  |  | CDC | 366 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | KVAR | 科七二線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | 272 | 乏 | 科七十二 K272 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七二線KVAR | 23KV科七二線 KVAR | FEEDER |  |  |  |  | CDC | 367 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | I_R | 科七二線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | 272 | R相電流 | 科七十二 K272 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七二線A1 | 23KV科七二線 R相AMP | FEEDER |  |  |  |  | CDC | 368 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | I_S | 科七二線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 272 | S相電流 | 科七十二 K272 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七二線A2 | 23KV科七二線 S相AMP | FEEDER |  |  |  |  | CDC | 369 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | I_T | 科七二線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 272 | T相電流 | 科七十二 K272 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七二線A3 | 23KV科七二線 T相AMP | FEEDER |  |  |  |  | CDC | 370 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | I_N | 科七二線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 272 | N相電流 | 科七十二 K272 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七二線A0 | 23KV科七二線 N相AMP | FEEDER |  |  |  |  | CDC | 371 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | KVAR | 科七三線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 273 | 乏 | 科七十三 K273 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七三線KVAR | 23KV科七三線 KVAR | FEEDER |  |  |  |  | CDC | 372 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | I_R | 科七三線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 273 | R相電流 | 科七十三 K273 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七三線A1 | 23KV科七三線 R相AMP | FEEDER |  |  |  |  | CDC | 373 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | I_S | 科七三線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 273 | S相電流 | 科七十三 K273 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七三線A2 | 23KV科七三線 S相AMP | FEEDER |  |  |  |  | CDC | 374 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | I_T | 科七三線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 273 | T相電流 | 科七十三 K273 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七三線A3 | 23KV科七三線 T相AMP | FEEDER |  |  |  |  | CDC | 375 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | I_N | 科七三線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 273 | N相電流 | 科七十三 K273 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七三線A0 | 23KV科七三線 N相AMP | FEEDER |  |  |  |  | CDC | 376 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | KVAR | 科七四線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 274 | 乏 | 科七十四 K274 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七四線KVAR | 23KV科七四線 KVAR | FEEDER |  |  |  |  | CDC | 377 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | I_R | 科七四線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 274 | R相電流 | 科七十四 K274 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七四線A1 | 23KV科七四線 R相AMP | FEEDER |  |  |  |  | CDC | 378 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | I_S | 科七四線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 274 | S相電流 | 科七十四 K274 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七四線A2 | 23KV科七四線 S相AMP | FEEDER |  |  |  |  | CDC | 379 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | I_T | 科七四線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 274 | T相電流 | 科七十四 K274 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七四線A3 | 23KV科七四線 T相AMP | FEEDER |  |  |  |  | CDC | 380 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | I_N | 科七四線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 274 | N相電流 | 科七十四 K274 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七四線A0 | 23KV科七四線 N相AMP | FEEDER |  |  |  |  | CDC | 381 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | KVAR | 科七五線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 275 | 乏 | 科七十五 K275 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七五線KVAR | 23KV科七五線 KVAR | FEEDER |  |  |  |  | CDC | 382 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | I_R | 科七五線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 275 | R相電流 | 科七十五 K275 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七五線A1 | 23KV科七五線 R相AMP | FEEDER |  |  |  |  | CDC | 383 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | I_S | 科七五線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 275 | S相電流 | 科七十五 K275 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七五線A2 | 23KV科七五線 S相AMP | FEEDER |  |  |  |  | CDC | 384 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | I_T | 科七五線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 275 | T相電流 | 科七十五 K275 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七五線A3 | 23KV科七五線 T相AMP | FEEDER |  |  |  |  | CDC | 385 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | I_N | 科七五線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | 275 | N相電流 | 科七十五 K275 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七五線A0 | 23KV科七五線 N相AMP | FEEDER |  |  |  |  | CDC | 386 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | KVAR | 科七六線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | 276 | 乏 | 科七十六 K276 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七六線KVAR | 23KV科七六線 KVAR | FEEDER |  |  |  |  | CDC | 387 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | I_R | 科七六線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | 276 | R相電流 | 科七十六 K276 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七六線A1 | 23KV科七六線 R相AMP | FEEDER |  |  |  |  | CDC | 388 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | I_S | 科七六線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | 276 | S相電流 | 科七十六 K276 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七六線A2 | 23KV科七六線 S相AMP | FEEDER |  |  |  |  | CDC | 389 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | I_T | 科七六線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | 276 | T相電流 | 科七十六 K276 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七六線A3 | 23KV科七六線 T相AMP | FEEDER |  |  |  |  | CDC | 390 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | I_N | 科七六線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | 276 | N相電流 | 科七十六 K276 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七六線A0 | 23KV科七六線 N相AMP | FEEDER |  |  |  |  | CDC | 391 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | KVAR | 科七七線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | 277 | 乏 | 科七十七 K277 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七七線KVAR | 23KV科七七線 KVAR | FEEDER |  |  |  |  | CDC | 392 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | I_R | 科七七線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | 277 | R相電流 | 科七十七 K277 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七七線A1 | 23KV科七七線 R相AMP | FEEDER |  |  |  |  | CDC | 393 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | I_S | 科七七線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | 277 | S相電流 | 科七十七 K277 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七七線A2 | 23KV科七七線 S相AMP | FEEDER |  |  |  |  | CDC | 394 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | I_T | 科七七線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | 277 | T相電流 | 科七十七 K277 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七七線A3 | 23KV科七七線 T相AMP | FEEDER |  |  |  |  | CDC | 395 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | I_N | 科七七線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | 277 | N相電流 | 科七十七 K277 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七七線A0 | 23KV科七七線 N相AMP | FEEDER |  |  |  |  | CDC | 396 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | KVAR | 科七八線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | 278 | 乏 | 科七十八 K278 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七八線KVAR | 23KV科七八線 KVAR | FEEDER |  |  |  |  | CDC | 397 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | I_R | 科七八線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | 278 | R相電流 | 科七十八 K278 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七八線A1 | 23KV科七八線 R相AMP | FEEDER |  |  |  |  | CDC | 398 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | I_S | 科七八線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0244 |  |  | 2-F4 |  |  | 278 | S相電流 | 科七十八 K278 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七八線A2 | 23KV科七八線 S相AMP | FEEDER |  |  |  |  | CDC | 399 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | I_T | 科七八線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0245 |  |  | 2-F5 |  |  | 278 | T相電流 | 科七十八 K278 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七八線A3 | 23KV科七八線 T相AMP | FEEDER |  |  |  |  | CDC | 400 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | I_N | 科七八線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | 278 | N相電流 | 科七十八 K278 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科七八線A0 | 23KV科七八線 N相AMP | FEEDER |  |  |  |  | CDC | 401 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_120 | 96 | 108 | 114 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | KVAR | 科7A線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | F27 | 乏 | 科7A線 K27A 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7A線KVAR | 23KV科7A線 KVAR | FEEDER |  |  |  |  | CDC | 402 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | I_R | 科7A線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | F27 | R相電流 | 科7A線 K27A R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7A線A1 | 23KV科7A線 R相AMP | FEEDER |  |  |  |  | CDC | 403 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | I_S | 科7A線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | F27 | S相電流 | 科7A線 K27A S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7A線A2 | 23KV科7A線 S相AMP | FEEDER |  |  |  |  | CDC | 404 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | I_T | 科7A線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | F27 | T相電流 | 科7A線 K27A T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7A線A3 | 23KV科7A線 T相AMP | FEEDER |  |  |  |  | CDC | 405 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | I_N | 科7A線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | F27 | N相電流 | 科7A線 K27A N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7A線A0 | 23KV科7A線 N相AMP | FEEDER |  |  |  |  | CDC | 406 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | KVAR | 科7B線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | F28 | 乏 | 科7B線 K27B 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7B線KVAR | 23KV科7B線 KVAR | FEEDER |  |  |  |  | CDC | 407 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | I_R | 科7B線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | F28 | R相電流 | 科7B線 K27B R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7B線A1 | 23KV科7B線 R相AMP | FEEDER |  |  |  |  | CDC | 408 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | I_S | 科7B線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | F28 | S相電流 | 科7B線 K27B S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7B線A2 | 23KV科7B線 S相AMP | FEEDER |  |  |  |  | CDC | 409 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | I_T | 科7B線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | F28 | T相電流 | 科7B線 K27B T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7B線A3 | 23KV科7B線 T相AMP | FEEDER |  |  |  |  | CDC | 410 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | I_N | 科7B線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | F28 | N相電流 | 科7B線 K27B N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7B線A0 | 23KV科7B線 N相AMP | FEEDER |  |  |  |  | CDC | 411 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | KVAR | 科7C線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | F29 | 乏 | 科7C線 K27C 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7C線KVAR | 23KV科7C線 KVAR | FEEDER |  |  |  |  | CDC | 412 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | I_R | 科7C線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | F29 | R相電流 | 科7C線 K27C R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7C線A1 | 23KV科7C線 R相AMP | FEEDER |  |  |  |  | CDC | 413 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | I_S | 科7C線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | F29 | S相電流 | 科7C線 K27C S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7C線A2 | 23KV科7C線 S相AMP | FEEDER |  |  |  |  | CDC | 414 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | I_T | 科7C線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | F29 | T相電流 | 科7C線 K27C T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7C線A3 | 23KV科7C線 T相AMP | FEEDER |  |  |  |  | CDC | 415 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | I_N | 科7C線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | F29 | N相電流 | 科7C線 K27C N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7C線A0 | 23KV科7C線 N相AMP | FEEDER |  |  |  |  | CDC | 416 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | KVAR | 科7D線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | F30 | 乏 | 科7D線 K27D 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7D線KVAR | 23KV科7D線 KVAR | FEEDER |  |  |  |  | CDC | 417 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | I_R | 科7D線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | F30 | R相電流 | 科7D線 K27D R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7D線A1 | 23KV科7D線 R相AMP | FEEDER |  |  |  |  | CDC | 418 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | I_S | 科7D線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0281 |  |  | 3-99 |  |  | F30 | S相電流 | 科7D線 K27D S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7D線A2 | 23KV科7D線 S相AMP | FEEDER |  |  |  |  | CDC | 419 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | I_T | 科7D線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0282 |  |  | 3-9A |  |  | F30 | T相電流 | 科7D線 K27D T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7D線A3 | 23KV科7D線 T相AMP | FEEDER |  |  |  |  | CDC | 420 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | I_N | 科7D線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0283 |  |  | 3-9B |  |  | F30 | N相電流 | 科7D線 K27D N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科7D線A0 | 23KV科7D線 N相AMP | FEEDER |  |  |  |  | CDC | 421 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | KVAR | 科21線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | F31 | 乏 | 科21線 K221 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科21線KVAR | 11KV科21線 KVAR | FEEDER |  |  |  |  | CDC | 422 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | I_R | 科21線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | F31 | R相電流 | 科21線 K221 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科21線A1 | 11KV科21線 R相AMP | FEEDER |  |  |  |  | CDC | 423 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | I_S | 科21線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | F31 | S相電流 | 科21線 K221 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科21線A2 | 11KV科21線 S相AMP | FEEDER |  |  |  |  | CDC | 424 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | I_T | 科21線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0287 |  |  | 3-9F |  |  | F31 | T相電流 | 科21線 K221 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科21線A3 | 11KV科21線 T相AMP | FEEDER |  |  |  |  | CDC | 425 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | I_N | 科21線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0288 |  |  | 3-A0 |  |  | F31 | N相電流 | 科21線 K221 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科21線A0 | 11KV科21線 N相AMP | FEEDER |  |  |  |  | CDC | 426 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | KVAR | 科22線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0295 |  |  | 3-A7 |  |  | F32 | 乏 | 科22線 K222 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科22線KVAR | 11KV科22線 KVAR | FEEDER |  |  |  |  | CDC | 427 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | I_R | 科22線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0296 |  |  | 3-A8 |  |  | F32 | R相電流 | 科22線 K222 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科22線A1 | 11KV科22線 R相AMP | FEEDER |  |  |  |  | CDC | 428 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | I_S | 科22線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0297 |  |  | 3-A9 |  |  | F32 | S相電流 | 科22線 K222 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科22線A2 | 11KV科22線 S相AMP | FEEDER |  |  |  |  | CDC | 429 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | I_T | 科22線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0298 |  |  | 3-AA |  |  | F32 | T相電流 | 科22線 K222 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科22線A3 | 11KV科22線 T相AMP | FEEDER |  |  |  |  | CDC | 430 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | I_N | 科22線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0299 |  |  | 3-AB |  |  | F32 | N相電流 | 科22線 K222 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科22線A0 | 11KV科22線 N相AMP | FEEDER |  |  |  |  | CDC | 431 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | KVAR | 科23線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0300 |  |  | 3-AC |  |  | F33 | 乏 | 科23線 K223 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科23線KVAR | 11KV科23線 KVAR | FEEDER |  |  |  |  | CDC | 432 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | I_R | 科23線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0301 |  |  | 3-AD |  |  | F33 | R相電流 | 科23線 K223 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科23線A1 | 11KV科23線 R相AMP | FEEDER |  |  |  |  | CDC | 433 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | I_S | 科23線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0302 |  |  | 3-AE |  |  | F33 | S相電流 | 科23線 K223 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科23線A2 | 11KV科23線 S相AMP | FEEDER |  |  |  |  | CDC | 434 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | I_T | 科23線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0303 |  |  | 3-AF |  |  | F33 | T相電流 | 科23線 K223 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科23線A3 | 11KV科23線 T相AMP | FEEDER |  |  |  |  | CDC | 435 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | I_N | 科23線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0304 |  |  | 3-B0 |  |  | F33 | N相電流 | 科23線 K223 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科23線A0 | 11KV科23線 N相AMP | FEEDER |  |  |  |  | CDC | 436 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | KVAR | 科24線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0305 |  |  | 3-B1 |  |  | F34 | 乏 | 科24線 K224 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科24線KVAR | 11KV科24線 KVAR | FEEDER |  |  |  |  | CDC | 437 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | I_R | 科24線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0306 |  |  | 3-B2 |  |  | F34 | R相電流 | 科24線 K224 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科24線A1 | 11KV科24線 R相AMP | FEEDER |  |  |  |  | CDC | 438 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | I_S | 科24線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0307 |  |  | 3-B3 |  |  | F34 | S相電流 | 科24線 K224 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科24線A2 | 11KV科24線 S相AMP | FEEDER |  |  |  |  | CDC | 439 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | I_T | 科24線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0308 |  |  | 3-B4 |  |  | F34 | T相電流 | 科24線 K224 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科24線A3 | 11KV科24線 T相AMP | FEEDER |  |  |  |  | CDC | 440 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | I_N | 科24線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0309 |  |  | 3-B5 |  |  | F34 | N相電流 | 科24線 K224 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科24線A0 | 11KV科24線 N相AMP | FEEDER |  |  |  |  | CDC | 441 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | KVAR | 科25線 | B3 | MvMoment | KVAR |  | Y |  | AI | [6 empty] | 0310 |  |  | 3-B6 |  |  | F35 | 乏 | 科25線 K225 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科25線KVAR | 11KV科25線 KVAR | FEEDER |  |  |  |  | CDC | 442 | AI_FEEDER |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | I_R | 科25線 | B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0311 |  |  | 3-B7 |  |  | F35 | R相電流 | 科25線 K225 R相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科25線A1 | 11KV科25線 R相AMP | FEEDER |  |  |  |  | CDC | 443 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | I_S | 科25線 | B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0312 |  |  | 3-B8 |  |  | F35 | S相電流 | 科25線 K225 S相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科25線A2 | 11KV科25線 S相AMP | FEEDER |  |  |  |  | CDC | 444 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | I_T | 科25線 | B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0313 |  |  | 3-B9 |  |  | F35 | T相電流 | 科25線 K225 T相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科25線A3 | 11KV科25線 T相AMP | FEEDER |  |  |  |  | CDC | 445 | AI_FEEDER |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | I_N | 科25線 | B3 | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0314 |  |  | 3-BA |  |  | F35 | N相電流 | 科25線 K225 N相電流 | A_-600_600(-2000_2000) |  | B2/E02_D1 |  |  | 600 | [5 empty] | 南科ES.科25線A0 | 11KV科25線 N相AMP | FEEDER |  |  |  |  | CDC | 446 | AI_FEEDER |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | 251 | PHA | 科51線 K251 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K251_PHA | 23KV科51線(K251) 相間RY | FEEDER |  |  |  |  | CDC | 447 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | 251 | GDA | 科51線 K251 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K251_GDA | 23KV科51線(K251) 接地RY | FEEDER |  |  |  |  | CDC | 448 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0901 |  | 0178 | 2-38-05 |  | 2-32 | 251 | 79 RY U/L | 科51線 K251 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K251_79UL | 23KV科51線(K251) 79RY U/L | FEEDER |  |  |  |  | CDC | 449 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0902 |  | 0179 | 2-38-06 |  | 2-33 | 251 | LCO 分流器 | 科51線 K251 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K251_LCO_TAP | 23KV科51線(K251) LCO TAP | FEEDER |  |  |  |  | CDC | 450 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | 252 | PHA | 科52線 K252 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K252_PHA | 23KV科52線(K252) 相間RY | FEEDER |  |  |  |  | CDC | 451 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | 252 | GDA | 科52線 K252 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K252_GDA | 23KV科52線(K252) 接地RY | FEEDER |  |  |  |  | CDC | 452 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0903 |  | 0180 | 2-38-07 |  | 2-34 | 252 | 79 RY U/L | 科52線 K252 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K252_79UL | 23KV科52線(K252) 79RY U/L | FEEDER |  |  |  |  | CDC | 453 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0904 |  | 0181 | 2-38-08 |  | 2-35 | 252 | LCO 分流器 | 科52線 K252 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K252_LCO_TAP | 23KV科52線(K252) LCO TAP | FEEDER |  |  |  |  | CDC | 454 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | 253 | PHA | 科53線 K253 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K253_PHA | 23KV科53線(K253) 相間RY | FEEDER |  |  |  |  | CDC | 455 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | 253 | GDA | 科53線 K253 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K253_GDA | 23KV科53線(K253) 接地RY | FEEDER |  |  |  |  | CDC | 456 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0905 |  | 0182 | 2-38-09 |  | 2-36 | 253 | 79 RY U/L | 科53線 K253 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K253_79UL | 23KV科53線(K253) 79RY U/L | FEEDER |  |  |  |  | CDC | 457 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0906 |  | 0183 | 2-38-10 |  | 2-37 | 253 | LCO 分流器 | 科53線 K253 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K253_LCO_TAP | 23KV科53線(K253) LCO TAP | FEEDER |  |  |  |  | CDC | 458 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | 254 | PHA | 科54線 K254 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K254_PHA | 23KV科54線(K254) 相間RY | FEEDER |  |  |  |  | CDC | 459 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | 254 | GDA | 科54線 K254 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K254_GDA | 23KV科54線(K254) 接地RY | FEEDER |  |  |  |  | CDC | 460 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0907 |  | 0184 | 2-38-11 |  | 2-38 | 254 | 79 RY U/L | 科54線 K254 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K254_79UL | 23KV科54線(K254) 79RY U/L | FEEDER |  |  |  |  | CDC | 461 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0908 |  | 0185 | 2-38-12 |  | 2-39 | 254 | LCO 分流器 | 科54線 K254 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K254_LCO_TAP | 23KV科54線(K254) LCO TAP | FEEDER |  |  |  |  | CDC | 462 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | 216 | PHA | 科十六 K216 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K216_PHA | 11KV科十六線(K216) 相間RY | FEEDER |  |  |  |  | CDC | 463 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0276 |  |  | 2-02-04 |  |  | 216 | GDA | 科十六 K216 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K216_GDA | 11KV科十六線(K216) 接地RY | FEEDER |  |  |  |  | CDC | 464 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0909 |  | 0186 | 2-38-13 |  | 2-3A | 216 | 79 RY U/L | 科十六 K216 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K216_79UL | 11KV科十六線(K216) 79RY U/L | FEEDER |  |  |  |  | CDC | 465 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0910 |  | 0187 | 2-38-14 |  | 2-3B | 216 | LCO 分流器 | 科十六 K216 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K216_LCO_TAP | 11KV科十六線(K216) LCO TAP | FEEDER |  |  |  |  | CDC | 466 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | 217 | PHA | 科十七 K217 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K217_PHA | 11KV科十七線(K217) 相間RY | FEEDER |  |  |  |  | CDC | 467 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0279 |  |  | 2-02-07 |  |  | 217 | GDA | 科十七 K217 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K217_GDA | 11KV科十七線(K217) 接地RY | FEEDER |  |  |  |  | CDC | 468 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0911 |  | 0188 | 2-38-15 |  | 2-3C | 217 | 79 RY U/L | 科十七 K217 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K217_79UL | 11KV科十七線(K217) 79RY U/L | FEEDER |  |  |  |  | CDC | 469 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0912 |  | 0189 | 2-39-00 |  | 2-3D | 217 | LCO 分流器 | 科十七 K217 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K217_LCO_TAP | 11KV科十七線(K217) LCO TAP | FEEDER |  |  |  |  | CDC | 470 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | 218 | PHA | 科十八 K218 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K218_PHA | 11KV科十八線(K218) 相間RY | FEEDER |  |  |  |  | CDC | 471 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | 218 | GDA | 科十八 K218 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K218_GDA | 11KV科十八線(K218) 接地RY | FEEDER |  |  |  |  | CDC | 472 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0913 |  | 0190 | 2-39-01 |  | 2-3E | 218 | 79 RY U/L | 科十八 K218 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K218_79UL | 11KV科十八線(K218) 79RY U/L | FEEDER |  |  |  |  | CDC | 473 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0914 |  | 0191 | 2-39-02 |  | 2-3F | 218 | LCO 分流器 | 科十八 K218 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K218_LCO_TAP | 11KV科十八線(K218) LCO TAP | FEEDER |  |  |  |  | CDC | 474 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | 219 | PHA | 科十九 K219 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K219_PHA | 11KV科十九線(K219) 相間RY | FEEDER |  |  |  |  | CDC | 475 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | 219 | GDA | 科十九 K219 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K219_GDA | 11KV科十九線(K219) 接地RY | FEEDER |  |  |  |  | CDC | 476 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0915 |  | 0192 | 2-39-03 |  | 2-40 | 219 | 79 RY U/L | 科十九 K219 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K219_79UL | 11KV科十九線(K219) 79RY U/L | FEEDER |  |  |  |  | CDC | 477 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0916 |  | 0193 | 2-39-04 |  | 2-41 | 219 | LCO 分流器 | 科十九 K219 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K219_LCO_TAP | 11KV科十九線(K219) LCO TAP | FEEDER |  |  |  |  | CDC | 478 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | 220 | PHA | 科二十 K220 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K220_PHA | 11KV科二十線(K220) 相間RY | FEEDER |  |  |  |  | CDC | 479 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 2-04-00 |  |  | 220 | GDA | 科二十 K220 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K220_GDA | 11KV科二十線(K220) 接地RY | FEEDER |  |  |  |  | CDC | 480 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0917 |  | 0194 | 2-39-05 |  | 2-42 | 220 | 79 RY U/L | 科二十 K220 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K220_79UL | 11KV科二十線(K220) 79RY U/L | FEEDER |  |  |  |  | CDC | 481 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0918 |  | 0195 | 2-39-06 |  | 2-43 | 220 | LCO 分流器 | 科二十 K220 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K220_LCO_TAP | 11KV科二十線(K220) LCO TAP | FEEDER |  |  |  |  | CDC | 482 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | 261 | PHA | 科六十一 K261 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K261_PHA | 23KV科六一線(K261) 相間RY | FEEDER |  |  |  |  | CDC | 483 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | 261 | GDA | 科六十一 K261 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K261_GDA | 23KV科六一線(K261) 接地RY | FEEDER |  |  |  |  | CDC | 484 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0919 |  | 0196 | 2-39-07 |  | 2-44 | 261 | 79 RY U/L | 科六十一 K261 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K261_79UL | 23KV科六一線(K261) 79RY U/L | FEEDER |  |  |  |  | CDC | 485 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0920 |  | 0197 | 2-39-08 |  | 2-45 | 261 | LCO 分流器 | 科六十一 K261 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K261_LCO_TAP | 23KV科六一線(K261) LCO TAP | FEEDER |  |  |  |  | CDC | 486 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | 262 | PHA | 科六十二 K262 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K262_PHA | 23KV科六二線(K262) 相間RY | FEEDER |  |  |  |  | CDC | 487 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | 262 | GDA | 科六十二 K262 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K262_GDA | 23KV科六二線(K262) 接地RY | FEEDER |  |  |  |  | CDC | 488 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0921 |  | 0198 | 2-39-09 |  | 2-46 | 262 | 79 RY U/L | 科六十二 K262 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K262_79UL | 23KV科六二線(K262) 79RY U/L | FEEDER |  |  |  |  | CDC | 489 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0922 |  | 0199 | 2-39-10 |  | 2-47 | 262 | LCO 分流器 | 科六十二 K262 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K262_LCO_TAP | 23KV科六二線(K262) LCO TAP | FEEDER |  |  |  |  | CDC | 490 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | 263 | PHA | 科六十三 K263 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K263_PHA | 23KV科六三線(K263) 相間RY | FEEDER |  |  |  |  | CDC | 491 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | 263 | GDA | 科六十三 K263 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K263_GDA | 23KV科六三線(K263) 接地RY | FEEDER |  |  |  |  | CDC | 492 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0923 |  | 0200 | 2-39-11 |  | 2-48 | 263 | 79 RY U/L | 科六十三 K263 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K263_79UL | 23KV科六三線(K263) 79RY U/L | FEEDER |  |  |  |  | CDC | 493 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0924 |  | 0201 | 2-39-12 |  | 2-49 | 263 | LCO 分流器 | 科六十三 K263 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K263_LCO_TAP | 23KV科六三線(K263) LCO TAP | FEEDER |  |  |  |  | CDC | 494 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | 264 | PHA | 科六十四 K264 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K264_PHA | 23KV科六四線(K264) 相間RY | FEEDER |  |  |  |  | CDC | 495 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | 264 | GDA | 科六十四 K264 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K264_GDA | 23KV科六四線(K264) 接地RY | FEEDER |  |  |  |  | CDC | 496 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0925 |  | 0202 | 2-39-13 |  | 2-4A | 264 | 79 RY U/L | 科六十四 K264 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K264_79UL | 23KV科六四線(K264) 79RY U/L | FEEDER |  |  |  |  | CDC | 497 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0926 |  | 0203 | 2-39-14 |  | 2-4B | 264 | LCO 分流器 | 科六十四 K264 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K264_LCO_TAP | 23KV科六四線(K264) LCO TAP | FEEDER |  |  |  |  | CDC | 498 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | 265 | PHA | 科六十五 K265 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K265_PHA | 23KV科六五線(K265) 相間RY | FEEDER |  |  |  |  | CDC | 499 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | 265 | GDA | 科六十五 K265 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K265_GDA | 23KV科六五線(K265) 接地RY | FEEDER |  |  |  |  | CDC | 500 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0927 |  | 0204 | 2-39-15 |  | 2-4C | 265 | 79 RY U/L | 科六十五 K265 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K265_79UL | 23KV科六五線(K265) 79RY U/L | FEEDER |  |  |  |  | CDC | 501 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0928 |  | 0205 | 2-3A-00 |  | 2-4D | 265 | LCO 分流器 | 科六十五 K265 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K265_LCO_TAP | 23KV科六五線(K265) LCO TAP | FEEDER |  |  |  |  | CDC | 502 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | 266 | PHA | 科六十六 K266 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K266_PHA | 23KV科六六線(K266) 相間RY | FEEDER |  |  |  |  | CDC | 503 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | 266 | GDA | 科六十六 K266 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K266_GDA | 23KV科六六線(K266) 接地RY | FEEDER |  |  |  |  | CDC | 504 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0929 |  | 0206 | 2-3A-01 |  | 2-4E | 266 | 79 RY U/L | 科六十六 K266 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K266_79UL | 23KV科六六線(K266) 79RY U/L | FEEDER |  |  |  |  | CDC | 505 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0930 |  | 0207 | 2-3A-02 |  | 2-4F | 266 | LCO 分流器 | 科六十六 K266 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K266_LCO_TAP | 23KV科六六線(K266) LCO TAP | FEEDER |  |  |  |  | CDC | 506 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | 267 | PHA | 科六十七 K267 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K267_PHA | 23KV科六七線(K267) 相間RY | FEEDER |  |  |  |  | CDC | 507 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | 267 | GDA | 科六十七 K267 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K267_GDA | 23KV科六七線(K267) 接地RY | FEEDER |  |  |  |  | CDC | 508 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0931 |  | 0208 | 2-3A-03 |  | 2-50 | 267 | 79 RY U/L | 科六十七 K267 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K267_79UL | 23KV科六七線(K267) 79RY U/L | FEEDER |  |  |  |  | CDC | 509 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0932 |  | 0209 | 2-3A-04 |  | 2-51 | 267 | LCO 分流器 | 科六十七 K267 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K267_LCO_TAP | 23KV科六七線(K267) LCO TAP | FEEDER |  |  |  |  | CDC | 510 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | 268 | PHA | 科六十八 K268 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K268_PHA | 23KV科六八線(K268) 相間RY | FEEDER |  |  |  |  | CDC | 511 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | 268 | GDA | 科六十八 K268 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K268_GDA | 23KV科六八線(K268) 接地RY | FEEDER |  |  |  |  | CDC | 512 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0933 |  | 0210 | 2-3A-05 |  | 2-52 | 268 | 79 RY U/L | 科六十八 K268 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K268_79UL | 23KV科六八線(K268) 79RY U/L | FEEDER |  |  |  |  | CDC | 513 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0934 |  | 0211 | 2-3A-06 |  | 2-53 | 268 | LCO 分流器 | 科六十八 K268 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K268_LCO_TAP | 23KV科六八線(K268) LCO TAP | FEEDER |  |  |  |  | CDC | 514 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | 271 | PHA | 科七十一 K271 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K271_PHA | 23KV科七一線(K271) 相間RY | FEEDER |  |  |  |  | CDC | 515 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | 271 | GDA | 科七十一 K271 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K271_GDA | 23KV科七一線(K271) 接地RY | FEEDER |  |  |  |  | CDC | 516 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0935 |  | 0212 | 2-3A-07 |  | 2-54 | 271 | 79 RY U/L | 科七十一 K271 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K271_79UL | 23KV科七一線(K271) 79RY U/L | FEEDER |  |  |  |  | CDC | 517 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0936 |  | 0213 | 2-3A-08 |  | 2-55 | 271 | LCO 分流器 | 科七十一 K271 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K271_LCO_TAP | 23KV科七一線(K271) LCO TAP | FEEDER |  |  |  |  | CDC | 518 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | 272 | PHA | 科七十二 K272 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K272_PHA | 23KV科七二線(K272) 相間RY | FEEDER |  |  |  |  | CDC | 519 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | 272 | GDA | 科七十二 K272 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K272_GDA | 23KV科七二線(K272) 接地RY | FEEDER |  |  |  |  | CDC | 520 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0937 |  | 0214 | 2-3A-09 |  | 2-56 | 272 | 79 RY U/L | 科七十二 K272 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K272_79UL | 23KV科七二線(K272) 79RY U/L | FEEDER |  |  |  |  | CDC | 521 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0938 |  | 0215 | 2-3A-10 |  | 2-57 | 272 | LCO 分流器 | 科七十二 K272 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K272_LCO_TAP | 23KV科七二線(K272) LCO TAP | FEEDER |  |  |  |  | CDC | 522 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-0A-05 |  |  | 273 | PHA | 科七十三 K273 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K273_PHA | 23KV科七三線(K273) 相間RY | FEEDER |  |  |  |  | CDC | 523 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 2-0A-06 |  |  | 273 | GDA | 科七十三 K273 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K273_GDA | 23KV科七三線(K273) 接地RY | FEEDER |  |  |  |  | CDC | 524 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0939 |  | 0216 | 2-3A-11 |  | 2-58 | 273 | 79 RY U/L | 科七十三 K273 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K273_79UL | 23KV科七三線(K273) 79RY U/L | FEEDER |  |  |  |  | CDC | 525 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0940 |  | 0217 | 2-3A-12 |  | 2-59 | 273 | LCO 分流器 | 科七十三 K273 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K273_LCO_TAP | 23KV科七三線(K273) LCO TAP | FEEDER |  |  |  |  | CDC | 526 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-0B-00 |  |  | 274 | PHA | 科七十四 K274 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K274_PHA | 23KV科七四線(K274) 相間RY | FEEDER |  |  |  |  | CDC | 527 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-0B-01 |  |  | 274 | GDA | 科七十四 K274 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K274_GDA | 23KV科七四線(K274) 接地RY | FEEDER |  |  |  |  | CDC | 528 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0941 |  | 0218 | 2-3A-13 |  | 2-5A | 274 | 79 RY U/L | 科七十四 K274 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K274_79UL | 23KV科七四線(K274) 79RY U/L | FEEDER |  |  |  |  | CDC | 529 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0942 |  | 0219 | 2-3A-14 |  | 2-5B | 274 | LCO 分流器 | 科七十四 K274 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K274_LCO_TAP | 23KV科七四線(K274) LCO TAP | FEEDER |  |  |  |  | CDC | 530 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-0C-01 |  |  | 275 | PHA | 科七十五 K275 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K275_PHA | 23KV科七五線(K275) 相間RY | FEEDER |  |  |  |  | CDC | 531 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-0C-02 |  |  | 275 | GDA | 科七十五 K275 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K275_GDA | 23KV科七五線(K275) 接地RY | FEEDER |  |  |  |  | CDC | 532 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0943 |  | 0220 | 2-3A-15 |  | 2-5C | 275 | 79 RY U/L | 科七十五 K275 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K275_79UL | 23KV科七五線(K275) 79RY U/L | FEEDER |  |  |  |  | CDC | 533 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0944 |  | 0221 | 2-3B-00 |  | 2-5D | 275 | LCO 分流器 | 科七十五 K275 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K275_LCO_TAP | 23KV科七五線(K275) LCO TAP | FEEDER |  |  |  |  | CDC | 534 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0356 |  |  | 2-0C-04 |  |  | 276 | PHA | 科七十六 K276 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K276_PHA | 23KV科七六線(K276) 相間RY | FEEDER |  |  |  |  | CDC | 535 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0357 |  |  | 2-0C-05 |  |  | 276 | GDA | 科七十六 K276 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K276_GDA | 23KV科七六線(K276) 接地RY | FEEDER |  |  |  |  | CDC | 536 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0945 |  | 0222 | 2-3B-01 |  | 2-5E | 276 | 79 RY U/L | 科七十六 K276 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K276_79UL | 23KV科七六線(K276) 79RY U/L | FEEDER |  |  |  |  | CDC | 537 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0946 |  | 0223 | 2-3B-02 |  | 2-5F | 276 | LCO 分流器 | 科七十六 K276 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K276_LCO_TAP | 23KV科七六線(K276) LCO TAP | FEEDER |  |  |  |  | CDC | 538 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 2-0C-07 |  |  | 277 | PHA | 科七十七 K277 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K277_PHA | 23KV科七七線(K277) 相間RY | FEEDER |  |  |  |  | CDC | 539 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0360 |  |  | 2-0D-00 |  |  | 277 | GDA | 科七十七 K277 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K277_GDA | 23KV科七七線(K277) 接地RY | FEEDER |  |  |  |  | CDC | 540 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0947 |  | 0224 | 2-3B-03 |  | 2-60 | 277 | 79 RY U/L | 科七十七 K277 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K277_79UL | 23KV科七七線(K277) 79RY U/L | FEEDER |  |  |  |  | CDC | 541 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0948 |  | 0225 | 2-3B-04 |  | 2-61 | 277 | LCO 分流器 | 科七十七 K277 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K277_LCO_TAP | 23KV科七七線(K277) LCO TAP | FEEDER |  |  |  |  | CDC | 542 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0362 |  |  | 2-0D-02 |  |  | 278 | PHA | 科七十八 K278 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K278_PHA | 23KV科七八線(K278) 相間RY | FEEDER |  |  |  |  | CDC | 543 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0363 |  |  | 2-0D-03 |  |  | 278 | GDA | 科七十八 K278 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K278_GDA | 23KV科七八線(K278) 接地RY | FEEDER |  |  |  |  | CDC | 544 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0949 |  | 0226 | 2-3B-05 |  | 2-62 | 278 | 79 RY U/L | 科七十八 K278 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K278_79UL | 23KV科七八線(K278) 79RY U/L | FEEDER |  |  |  |  | CDC | 545 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0950 |  | 0227 | 2-3B-06 |  | 2-63 | 278 | LCO 分流器 | 科七十八 K278 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K278_LCO_TAP | 23KV科七八線(K278) LCO TAP | FEEDER |  |  |  |  | CDC | 546 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0388 |  |  | 3-10-04 |  |  | F27 | PHA | 科7A線 K27A PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27A_PHA | 23KV科7A線(K27A) 相間RY | FEEDER |  |  |  |  | CDC | 547 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0389 |  |  | 3-10-05 |  |  | F27 | GDA | 科7A線 K27A GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27A_GDA | 23KV科7A線(K27A) 接地RY | FEEDER |  |  |  |  | CDC | 548 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0866 |  | 0322 | 3-36-02 |  | 3-42 | F27 | 79 RY U/L | 科7A線 K27A 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27A_79UL | 23KV科7A線(K27A) 79RY U/L | FEEDER |  |  |  |  | CDC | 549 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0867 |  | 0323 | 3-36-03 |  | 3-43 | F27 | LCO 分流器 | 科7A線 K27A LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27A_LCO_TAP | 23KV科7A線(K27A) LCO TAP | FEEDER |  |  |  |  | CDC | 550 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0392 |  |  | 3-11-00 |  |  | F28 | PHA | 科7B線 K27B PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27B_PHA | 23KV科7B線(K27B) 相間RY | FEEDER |  |  |  |  | CDC | 551 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0393 |  |  | 3-11-01 |  |  | F28 | GDA | 科7B線 K27B GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27B_GDA | 23KV科7B線(K27B) 接地RY | FEEDER |  |  |  |  | CDC | 552 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0868 |  | 0324 | 3-36-04 |  | 3-44 | F28 | 79 RY U/L | 科7B線 K27B 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27B_79UL | 23KV科7B線(K27B) 79RY U/L | FEEDER |  |  |  |  | CDC | 553 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0869 |  | 0325 | 3-36-05 |  | 3-45 | F28 | LCO 分流器 | 科7B線 K27B LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27B_LCO_TAP | 23KV科7B線(K27B) LCO TAP | FEEDER |  |  |  |  | CDC | 554 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0396 |  |  | 3-11-04 |  |  | F29 | PHA | 科7C線 K27C PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27C_PHA | 23KV科7C線(K27C) 相間RY | FEEDER |  |  |  |  | CDC | 555 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0397 |  |  | 3-11-05 |  |  | F29 | GDA | 科7C線 K27C GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27C_GDA | 23KV科7C線(K27C) 接地RY | FEEDER |  |  |  |  | CDC | 556 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0870 |  | 0326 | 3-36-06 |  | 3-46 | F29 | 79 RY U/L | 科7C線 K27C 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27C_79UL | 23KV科7C線(K27C) 79RY U/L | FEEDER |  |  |  |  | CDC | 557 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0871 |  | 0327 | 3-36-07 |  | 3-47 | F29 | LCO 分流器 | 科7C線 K27C LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27C_LCO_TAP | 23KV科7C線(K27C) LCO TAP | FEEDER |  |  |  |  | CDC | 558 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0400 |  |  | 3-12-00 |  |  | F30 | PHA | 科7D線 K27D PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27D_PHA | 23KV科7D線(K27D) 相間RY | FEEDER |  |  |  |  | CDC | 559 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0401 |  |  | 3-12-01 |  |  | F30 | GDA | 科7D線 K27D GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27D_GDA | 23KV科7D線(K27D) 接地RY | FEEDER |  |  |  |  | CDC | 560 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0872 |  | 0328 | 3-36-08 |  | 3-48 | F30 | 79 RY U/L | 科7D線 K27D 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27D_79UL | 23KV科7D線(K27D) 79RY U/L | FEEDER |  |  |  |  | CDC | 561 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0873 |  | 0329 | 3-36-09 |  | 3-49 | F30 | LCO 分流器 | 科7D線 K27D LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27D_LCO_TAP | 23KV科7D線(K27D) LCO TAP | FEEDER |  |  |  |  | CDC | 562 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0407 |  |  | 3-12-07 |  |  | F31 | PHA | 科21線 K221 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K221_PHA | 11KV科21線(K221) 相間RY | FEEDER |  |  |  |  | CDC | 563 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0408 |  |  | 3-13-00 |  |  | F31 | GDA | 科21線 K221 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K221_GDA | 11KV科21線(K221) 接地RY | FEEDER |  |  |  |  | CDC | 564 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0874 |  | 0330 | 3-36-10 |  | 3-4A | F31 | 79 RY U/L | 科21線 K221 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K221_79UL | 11KV科21線(K221) 79RY U/L | FEEDER |  |  |  |  | CDC | 565 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0875 |  | 0331 | 3-36-11 |  | 3-4B | F31 | LCO 分流器 | 科21線 K221 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K221_LCO_TAP | 11KV科21線(K221) LCO TAP | FEEDER |  |  |  |  | CDC | 566 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0411 |  |  | 3-13-03 |  |  | F32 | PHA | 科22線 K222 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K222_PHA | 11KV科22線(K222) 相間RY | FEEDER |  |  |  |  | CDC | 567 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0412 |  |  | 3-13-04 |  |  | F32 | GDA | 科22線 K222 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K222_GDA | 11KV科22線(K222) 接地RY | FEEDER |  |  |  |  | CDC | 568 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0876 |  | 0332 | 3-36-12 |  | 3-4C | F32 | 79 RY U/L | 科22線 K222 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K222_79UL | 11KV科22線(K222) 79RY U/L | FEEDER |  |  |  |  | CDC | 569 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0877 |  | 0333 | 3-36-13 |  | 3-4D | F32 | LCO 分流器 | 科22線 K222 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K222_LCO_TAP | 11KV科22線(K222) LCO TAP | FEEDER |  |  |  |  | CDC | 570 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0415 |  |  | 3-13-07 |  |  | F33 | PHA | 科23線 K223 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K223_PHA | 11KV科23線(K223) 相間RY | FEEDER |  |  |  |  | CDC | 571 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0416 |  |  | 3-14-00 |  |  | F33 | GDA | 科23線 K223 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K223_GDA | 11KV科23線(K223) 接地RY | FEEDER |  |  |  |  | CDC | 572 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0878 |  | 0334 | 3-36-14 |  | 3-4E | F33 | 79 RY U/L | 科23線 K223 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K223_79UL | 11KV科23線(K223) 79RY U/L | FEEDER |  |  |  |  | CDC | 573 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0879 |  | 0335 | 3-36-15 |  | 3-4F | F33 | LCO 分流器 | 科23線 K223 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K223_LCO_TAP | 11KV科23線(K223) LCO TAP | FEEDER |  |  |  |  | CDC | 574 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0419 |  |  | 3-14-03 |  |  | F34 | PHA | 科24線 K224 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K224_PHA | 11KV科24線(K224) 相間RY | FEEDER |  |  |  |  | CDC | 575 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0420 |  |  | 3-14-04 |  |  | F34 | GDA | 科24線 K224 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K224_GDA | 11KV科24線(K224) 接地RY | FEEDER |  |  |  |  | CDC | 576 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0880 |  | 0336 | 3-37-00 |  | 3-50 | F34 | 79 RY U/L | 科24線 K224 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K224_79UL | 11KV科24線(K224) 79RY U/L | FEEDER |  |  |  |  | CDC | 577 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0881 |  | 0337 | 3-37-01 |  | 3-51 | F34 | LCO 分流器 | 科24線 K224 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K224_LCO_TAP | 11KV科24線(K224) LCO TAP | FEEDER |  |  |  |  | CDC | 578 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0423 |  |  | 3-14-07 |  |  | F35 | PHA | 科25線 K225 PHA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K225_PHA | 11KV科25線(K225) 相間RY | FEEDER |  |  |  |  | CDC | 579 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0424 |  |  | 3-15-00 |  |  | F35 | GDA | 科25線 K225 GDA |  |  | B2/E02_D1 | [8 empty] | 南科ES.K225_GDA | 11KV科25線(K225) 接地RY | FEEDER |  |  |  |  | CDC | 580 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0882 |  | 0338 | 3-37-02 |  | 3-52 | F35 | 79 RY U/L | 科25線 K225 79 RY U/L |  |  | B2/E02_D1 | [8 empty] | 南科ES.K225_79UL | 11KV科25線(K225) 79RY U/L | FEEDER |  |  |  |  | CDC | 581 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | IED_ADJ |  |  | Status | LCO TAP | Use/Lock | Y | 7 | DI-SP | [6 empty] | 0883 |  | 0339 | 3-37-03 |  | 3-53 | F35 | LCO 分流器 | 科25線 K225 LCO 分流器 |  |  | B2/E02_D1 | [8 empty] | 南科ES.K225_LCO_TAP | 11KV科25線(K225) LCO TAP | FEEDER |  |  |  |  | CDC | 582 | DI_FEEDER(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/K251/T1 |  |  | 0259 |  | 0130 | 2-00-03 |  | 2-02 | 251 | ON/OFF | 科51線 K251 CB |  | aadb | B2/E02_D1 | [8 empty] | 南科ES.K251_CB | K251(23KV科51線) CB | FEEDER |  |  |  |  | CDC | 583 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 584 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 585 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/K252/T1 |  |  | 0262 |  | 0131 | 2-00-06 |  | 2-03 | 252 | ON/OFF | 科52線 K252 CB |  | aacb | B2/E02_D1 | [8 empty] | 南科ES.K252_CB | K252(23KV科52線) CB | FEEDER |  |  |  |  | CDC | 586 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 587 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 588 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/K253/T1 |  |  | 0265 |  | 0132 | 2-01-01 |  | 2-04 | 253 | ON/OFF | 科53線 K253 CB |  | aabb | B2/E02_D1 | [8 empty] | 南科ES.K253_CB | K253(23KV科53線) CB | FEEDER |  |  |  |  | CDC | 589 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 590 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 591 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | L/K254/T1 |  |  | 0268 |  | 0133 | 2-01-04 |  | 2-05 | 254 | ON/OFF | 科54線 K254 CB |  | aaab | B2/E02_D1 | [8 empty] | 南科ES.K254_CB | K254(23KV科54線) CB | FEEDER |  |  |  |  | CDC | 592 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 593 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 594 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/K216/T1 |  |  | 0274 |  | 0135 | 2-02-02 |  | 2-07 | 216 | ON/OFF | 科十六 K216 CB |  | abeb | B2/E02_D1 | [8 empty] | 南科ES.K216_CB | K216(11KV科十六線) CB | FEEDER |  |  |  |  | CDC | 595 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 596 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 597 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/K217/T1 |  |  | 0277 |  | 0136 | 2-02-05 |  | 2-08 | 217 | ON/OFF | 科十七 K217 CB |  | abfb | B2/E02_D1 | [8 empty] | 南科ES.K217_CB | K217(11KV科十七線) CB | FEEDER |  |  |  |  | CDC | 598 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 599 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 600 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/K218/T1 |  |  | 0280 |  | 0137 | 2-03-00 |  | 2-09 | 218 | ON/OFF | 科十八 K218 CB |  | abgb | B2/E02_D1 | [8 empty] | 南科ES.K218_CB | K218(11KV科十八線) CB | FEEDER |  |  |  |  | CDC | 601 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 602 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 603 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/K219/T1 |  |  | 0283 |  | 0138 | 2-03-03 |  | 2-0A | 219 | ON/OFF | 科十九 K219 CB |  | abhb | B2/E02_D1 | [8 empty] | 南科ES.K219_CB | K219(11KV科十九線) CB | FEEDER |  |  |  |  | CDC | 604 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 605 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 606 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | L/K220/T1 |  |  | 0286 |  | 0139 | 2-03-06 |  | 2-0B | 220 | ON/OFF | 科二十 K220 CB |  | abib | B2/E02_D1 | [8 empty] | 南科ES.K220_CB | K220(11KV科二十線) CB | FEEDER |  |  |  |  | CDC | 607 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 608 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 609 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/K261/T1 |  |  | 0295 |  | 0143 | 2-04-07 |  | 2-0F | 261 | ON/OFF | 科六十一 K261 CB |  | bafb | B2/E02_D1 | [8 empty] | 南科ES.K261_CB | K261(23KV科六一線) CB | FEEDER |  |  |  |  | CDC | 610 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 611 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 612 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/K262/T1 |  |  | 0298 |  | 0144 | 2-05-02 |  | 2-10 | 262 | ON/OFF | 科六十二 K262 CB |  | bagb | B2/E02_D1 | [8 empty] | 南科ES.K262_CB | K262(23KV科六二線) CB | FEEDER |  |  |  |  | CDC | 613 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 614 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 615 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/K263/T1 |  |  | 0301 |  | 0145 | 2-05-05 |  | 2-11 | 263 | ON/OFF | 科六十三 K263 CB |  | bahb | B2/E02_D1 | [8 empty] | 南科ES.K263_CB | K263(23KV科六三線) CB | FEEDER |  |  |  |  | CDC | 616 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 617 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 618 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | L/K264/T1 |  |  | 0304 |  | 0146 | 2-06-00 |  | 2-12 | 264 | ON/OFF | 科六十四 K264 CB |  | baib | B2/E02_D1 | [8 empty] | 南科ES.K264_CB | K264(23KV科六四線) CB | FEEDER |  |  |  |  | CDC | 619 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 620 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 621 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/K265/T1 |  |  | 0313 |  | 0149 | 2-07-01 |  | 2-15 | 265 | ON/OFF | 科六十五 K265 CB |  | bbfb | B2/E02_D1 | [8 empty] | 南科ES.K265_CB | K265(23KV科六五線) CB | FEEDER |  |  |  |  | CDC | 622 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 623 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 624 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/K266/T1 |  |  | 0316 |  | 0150 | 2-07-04 |  | 2-16 | 266 | ON/OFF | 科六十六 K266 CB |  | bbgb | B2/E02_D1 | [8 empty] | 南科ES.K266_CB | K266(23KV科六六線) CB | FEEDER |  |  |  |  | CDC | 625 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 626 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 627 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/K267/T1 |  |  | 0319 |  | 0151 | 2-07-07 |  | 2-17 | 267 | ON/OFF | 科六十七 K267 CB |  | bbhb | B2/E02_D1 | [8 empty] | 南科ES.K267_CB | K267(23KV科六七線) CB | FEEDER |  |  |  |  | CDC | 628 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 629 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 630 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | L/K268/T1 |  |  | 0322 |  | 0152 | 2-08-02 |  | 2-18 | 268 | ON/OFF | 科六十八 K268 CB |  | bbib | B2/E02_D1 | [8 empty] | 南科ES.K268_CB | K268(23KV科六八線) CB | FEEDER |  |  |  |  | CDC | 631 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 632 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 633 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | L/K271/T1 |  |  | 0334 |  | 0156 | 2-09-06 |  | 2-1C | 271 | ON/OFF | 科七十一 K271 CB |  | bcab | B2/E02_D1 | [8 empty] | 南科ES.K271_CB | K271(23KV科七一線) CB | FEEDER |  |  |  |  | CDC | 634 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 635 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 636 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | L/K272/T1 |  |  | 0337 |  | 0157 | 2-0A-01 |  | 2-1D | 272 | ON/OFF | 科七十二 K272 CB |  | bcbb | B2/E02_D1 | [8 empty] | 南科ES.K272_CB | K272(23KV科七二線) CB | FEEDER |  |  |  |  | CDC | 637 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 638 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 639 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | L/K273/T1 |  |  | 0340 |  | 0158 | 2-0A-04 |  | 2-1E | 273 | ON/OFF | 科七十三 K273 CB |  | bccb | B2/E02_D1 | [8 empty] | 南科ES.K273_CB | K273(23KV科七三線) CB | FEEDER |  |  |  |  | CDC | 640 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 641 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 642 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | L/K274/T1 |  |  | 0343 |  | 0159 | 2-0A-07 |  | 2-1F | 274 | ON/OFF | 科七十四 K274 CB |  | bcdb | B2/E02_D1 | [8 empty] | 南科ES.K274_CB | K274(23KV科七四線) CB | FEEDER |  |  |  |  | CDC | 643 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 644 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 645 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | L/K275/T1 |  |  | 0352 |  | 0163 | 2-0C-00 |  | 2-23 | 275 | ON/OFF | 科七十五 K275 CB |  | bdjb | B2/E02_D1 | [8 empty] | 南科ES.K275_CB | K275(23KV科七五線) CB | FEEDER |  |  |  |  | CDC | 646 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 647 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 648 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | L/K276/T1 |  |  | 0355 |  | 0164 | 2-0C-03 |  | 2-24 | 276 | ON/OFF | 科七十六 K276 CB |  | bdib | B2/E02_D1 | [8 empty] | 南科ES.K276_CB | K276(23KV科七六線) CB | FEEDER |  |  |  |  | CDC | 649 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 650 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 651 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | L/K277/T1 |  |  | 0358 |  | 0165 | 2-0C-06 |  | 2-25 | 277 | ON/OFF | 科七十七 K277 CB |  | bdhb | B2/E02_D1 | [8 empty] | 南科ES.K277_CB | K277(23KV科七七線) CB | FEEDER |  |  |  |  | CDC | 652 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 653 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 654 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | L/K278/T1 |  |  | 0361 |  | 0166 | 2-0D-01 |  | 2-26 | 278 | ON/OFF | 科七十八 K278 CB |  | bdgb | B2/E02_D1 | [8 empty] | 南科ES.K278_CB | K278(23KV科七八線) CB | FEEDER |  |  |  |  | CDC | 655 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 656 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 657 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | L/K27A/T1 |  |  | 0387 |  | 0305 | 3-10-03 |  | 3-31 | F27 | ON/OFF | 科7A線 K27A CB |  | acbb | B2/E02_D1 | [8 empty] | 南科ES.K27A_CB | K27A(23KV科7A線) CB | FEEDER |  |  |  |  | CDC | 658 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 659 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 660 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | L/K27B/T1 |  |  | 0391 |  | 0306 | 3-10-07 |  | 3-32 | F28 | ON/OFF | 科7B線 K27B CB |  | accb | B2/E02_D1 | [8 empty] | 南科ES.K27B_CB | K27B(23KV科7B線) CB | FEEDER |  |  |  |  | CDC | 661 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 662 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 663 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | L/K27C/T1 |  |  | 0395 |  | 0307 | 3-11-03 |  | 3-33 | F29 | ON/OFF | 科7C線 K27C CB |  | acdb | B2/E02_D1 | [8 empty] | 南科ES.K27C_CB | K27C(23KV科7C線) CB | FEEDER |  |  |  |  | CDC | 664 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 665 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 666 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | L/K27C/T1 |  |  | 0399 |  | 0308 | 3-11-07 |  | 3-34 | F30 | ON/OFF | 科7D線 K27D CB |  | aceb | B2/E02_D1 | [8 empty] | 南科ES.K27D_CB | K27D(23KV科7D線) CB | FEEDER |  |  |  |  | CDC | 667 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 668 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 669 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | L/K221/T1 |  |  | 0406 |  | 0310 | 3-12-06 |  | 3-36 | F31 | ON/OFF | 科21線 K221 CB |  | adib | B2/E02_D1 | [8 empty] | 南科ES.K221_CB | K221(11KV科21線) CB | FEEDER |  |  |  |  | CDC | 670 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 671 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 672 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | L/K222/T1 |  |  | 0410 |  | 0311 | 3-13-02 |  | 3-37 | F32 | ON/OFF | 科22線 K222 CB |  | adhb | B2/E02_D1 | [8 empty] | 南科ES.K222_CB | K222(11KV科22線) CB | FEEDER |  |  |  |  | CDC | 673 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 674 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 675 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | L/K223/T1 |  |  | 0414 |  | 0312 | 3-13-06 |  | 3-38 | F33 | ON/OFF | 科23線 K223 CB |  | adgb | B2/E02_D1 | [8 empty] | 南科ES.K223_CB | K223(11KV科23線) CB | FEEDER |  |  |  |  | CDC | 676 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 677 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 678 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | L/K224/T1 |  |  | 0418 |  | 0313 | 3-14-02 |  | 3-39 | F34 | ON/OFF | 科24線 K224 CB |  | adfb | B2/E02_D1 | [8 empty] | 南科ES.K224_CB | K224(11KV科24線) CB | FEEDER |  |  |  |  | CDC | 679 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 680 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 681 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | L/K225/T1 |  |  | 0422 |  | 0314 | 3-14-06 |  | 3-3A | F35 | ON/OFF | 科25線 K225 CB |  | adeb | B2/E02_D1 | [8 empty] | 南科ES.K225_CB | K225(11KV科25線) CB | FEEDER |  |  |  |  | CDC | 682 | DI_FEEDER(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | DS1 | (非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/E02_D1 | [16 empty] | 683 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_D1 | [16 empty] | 684 | DI_FEEDER(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1500 | R相電流 | 161KV TIE 1500 R相電流 | A_-2000_2000(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 685 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C20R1600 | 1520 | 1600 | 1760 | 1968 | 2.27 | -1520 | -1600 | -1760 | -1968 | 1 | 0.01 | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 1700 | R相電流 | 161KV TIE 1700 R相電流 | A_-3000_3000(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1700TIE_AMP | 1700TIE AMP | TIE |  |  |  |  | CDC | 686 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C30R2020 | 1919 | 2020 | 2222 | 2484.6 | 1.56 | -1919 | -2020 | -2222 | -2484.6 | 1 | 0.01 | C30R2020 | 1818.000000 | 1818.000000 | 2020.000000 | 3000.000000 | 1.560000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 1800 | R相電流 | 161KV TIE 1800 R相電流 | A_-3000_3000(-2000_2000) |  | B2/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.1800TIE_AMP | 1800TIE AMP | TIE |  |  |  |  | CDC | 687 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C30R2020 | 1919 | 2020 | 2222 | 2484.6 | 1.56 | -1919 | -2020 | -2222 | -2484.6 | 1 | 0.01 | C30R2020 | 1818.000000 | 1818.000000 | 2020.000000 | 3000.000000 | 1.560000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0334 |  |  | 3-CE |  |  | Locate Empty | R相電流 | 100 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_100_A1 | 23KV 100 R相AMP | TIE |  |  |  |  | CDC | 688 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0335 |  |  | 3-CF |  |  | Locate Empty | S相電流 | 100 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_100_A2 | 23KV 100 S相AMP | TIE |  |  |  |  | CDC | 689 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0336 |  |  | 3-D0 |  |  | Locate Empty | T相電流 | 100 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_100_A3 | 23KV 100 T相AMP | TIE |  |  |  |  | CDC | 690 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 200 | R相電流 | 200 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.11KV_200_A1 | 11KV 200 R相AMP | TIE |  |  |  |  | CDC | 691 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 200 | S相電流 | 200 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.11KV_200_A2 | 11KV 200 S相AMP | TIE |  |  |  |  | CDC | 692 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 200 | T相電流 | 200 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.11KV_200_A3 | 11KV 200 T相AMP | TIE |  |  |  |  | CDC | 693 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | 300 | R相電流 | 300 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_300_A1 | 23KV 300 R相AMP | TIE |  |  |  |  | CDC | 694 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 300 | S相電流 | 300 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_300_A2 | 23KV 300 S相AMP | TIE |  |  |  |  | CDC | 695 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 300 | T相電流 | 300 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_300_A3 | 23KV 300 T相AMP | TIE |  |  |  |  | CDC | 696 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | 400 | R相電流 | 400 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_400_A1 | 23KV 400 R相AMP | TIE |  |  |  |  | CDC | 697 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | 400 | S相電流 | 400 TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_400_A2 | 23KV 400 S相AMP | TIE |  |  |  |  | CDC | 698 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | 400 | T相電流 | 400 TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/E02_A1 |  |  | 2000 | [5 empty] | 南科ES.23KV_400_A3 | 23KV 400 T相AMP | TIE |  |  |  |  | CDC | 699 | AI_TIE23_11 |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0000 |  | 0005 | 1-00-00 |  | 1-05 | 1500 | ON/OFF | 161KV TIE 1500 CB |  | aagz | B2/E02_A1 | [8 empty] | 南科ES.1500_CB | 1500(TIE) CB | TIE |  |  |  |  | CDC | 700 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 1500 | 50A | 161KV TIE 1500 50A |  |  | B2/E02_A1 | [8 empty] | 南科ES.1500_50A | 161KV TIE(1500) 50RY | TIE |  |  |  |  | CDC | 701 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1Bus | B/3Bus |  |  | 0044 |  | 0012 | 1-05-04 |  | 1-0C | 1700 | ON/OFF | 161KV TIE 1700 CB |  | no rule | B2/E02_A1 | [8 empty] | 南科ES.1700_CB | 1700(TIE) CB | TIE |  |  |  |  | CDC | 702 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/2Bus | B/4Bus |  |  | 0046 |  | 0013 | 1-05-06 |  | 1-0D | 1800 | ON/OFF | 161KV TIE 1800 CB |  | no rule | B2/E02_A1 | [8 empty] | 南科ES.1800_CB | 1800(TIE) CB | TIE |  |  |  |  | CDC | 703 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1BBus | B/4BBus |  |  | 0292 |  | 0140 | 2-04-04 |  | 2-0C | 200 | ON/OFF | 200 TIE CB |  | abjb | B3/E02_A1 | [8 empty] | 南科ES.200_CB | 200(TIE) CB | TIE |  |  |  |  | CDC | 704 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | 200 | PHA | 200 TIE PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.200_51A | 11KV TIE(200) 51RY | TIE |  |  |  |  | CDC | 705 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | 200 | GDA | 200 TIE GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.200_51NA | 11KV TIE(200) 51N RY | TIE |  |  |  |  | CDC | 706 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/2BBus | B/3ABus |  |  | 0331 |  | 0153 | 2-09-03 |  | 2-19 | 300 | ON/OFF | 300 TIE CB |  | bbjb | B3/E02_A1 | [8 empty] | 南科ES.300_CB | 300(TIE) CB | TIE |  |  |  |  | CDC | 707 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | 300 | PHA | 300 TIE PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.300_51A | 11KV TIE(300) 51RY | TIE |  |  |  |  | CDC | 708 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | 300 | GDA | 300 TIE GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.300_51NA | 11KV TIE(300) 51N RY | TIE |  |  |  |  | CDC | 709 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/3BBus | B/2ABus |  |  | 0370 |  | 0160 | 2-0E-02 |  | 2-20 | 400 | ON/OFF | 400 TIE CB |  | bdab | B3/E02_A1 | [8 empty] | 南科ES.400_CB | 400(TIE) CB | TIE |  |  |  |  | CDC | 710 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0371 |  |  | 2-0E-03 |  |  | 400 | PHA | 400 TIE PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.400_51A | 23KV TIE(400) 51RY | TIE |  |  |  |  | CDC | 711 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0372 |  |  | 2-0E-04 |  |  | 400 | GDA | 400 TIE GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.400_51NA | 23KV TIE(400) 51N RY | TIE |  |  |  |  | CDC | 712 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect1B | B/1ABus | B/4ABUS |  |  | 0373 |  | 0167 | 2-0E-05 |  | 2-27 | 100 | ON/OFF | 100 TIE CB |  | aajb | B3/E02_A1 | [8 empty] | 南科ES.100_CB | 100(TIE) CB | TIE |  |  |  |  | CDC | 713 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0374 |  |  | 2-0E-06 |  |  | 100 | PHA | 100 TIE PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.100_51A | 23KV TIE(100) 51RY | TIE |  |  |  |  | CDC | 714 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0375 |  |  | 2-0E-07 |  |  | 100 | GDA | 100 TIE GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.100_51NA | 23KV TIE(100) 51N RY | TIE |  |  |  |  | CDC | 715 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 673 | 0056 | 1-3A-00 | 1-3A-01 | 1-38 | 1501 |  | 161KV TIE 1501 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1501_DS | 1501(TIE) DS | TIE |  |  |  |  | CDC | 716 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0674 | 675 | 0057 | 1-3A-02 | 1-3A-03 | 1-39 | 1502 |  | 161KV TIE 1502 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1502_DS | 1502(TIE) DS | TIE |  |  |  |  | CDC | 717 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 718 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 719 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0724 | 725 | 0082 | 1-3D-04 | 1-3D-05 | 1-52 | 1701 |  | 161KV TIE 1701 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1701_DS | 1701(TIE) DS | TIE |  |  |  |  | CDC | 720 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | DS2 | 1703 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0726 | 727 | 0083 | 1-3D-06 | 1-3D-07 | 1-53 | 1703 |  | 161KV TIE 1703 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1703_DS | 1703(TIE) DS | TIE |  |  |  |  | CDC | 721 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | E1 | 1701E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 722 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | E2 | 1703E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 723 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | DS1 | 1802 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0728 | 729 | 0084 | 1-3D-08 | 1-3D-09 | 1-54 | 1802 |  | 161KV TIE 1802 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1802_DS | 1802(TIE) DS | TIE |  |  |  |  | CDC | 724 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1804 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0730 | 731 | 0085 | 1-3D-10 | 1-3D-11 | 1-55 | 1804 |  | 161KV TIE 1804 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1804_DS | 1804(TIE) DS | TIE |  |  |  |  | CDC | 725 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | E1 | 1802E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 726 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | E2 | 1804E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 727 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | DS1 | 101(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 728 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | E1 | 101E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 729 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | DS1 | 201(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 730 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | E1 | 201E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 731 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | DS1 | 301(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 732 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | E1 | 301E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 733 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | DS1 | 401(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 734 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | E1 | 401E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 735 | DI_TIE(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 310 | 瓦 | 310 M1A 瓦 | MW_-108_108(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR |  |  |  |  | CDC | 736 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 310 | 乏 | 310 M1A 乏 | MVAR_-72_72(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR |  |  |  |  | CDC | 737 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 310 | R相電流 | 310 M1A R相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR |  |  |  |  | CDC | 738 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 310 | S相電流 | 310 M1A S相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR |  |  |  |  | CDC | 739 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 310 | T相電流 | 310 M1A T相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR |  |  |  |  | CDC | 740 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 320 | 瓦 | 320 M1B 瓦 | MW_-54_54(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR |  |  |  |  | CDC | 741 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 320 | 乏 | 320 M1B 乏 | MVAR_-36_36(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR |  |  |  |  | CDC | 742 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 320 | R相電流 | 320 M1B R相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR |  |  |  |  | CDC | 743 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 320 | S相電流 | 320 M1B S相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR |  |  |  |  | CDC | 744 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 320 | T相電流 | 320 M1B T相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR |  |  |  |  | CDC | 745 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(330) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 340 | 瓦 | #2 DTTr.二次側 瓦 | MW_-108_108(-2000_2000) |  | B3/E02_A1 | 60 |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#2DTR_MW | #2DTR二次側 MW | MTR |  |  |  |  | CDC | 746 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(330) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 340 | 乏 | #2 DTTr.二次側 乏 | MVAR_-72_72(-2000_2000) |  | B3/E02_A1 | 60 |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#2DTR_MVAR | #2DTR二次側 MVAR | MTR |  |  |  |  | CDC | 747 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(330) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 340 | R相電流 | #2 DTTr.二次側 R相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#2DTR_A1 | #2DTR二次側 R相AMP | MTR |  |  |  |  | CDC | 748 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(330) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 340 | S相電流 | #2 DTTr.二次側 S相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#2DTR_A2 | #2DTR二次側 S相AMP | MTR |  |  |  |  | CDC | 749 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(330) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | 340 | T相電流 | #2 DTTr.二次側 T相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#2DTR_A3 | #2DTR二次側 T相AMP | MTR |  |  |  |  | CDC | 750 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(350) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 350 | 瓦 | #3 DTTr.二次側 瓦 | MW_-108_108(-2000_2000) |  | B3/E02_A1 | 60 |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#3DTR_MW | #3DTR二次側 MW | MTR |  |  |  |  | CDC | 751 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(350) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 350 | 乏 | #3 DTTr.二次側 乏 | MVAR_-72_72(-2000_2000) |  | B3/E02_A1 | 60 |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#3DTR_MVAR | #3DTR二次側 MVAR | MTR |  |  |  |  | CDC | 752 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(350) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 350 | R相電流 | #3 DTTr.二次側 R相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#3DTR_A1 | #3DTR二次側 R相AMP | MTR |  |  |  |  | CDC | 753 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(350) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 350 | S相電流 | #3 DTTr.二次側 S相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#3DTR_A2 | #3DTR二次側 S相AMP | MTR |  |  |  |  | CDC | 754 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(350) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 350 | T相電流 | #3 DTTr.二次側 T相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 60 |  |  | 1500 | 1000 | 南科ES.#3DTR_A3 | #3DTR二次側 T相AMP | MTR |  |  |  |  | CDC | 755 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0258 |  |  | 3-82 |  |  | 370 | 瓦 | #4DTR 4A 370 瓦 | MW_-108_108(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(A)_MW | #4DTR二次側(A) MW | MTR |  |  |  |  | CDC | 756 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.216 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | 370 | 乏 | #4DTR 4A 370 乏 | MVAR_-72_72(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(A)_MVAR | #4DTR二次側(A) MVAR | MTR |  |  |  |  | CDC | 757 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 370 | R相電流 | #4DTR 4A 370 R相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(A)_A1 | #4DTR二次側(A) R相AMP | MTR |  |  |  |  | CDC | 758 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 370 | S相電流 | #4DTR 4A 370 S相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(A)_A2 | #4DTR二次側(A) S相AMP | MTR |  |  |  |  | CDC | 759 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 370 | T相電流 | #4DTR 4A 370 T相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(A)_A3 | #4DTR二次側(A) T相AMP | MTR |  |  |  |  | CDC | 760 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | MW |  | B2,B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0289 |  |  | 3-A1 |  |  | 380 | 瓦 | #4DTR 4B 380 瓦 | MW_-54_54(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(B)_MW | #4DTR二次側(B) MW | MTR |  |  |  |  | CDC | 761 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | MVAR |  | B2,B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0290 |  |  | 3-A2 |  |  | 380 | 乏 | #4DTR 4B 380 乏 | MVAR_-36_36(-2000_2000) |  | B3/E02_A1 | 30 |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(B)_MVAR | #4DTR二次側(B) MVAR | MTR |  |  |  |  | CDC | 762 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | I_R |  | B2,B3 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0291 |  |  | 3-A3 |  |  | 380 | R相電流 | #4DTR 4B 380 R相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(B)_A1 | #4DTR二次側(B) R相AMP | MTR |  |  |  |  | CDC | 763 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | I_S |  | B2,B3 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0292 |  |  | 3-A4 |  |  | 380 | S相電流 | #4DTR 4B 380 S相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(B)_A2 | #4DTR二次側(B) S相AMP | MTR |  |  |  |  | CDC | 764 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | I_T |  | B2,B3 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0293 |  |  | 3-A5 |  |  | 380 | T相電流 | #4DTR 4B 380 T相電流 | A_-3000_3000(-2000_2000) |  | B3/E02_A1 |  |  | 3000 | 30 |  |  | 1500 | 1000 | 南科ES.#4DTR(B)_A3 | #4DTR二次側(B) T相AMP | MTR |  |  |  |  | CDC | 765 | AI_MTR161(1) |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | Locate Empty | 油溫 | #1DTR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_OIL | #1DTR 油溫 | MTR |  |  |  |  | CDC | 766 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | Locate Empty | 線溫 | #1ADTR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR |  |  |  |  | CDC | 767 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0054 |  | 0029 | 1-B6 |  | 1-1D | Locate Empty | TAP位置 | #1ADTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR |  |  |  |  | CDC | 768 | AI_MTR161(2) |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | Locate Empty | 線溫 | #1BDTR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR |  |  |  |  | CDC | 769 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0055 |  | 0031 | 1-B7 |  | 1-1F | Locate Empty | TAP位置 | #1BDTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR |  |  |  |  | CDC | 770 | AI_MTR161(2) |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | Locate Empty | 油溫 | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_OIL | #2DTR 油溫 | MTR |  |  |  |  | CDC | 771 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 2DTR | #2DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | Locate Empty | 線溫 | #2DTR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_COIL | #2DTR 線溫 | MTR |  |  |  |  | CDC | 772 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 2DTR | #2DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0058 |  | 0033 | 1-BA |  | 1-21 | Locate Empty | TAP位置 | #2DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_TAP | #2DTR OLTC TAP | MTR |  |  |  |  | CDC | 773 | AI_MTR161(2) |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | Locate Empty | 油溫 | #3DTR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_OIL | #3DTR 油溫 | MTR |  |  |  |  | CDC | 774 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 3DTR | #3DTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | Locate Empty | 線溫 | #3DTR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_COIL | #3DTR 線溫 | MTR |  |  |  |  | CDC | 775 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 3DTR | #3DTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0061 |  | 0035 | 1-BD |  | 1-23 | Locate Empty | TAP位置 | #3DTR TAP位置 | TAP_-8.5_8.5(0_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_TAP | #3DTR OLTC TAP | MTR |  |  |  |  | CDC | 776 | AI_MTR161(2) |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | Locate Empty | 油溫 | #4DTR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_OIL | #4DTR 油溫 | MTR |  |  |  |  | CDC | 777 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | Locate Empty | 線溫 | #4DTR 4A 線溫 | COIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(A)_COIL | #4DTR(A) 線溫 | MTR |  |  |  |  | CDC | 778 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0067 |  | 0037 | 1-C3 |  | 1-25 | Locate Empty | TAP位置 | #4DTR 4A TAP位置 | TAP_-8.5_8.5(0_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(A)_TAP | #4DTR(A) OLTC TAP | MTR |  |  |  |  | CDC | 779 | AI_MTR161(2) |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | Locate Empty | 線溫 | #4DTR 4B 線溫 | COIL_-120_120(-2000_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(B)_COIL | #4DTR(B) 線溫 | MTR |  |  |  |  | CDC | 780 | AI_MTR161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0068 |  | 0039 | 1-C4 |  | 1-27 | Locate Empty | TAP位置 | #4DTR 4B TAP位置 | TAP_-8.5_8.5(0_2000) |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(B)_TAP | #4DTR(B) OLTC TAP | MTR |  |  |  |  | CDC | 781 | AI_MTR161(2) |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0058 |  | 0016 | 1-07-02 |  | 1-10 | 1750 | ON/OFF | #1DTR 1750 CB |  | aacb | ELEM/E02_A1 | [8 empty] | 南科ES.1750_CB | 1750(#1DTR) CB | MTR |  |  |  |  | CDC | 782 | DI_MTR161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 783 | DI_MTR161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/2DTR |  | 0072 |  | 0019 | 1-09-00 |  | 1-13 | 1760 | ON/OFF | #2DTR 1760 CB |  | abcb | ELEM/E02_A1 | [8 empty] | 南科ES.1760_CB | 1760(#2DTR) CB | MTR |  |  |  |  | CDC | 784 | DI_MTR161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 785 | DI_MTR161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/3DTR |  | 0086 |  | 0022 | 1-0A-06 |  | 1-16 | 1770 | ON/OFF | #3DTR 1770 CB |  | abhb | ELEM/E02_A1 | [8 empty] | 南科ES.1770_CB | 1770(#3DTR) CB | MTR |  |  |  |  | CDC | 786 | DI_MTR161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 787 | DI_MTR161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4DTR |  | 0100 |  | 0025 | 1-0C-04 |  | 1-19 | 1780 | ON/OFF | #4DTR 1780 CB |  | aadb | ELEM/E02_A1 | [8 empty] | 南科ES.1780_CB | 1780(#4DTR) CB | MTR |  |  |  |  | CDC | 788 | DI_MTR161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 789 | DI_MTR161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1DTR(A) |  |  | 0066 |  | 0017 | 1-08-02 |  | 1-11 | 310 | ON/OFF | 310 M1A CB |  | aaia | B3/E02_A1 | [8 empty] | 南科ES.310_CB | 310(#1DTR) CB | MTR |  |  |  |  | CDC | 790 | DI_MTR161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | A/340^T/2DTR(A) |  |  | 0080 |  | 0020 | 1-0A-00 |  | 1-14 | 330 | ON/OFF | 330 M2A CB |  | baaa | B3/E02_A1 | [8 empty] | 南科ES.330_CB | 330(#2DTR) CB | MTR |  |  |  |  | CDC | 791 | DI_MTR161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | A/330^T/2DTR(B) |  |  | 0083 |  | 0021 | 1-0A-03 |  | 1-15 | 340 | ON/OFF | 340 M2B CB |  | bbaa | B3/E02_A1 | [8 empty] | 南科ES.340_CB | 340(#2DTR) CB | MTR |  |  |  |  | CDC | 792 | DI_MTR161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | A/360^T/3DTR(A) |  |  | 0094 |  | 0023 | 1-0B-06 |  | 1-17 | 350 | ON/OFF | 350 M3A CB |  | bcia | B3/E02_A1 | [8 empty] | 南科ES.350_CB | 350(#3DTR) CB | MTR |  |  |  |  | CDC | 793 | DI_MTR161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | A/350^T/3DTR(B) |  |  | 0097 |  | 0024 | 1-0C-01 |  | 1-18 | 360 | ON/OFF | 360 M3B CB |  | bdba | B3/E02_A1 | [8 empty] | 南科ES.360_CB | 360(#3DTR) CB | MTR |  |  |  |  | CDC | 794 | DI_MTR161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | T/4DTR(A) |  |  | 0108 |  | 0026 | 1-0D-04 |  | 1-1A | Locate Empty | ON/OFF | #4DTR 4A 370 CB |  | acga | B3/E02_A1 | [8 empty] | 南科ES.370_CB | 370(#4DTR) CB | MTR |  |  |  |  | CDC | 795 | DI_MTR161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | T/1DTR(B) |  |  | 0069 |  | 0018 | 1-08-05 |  | 1-12 | 320 | ON/OFF | 320 M1B CB |  | abaa | B3/E02_A1 | [8 empty] | 南科ES.320_CB | 320(#1DTR) CB | MTR |  |  |  |  | CDC | 796 | DI_MTR161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | T/4DTR(B) |  |  | 0111 |  | 0027 | 1-0D-07 |  | 1-1B | Locate Empty | ON/OFF | #4DTR 4B 380 CB |  | adaa | B3/E02_A1 | [8 empty] | 南科ES.380_CB | 380(#4DTR) CB | MTR |  |  |  |  | CDC | 797 | DI_MTR161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 1750 | PHA | #1DTR 1750 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_51A | #1DTR 51RY | MTR |  |  |  |  | CDC | 798 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0063 |  |  | 1-07-07 |  |  | 1750 | GDA | #1DTR 1750 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_51NA | #1DTR 51N RY | MTR |  |  |  |  | CDC | 799 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | Locate Empty | 51ZA | #1DTR 51ZA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_51ZA | #1DTR 51Z RY | MTR |  |  |  |  | CDC | 800 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | Locate Empty | 87A | #1DTR 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_87A | #1DTR 87RY | MTR |  |  |  |  | CDC | 801 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | Locate Empty | 87S | #1DTR 87S |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER |  |  |  |  | CDC | 802 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 1760 | PHA | #2DTR 1760 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_51A | #2DTR 51RY | MTR |  |  |  |  | CDC | 803 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 1760 | GDA | #2DTR 1760 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_51NA | #2DTR 51N RY | MTR |  |  |  |  | CDC | 804 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0075 |  |  | 1-09-03 |  |  | Locate Empty | 51ZA | #2DTR 51ZA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_51ZA | #2DTR 51Z RY | MTR |  |  |  |  | CDC | 805 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | Locate Empty | 87A | #2DTR 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_87A | #2DTR 87RY | MTR |  |  |  |  | CDC | 806 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0574 |  |  | 1-33-14 |  |  | Locate Empty | 87S | #2DTR 87S |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER |  |  |  |  | CDC | 807 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 1770 | PHA | #3DTR 1770 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_51A | #3DTR 51RY | MTR |  |  |  |  | CDC | 808 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 1770 | GDA | #3DTR 1770 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_51NA | #3DTR 51N RY | MTR |  |  |  |  | CDC | 809 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | Locate Empty | 51ZA | #3DTR 51ZA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_51ZA | #3DTR 51Z RY | MTR |  |  |  |  | CDC | 810 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | Locate Empty | 87A | #3DTR 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_87A | #3DTR 87RY | MTR |  |  |  |  | CDC | 811 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0584 |  |  | 1-34-08 |  |  | Locate Empty | 87S | #3DTR 87S |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER |  |  |  |  | CDC | 812 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | 1780 | PHA | #4DTR 1780 PHA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_51A | #4DTR 51RY | MTR |  |  |  |  | CDC | 813 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 1780 | GDA | #4DTR 1780 GDA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_51NA | #4DTR 51N RY | MTR |  |  |  |  | CDC | 814 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | Locate Empty | 51ZA | #4DTR 51ZA |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_51ZA | #4DTR 51Z RY | MTR |  |  |  |  | CDC | 815 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | Locate Empty | 87A | #4DTR 87A |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_87A | #4DTR 87RY | MTR |  |  |  |  | CDC | 816 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0594 |  |  | 1-35-02 |  |  | Locate Empty | 87S | #4DTR 87S |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#4DTR_187UL | 161KV #4DTR 187RY U/L | OTHER |  |  |  |  | CDC | 817 | DI_MTR161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA | 51A1 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 310 | PHA | #1DTR 二次 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.310_51A | #1DTR二次側(310) 51RY | MTR |  |  |  |  | CDC | 818 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA | 51A1 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 320 | PHA | #1DTR 二次 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.320_51A | #1DTR二次側(320) 51RY | MTR |  |  |  |  | CDC | 819 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA | 51A1 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 330 | PHA | #2DTR 二次 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.330_51A | #2DTR二次側(330) 51RY | MTR |  |  |  |  | CDC | 820 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA | 51A2 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 340 | PHA | #2DTR 二次 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.340_51A | #2DTR二次側(340) 51RY | MTR |  |  |  |  | CDC | 821 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA | 51A1 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 350 | PHA | #3DTR 二次 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.350_51A | #3DTR二次側(350) 51RY | MTR |  |  |  |  | CDC | 822 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA | 51A2 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 360 | PHA | #3DTR 二次 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.360_51A | #3DTR二次側(360) 51RY | MTR |  |  |  |  | CDC | 823 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | PHA | 51A1 | Element | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | Locate Empty | PHA | #4DTR 二次 370 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.370_51A | #4DTR二次側(370) 51RY | MTR |  |  |  |  | CDC | 824 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | GDA | 51A1 | Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | Locate Empty | GDA | #4DTR 二次 380 PHA(3相) |  |  | B3/E02_A1 | [8 empty] | 南科ES.380_51A | #4DTR二次側(380) 51RY | MTR |  |  |  |  | CDC | 825 | DI_MTR161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | Locate Empty | 96PA | #1DTR 機械保護動作(96PA) |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_96PA | #1DTR 機械保護動作 | MTR |  |  |  |  | CDC | 826 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0571 |  |  | 1-33-11 |  |  | Locate Empty | 96D | #1DTR 96D |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_96D | #1DTR 96D RY | MTR |  |  |  |  | CDC | 827 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0572 |  |  | 1-33-12 |  |  | Locate Empty | 96P | #1DTR 96P |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_96P | #1DTR 96P RY | MTR |  |  |  |  | CDC | 828 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0573 |  |  | 1-33-13 |  |  | Locate Empty | 63Q | #1DTR 63Q |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_63Q | #1DTR 63Q RY | MTR |  |  |  |  | CDC | 829 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0569 |  |  | 1-33-09 |  |  | Locate Empty | 96B1 | #1DTR 96B1 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_96B1 | #1DTR 96B1 RY | MTR |  |  |  |  | CDC | 830 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0570 |  |  | 1-33-10 |  |  | Locate Empty | 96B2 | #1DTR 96B2 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_96B2 | #1DTR 96B2 RY | MTR |  |  |  |  | CDC | 831 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | Locate Empty | 96PA | #2DTR 機械保護動作(96PA) |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_96PA | #2DTR 機械保護動作 | MTR |  |  |  |  | CDC | 832 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0581 |  |  | 1-34-05 |  |  | Locate Empty | 96D | #2DTR 96D |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_96D | #2DTR 96D RY | MTR |  |  |  |  | CDC | 833 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0582 |  |  | 1-34-06 |  |  | Locate Empty | 96P | #2DTR 96P |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_96P | #2DTR 96P RY | MTR |  |  |  |  | CDC | 834 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0583 |  |  | 1-34-07 |  |  | Locate Empty | 63Q | #2DTR 63Q |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_63Q | #2DTR 63Q RY | MTR |  |  |  |  | CDC | 835 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0579 |  |  | 1-34-03 |  |  | Locate Empty | 96B1 | #2DTR 96B1 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_96B1 | #2DTR 96B1 RY | MTR |  |  |  |  | CDC | 836 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0580 |  |  | 1-34-04 |  |  | Locate Empty | 96B2 | #2DTR 96B2 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_96B2 | #2DTR 96B2 RY | MTR |  |  |  |  | CDC | 837 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | Locate Empty | 96PA | #3DTR 機械保護動作(96PA) |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_96PA | #3DTR 機械保護動作 | MTR |  |  |  |  | CDC | 838 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0591 |  |  | 1-34-15 |  |  | Locate Empty | 96D | #3DTR 96D |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_96D | #3DTR 96D RY | MTR |  |  |  |  | CDC | 839 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0592 |  |  | 1-35-00 |  |  | Locate Empty | 96P | #3DTR 96P |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_96P | #3DTR 96P RY | MTR |  |  |  |  | CDC | 840 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0593 |  |  | 1-35-01 |  |  | Locate Empty | 63Q | #3DTR 63Q |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_63Q | #3DTR 63Q RY | MTR |  |  |  |  | CDC | 841 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0589 |  |  | 1-34-13 |  |  | Locate Empty | 96B1 | #3DTR 96B1 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_96B1 | #3DTR 96B1 RY | MTR |  |  |  |  | CDC | 842 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0590 |  |  | 1-34-14 |  |  | Locate Empty | 96B2 | #3DTR 96B2 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_96B2 | #3DTR 96B2 RY | MTR |  |  |  |  | CDC | 843 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | Locate Empty | 96PA | #4DTR 機械保護動作(96PA) |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_96PA | #4DTR 機械保護動作 | MTR |  |  |  |  | CDC | 844 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0603 |  |  | 1-35-11 |  |  | #4DTR | 96D | #4DTR 放壓裝置 96D |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_96D | #4DTR 96D RY | MTR |  |  |  |  | CDC | 845 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0604 |  |  | 1-35-12 |  |  | #4DTR | 96P | #4DTR 衝擊油壓 96P |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_96P | #4DTR 96P RY | MTR |  |  |  |  | CDC | 846 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0605 |  |  | 1-35-13 |  |  | #4DTR | 63Q | #4DTR OLTC 63Q |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_63Q | #4DTR 63Q RY | MTR |  |  |  |  | CDC | 847 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0601 |  |  | 1-35-09 |  |  | #4DTR | 96B1 | #4DTR 撲氣電驛1 96B1 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_96B1 | #4DTR 96B1 RY | MTR |  |  |  |  | CDC | 848 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0602 |  |  | 1-35-10 |  |  | #4DTR | 96B2 | #4DTR 撲氣電驛2 96B2 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_96B2 | #4DTR 96B2 RY | MTR |  |  |  |  | CDC | 849 | DI_MTR161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0568 |  |  | 1-33-08 |  |  | Locate Empty | 重故障 | #1DTR TRA 重故障 |  | a | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_TRA | #1DTR 重故障 | MTR |  |  |  |  | CDC | 850 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0567 |  |  | 1-33-07 |  |  | Locate Empty | 輕故障 | #1DTR TRF 輕故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR_TRF | #1DTR 輕故障 | MTR |  |  |  |  | CDC | 851 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  | B2,B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | Locate Empty | S/L | #1ATR OLTC S/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR |  |  |  |  | CDC | 852 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  | B2,B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | Locate Empty | S/L | #1BTR OLTC S/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR |  |  |  |  | CDC | 853 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | B2,B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0564 |  | 0028 | 1-33-04 |  | 1-1C | Locate Empty | A/M | #1ATR OLTC A/M |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR |  |  |  |  | CDC | 854 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | B2,B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0566 |  | 0030 | 1-33-06 |  | 1-1E | Locate Empty | A/M | #1BTR OLTC A/M |  |  | B2/E02_A1 | [8 empty] | 南科ES.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR |  |  |  |  | CDC | 855 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E02 | 南科ES |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0578 |  |  | 1-34-02 |  |  | Locate Empty | 重故障 | #2DTR TRA 重故障 |  | a | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_TRA | #2DTR 重故障 | MTR |  |  |  |  | CDC | 856 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0577 |  |  | 1-34-01 |  |  | Locate Empty | 輕故障 | #2DTR TRF 輕故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_TRF | #2DTR 輕故障 | MTR |  |  |  |  | CDC | 857 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 2DTR | #2DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0575 |  |  | 1-33-15 |  |  | Locate Empty | S/L | #2DTR OLTC S/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_S/L | #2DTR OLTC S/L | MTR |  |  |  |  | CDC | 858 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES |  |  | 2DTR | #2DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0576 |  | 0032 | 1-34-00 |  | 1-20 | Locate Empty | A/M | #2DTR OLTC A/M |  |  | B2/E02_A1 | [8 empty] | 南科ES.#2DTR_A/M | #2DTR OLTC A/M | MTR |  |  |  |  | CDC | 859 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E02 | 南科ES |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR |  |  |  |  | 0587 |  |  | 1-34-11 |  |  | Locate Empty | 重故障 | #3DTR TRA 重故障 |  | a | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_TRA | #3DTR 重故障 | MTR |  |  |  |  | CDC | 860 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0586 |  |  | 1-34-10 |  |  | Locate Empty | 輕故障 | #3DTR TRF 輕故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_TRF | #3DTR 輕故障 | MTR |  |  |  |  | CDC | 861 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 3DTR | #3DTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0585 |  |  | 1-34-09 |  |  | Locate Empty | S/L | #3DTR OLTC S/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_S/L | #3DTR OLTC S/L | MTR |  |  |  |  | CDC | 862 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES |  |  | 3DTR | #3DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0588 |  | 0034 | 1-34-12 |  | 1-22 | Locate Empty | A/M | #3DTR OLTC A/M |  |  | B2/E02_A1 | [8 empty] | 南科ES.#3DTR_A/M | #3DTR OLTC A/M | MTR |  |  |  |  | CDC | 863 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E02 | 南科ES |  |  | 4DTR | #4DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0600 |  |  | 1-35-08 |  |  | #4DTR | 重故障 | #4DTR TRA 重故障 |  | a | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_TRA | #4DTR 重故障 | MTR |  |  |  |  | CDC | 864 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR | #4DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0599 |  |  | 1-35-07 |  |  | #4DTR | 輕故障 | #4DTR TRF 輕故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR_TRF | #4DTR 輕故障 | MTR |  |  |  |  | CDC | 865 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | SupLocal |  | B2,B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0595 |  |  | 1-35-03 |  |  | #4DTR | S/L | #4DTR 4A OLTC S/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(A)_S/L | #4DTR(A) OLTC S/L | MTR |  |  |  |  | CDC | 866 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | SupLocal |  | B2,B3 | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0597 |  |  | 1-35-05 |  |  | #4DTR | S/L | #4DTR 4B OLTC S/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(B)_S/L | #4DTR(B) OLTC S/L | MTR |  |  |  |  | CDC | 867 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | Tap Chan |  | B2,B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0596 |  | 0036 | 1-35-04 |  | 1-24 | #4DTR | A/M | #4DTR 4A OLTC A/M |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(A)_A/M | #4DTR(A) OLTC A/M | MTR |  |  |  |  | CDC | 868 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | Tap Chan |  | B2,B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0598 |  | 0038 | 1-35-06 |  | 1-26 | #4DTR | A/M | #4DTR 4B OLTC A/M |  |  | B2/E02_A1 | [8 empty] | 南科ES.#4DTR(B)_A/M | #4DTR(B) OLTC A/M | MTR |  |  |  |  | CDC | 869 | DI_MTR161(7) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0748 | 749 | 0096 | 1-3E-12 | 1-3E-13 | 1-60 | 1751 |  | #1DTR 1751 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1751_DS | 1751(#1DTR) DS | MTR |  |  |  |  | CDC | 870 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0750 | 751 | 0097 | 1-3E-14 | 1-3E-15 | 1-61 | 1752 |  | #1DTR 1752 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1752_DS | 1752(#1DTR) DS | MTR |  |  |  |  | CDC | 871 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 872 | DI_MTR161(8) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0752 | 753 | 0098 | 1-3F-00 | 1-3F-01 | 1-62 | 1761 |  | #2DTR 1761 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1761_DS | 1761(#2DTR) DS | MTR |  |  |  |  | CDC | 873 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0754 | 755 | 0099 | 1-3F-02 | 1-3F-03 | 1-63 | 1762 |  | #2DTR 1762 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1762_DS | 1762(#2DTR) DS | MTR |  |  |  |  | CDC | 874 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 875 | DI_MTR161(8) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0756 | 757 | 0100 | 1-3F-04 | 1-3F-05 | 1-64 | 1771 |  | #3DTR 1771 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1771_DS | 1771(#3DTR) DS | MTR |  |  |  |  | CDC | 876 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0758 | 759 | 0101 | 1-3F-06 | 1-3F-07 | 1-65 | 1772 |  | #3DTR 1772 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1772_DS | 1772(#3DTR) DS | MTR |  |  |  |  | CDC | 877 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 878 | DI_MTR161(8) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0760 | 761 | 0102 | 1-3F-08 | 1-3F-09 | 1-66 | 1781 |  | #4DTR 1781 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1781_DS | 1781(#4DTR) DS | MTR |  |  |  |  | CDC | 879 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0762 | 763 | 0103 | 1-3F-10 | 1-3F-11 | 1-67 | 1782 |  | #4DTR 1782 DS |  |  | B2/E02_A1 | [8 empty] | 南科ES.1782_DS | 1782(#4DTR) DS | MTR |  |  |  |  | CDC | 880 | DI_MTR161(8) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E02_A1 | [16 empty] | 881 | DI_MTR161(8) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | DS1 | 311(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 882 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | BE0 | 311E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 883 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | DS1 | 321(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 884 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | BE0 | 321E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 885 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | DS1 | 331(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 886 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | BE0 | 331E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 887 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | DS1 | 341(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 888 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | BE0 | 341E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 889 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | DS1 | 351(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 890 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | BE0 | 351E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 891 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | DS1 | 361(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 892 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | BE0 | 361E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 893 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | DS1 | 371(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 894 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | BE0 | 371E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 895 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | DS1 | 381(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 896 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | BE0 | 381E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 897 | DI_MTR161(9) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 190 | #1SSTR(190) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | T/1SSTR |  |  | 0256 |  | 0129 | 2-00-00 |  | 2-01 | 190 | ON/OFF | 190 #1SSTR CB |  | aaeb | B3/E02_A1 | [8 empty] | 南科ES.190_CB | 190(#1SSTR) CB | OTHER |  |  |  |  | CDC | 898 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 190 | #1SSTR(190) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 190 | PHA | 190 #1SSTR PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 899 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 190 | #1SSTR(190) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | 190 | GDA | 190 #1SSTR GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#1SSTR_51NA | #1SSTR 51N RY | OTHER |  |  |  |  | CDC | 900 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 190 | #1SSTR(190) |  | DS1 | 191(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 901 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 190 | #1SSTR(190) |  | BE0 | 191E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 902 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 390 | #3SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | T/3SSTR |  |  | 0328 |  | 0148 | 2-09-00 |  | 2-14 | 390 | ON/OFF | 390 #3SSTR CB |  | bbeb | B3/E02_A1 | [8 empty] | 南科ES.390_CB | 390(#3SSTR) CB | OTHER |  |  |  |  | CDC | 903 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 390 | #3SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | 390 | PHA | 390 #3SSTR PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#3SSTR_51A | #3SSTR 51RY | OTHER |  |  |  |  | CDC | 904 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 390 | #3SSTR(390) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | 390 | GDA | 390 #3SSTR GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#3SSTR_51NA | #3SSTR 51N RY | OTHER |  |  |  |  | CDC | 905 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 390 | #3SSTR(390) |  | DS1 | 391(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 906 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 390 | #3SSTR(390) |  | BE0 | 391E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 907 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 490 | #4SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | T/4SSTR |  |  | 0384 |  | 0304 | 3-10-00 |  | 3-30 | 490 | ON/OFF | 490 #4SSTR CB |  | acab | B3/E02_A1 | [8 empty] | 南科ES.490_CB | 490(#4SSTR) CB | OTHER |  |  |  |  | CDC | 908 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 490 | #4SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0385 |  |  | 3-10-01 |  |  | 490 | PHA | 490 #4SSTR PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#4SSTR_51A | #4SSTR 51RY | OTHER |  |  |  |  | CDC | 909 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 490 | #4SSTR(490) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0386 |  |  | 3-10-02 |  |  | 490 | GDA | 490 #4SSTR GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#4SSTR_51NA | #4SSTR 51N RY | OTHER |  |  |  |  | CDC | 910 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 490 | #4SSTR(490) |  | DS1 | 491(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 911 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 490 | #4SSTR(490) |  | BE0 | 491E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 912 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 290 | #2SSTR(290) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | T/2SSTR |  |  | 0367 |  | 0162 | 2-0D-07 |  | 2-22 | 290 | ON/OFF | 290 #2SSTR CB |  | bddb | B3/E02_A1 | [8 empty] | 南科ES.290_CB | 290(#2SSTR) CB | OTHER |  |  |  |  | CDC | 913 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 290 | #2SSTR(290) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0368 |  |  | 2-0E-00 |  |  | 290 | PHA | 290 #2SSTR PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 914 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 290 | #2SSTR(290) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0369 |  |  | 2-0E-01 |  |  | 290 | GDA | 290 #2SSTR GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.#2SSTR_51NA | #2SSTR 51N RY | OTHER |  |  |  |  | CDC | 915 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 290 | #2SSTR(290) |  | DS1 | 291(非取樣點) | Add | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 916 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 290 | #2SSTR(290) |  | BE0 | 291E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 917 | DI_SSTR(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1ABus | C/1SC |  |  | 0271 |  | 0128 | 2-01-07 |  | 2-00 | 210 | ON/OFF | 210 #1SC CB |  | aahb | B3/E02_A1 |  | 9 | [6 empty] | 南科ES.210_CB | 210(23KV #1SC) CB | SC |  |  |  |  | CDC | 918 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | E1 | 211E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 919 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/1BBus | A/LBS220^C/2SC(A) |  |  | 0289 |  | 0134 | 2-04-01 |  | 2-06 | 220 | ON/OFF | 220 #2SC CB |  | abdb | B3/E02_A1 |  | 6 | [6 empty] | 南科ES.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 920 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | E1 | 221E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 921 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2ABus | C/3SC |  |  | 0307 |  | 0141 | 2-06-03 |  | 2-0D | 230 | ON/OFF | 230 #3SC CB |  | babb | B3/E02_A1 |  | 9 | [6 empty] | 南科ES.230_CB | 230(23KV #3SC) CB | SC |  |  |  |  | CDC | 922 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | E1 | 231E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 923 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/2BBus | C/4SC |  |  | 0325 |  | 0147 | 2-08-05 |  | 2-13 | 240 | ON/OFF | 240 #4SC CB |  | bbdb | B3/E02_A1 |  | 9 | [6 empty] | 南科ES.240_CB | 240(23KV #4SC) CB | SC |  |  |  |  | CDC | 924 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | E1 | 241E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 925 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3ABus | C/5SC |  |  | 0346 |  | 0154 | 2-0B-02 |  | 2-1A | 250 | ON/OFF | 250 #5SC CB |  | bcfb | B3/E02_A1 |  | 9 | [6 empty] | 南科ES.250_CB | 250(23KV #5SC) CB | SC |  |  |  |  | CDC | 926 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | E1 | 251E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 927 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/3BBus | C/6SC |  |  | 0364 |  | 0161 | 2-0D-04 |  | 2-21 | 260 | ON/OFF | 260 #6SC CB |  | bdcb | B3/E02_A1 |  | 9 | [6 empty] | 南科ES.260_CB | 260(23KV #6SC) CB | SC |  |  |  |  | CDC | 928 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | E1 | 261E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 929 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4ABus | C/7SC |  |  | 0403 |  | 0309 | 3-12-03 |  | 3-35 | 270 | ON/OFF | #7SC 270 CB |  | acfb | B3/E02_A1 |  | 9 | [6 empty] | 南科ES.270_CB | 270(23KV #7SC) CB | SC |  |  |  |  | CDC | 930 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | E1 | 271E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 931 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1BbD | B/4BBus | A/LBS280^C/8SC(A) |  |  | 0426 |  | 0315 | 3-15-02 |  | 3-3B | 280 | ON/OFF | #8SC 280 CB |  | adbb | B3/E02_A1 |  | 6 | [6 empty] | 南科ES.280_CB | 280(11KV #8SC) CB | SC |  |  |  |  | CDC | 932 | DI_SC(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | E1 | 281E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 933 | DI_SC(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | 210 | SCA | 210 #1SC SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.210_SCA | 23KV #1SC 51,51N RY | SC |  |  |  |  | CDC | 934 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0273 |  |  | 2-02-01 |  |  | 210 | UVA | 210 #1SC UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.210_UVA | 23KV #1SC 27RY(欠壓) | SC |  |  |  |  | CDC | 935 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | CE0 | 210SC_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 936 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | 220 | SCA | 220 #2SC SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.220_SCA | 11KV #2SC 51,51N RY | SC |  |  |  |  | CDC | 937 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | 220 | UVA | 220 #2SC UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.220_UVA | 11KV #2SC 27RY(欠壓) | SC |  |  |  |  | CDC | 938 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 280 | #2SC(280) |  | CE0 | 220SC1_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 939 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | 230 | SCA | 230 #3SC SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.230_SCA | 23KV #3SC 51,51N RY | SC |  |  |  |  | CDC | 940 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | 230 | UVA | 230 #3SC UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.230_UVA | 23KV #3SC 27RY(欠壓) | SC |  |  |  |  | CDC | 941 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | CE0 | 230SC_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 942 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | 240 | SCA | 240 #4SC SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.240_SCA | 23KV #4SC 51,51N RY | SC |  |  |  |  | CDC | 943 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | 240 | UVA | 240 #4SC UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.240_UVA | 23KV #4SC 27RY(欠壓) | SC |  |  |  |  | CDC | 944 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | CE0 | 240SC_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 945 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0347 |  |  | 2-0B-03 |  |  | 250 | SCA | 250 #5SC SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.250_SCA | 23KV #5SC 51,51N RY | SC |  |  |  |  | CDC | 946 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0348 |  |  | 2-0B-04 |  |  | 250 | UVA | 250 #5SC UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.250_UVA | 23KV #5SC 27RY(欠壓) | SC |  |  |  |  | CDC | 947 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | CE0 | 250SC_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 948 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0365 |  |  | 2-0D-05 |  |  | 260 | SCA | 260 #6SC SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.260_SCA | 23KV #6SC 51,51N RY | SC |  |  |  |  | CDC | 949 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0366 |  |  | 2-0D-06 |  |  | 260 | UVA | 260 #6SC UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.260_UVA | 23KV #6SC 27RY(欠壓) | SC |  |  |  |  | CDC | 950 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | CE0 | 260SC_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 951 | DI_SC(3) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0404 |  |  | 3-12-04 |  |  | 270 | SCA | #7SC 270 SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.270_SCA | 23KV #7SC 51,51N RY | SC |  |  |  |  | CDC | 952 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0405 |  |  | 3-12-05 |  |  | 270 | UVA | #7SC 270 UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.270_UVA | 23KV #7SC 27RY(欠壓) | SC |  |  |  |  | CDC | 953 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 280 | #2SC(280) |  | SCA |  | B3 | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0427 |  |  | 3-15-03 |  |  | 280 | SCA | #8SC 280 SCA |  |  | B3/E02_A1 | [8 empty] | 南科ES.280_SCA | 11KV #8SC 51,51N RY | SC |  |  |  |  | CDC | 954 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 280 | #2SC(280) |  | UVA |  | B3 | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0428 |  |  | 3-15-04 |  |  | 280 | UVA | #8SC 280 UVA |  |  | B3/E02_A1 | [8 empty] | 南科ES.280_UVA | 11KV #8SC 27RY(欠壓) | SC |  |  |  |  | CDC | 955 | DI_SC(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | D1 | 211(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 956 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | D1 | 221(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 957 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | D1 | 231(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 958 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | D1 | 241(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 959 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | D1 | 251(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 960 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | D1 | 261(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 961 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | D1 | 271(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 962 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | D1 | 281(非取樣點) |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 963 | DI_SC(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | LBS220 | #2SC(220) |  | LBS |  | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/220 | C/2SC(B) |  |  | 0850 | 851 | 0301 | 3-35-02 | 3-35-03 | 3-2D | 220 | LBS | 220 #2SC LBS |  |  | B3/E02_A1 | [8 empty] | 南科ES.220_LBS | 220(11KV #2SC) LBS | SC |  |  |  |  | CDC | 964 | DI_SC(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | CE0 | 220SC2_ES(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 965 | DI_SC(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | LBS280 | #8SC(280) |  | LBS | 280 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP |  | Bay1BbLBS | A/280 | C/8SC(B) |  |  | 0852 | 853 | 0316 | 3-35-04 | 3-35-05 | 3-3C | 280 | LBS | #8SC 280 CB LBS |  |  | B3/E02_A1 | [8 empty] | 南科ES.280_LBS | 280(11KV #8SC) LBS | SC |  |  |  |  | CDC | 966 | DI_SC(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | Locate Empty |  | Card 1 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 967 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | Locate Empty |  | Card 1 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 968 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | Locate Empty |  | Card 2 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 969 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | Locate Empty |  | Card 2 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 970 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | Locate Empty |  | Card 3 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 971 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | Locate Empty |  | Card 3 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 972 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | Locate Empty |  | Card 4 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 973 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | Locate Empty |  | Card 4 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 974 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | Locate Empty |  | Card X-1 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER |  |  |  |  | CDC | 975 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | Locate Empty |  | Card X-1 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER |  |  |  |  | CDC | 976 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCL6 | [14 empty] | 0320 |  |  | 3-C0 |  |  | Locate Empty |  | Card 19-2 ADCL1 | ADCL_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCL6 | AI 10%參考點 ADCL6 | OTHER |  |  |  |  | CDC | 977 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | RTU | RTU |  | ADCH6 | [14 empty] | 0321 |  |  | 3-C1 |  |  | Locate Empty |  | Card 19-2 ADCH1 | ADCH_-2000_2000(-2000_2000) |  | B3/E02_A1 | [8 empty] | 南科ES.AI_ADCH6 | AI 90%參考點 ADCH6 | OTHER |  |  |  |  | CDC | 978 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES |  |  | 1DTR | #1DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0250 |  |  | 2-FA |  |  | Locate Empty | TOG | #1DTR TCG |  |  | B2/E02_A1 | [15 empty] | CDC | 979 | AI_OTHERS(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES |  |  | 4DTR | #4DTR |  | Tap Chan |  |  | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0253 |  |  | 2-FD |  |  | Locate Empty |  | SPARE |  |  | B2/E02_A1 | [15 empty] | CDC | 980 | AI_OTHERS(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | Locate Empty |  | DC-P 電壓 | kV_-150_150(-2000_2000) |  | ELEM/E02_A1 | [8 empty] | 南科ES.直流P電源電壓 | 直流P電源電壓 | OTHER |  |  |  |  | CDC | 981 | AI_DC_SOURCE |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | Locate Empty |  | DC-N 電壓 | kV_-150_150(-2000_2000) |  | ELEM/E02_A1 | [8 empty] | 南科ES.直流N電源電壓 | 直流N電源電壓 | OTHER |  |  |  |  | CDC | 982 | AI_DC_SOURCE |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | Locate Empty | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 南科ES.TEST_CB | TEST CB | OTHER |  |  |  |  | CDC | 983 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | Locate Empty | ON/OFF | L/R STATUS |  |  | B3/E02_A1 | [8 empty] | 南科ES.RTU_S/L | RTU SUPY/LOCAL | OTHER |  |  |  |  | CDC | 984 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0114 |  |  | 1-0E-02 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B2/E02_A1 | [8 empty] | 南科ES.161KV_OSCA | 161KV示波器啟動警報 | OTHER |  |  |  |  | CDC | 985 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | BFA |  |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0115 |  |  | 1-0E-03 |  |  | Locate Empty |  | BFA 161KV B.F. RY |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.161KV_BFA | 161KV斷路器失靈(BF)RY | OTHER |  |  |  |  | CDC | 986 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0116 |  |  | 1-0E-04 |  |  | Locate Empty |  | RCA 161KV 復閉失敗 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 987 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0898 |  |  | 2-38-02 |  |  | Locate Empty | 復閉失敗 | 23LOA 23KV 復閉失敗 |  |  | B3/E02_A1 | [8 empty] | 南科ES.FEEDER_RCA | 饋線復閉電驛動作(23KV) | FEEDER |  |  |  |  | CDC | 988 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | PSA |  |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0979 |  |  | 2-3D-03 |  |  | Locate Empty | 重故障 | PSA 其他重故障 |  |  | B3/E02_A1 | [8 empty] | 南科ES.其他重故障 | 變電所內其他重故障 | OTHER |  |  |  |  | CDC | 989 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | PSF |  |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0978 |  |  | 2-3D-02 |  |  | Locate Empty | 輕故障 | PSF 其他輕故障 |  |  | B3/E02_A1 | [8 empty] | 南科ES.其他輕故障 | 變電所內其他輕故障 | OTHER |  |  |  |  | CDC | 990 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0980 |  |  | 2-3D-04 |  |  | Locate Empty | 無人化門禁一 | DOOR1 無人化門禁一 |  |  | B3/E02_A1 | [8 empty] | 南科ES.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER |  |  |  |  | CDC | 991 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0981 |  |  | 2-3D-05 |  |  | Locate Empty | 無人化門禁二 | DOOR2 無人化門禁二 |  |  | B3/E02_A1 | [8 empty] | 南科ES.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER |  |  |  |  | CDC | 992 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0982 |  |  | 2-3D-06 |  |  | Locate Empty | 無人化門禁三 | DOOR3 無人化門禁三 |  |  | B3/E02_A1 | [8 empty] | 南科ES.無人化門禁(3) | 無人化門禁(3) | OTHER |  |  |  |  | CDC | 993 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0986 |  |  | 2-3D-10 |  |  | Locate Empty | 無人化防盜一 | 無人化防盜一 |  |  | B3/E02_A1 | [8 empty] | 南科ES.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER |  |  |  |  | CDC | 994 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0987 |  |  | 2-3D-11 |  |  | Locate Empty | 無人化防盜二 | 無人化防盜二 |  |  | B3/E02_A1 | [8 empty] | 南科ES.無人化防盜(2) | 無人化防盜(2)sp | OTHER |  |  |  |  | CDC | 995 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0988 |  |  | 2-3D-12 |  |  | Locate Empty | 無人化防盜三 | 無人化防盜三 |  |  | B3/E02_A1 | [8 empty] | 南科ES.無人化防盜(3) | 無人化防盜(3)sp | OTHER |  |  |  |  | CDC | 996 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0510 |  | 0302 | 3-3B-14 |  | 3-2E | Locate Empty | ON/OFF | FLA 開關場照明(A) |  |  | B3/E02_A1 | [8 empty] | 南科ES.開關場照明(A) | 開關場照明(A) | OTHER |  |  |  |  | CDC | 997 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0511 |  | 0303 | 3-3B-15 |  | 3-2F | Locate Empty | ON/OFF | FLB 開關場照明(B) |  |  | B3/E02_A1 | [8 empty] | 南科ES.開關場照明(B) | 開關場照明(B) | OTHER |  |  |  |  | CDC | 998 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0983 |  |  | 2-3D-07 |  |  | 火災警報(1) |  | 火災警報(1)受信總機 |  |  | B3/E02_A1 | [8 empty] | 南科ES.火災警報(1) | 火災警報(1)受信總機 | OTHER |  |  |  |  | CDC | 999 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0984 |  |  | 2-3D-08 |  |  | 火災警報(2) |  | 火災警報(2)建物-B棟 |  |  | B3/E02_A1 | [8 empty] | 南科ES.火災警報(2) | 火災警報(2)建物B棟 | OTHER |  |  |  |  | CDC | 1000 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0985 |  |  | 2-3D-09 |  |  | 火災警報(3) |  | 火災警報(3)消防閘門動作 |  |  | B3/E02_A1 | [8 empty] | 南科ES.火災警報(3) | 火災警報(3)消防閘門動作 | OTHER |  |  |  |  | CDC | 1001 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0630 |  |  | 1-37-06 |  |  | Locate Empty | 充電電纜 | OPA 充電電纜(無接線) |  |  | B3/E02_A1 | [8 empty] | 南科ES.充油電纜OPA | 充油電纜低油壓警報 | OTHER |  |  |  |  | CDC | 1002 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0967 |  | 0168 | 2-3C-07 |  | 2-28 | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/E02_A1 | [8 empty] | 南科ES.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 1003 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0968 |  | 0169 | 2-3C-08 |  | 2-29 | ACB TIE | ON/OFF | 所內電源ACB TIE |  |  | B3/E02_A1 | [8 empty] | 南科ES.所內電源ACBT | 所內電源開關ACB TIE | OTHER |  |  |  |  | CDC | 1004 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0969 |  | 0170 | 2-3C-09 |  | 2-2A | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/E02_A1 | [8 empty] | 南科ES.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 1005 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0621 |  |  | 1-36-13 |  |  | Locate Empty | ACB 警報 | ACBA ACB 警報 |  |  | B3/E02_A1 | [8 empty] | 南科ES.所內電源ACBA | 所內電源故障警報 | OTHER |  |  |  |  | CDC | 1006 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0970 |  |  | 2-3C-10 |  |  | Locate Empty | 所內欠壓 | STUV 所內欠壓 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.所內電源欠壓 | 所內電源欠壓警報 | OTHER |  |  |  |  | CDC | 1007 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0622 |  |  | 1-36-14 |  |  | Locate Empty | 直流跳脫 | DCA 直流跳脫 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.直流電源DCA | 直流電源故障警報 | OTHER |  |  |  |  | CDC | 1008 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0619 |  |  | 1-36-11 |  |  | Locate Empty | 直流接地 | DCE 直流接地 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.直流電源DCE | 直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 1009 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0613 |  |  | 1-36-05 |  |  | Locate Empty | 重故障 | CBA 161KV CB重故障 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.161KV_CBA | 161KV斷路器重故障 | OTHER |  |  |  |  | CDC | 1010 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0612 |  |  | 1-36-04 |  |  | Locate Empty | 輕故障 | CBF 161KV CB輕故障 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.161KV_CBF | 161KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 1011 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0896 |  |  | 2-38-00 |  |  | Locate Empty | ON/OFF | 23CBA 23KV CB 重故障 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER |  |  |  |  | CDC | 1012 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0897 |  |  | 2-38-01 |  |  | Locate Empty | ON/OFF | 23CBF 23KV CB 輕故障 |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 1013 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0966 |  |  | 2-3C-06 |  |  | Locate Empty | 同步校核超時 | 25TA 同步校核超時 |  |  | B3/E02_A1 | [8 empty] | 南科ES.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER |  |  |  |  | CDC | 1014 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0965 |  |  | 2-3C-05 |  |  | Locate Empty | 同步校核故障 | 25PFA 同步校核故障 |  |  | B3/E02_A1 | [8 empty] | 南科ES.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER |  |  |  |  | CDC | 1015 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0625 |  |  | 1-37-01 |  |  | Locate Empty | 洩油池警報 | WSF 洩油池警報 |  |  | B3/E02_A1 | [8 empty] | 南科ES.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 1016 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0614 |  |  | 1-36-06 |  |  | Locate Empty | 空壓機 | COMT 161KV 空壓機 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER |  |  |  |  | CDC | 1017 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0624 |  |  | 1-37-00 |  |  | Locate Empty | 60RY | 60A 23KV 60RY |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.23KV_SC_60A | 23/11KV SC 60A | OTHER |  |  |  |  | CDC | 1018 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0991 |  |  | 2-3D-15 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B2/E02_A1 | [8 empty] | 南科ES.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER |  |  |  |  | CDC | 1019 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | CHG1_1 | #1充電機故障 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0620 |  |  | 1-36-12 |  |  | Locate Empty | 變電用充電機 | CHG1 變電用充電機 |  |  | B3/E02_A1 | [8 empty] | 南科ES.ㄧ號充電機故障 | ㄧ號充電機故障 | OTHER |  |  |  |  | CDC | 1020 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | CHG1_2 | #2充電機故障 | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0631 |  |  | 1-37-07 |  |  | Locate Empty | 充電機警報 | CHG2 充電機警報 |  |  | B3/E02_A1 | [8 empty] | 南科ES.二號充電機故障 | 二號充電機故障 | OTHER |  |  |  |  | CDC | 1021 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | 7A5Other | 空調機故障 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0629 |  |  | 1-37-05 |  |  | Locate Empty | 空調機故障 | 空調機故障 |  |  | B3/E02_A1 | [8 empty] | 南科ES.空調機故障 | 空調機故障或電源跳脫 | OTHER |  |  |  |  | CDC | 1022 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 310 | PHA | 310 M1A PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.310_PHA2 | 310開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1023 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 310 | GDA | 310 M1A GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.310_GDA | 310開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1024 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 320 | PHA | 320 M1B PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.320_PHA2 | 320開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1025 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 320 | GDA | 320 M1B GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.320_GDA | 320開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1026 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 330 | PHA | 330 M2A PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.330_PHA2 | 330開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1027 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 330 | GDA | 330 M2A GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.330_GDA | 330開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1028 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 340 | PHA | 340 M2B PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.340_PHA2 | 340開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1029 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 340 | GDA | 340 M2B GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.340_GDA | 340開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1030 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0095 |  |  | 1-0B-07 |  |  | 350 | PHA | 350 M3A PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.350_PHA2 | 350開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1031 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-0C-00 |  |  | 350 | GDA | 350 M3A GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.350_GDA | 350開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1032 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | 360 | PHA | 360 M3B PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.360_PHA2 | 360開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1033 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 360 | GDA | 360 M3B GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.360_GDA | 360開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1034 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | Locate Empty | PHA | #4DTR 4A 370 PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.370_PHA2 | 370開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1035 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | GDA |  | B2,B3,Element | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | Locate Empty | GDA | #4DTR 4A 370 GDA |  |  | B3/E02_A1 | [8 empty] | 南科ES.370_GDA | 370開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 1036 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0112 |  |  | 1-0E-00 |  |  | Locate Empty | PHA | #4DTR 4B 380 PHA |  |  | B3/E02_A1 | [8 empty] | 南科ES.380_PHA2 | 380開關箱IED RY PHA | OTHER |  |  |  |  | CDC | 1037 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0971 |  |  | 2-3C-11 |  |  | Locate Empty | 水位警報一 | OW1 水位警報一 |  |  | B3/E02_A1 | [8 empty] | 南科ES.OW1 | 水位警報1 | OTHER |  |  |  |  | CDC | 1038 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0972 |  |  | 2-3C-12 |  |  | Locate Empty | 水位警報二 | OW2 水位警報二 |  |  | B3/E02_A1 | [8 empty] | 南科ES.OW2 | 水位警報2 | OTHER |  |  |  |  | CDC | 1039 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | DS2 | 102(非取樣點) | B2,B3,Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 1040 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 100 | TIE(100) |  | E2 | 102E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 1041 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | DS2 | 202(非取樣點) | B2,B3,Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 1042 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 11 | 11kV | 200 | TIE(200) |  | E2 | 202E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 1043 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | DS2 | 302(非取樣點) | B2,B3,Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 1044 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 300 | TIE(300) |  | E2 | 302E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 1045 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | DS2 | 402(非取樣點) | B2,B3,Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B3/E02_A1 | [16 empty] | 1046 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 22 | 22kV | 400 | TIE(400) |  | E2 | 402E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E02_A1 | [16 empty] | 1047 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | 1510 | 87CFA | 南科道爺一路 1510 電驛通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_87CFA | 南科道爺ㄧ路(1510)87RY通訊故障 | OTHER |  |  |  |  | CDC | 1048 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | 1510 | RYFA | 南科道爺一路 1510 電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1510_RYFA | 南科道爺ㄧ路(1510)數位電驛故障 | OTHER |  |  |  |  | CDC | 1049 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | 1520 | 87CFA | 南科道爺二路 1520 電驛通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_87CFA | 南科道爺二路(1520)87RY通訊故障 | OTHER |  |  |  |  | CDC | 1050 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 1520 | RYFA | 南科道爺二路 1520 電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1520_RYFA | 南科道爺二路(1520)數位電驛故障 | OTHER |  |  |  |  | CDC | 1051 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | 1570 | 87CFA | 南科道爺三路 1570 87 CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_87CFA | 南科道爺三路(1570)87RY通訊故障 | OTHER |  |  |  |  | CDC | 1052 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | 1570 | RYFA | 南科道爺三路 1570 RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1570_RYFA | 南科道爺三路(1570)數位電驛故障 | OTHER |  |  |  |  | CDC | 1053 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | 1580 | 87CFA | 南科道爺四路 1580 87 CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_87CFA | 南科道爺四路(1580)87RY通訊故障 | OTHER |  |  |  |  | CDC | 1054 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | 1580 | RYFA | 南科道爺四路 1580 RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1580_RYFA | 南科道爺四路(1580)數位電驛故障 | OTHER |  |  |  |  | CDC | 1055 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | 1630 | 87L CFA | 南科豐華紅線 1630 87L CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_87CFA | 南科豐華紅線(1630)電驛通訊故障 | OTHER |  |  |  |  | CDC | 1056 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | 1630 | RYFA | 南科豐華紅線 1630 RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1630_87FA | 南科豐華紅線(1630)數位電驛故障 | OTHER |  |  |  |  | CDC | 1057 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0466 |  |  | 3-39-02 |  |  | 1710 | 87CFA | 南科~和鑫二線 1710 87CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_87CFA | 南科和鑫二線(1710)電驛通訊故障 | OTHER |  |  |  |  | CDC | 1058 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0467 |  |  | 3-39-03 |  |  | 1710 | RYFA | 南科~和鑫二線 1710 RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1710_RYFA | 南科和鑫二線(1710)數位電驛故障 | OTHER |  |  |  |  | CDC | 1059 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0470 |  |  | 3-39-06 |  |  | 1720 | 87CFA | 南科積P3白線 1720 87CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_87CFA | 南科積P3線(1720)電驛通訊故障 | OTHER |  |  |  |  | CDC | 1060 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0471 |  |  | 3-39-07 |  |  | 1720 | RYFA | 南科積P3白線 1720 RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1720_RYFA | 南科積P3線(1720)數位電驛故障 | OTHER |  |  |  |  | CDC | 1061 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | 12B_RYFA | 12BUS_RYFA | Element | Status | #1#2 BUS RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0635 |  |  | 1-37-11 |  |  | 161kV #1,2Bus | RYFA | 161kV #1,2Bus RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.161_12BUS_RYFA | 161KV#1,2BUS 87RY數位電驛故障 | OTHER |  |  |  |  | CDC | 1062 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | 12B_CTFA | 12BUS_CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0636 |  |  | 1-37-12 |  |  | 161kV #1,2Bus | CTFA | 161kV #1,2Bus CTFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.161_12BUS_CTFA | 161KV#1,2BUS 87RY CT迴路故障 | OTHER |  |  |  |  | CDC | 1063 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | 34B_RYFA | 34BUS_RYFA | Element | Status | #3#4 BUS RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0637 |  |  | 1-37-13 |  |  | 161kV #3,4Bus | RYFA | 161kV #3,4Bus RYFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.161_34BUS_RYFA | 161KV#3,4BUS 87RY數位電驛故障 | OTHER |  |  |  |  | CDC | 1064 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | 34B_CTFA | 34BUS_CTFA | Element | Status | #3#4 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0638 |  |  | 1-37-14 |  |  | 161kV #3,4Bus | CTFA | 161kV #3,4Bus CTFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.161_34BUS_CTFA | 161KV#3,4BUS 87RY CT迴路故障 | OTHER |  |  |  |  | CDC | 1065 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  | B2,B3,Element | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0632 |  |  | 1-37-08 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 1066 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0864 |  | 0320 | 3-36-00 |  | 3-40 | 370 | U/L | #4DTR 4A 370 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.370_81RY_U/L | #4DTR 370CB 81RY U/L | OTHER |  |  |  |  | CDC | 1067 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0865 |  | 0321 | 3-36-01 |  | 3-41 | 380 | U/L | #4DTR 4B 380 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.380_81RY_U/L | #4DTR 380CB 81RY U/L | OTHER |  |  |  |  | CDC | 1068 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 370 | #4DTR(A)(370) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | 370 | A/N | #4DTR 4A 370 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.370_81A | #4DTR 370CB 81RY | OTHER |  |  |  |  | CDC | 1069 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 380 | #4DTR(B)(380) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | 380 | A/N | #4DTR 4B 380 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.380_81A | #4DTR 380CB 81RY | OTHER |  |  |  |  | CDC | 1070 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0390 |  |  | 3-10-06 |  |  | F27 | 81A | 科7A線 K27A CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27A_81A | 科7A線CB 81RY | OTHER |  |  |  |  | CDC | 1071 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0394 |  |  | 3-11-02 |  |  | F28 | 81A | 科7B線 K27B CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27B_81A | 科7B線CB 81RY | OTHER |  |  |  |  | CDC | 1072 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0398 |  |  | 3-11-06 |  |  | F29 | 81A | 科7C線 K27C CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27C_81A | 科7C線CB 81RY | OTHER |  |  |  |  | CDC | 1073 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0402 |  |  | 3-12-02 |  |  | F30 | 81A | 科7D線 K27D CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K27D_81A | 科7D線CB 81RY | OTHER |  |  |  |  | CDC | 1074 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0409 |  |  | 3-13-01 |  |  | F31 | 81A | 科21線 K221 CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K221_81A | 科21線CB 81RY | OTHER |  |  |  |  | CDC | 1075 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0413 |  |  | 3-13-05 |  |  | F32 | 81A | 科22線 K222 CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K222_81A | 科22線CB 81RY | OTHER |  |  |  |  | CDC | 1076 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0417 |  |  | 3-14-01 |  |  | F33 | 81A | 科23線 K223 CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K223_81A | 科23線CB 81RY | OTHER |  |  |  |  | CDC | 1077 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0421 |  |  | 3-14-05 |  |  | F34 | 81A | 科24線 K224 CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K224_81A | 科24線CB 81RY | OTHER |  |  |  |  | CDC | 1078 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0425 |  |  | 3-15-01 |  |  | F35 | ON/OFF | 科25線 K225 CB 81A |  |  | B2/E02_D1 | [8 empty] | 南科ES.K225_81A | 科25線CB 81RY | OTHER |  |  |  |  | CDC | 1079 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0992 |  |  | 2-3E-00 |  |  | Power Meter | PMA | 電力量測表計故障 PMA (#4DTR) |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.PMA | 電力量測表計故障(#4DTR) | OTHER |  |  |  |  | CDC | 1080 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | 8A5Other | SOE_SYN | Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | Locate Empty |  |  |  |  | B3/E02_A1 | [15 empty] | CDC | 1081 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0608 |  | 0116 | 1-36-00 |  | 1-74 | Locate Empty | 87B1S | 161KV #1BUS 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 1082 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0609 |  | 0117 | 1-36-01 |  | 1-75 | Locate Empty | 87B2S | 161KV #2BUS 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 1083 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 3BUS | #3BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0610 |  | 0118 | 1-36-02 |  | 1-76 | Locate Empty | 87B3S | 161KV #3BUS 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER |  |  |  |  | CDC | 1084 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 4BUS | #4BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0611 |  | 0119 | 1-36-03 |  | 1-77 | Locate Empty | 87B4S | 161KV #4BUS 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER |  |  |  |  | CDC | 1085 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | BFS |  |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0639 |  |  | 1-37-15 |  |  | Locate Empty | BFS | 161kV BFRy U/L |  |  | ELEM/E02_A1 | [8 empty] | 南科ES.161KV_BFS | 161KV 斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 1086 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | GRZ100 | BVS_RY | Element | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0484 |  |  | 3-3A-04 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.BVS_RY | 161KV #34BUS GRZ100 RY U/L | OTHER |  |  |  |  | CDC | 1087 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 1640 | 87A1 | 南科豐華白線 1640 #1 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_87A1 | 南科豐華白線(1640) 87A1 | OTHER |  |  |  |  | CDC | 1088 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 3-00-05 |  |  | 1650 | 87A1 | 南科三竹一路 1650 #1 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_87A1 | 南科三竹ㄧ路(1650) 87A1 | OTHER |  |  |  |  | CDC | 1089 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 3-00-01 |  |  | 1660 | 87A1 | 南科三竹二路 1660 #1 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_87A1 | 南科三竹二路(1660) 87A1 | OTHER |  |  |  |  | CDC | 1090 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 3-05-04 |  |  | 1640 | 87A2 | 南科豐華白線 1640 #2 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_87A2 | 南科豐華白線(1640) 87A2 | OTHER |  |  |  |  | CDC | 1091 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0173 |  |  | 3-05-05 |  |  | 1650 | 87A2 | 南科三竹一路 1650 #2 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_87A2 | 南科三竹ㄧ路(1650) 87A2 | OTHER |  |  |  |  | CDC | 1092 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 |  |  | 3-05-06 |  |  | 1660 | 87A2 | 南科三竹二路 1660 #2 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_87A2 | 南科三竹二路(1660) 87A2 | OTHER |  |  |  |  | CDC | 1093 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | 1_87UL1 |  | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0558 |  | 0126 | 1-32-14 |  | 1-7E | 1640 | 87UL1 | 南科豐華白線 1640 #1 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_87UL1 | 南科豐華白線(1640) 87RY1 U/L | OTHER |  |  |  |  | CDC | 1094 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | 1_87UL1 |  | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0452 |  | 0242 | 3-38-04 |  | 2-72 | 1650 | 87UL1 | 南科三竹一路 1650 #1 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_87UL1 | 南科三竹ㄧ路(1650) 87RY1 U/L | OTHER |  |  |  |  | CDC | 1095 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | 1_87UL1 |  | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0448 |  | 0240 | 3-38-00 |  | 2-70 | 1660 | 87UL1 | 南科三竹二路 1660 #1 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_87UL1 | 南科三竹二路(1660) 87RY1 U/L | OTHER |  |  |  |  | CDC | 1096 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | 1_87UL2 |  | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0485 |  | 0228 | 3-3A-05 |  | 2-64 | 1640 | 87UL2 | 南科豐華白線 1640 #2 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_87UL2 | 南科豐華白線(1640) 87RY2 U/L | OTHER |  |  |  |  | CDC | 1097 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | 1_87UL2 |  | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0486 |  | 0229 | 3-3A-06 |  | 2-65 | 1650 | 87UL2 | 南科三竹一路 1650 #2 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_87UL2 | 南科三竹ㄧ路(1650) 87RY2 U/L | OTHER |  |  |  |  | CDC | 1098 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | 1_87UL2 |  | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0487 |  | 0230 | 3-3A-07 |  | 2-66 | 1660 | 87UL2 | 南科三竹二路 1660 #2 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_87UL2 | 南科三竹二路(1660) 87RY2 U/L | OTHER |  |  |  |  | CDC | 1099 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | 1640 | RYFA | 南科豐華白線 1640 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_RYFA | 南科豐華白線(1640)數位電驛故障 | OTHER |  |  |  |  | CDC | 1100 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0455 |  |  | 3-38-07 |  |  | 1650 | RYFA | 南科三竹一路 1650 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_RYFA | 南科三竹ㄧ路(1650)數位電驛故障 | OTHER |  |  |  |  | CDC | 1101 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0451 |  |  | 3-38-03 |  |  | 1660 | RYFA | 南科三竹二路 1660 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_RYFA | 南科三竹二路(1660)數位電驛故障 | OTHER |  |  |  |  | CDC | 1102 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | 1640 | 87CFA | 南科豐華白線 1640 87RY通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1640_87CFA | 南科豐華白線(1640)電驛通訊故障 | OTHER |  |  |  |  | CDC | 1103 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0454 |  |  | 3-38-06 |  |  | 1650 | 87CFA | 南科三竹一路 1650 87RY通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1650_87CFA | 南科三竹ㄧ路(1650)電驛通訊故障 | OTHER |  |  |  |  | CDC | 1104 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0450 |  |  | 3-38-02 |  |  | 1660 | 87CFA | 南科三竹二路 1660 87RY通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1660_87CFA | 南科三竹二路(1660)電驛通訊故障 | OTHER |  |  |  |  | CDC | 1105 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | 9A5Other | GEN1 | Element | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0993 |  |  | 2-3E-01 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉(洞道機房用) |  |  | B3/E02_A1 | [8 empty] | 南科ES.GEN1 | 緊急發電機運轉(洞道機房用) | OTHER |  |  |  |  | CDC | 1106 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | 10A5Other | GEN2 | Element | [12 empty] | 0994 |  |  | 2-3E-02 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉(所內用電用) |  |  | B3/E02_A1 | [8 empty] | 南科ES.GEN2 | 緊急發電機運轉(所內用電用) | OTHER |  |  |  |  | CDC | 1107 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ON/OFF | OFF
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | RYFA |  | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0488 |  |  | 3-3A-08 |  |  | Locate Empty | RYFA | 161KV斷路器失靈電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.161KV_BF_RYFA | 161KV斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 1108 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 1530 | 87CFA | 南科~三福一線 1530 87RY 通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_87CFA | 南科三福一線1530 87RY通訊故障 | OTHER |  |  |  |  | CDC | 1109 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 1530 | RYFA | 南科~三福一線 1530 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_RYFA | 南科三福一線1530 數位電驛故障 | OTHER |  |  |  |  | CDC | 1110 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | 1540 | 87CFA | 南科~積E六線 1540 87RY 通訊故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_87CFA | 南科積E六線1540 87RY通訊故障 | OTHER |  |  |  |  | CDC | 1111 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | 1540 | RYFA | 南科~積E六線 1540 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_RYFA | 南科積E六線1540 數位電驛故障 | OTHER |  |  |  |  | CDC | 1112 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 1530 | 87A1 | 南科~三福一線 1530 #1 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_87A1 | 南科三福一線(1530) 87A1 | OTHER |  |  |  |  | CDC | 1113 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 87A1 |  | B2,B3,Element | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 1540 | 87A1 | 南科~積E六線 1540 #1 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_87A1 | 南科積E六線(1540) 87A1 | OTHER |  |  |  |  | CDC | 1114 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 3-05-07 |  |  | 1530 | 87A2 | 南科~三福一線 1530 #2 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_87A2 | 南科三福一線(1530) 87A2 | OTHER |  |  |  |  | CDC | 1115 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 87A2 |  | B2,B3,Element | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 3-06-00 |  |  | 1540 | 87A2 | 南科~積E六線 1540 #2 87RY |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_87A2 | 南科積E六線(1540) 87A2 | OTHER |  |  |  |  | CDC | 1116 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 1_87UL2 |  | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0489 |  | 0232 | 3-3A-09 |  | 2-68 | 1530 | 87UL2 | 南科~三福一線 1530 #2 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_87UL2 | 南科三福一線(1530) 87RY2 U/L | OTHER |  |  |  |  | CDC | 1117 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 1_87UL2 |  | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0490 |  | 0235 | 3-3A-10 |  | 2-6B | 1540 | 87UL2 | 南科~積E六線 1540 #2 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_87UL2 | 南科積E六線(1540) 87RY2 U/L | OTHER |  |  |  |  | CDC | 1118 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | DTTA |  | B2,B3,Element | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0491 |  |  | 3-3A-11 |  |  | 1530 | DTTA | 南科~三福一線 1530 遠方遙跳 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_DTTA | 南科三福一線(1530) 遠方遙跳 | OTHER |  |  |  |  | CDC | 1119 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | DTTA |  | B2,B3,Element | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0492 |  |  | 3-3A-12 |  |  | 1540 | DTTA | 南科~積E六線 1540 遠方遙跳 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_DTTA | 南科積E六線(1540) 遠方遙跳 | OTHER |  |  |  |  | CDC | 1120 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | 1_87UL1 |  | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0231 | 1-30-02 |  | 2-67 | 1530 | 87UL1 | 南科~三福一線 1530 #1 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1530_87UL1 | 南科三福一線(1530) 87RY1 U/L | OTHER |  |  |  |  | CDC | 1121 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | 1_87UL1 |  | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0234 | 1-30-14 |  | 2-6A | 1540 | 87UL1 | 南科~積E六線 1540 #1 87RY U/L |  |  | B2/E02_A1 | [8 empty] | 南科ES.1540_87UL1 | 南科積E六線(1540) 87RY1 U/L | OTHER |  |  |  |  | CDC | 1122 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0458 |  |  | 3-38-10 |  |  | 1670 | 87CFA | 積六線 1670 87CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_87CFA | 積六線(1670) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 1123 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0459 |  |  | 3-38-11 |  |  | 1670 | RYFA | 積六線 1670 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1670_RYFA | 積六線(1670) 數位電驛故障 | OTHER |  |  |  |  | CDC | 1124 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0462 |  |  | 3-38-14 |  |  | 1680 | 87CFA | 康寧線 1680 87CFA |  |  | B2/E02_A1 | [8 empty] | 南科ES.1680_87CFA | 康寧線(1680) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 1125 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0463 |  |  | 3-38-15 |  |  | 1680 | RYFA | 康寧線 1680 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1680_RYFA | 康寧線(1680) 數位電驛故障 | OTHER |  |  |  |  | CDC | 1126 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | 1550 | RYFA | 三福科線 1550 數位電驛故障 |  |  | B2/E02_A1 | [8 empty] | 南科ES.1550_RYFA | 三福科線(1550) 數位電驛故障 | OTHER |  |  |  |  | CDC | 1127 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | ComPoint |  |  | RTU_MCT | MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0177 |  |  | 3-06-01 |  |  | 161RTU | MCT_ SOE | 161 RTU MASTER RY SOE |  |  | B2/E02_A1 | [15 empty] | CDC | 1128 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E02 | 南科ES | 0 |  | StaDev | 所內設施 |  | OLTC_A | OLTCA | Element | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0493 |  |  | 3-3A-13 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/E02_A1 | [8 empty] | 南科ES.OLTCA | OLTC 15分鐘連動3次 | OTHER |  |  |  |  | CDC | 1129 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | ComPoint |  |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 3-37-10 |  |  | Locate Empty | RYFA | 南科E/S 11/23kV RYFA |  |  | B2/E02_D1 | [8 empty] | 南科ES.11/23KV_RYFA | 11/23KV IED 故障 | OTHER |  |  |  |  | CDC | 1130 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 |  |  | 3-06-04 |  |  | 310 |  | #1DTR 1A 310 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.310_81A | #1DTR 310CB 81RY | OTHER |  |  |  |  | CDC | 1131 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 310 | #1DTR(A)(310) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0884 |  | 0340 | 3-37-04 |  | 3-54 | 310 | U/L | #1DTR 1A 310 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.310_81RY_U/L | #1DTR 310CB 81RY U/L | OTHER |  |  |  |  | CDC | 1132 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 3-06-05 |  |  | 320 |  | #1DTR 1B 320 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.320_81A | #1DTR 320CB 81RY | OTHER |  |  |  |  | CDC | 1133 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 320 | #1DTR(B)(320) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0885 |  | 0341 | 3-37-05 |  | 3-55 | 320 | U/L | #1DTR 1B 320 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.320_81RY_U/L | #1DTR 320CB 81RY U/L | OTHER |  |  |  |  | CDC | 1134 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0182 |  |  | 3-06-06 |  |  | 330 |  | #2DTR 2A 330 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.330_81A | #2DTR 330CB 81RY | OTHER |  |  |  |  | CDC | 1135 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 330 | #2DTR(A)(330) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0886 |  | 0342 | 3-37-06 |  | 3-56 | 330 | U/L | #2DTR 2A 330 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.330_81RY_U/L | #2DTR 330CB 81RY U/L | OTHER |  |  |  |  | CDC | 1136 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 3-06-07 |  |  | 340 |  | #2DTR 2B 340 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.340_81A | #2DTR 340CB 81RY | OTHER |  |  |  |  | CDC | 1137 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 340 | #2DTR(B)(340) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0887 |  | 0343 | 3-37-07 |  | 3-57 | 340 | U/L | #2DTR 2B 340 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.340_81RY_U/L | #2DTR 340CB 81RY U/L | OTHER |  |  |  |  | CDC | 1138 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0184 |  |  | 3-07-00 |  |  | 350 |  | #3DTR 3A 350 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.350_81A | #3DTR 350CB 81RY | OTHER |  |  |  |  | CDC | 1139 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 350 | #3DTR(A)(350) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0888 |  | 0344 | 3-37-08 |  | 3-58 | 350 | U/L | #3DTR 3A 350 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.350_81RY_U/L | #3DTR 350CB 81RY U/L | OTHER |  |  |  |  | CDC | 1140 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | 81A |  | B2,B3,Element | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 3-07-01 |  |  | 360 |  | #3DTR 3B 360 CB 81A |  |  | B3/E02_A1 | [8 empty] | 南科ES.360_81A | #3DTR 360CB 81RY | OTHER |  |  |  |  | CDC | 1141 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 360 | #3DTR(B)(360) |  | 81UL |  | B2,B3,Element | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0889 |  | 0345 | 3-37-09 |  | 3-59 | 360 | U/L | #3DTR 3B 360 CB 81RY U/L |  |  | B3/E02_A1 | [8 empty] | 南科ES.360_81RY_U/L | #3DTR 360CB 81RY U/L | OTHER |  |  |  |  | CDC | 1142 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
E02 | 南科ES | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/E02_C | [17 empty] | v_best_161_12 | OPRD1: E02/161/1BUS/V; OPRD2: E02/161/2BUS/V
E02 | 南科ES | 0 |  | CalcPoint |  |  | Vbs5 | [9 empty] | B1/E02_C | [17 empty] | v_best_161_34 | OPRD1: E02/161/3BUS/V; OPRD2: E02/161/4BUS/V
E02 | 南科ES |  |  | 1DTR | 1DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/310/MVAR; OPRD2: E02/11/320/MVAR
E02 | 南科ES |  |  | 1DTR | 1DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/310/MW; OPRD2: E02/11/320/MW
E02 | 南科ES |  |  | 4DTR | 4DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/370/MVAR; OPRD2: E02/11/380/MVAR
E02 | 南科ES |  |  | 4DTR | 4DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/370/MW; OPRD2: E02/11/380/MW
E02 | 南科ES | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/E02_C | [17 empty] | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: E02/0/CalcPoint/Vbs4; OPRD5: E02/0/CalcPoint/Vbs5; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
E02 | 南科ES | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/E02_C | [17 empty] | p_sum_19 | OPRD1: E02/161/1510/MW; OPRD2: E02/161/1520/MW; OPRD3: E02/161/1530/MW; OPRD4: E02/161/1540/MW; OPRD5: E02/161/1550/MW; OPRD6: E02/161/1570/MW; OPRD7: E02/161/1580/MW; OPRD8: E02/161/1610/MW; OPRD9: E02/161/1620/MW; OPRD10: E02/161/1630/MW; OPRD11: E02/161/1640/MW; OPRD12: E02/161/1650/MW; OPRD13: E02/161/1660/MW; OPRD14: E02/161/1670/MW; OPRD15: E02/161/1680/MW; OPRD16: E02/161/1710/MW; OPRD17: E02/161/1720/MW; OPRD18: E02/22/330/MW; OPRD19: E02/22/350/MW
E02 | 南科ES | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/E02_C | [17 empty] | pwr_cnd2 | OPRD1: E02/0/CalcPoint/OPRN2_MW
E02 | 南科ES | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/E02_C | [17 empty] | none
E02 | 南科ES | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/E02_C | [17 empty] | pwr_fail | OPRD1: E02/0/CalcPoint/OPRN1; OPRD2: E02/0/CalcPoint/OPRN2; OPRD3: E02/0/CalcPoint/PRFL_UL
E02 | 南科ES |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/310/I_R; OPRD2: E02/11/320/I_R
E02 | 南科ES |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/310/I_S; OPRD2: E02/11/320/I_S
E02 | 南科ES |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/310/I_T; OPRD2: E02/11/320/I_T
E02 | 南科ES |  |  | 4DTR | 4DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/370/I_R; OPRD2: E02/11/380/I_R
E02 | 南科ES |  |  | 4DTR | 4DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/370/I_S; OPRD2: E02/11/380/I_S
E02 | 南科ES |  |  | 4DTR | 4DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | dtr_sum_cal | OPRD1: E02/22/370/I_T; OPRD2: E02/11/380/I_T
E02 | 南科ES | 161 | 161kV | 1510 | 南科~道爺一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1510/MW; OPRD2: E02/161/1510/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1520 | 南科~道爺二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1520/MW; OPRD2: E02/161/1520/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1530 | 南科~三福一線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1530/MW; OPRD2: E02/161/1530/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1540 | 南科~積E六線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1540/MW; OPRD2: E02/161/1540/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1550 | 南科～三福科線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1550/MW; OPRD2: E02/161/1550/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1570 | 南科～道爺三路(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1570/MW; OPRD2: E02/161/1570/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1580 | 南科～道爺四路(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1580/MW; OPRD2: E02/161/1580/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1610 | 南科~麻工一路(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1610/MW; OPRD2: E02/161/1610/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1620 | 南科~麻工二路(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1620/MW; OPRD2: E02/161/1620/MVAR; OPRD3: E02/0/CalcPoint/Vbs4
E02 | 南科ES | 161 | 161kV | 1630 | 南科～豐華紅線(1630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1630/MW; OPRD2: E02/161/1630/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1640 | 南科～豐華白線(1640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1640/MW; OPRD2: E02/161/1640/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1650 | 南科～三竹一路(1650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1650/MW; OPRD2: E02/161/1650/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1660 | 南科～三竹二路(1660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1660/MW; OPRD2: E02/161/1660/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1670 | 南科～積六線(1670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1670/MW; OPRD2: E02/161/1670/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1680 | 南科～康寧線(1680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1680/MW; OPRD2: E02/161/1680/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1710 | 南科～南積一線(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1710/MW; OPRD2: E02/161/1710/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 161 | 161kV | 1720 | 南科～積P3線(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E02_A1 | [17 empty] | amp_cal | OPRD1: E02/161/1720/MW; OPRD2: E02/161/1720/MVAR; OPRD3: E02/0/CalcPoint/Vbs5
E02 | 南科ES | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/11/1BBUS/V
E02 | 南科ES | 11 | 11kV | 4BBUS | #4BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/11/4BBUS/V
E02 | 南科ES | 22 | 22kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/22/1ABUS/V
E02 | 南科ES | 22 | 22kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/22/2ABUS/V
E02 | 南科ES | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/22/2BBUS/V
E02 | 南科ES | 22 | 22kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/22/3ABUS/V
E02 | 南科ES | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/22/3BBUS/V
E02 | 南科ES | 22 | 22kV | 4ABUS | #4ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/E02_A1 | [17 empty] | bus_uv | OPRD1: E02/22/4ABUS/V
E02 | 南科ES |  |  | 1DTR | 1DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_60 | 57 | 66 | 75 | 119 |  | -57 | -66 | -75 | -119 | [7 empty] | va_million | OPRD1: E02//1DTR/MW; OPRD2: E02//1DTR/MVAR
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 |  | -28.5 | -33 | -37.5 | -59 | [7 empty] | va_million | OPRD1: E02/22/310/MW; OPRD2: E02/22/310/MVAR
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 |  | -28.5 | -33 | -37.5 | -59 | [7 empty] | va_million | OPRD1: E02/11/320/MW; OPRD2: E02/11/320/MVAR
E02 | 南科ES |  |  | 2DTR | #2DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_60 | 57 | 66 | 75 | 119 |  | -57 | -66 | -75 | -119 | [7 empty] | va_million | OPRD1: E02/22/330/MW; OPRD2: E02/22/330/MVAR
E02 | 南科ES |  |  | 3DTR | #3DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_60 | 57 | 66 | 75 | 119 |  | -57 | -66 | -75 | -119 | [7 empty] | va_million | OPRD1: E02/22/350/MW; OPRD2: E02/22/350/MVAR
E02 | 南科ES |  |  | 4DTR | 4DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_60 | 57 | 66 | 75 | 119 |  | -57 | -66 | -75 | -119 | [7 empty] | va_million | OPRD1: E02//4DTR/MW; OPRD2: E02//4DTR/MVAR
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 |  | -28.5 | -33 | -37.5 | -59 | [7 empty] | va_million | OPRD1: E02/22/370/MW; OPRD2: E02/22/370/MVAR
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 |  | -28.5 | -33 | -37.5 | -59 | [7 empty] | va_million | OPRD1: E02/11/380/MW; OPRD2: E02/11/380/MVAR
E02 | 南科ES |  |  | 1DTR | 1DTR |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//1DTR/MVA; OPRD2: 30
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//1DTR(A)/MVA; OPRD2: 30
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//1DTR(B)/MVA; OPRD2: 30
E02 | 南科ES |  |  | 2DTR | #2DTR |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//2DTR/MVA; OPRD2: 60
E02 | 南科ES |  |  | 3DTR | #3DTR |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//3DTR/MVA; OPRD2: 60
E02 | 南科ES |  |  | 4DTR | 4DTR |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//4DTR/MVA; OPRD2: 30
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//4DTR(A)/MVA; OPRD2: 30
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | LOAD | [9 empty] | B2/E02_A1 | [17 empty] | tr_loading | OPRD1: E02//4DTR(B)/MVA; OPRD2: 30
E02 | 南科ES |  |  | 1DTR | 1DTR |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02//1DTR/MW; OPRD2: E02//1DTR/MVAR
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02/22/310/MW; OPRD2: E02/22/310/MVAR
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02/11/320/MW; OPRD2: E02/11/320/MVAR
E02 | 南科ES |  |  | 2DTR | #2DTR |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02/22/330/MW; OPRD2: E02/22/330/MVAR
E02 | 南科ES |  |  | 3DTR | #3DTR |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02/22/350/MW; OPRD2: E02/22/350/MVAR
E02 | 南科ES |  |  | 4DTR | 4DTR |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02//4DTR/MW; OPRD2: E02//4DTR/MVAR
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02/22/370/MW; OPRD2: E02/22/370/MVAR
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | PF | [9 empty] | B2/E02_A1 | [17 empty] | pf_cal | OPRD1: E02/11/380/MW; OPRD2: E02/11/380/MVAR
E02 | 南科ES |  |  | 1DTR | #1DTR |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: NULL; OPRD2: E02//1DTR/Tap Chan
E02 | 南科ES |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: E02//1DTR(A)/SupLocal; OPRD2: E02//1DTR(A)/Tap Chan
E02 | 南科ES |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: E02//1DTR(B)/SupLocal; OPRD2: E02//1DTR(B)/Tap Chan
E02 | 南科ES |  |  | 2DTR | #2DTR |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: E02//2DTR/SupLocal; OPRD2: E02//2DTR/Tap Chan
E02 | 南科ES |  |  | 3DTR | #3DTR |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: E02//3DTR/SupLocal; OPRD2: E02//3DTR/Tap Chan
E02 | 南科ES |  |  | 4DTR | #4DTR |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: NULL; OPRD2: E02//4DTR/Tap Chan
E02 | 南科ES |  |  | 4DTR(A) | #4DTR(A) |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: E02//4DTR(A)/SupLocal; OPRD2: E02//4DTR(A)/Tap Chan
E02 | 南科ES |  |  | 4DTR(B) | #4DTR(B) |  | TR_PERM | [9 empty] | B2/E02_A1 | [17 empty] | dtr_perm | OPRD1: E02//4DTR(B)/SupLocal; OPRD2: E02//4DTR(B)/Tap Chan
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/1BBUS/V; OPRD2: E02/11/K216/I_R; OPRD3: E02/11/K216/I_S; OPRD4: E02/11/K216/I_T
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/1BBUS/V; OPRD2: E02/11/K217/I_R; OPRD3: E02/11/K217/I_S; OPRD4: E02/11/K217/I_T
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/1BBUS/V; OPRD2: E02/11/K218/I_R; OPRD3: E02/11/K218/I_S; OPRD4: E02/11/K218/I_T
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/1BBUS/V; OPRD2: E02/11/K219/I_R; OPRD3: E02/11/K219/I_S; OPRD4: E02/11/K219/I_T
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/1BBUS/V; OPRD2: E02/11/K220/I_R; OPRD3: E02/11/K220/I_S; OPRD4: E02/11/K220/I_T
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/4BBUS/V; OPRD2: E02/11/K221/I_R; OPRD3: E02/11/K221/I_S; OPRD4: E02/11/K221/I_T
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/4BBUS/V; OPRD2: E02/11/K222/I_R; OPRD3: E02/11/K222/I_S; OPRD4: E02/11/K222/I_T
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/4BBUS/V; OPRD2: E02/11/K223/I_R; OPRD3: E02/11/K223/I_S; OPRD4: E02/11/K223/I_T
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/4BBUS/V; OPRD2: E02/11/K224/I_R; OPRD3: E02/11/K224/I_S; OPRD4: E02/11/K224/I_T
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/11/4BBUS/V; OPRD2: E02/11/K225/I_R; OPRD3: E02/11/K225/I_S; OPRD4: E02/11/K225/I_T
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/1ABUS/V; OPRD2: E02/22/K251/I_R; OPRD3: E02/22/K251/I_S; OPRD4: E02/22/K251/I_T
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/1ABUS/V; OPRD2: E02/22/K252/I_R; OPRD3: E02/22/K252/I_S; OPRD4: E02/22/K252/I_T
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/1ABUS/V; OPRD2: E02/22/K253/I_R; OPRD3: E02/22/K253/I_S; OPRD4: E02/22/K253/I_T
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/1ABUS/V; OPRD2: E02/22/K254/I_R; OPRD3: E02/22/K254/I_S; OPRD4: E02/22/K254/I_T
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2ABUS/V; OPRD2: E02/22/K261/I_R; OPRD3: E02/22/K261/I_S; OPRD4: E02/22/K261/I_T
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2ABUS/V; OPRD2: E02/22/K262/I_R; OPRD3: E02/22/K262/I_S; OPRD4: E02/22/K262/I_T
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2ABUS/V; OPRD2: E02/22/K263/I_R; OPRD3: E02/22/K263/I_S; OPRD4: E02/22/K263/I_T
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2ABUS/V; OPRD2: E02/22/K264/I_R; OPRD3: E02/22/K264/I_S; OPRD4: E02/22/K264/I_T
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2BBUS/V; OPRD2: E02/22/K265/I_R; OPRD3: E02/22/K265/I_S; OPRD4: E02/22/K265/I_T
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2BBUS/V; OPRD2: E02/22/K266/I_R; OPRD3: E02/22/K266/I_S; OPRD4: E02/22/K266/I_T
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2BBUS/V; OPRD2: E02/22/K267/I_R; OPRD3: E02/22/K267/I_S; OPRD4: E02/22/K267/I_T
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/2BBUS/V; OPRD2: E02/22/K268/I_R; OPRD3: E02/22/K268/I_S; OPRD4: E02/22/K268/I_T
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3ABUS/V; OPRD2: E02/22/K271/I_R; OPRD3: E02/22/K271/I_S; OPRD4: E02/22/K271/I_T
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3ABUS/V; OPRD2: E02/22/K272/I_R; OPRD3: E02/22/K272/I_S; OPRD4: E02/22/K272/I_T
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3ABUS/V; OPRD2: E02/22/K273/I_R; OPRD3: E02/22/K273/I_S; OPRD4: E02/22/K273/I_T
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3ABUS/V; OPRD2: E02/22/K274/I_R; OPRD3: E02/22/K274/I_S; OPRD4: E02/22/K274/I_T
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3BBUS/V; OPRD2: E02/22/K275/I_R; OPRD3: E02/22/K275/I_S; OPRD4: E02/22/K275/I_T
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3BBUS/V; OPRD2: E02/22/K276/I_R; OPRD3: E02/22/K276/I_S; OPRD4: E02/22/K276/I_T
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3BBUS/V; OPRD2: E02/22/K277/I_R; OPRD3: E02/22/K277/I_S; OPRD4: E02/22/K277/I_T
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/3BBUS/V; OPRD2: E02/22/K278/I_R; OPRD3: E02/22/K278/I_S; OPRD4: E02/22/K278/I_T
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/4ABUS/V; OPRD2: E02/22/K27A/I_R; OPRD3: E02/22/K27A/I_S; OPRD4: E02/22/K27A/I_T
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/4ABUS/V; OPRD2: E02/22/K27B/I_R; OPRD3: E02/22/K27B/I_S; OPRD4: E02/22/K27B/I_T
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/4ABUS/V; OPRD2: E02/22/K27C/I_R; OPRD3: E02/22/K27C/I_S; OPRD4: E02/22/K27C/I_T
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kva_cal | OPRD1: E02/22/4ABUS/V; OPRD2: E02/22/K27D/I_R; OPRD3: E02/22/K27D/I_S; OPRD4: E02/22/K27D/I_T
E02 | 南科ES | 11 | 11kV | K216 | K216 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K216/kVA; OPRD2: E02/11/K216/KVAR
E02 | 南科ES | 11 | 11kV | K217 | K217 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K217/kVA; OPRD2: E02/11/K217/KVAR
E02 | 南科ES | 11 | 11kV | K218 | K218 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K218/kVA; OPRD2: E02/11/K218/KVAR
E02 | 南科ES | 11 | 11kV | K219 | K219 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K219/kVA; OPRD2: E02/11/K219/KVAR
E02 | 南科ES | 11 | 11kV | K220 | K220 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K220/kVA; OPRD2: E02/11/K220/KVAR
E02 | 南科ES | 11 | 11kV | K221 | K221 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K221/kVA; OPRD2: E02/11/K221/KVAR
E02 | 南科ES | 11 | 11kV | K222 | K222 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K222/kVA; OPRD2: E02/11/K222/KVAR
E02 | 南科ES | 11 | 11kV | K223 | K223 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K223/kVA; OPRD2: E02/11/K223/KVAR
E02 | 南科ES | 11 | 11kV | K224 | K224 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K224/kVA; OPRD2: E02/11/K224/KVAR
E02 | 南科ES | 11 | 11kV | K225 | K225 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/11/K225/kVA; OPRD2: E02/11/K225/KVAR
E02 | 南科ES | 22 | 22kV | K251 | K251 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K251/kVA; OPRD2: E02/22/K251/KVAR
E02 | 南科ES | 22 | 22kV | K252 | K252 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K252/kVA; OPRD2: E02/22/K252/KVAR
E02 | 南科ES | 22 | 22kV | K253 | K253 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K253/kVA; OPRD2: E02/22/K253/KVAR
E02 | 南科ES | 22 | 22kV | K254 | K254 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K254/kVA; OPRD2: E02/22/K254/KVAR
E02 | 南科ES | 22 | 22kV | K261 | K261 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K261/kVA; OPRD2: E02/22/K261/KVAR
E02 | 南科ES | 22 | 22kV | K262 | K262 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K262/kVA; OPRD2: E02/22/K262/KVAR
E02 | 南科ES | 22 | 22kV | K263 | K263 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K263/kVA; OPRD2: E02/22/K263/KVAR
E02 | 南科ES | 22 | 22kV | K264 | K264 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K264/kVA; OPRD2: E02/22/K264/KVAR
E02 | 南科ES | 22 | 22kV | K265 | K265 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K265/kVA; OPRD2: E02/22/K265/KVAR
E02 | 南科ES | 22 | 22kV | K266 | K266 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K266/kVA; OPRD2: E02/22/K266/KVAR
E02 | 南科ES | 22 | 22kV | K267 | K267 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K267/kVA; OPRD2: E02/22/K267/KVAR
E02 | 南科ES | 22 | 22kV | K268 | K268 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K268/kVA; OPRD2: E02/22/K268/KVAR
E02 | 南科ES | 22 | 22kV | K271 | K271 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K271/kVA; OPRD2: E02/22/K271/KVAR
E02 | 南科ES | 22 | 22kV | K272 | K272 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K272/kVA; OPRD2: E02/22/K272/KVAR
E02 | 南科ES | 22 | 22kV | K273 | K273 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K273/kVA; OPRD2: E02/22/K273/KVAR
E02 | 南科ES | 22 | 22kV | K274 | K274 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K274/kVA; OPRD2: E02/22/K274/KVAR
E02 | 南科ES | 22 | 22kV | K275 | K275 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K275/kVA; OPRD2: E02/22/K275/KVAR
E02 | 南科ES | 22 | 22kV | K276 | K276 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K276/kVA; OPRD2: E02/22/K276/KVAR
E02 | 南科ES | 22 | 22kV | K277 | K277 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K277/kVA; OPRD2: E02/22/K277/KVAR
E02 | 南科ES | 22 | 22kV | K278 | K278 |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K278/kVA; OPRD2: E02/22/K278/KVAR
E02 | 南科ES | 22 | 22kV | K27A | K27A |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K27A/kVA; OPRD2: E02/22/K27A/KVAR
E02 | 南科ES | 22 | 22kV | K27B | K27B |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K27B/kVA; OPRD2: E02/22/K27B/KVAR
E02 | 南科ES | 22 | 22kV | K27C | K27C |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K27C/kVA; OPRD2: E02/22/K27C/KVAR
E02 | 南科ES | 22 | 22kV | K27D | K27D |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/E02_D1 | [17 empty] | kw_cal | OPRD1: E02/22/K27D/kVA; OPRD2: E02/22/K27D/KVAR
E02 | 南科ES | 0 |  | CalcPoint |  |  | DTR_MW | [9 empty] | B1/E02_C | [17 empty] | tot_tr_4 | OPRD1: E02//1DTR/MW; OPRD2: E02//4DTR/MW; OPRD3: E02/22/330/MW; OPRD4: E02/22/350/MW
E02 | 南科ES | 0 |  | CalcPoint |  |  | DTR_MVAR | [9 empty] | B1/E02_C | [17 empty] | tot_tr_4 | OPRD1: E02//1DTR/MVAR; OPRD2: E02//4DTR/MVAR; OPRD3: E02/22/330/MVAR; OPRD4: E02/22/350/MVAR
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/11/220/CB; OPRD2: 6.9; OPRD3: 6
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/11/280/CB; OPRD2: 6.9; OPRD3: 6
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/22/210/CB; OPRD2: 13.8; OPRD3: 9
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/22/230/CB; OPRD2: 13.8; OPRD3: 9
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/22/240/CB; OPRD2: 13.8; OPRD3: 9
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/22/250/CB; OPRD2: 13.8; OPRD3: 9
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/22/260/CB; OPRD2: 13.8; OPRD3: 9
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/E02_A1 | [17 empty] | sc_mvar | OPRD1: E02/22/270/CB; OPRD2: 13.8; OPRD3: 9
E02 | 南科ES | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/E02_C | [17 empty] | com_alarm_51 | E02//1DTR/87A | E02//1DTR/51ZA | E02//1DTR/96B2 | E02//1DTR/96B1 | E02//1DTR/TRA | E02//1DTR/96PA | E02//1DTR/63Q | E02//1DTR/96D | E02//2DTR/96PA | E02//2DTR/96B2 | E02//2DTR/TRA | E02//2DTR/96B1 | E02//2DTR/96D | E02//2DTR/63Q | E02//2DTR/87A | E02//2DTR/51ZA | E02//3DTR/96PA | E02//3DTR/87A | E02//3DTR/51ZA | E02//3DTR/96B2 | E02//3DTR/TRA | E02//3DTR/96B1 | E02//3DTR/96D | E02//3DTR/63Q | E02//4DTR/63Q | E02//4DTR/96D | E02//4DTR/96PA | E02//4DTR/TRA | E02//4DTR/96B2 | E02//4DTR/96B1 | E02//4DTR/51ZA | E02//4DTR/87A | E02/11/320/PHA | E02/11/320/GDA | E02/11/380/GDA | E02/161/1BUS/87A | E02/161/2BUS/87A | E02/161/3BUS/87A | E02/161/4BUS/87A | E02/22/310/GDA | E02/22/310/PHA | E02/22/330/GDA | E02/22/330/PHA | E02/22/340/PHA | E02/22/340/GDA | E02/22/350/GDA | E02/22/350/PHA | E02/22/360/GDA | E02/22/360/PHA | E02/22/370/GDA
E02 | 南科ES | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/E02_C | [17 empty] | com_alarm_4 | OPRD1: E02//1DTR/TRF; OPRD2: E02//2DTR/TRF; OPRD3: E02//3DTR/TRF; OPRD4: E02//4DTR/TRF
E02 | 南科ES | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/161/1750/CB
E02 | 南科ES | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/161/1760/CB
E02 | 南科ES | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/161/1770/CB
E02 | 南科ES | 161 | 161kV | 1780_D1 | #4DTR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/161/1780/CB
E02 | 南科ES | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/310/CB
E02 | 南科ES | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/330/CB
E02 | 南科ES | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/340/CB
E02 | 南科ES | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/350/CB
E02 | 南科ES | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/360/CB
E02 | 南科ES | 22 | 22kV | 370_D1 | #4DTR(A)(370) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/370/CB
E02 | 南科ES | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/11/320/CB
E02 | 南科ES | 11 | 11kV | 380_D1 | #4DTR(B)(380) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/11/380/CB
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/DCV_P
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/DCV_N
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Test_CB
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/RTU_R_L
E02 | 南科ES | 161 | 161kV | ComPoint_C |  |  | BFA |  |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/161/ComPoint/BFA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | FDR_RCA |  |  | Status | 11/22kV饋線79RY動作 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/FDR_RCA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | PSA | 變電所內其他重故障 |  | Status | 變電所內其他重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/PSA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | PSF | 變電所內其他輕故障 |  | Status | 變電所內其他輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/PSF
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Door1
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Door2 |  |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Door2
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Door3 |  |  | Status | 無人化門禁3 | Close/Open | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Door3
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Burglar1 |  |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Burglar1
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Burglar2 |  |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Burglar2
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Burglar3 |  |  | Status | 無人化防盜3 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Burglar3
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Lights1 |  |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Lights1
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Lights2 |  |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Lights2
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Fire1
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Fire2 |  |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Fire2
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/Fire3
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/OPA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/ACB1
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/ACBT
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/ACB2
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/ACBA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/STUV
E02 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/STUV
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/DCA
E02 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/DCA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/DCE
E02 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/DCE
E02 | 南科ES | 161 | 161kV | ComPoint_C |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/161/ComPoint/CBA
E02 | 南科ES | 161 | 161kV | ComPoint_C |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/161/ComPoint/CBF
E02 | 南科ES | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/ComPoint/CBA
E02 | 南科ES | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/ComPoint/CBF
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/25TA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/25PFA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/OilLeak
E02 | 南科ES | 22 | 22kV | ComPoint_D1 |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/ComPoint/FDR_60A
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 5A5Other | ㄧ號充電機故障 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/5A5Other
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 6A5Other | 二號充電機故障 |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/6A5Other
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 7A5Other | 空調機故障 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/7A5Other
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | OilLeak1 |  |  | Status | 洩油池水位警報1 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/OilLeak1
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | OilLeak2 |  |  | Status | 洩油池水位警報2 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/OilLeak2
E02 | 南科ES | 22 | 22kV | 370_D1 | #4DTR(A)(370) |  | 81A | 370_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/370/81A
E02 | 南科ES | 11 | 11kV | 380_D1 | #4DTR(B)(380) |  | 81A | 380_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/11/380/81A
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/PMA
E02 | 南科ES | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/PMA
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 8A5Other | SOE_SYN |  | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/8A5Other
E02 | 南科ES | 161 | 161kV | ComPoint_C |  |  | BFS |  |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP |  | ELEM/E02_C | [17 empty] | lamp2CC | OPRD1: E02/161/ComPoint/BFS
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | GRZ100 | BVS_RY |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/GRZ100
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 9A5Other | GEN1 |  | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/9A5Other
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | 10A5Other | GEN2 | [8 empty] | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/10A5Other
E02 | 南科ES | 0 |  | StaDev_C | 所內設施 |  | OLTC_A | OLTCA |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E02_C | [17 empty] | lamp2CC | OPRD1: E02/0/StaDev/OLTC_A
E02 | 南科ES | 22 | 22kV | 310_D1 | #1DTR(A)(310) |  | 81A | 310_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/310/81A
E02 | 南科ES | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | 81A | 320_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/11/320/81A
E02 | 南科ES | 22 | 22kV | 330_D1 | #2DTR(A)(330) |  | 81A | 330_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/330/81A
E02 | 南科ES | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | 81A | 340_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/340/81A
E02 | 南科ES | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | 81A | 350_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/350/81A
E02 | 南科ES | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | 81A | 360_81A |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/E02_D1 | [17 empty] | lamp2CC | OPRD1: E02/22/360/81A

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E02 | 南科ES | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | E02/0/RTU/ADCH1 |  |  |  | CDC | 2 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | E02/0/RTU/ADCH2 |  |  |  | CDC | 3 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | E02/0/RTU/ADCH3 |  |  |  | CDC | 4 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | E02/0/RTU/ADCH4 |  |  |  | CDC | 5 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | E02/0/RTU/ADCH5 |  |  |  | CDC | 6 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCH6 | [17 empty] | 3-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCH6 | AI 90%參考點 ADCH6 | OTHER | E02/0/RTU/ADCH6 |  |  |  | CDC | 7 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | E02/0/RTU/ADCL1 |  |  |  | CDC | 8 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | E02/0/RTU/ADCL2 |  |  |  | CDC | 9 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | E02/0/RTU/ADCL3 |  |  |  | CDC | 10 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | E02/0/RTU/ADCL4 |  |  |  | CDC | 11 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | E02/0/RTU/ADCL5 |  |  |  | CDC | 12 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | AI | AI |  | ADCL6 | [17 empty] | 3-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.AI_ADCL6 | AI 10%參考點 ADCL6 | OTHER | E02/0/RTU/ADCL6 |  |  |  | CDC | 13 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.161KV#1BUS_KV | 161KV #1BUS KV | BUS | E02/161/1BUS/V |  |  |  | CDC | 14 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.161KV#2BUS_KV | 161KV #2BUS KV | BUS | E02/161/2BUS/V |  |  |  | CDC | 15 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 3BUS | #3BUS |  | V | [17 empty] | 1-9B | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.161KV#3BUS_KV | 161KV #3BUS KV | BUS | E02/161/3BUS/V |  |  |  | CDC | 16 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 4BUS | #4BUS |  | V | [17 empty] | 1-9C | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.161KV#4BUS_KV | 161KV #4BUS KV | BUS | E02/161/4BUS/V |  |  |  | CDC | 17 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E02 | 南科ES | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-E9 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | E02/11/1BBUS/V |  |  |  | CDC | 18 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
E02 | 南科ES | 22 | 22kV | 2ABUS | #2ABUS |  | V | [17 empty] | 2-8F | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV#2ABUS_KV | 23KV #2ABUS KV | BUS | E02/22/2ABUS/V |  |  |  | CDC | 19 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-A9 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | E02/22/2BBUS/V |  |  |  | CDC | 20 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 3ABUS | #3ABUS |  | V | [17 empty] | 2-C8 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | E02/22/3ABUS/V |  |  |  | CDC | 21 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-E2 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | E02/22/3BBUS/V |  |  |  | CDC | 22 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 4ABUS | #4ABUS |  | V | [17 empty] | 3-87 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV#4ABUS_KV | 23KV #4ABUS KV | BUS | E02/22/4ABUS/V |  |  |  | CDC | 23 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | MW | [17 empty] | 1-87 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1510_MW | 南科道爺ㄧ路 MW | LINE161 | E02/161/1510/MW |  |  |  | CDC | 24 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | MVAR | [17 empty] | 1-88 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1510_MVAR | 南科道爺ㄧ路 MVAR | LINE161 | E02/161/1510/MVAR |  |  |  | CDC | 25 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1510LPD | 南科道爺ㄧ路(1510) |  | V | [17 empty] | 3-C4 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1510LPD_KV | 南科道爺ㄧ路(1510) LPD KV | LINE161 | E02/161/1510/V |  |  |  | CDC | 26 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | MW | [17 empty] | 1-89 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1520_MW | 南科道爺二路 MW | LINE161 | E02/161/1520/MW |  |  |  | CDC | 27 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | MVAR | [17 empty] | 1-8A | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1520_MVAR | 南科道爺二路 MVAR | LINE161 | E02/161/1520/MVAR |  |  |  | CDC | 28 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1520LPD | 南科道爺二路(1520) |  | V | [17 empty] | 3-C5 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1520LPD_KV | 南科道爺二路(1520) LPD KV | LINE161 | E02/161/1520/V |  |  |  | CDC | 29 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | MW | [17 empty] | 1-8D | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1550_MW | 三福科線 MW | LINE161 | E02/161/1550/MW |  |  |  | CDC | 30 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | MVAR | [17 empty] | 1-8E | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1550_MVAR | 三福科線 MVAR | LINE161 | E02/161/1550/MVAR |  |  |  | CDC | 31 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1610_MW | 麻工ㄧ路 MW | LINE161 | E02/161/1610/MW |  |  |  | CDC | 32 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1610_MVAR | 麻工ㄧ路 MVAR | LINE161 | E02/161/1610/MVAR |  |  |  | CDC | 33 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1610LPD | 麻工ㄧ路(1610) |  | V | [17 empty] | 3-C6 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1610LPD_KV | 麻工ㄧ路(1610) LPD KV | LINE161 | E02/161/1610/V |  |  |  | CDC | 34 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | MW | [17 empty] | 1-97 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1620_MW | 麻工二路 MW | LINE161 | E02/161/1620/MW |  |  |  | CDC | 35 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | MVAR | [17 empty] | 1-98 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1620_MVAR | 麻工二路 MVAR | LINE161 | E02/161/1620/MVAR |  |  |  | CDC | 36 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1620LPD | 麻工二路(1620) |  | V | [17 empty] | 3-C7 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1620LPD_KV | 麻工二路(1620) LPD KV | LINE161 | E02/161/1620/V |  |  |  | CDC | 37 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | MW | [17 empty] | 1-9D | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1630_MW | 南科豐華紅線 MW | LINE161 | E02/161/1630/MW |  |  |  | CDC | 38 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | MVAR | [17 empty] | 1-9E | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1630_MVAR | 南科豐華紅線 MVAR | LINE161 | E02/161/1630/MVAR |  |  |  | CDC | 39 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1630LPD | 南科豐華紅線(1630) |  | V | [17 empty] | 3-C8 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1630LPD_KV | 南科豐華紅線(1630) LPD KV | LINE161 | E02/161/1630/V |  |  |  | CDC | 40 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | MW | [17 empty] | 1-9F | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1640_MW | 南科豐華白線 MW | LINE161 | E02/161/1640/MW |  |  |  | CDC | 41 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | MVAR | [17 empty] | 1-A0 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1640_MVAR | 南科豐華白線 MVAR | LINE161 | E02/161/1640/MVAR |  |  |  | CDC | 42 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1640LPD | 南科豐華白線(1640) |  | V | [17 empty] | 3-C9 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1640LPD_KV | 南科豐華白線(1640) LPD KV | LINE161 | E02/161/1640/V |  |  |  | CDC | 43 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | MW | [17 empty] | 1-A3 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1650_MW | 三竹ㄧ路 MW | LINE161 | E02/161/1650/MW |  |  |  | CDC | 44 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | MVAR | [17 empty] | 1-A4 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1650_MVAR | 三竹ㄧ路 MVAR | LINE161 | E02/161/1650/MVAR |  |  |  | CDC | 45 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1650LPD | 三竹ㄧ路(1650) |  | V | [17 empty] | 3-CB | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1650LPD_KV | 三竹ㄧ路(1650) LPD KV | LINE161 | E02/161/1650/V |  |  |  | CDC | 46 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | MW | [17 empty] | 1-A1 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1660_MW | 三竹二路 MW | LINE161 | E02/161/1660/MW |  |  |  | CDC | 47 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | MVAR | [17 empty] | 1-A2 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1660_MVAR | 三竹二路 MVAR | LINE161 | E02/161/1660/MVAR |  |  |  | CDC | 48 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1660LPD | 三竹二路(1660) |  | V | [17 empty] | 3-CA | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1660LPD_KV | 三竹二路(1660) LPD KV | LINE161 | E02/161/1660/V |  |  |  | CDC | 49 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | MW | [17 empty] | 1-A5 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1670_MW | 積六線 MW | LINE161 | E02/161/1670/MW |  |  |  | CDC | 50 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | MVAR | [17 empty] | 1-A6 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1670_MVAR | 積六線 MVAR | LINE161 | E02/161/1670/MVAR |  |  |  | CDC | 51 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1670LPD | 積六線(1670) |  | V | [17 empty] | 3-CC | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1670LPD_KV | 積六線(1670) LPD KV | LINE161 | E02/161/1670/V |  |  |  | CDC | 52 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | MW | [17 empty] | 1-A7 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1680_MW | 康寧線 MW | LINE161 | E02/161/1680/MW |  |  |  | CDC | 53 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | MVAR | [17 empty] | 1-A8 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1680_MVAR | 康寧線 MVAR | LINE161 | E02/161/1680/MVAR |  |  |  | CDC | 54 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1710_MW | 南科和鑫二線 MW | LINE161 | E02/161/1710/MW |  |  |  | CDC | 55 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1710_MVAR | 南科和鑫二線 MVAR | LINE161 | E02/161/1710/MVAR |  |  |  | CDC | 56 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1710LPD | 南科和鑫二線(1710) |  | V | [17 empty] | 3-CD | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1710LPD_KV | 南科和鑫二線(1710) LPD KV | LINE161 | E02/161/1710/V |  |  |  | CDC | 57 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | MW | [17 empty] | 1-AB | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1720_MW | 南科積P3線 MW | LINE161 | E02/161/1720/MW |  |  |  | CDC | 58 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | MVAR | [17 empty] | 1-AC | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1720_MVAR | 南科積P3線 MVAR | LINE161 | E02/161/1720/MVAR |  |  |  | CDC | 59 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | MW | [17 empty] | 1-AD | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1730_MW | 積十八線 MW | LINE161 |  |  |  |  | CDC | 60 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | MVAR | [17 empty] | 1-AE | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1730_MVAR | 積十八線 MVAR | LINE161 |  |  |  |  | CDC | 61 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | MW | [17 empty] | 1-AF | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1740_MW | 積十九線 MW | LINE161 |  |  |  |  | CDC | 62 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | MVAR | [17 empty] | 1-B0 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1740_MVAR | 積十九線 MVAR | LINE161 |  |  |  |  | CDC | 63 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科二十線 | 科二十線 |  | 科二十線KVAR | [17 empty] | 2-82 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科二十線KVAR | 11KV科二十線 KVAR | FEEDER | E02/11/K220/KVAR |  |  |  | CDC | 64 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科二十線 | 科二十線 |  | 科二十線A1 | [17 empty] | 2-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科二十線A1 | 11KV科二十線 R相AMP | FEEDER | E02/11/K220/I_R |  |  |  | CDC | 65 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科二十線 | 科二十線 |  | 科二十線A2 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科二十線A2 | 11KV科二十線 S相AMP | FEEDER | E02/11/K220/I_S |  |  |  | CDC | 66 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科二十線 | 科二十線 |  | 科二十線A3 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科二十線A3 | 11KV科二十線 T相AMP | FEEDER | E02/11/K220/I_T |  |  |  | CDC | 67 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科二十線 | 科二十線 |  | 科二十線A0 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科二十線A0 | 11KV科二十線 N相AMP | FEEDER | E02/11/K220/I_N |  |  |  | CDC | 68 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十七線 | 科十七線 |  | 科十七線KVAR | [17 empty] | 1-EF | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十七線KVAR | 11KV科十七線 KVAR | FEEDER | E02/11/K217/KVAR |  |  |  | CDC | 69 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十七線 | 科十七線 |  | 科十七線A1 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十七線A1 | 11KV科十七線 R相AMP | FEEDER | E02/11/K217/I_R |  |  |  | CDC | 70 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十七線 | 科十七線 |  | 科十七線A2 | [17 empty] | 1-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十七線A2 | 11KV科十七線 S相AMP | FEEDER | E02/11/K217/I_S |  |  |  | CDC | 71 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十七線 | 科十七線 |  | 科十七線A3 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十七線A3 | 11KV科十七線 T相AMP | FEEDER | E02/11/K217/I_T |  |  |  | CDC | 72 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十七線 | 科十七線 |  | 科十七線A0 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十七線A0 | 11KV科十七線 N相AMP | FEEDER | E02/11/K217/I_N |  |  |  | CDC | 73 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十九線 | 科十九線 |  | 科十九線KVAR | [17 empty] | 1-F9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十九線KVAR | 11KV科十九線 KVAR | FEEDER | E02/11/K219/KVAR |  |  |  | CDC | 74 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十九線 | 科十九線 |  | 科十九線A1 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十九線A1 | 11KV科十九線 R相AMP | FEEDER | E02/11/K219/I_R |  |  |  | CDC | 75 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十九線 | 科十九線 |  | 科十九線A2 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十九線A2 | 11KV科十九線 S相AMP | FEEDER | E02/11/K219/I_S |  |  |  | CDC | 76 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十九線 | 科十九線 |  | 科十九線A3 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十九線A3 | 11KV科十九線 T相AMP | FEEDER | E02/11/K219/I_T |  |  |  | CDC | 77 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十九線 | 科十九線 |  | 科十九線A0 | [17 empty] | 1-FD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十九線A0 | 11KV科十九線 N相AMP | FEEDER | E02/11/K219/I_N |  |  |  | CDC | 78 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十八線 | 科十八線 |  | 科十八線KVAR | [17 empty] | 1-F4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十八線KVAR | 11KV科十八線 KVAR | FEEDER | E02/11/K218/KVAR |  |  |  | CDC | 79 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十八線 | 科十八線 |  | 科十八線A1 | [17 empty] | 1-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十八線A1 | 11KV科十八線 R相AMP | FEEDER | E02/11/K218/I_R |  |  |  | CDC | 80 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十八線 | 科十八線 |  | 科十八線A2 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十八線A2 | 11KV科十八線 S相AMP | FEEDER | E02/11/K218/I_S |  |  |  | CDC | 81 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十八線 | 科十八線 |  | 科十八線A3 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十八線A3 | 11KV科十八線 T相AMP | FEEDER | E02/11/K218/I_T |  |  |  | CDC | 82 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十八線 | 科十八線 |  | 科十八線A0 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十八線A0 | 11KV科十八線 N相AMP | FEEDER | E02/11/K218/I_N |  |  |  | CDC | 83 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十六線 | 科十六線 |  | 科十六線KVAR | [17 empty] | 1-EA | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十六線KVAR | 11KV科十六線 KVAR | FEEDER | E02/11/K216/KVAR |  |  |  | CDC | 84 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十六線 | 科十六線 |  | 科十六線A1 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十六線A1 | 11KV科十六線 R相AMP | FEEDER | E02/11/K216/I_R |  |  |  | CDC | 85 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十六線 | 科十六線 |  | 科十六線A2 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十六線A2 | 11KV科十六線 S相AMP | FEEDER | E02/11/K216/I_S |  |  |  | CDC | 86 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十六線 | 科十六線 |  | 科十六線A3 | [17 empty] | 1-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十六線A3 | 11KV科十六線 T相AMP | FEEDER | E02/11/K216/I_T |  |  |  | CDC | 87 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科十六線 | 科十六線 |  | 科十六線A0 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科十六線A0 | 11KV科十六線 N相AMP | FEEDER | E02/11/K216/I_N |  |  |  | CDC | 88 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七一線 | 科七一線 |  | 科七一線KVAR | [17 empty] | 2-C9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七一線KVAR | 23KV科七一線 KVAR | FEEDER | E02/22/K271/KVAR |  |  |  | CDC | 89 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七一線 | 科七一線 |  | 科七一線A1 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七一線A1 | 23KV科七一線 R相AMP | FEEDER | E02/22/K271/I_R |  |  |  | CDC | 90 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七一線 | 科七一線 |  | 科七一線A2 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七一線A2 | 23KV科七一線 S相AMP | FEEDER | E02/22/K271/I_S |  |  |  | CDC | 91 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七一線 | 科七一線 |  | 科七一線A3 | [17 empty] | 2-CC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七一線A3 | 23KV科七一線 T相AMP | FEEDER | E02/22/K271/I_T |  |  |  | CDC | 92 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七一線 | 科七一線 |  | 科七一線A0 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七一線A0 | 23KV科七一線 N相AMP | FEEDER | E02/22/K271/I_N |  |  |  | CDC | 93 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七七線 | 科七七線 |  | 科七七線KVAR | [17 empty] | 2-ED | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七七線KVAR | 23KV科七七線 KVAR | FEEDER | E02/22/K277/KVAR |  |  |  | CDC | 94 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七七線 | 科七七線 |  | 科七七線A1 | [17 empty] | 2-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七七線A1 | 23KV科七七線 R相AMP | FEEDER | E02/22/K277/I_R |  |  |  | CDC | 95 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七七線 | 科七七線 |  | 科七七線A2 | [17 empty] | 2-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七七線A2 | 23KV科七七線 S相AMP | FEEDER | E02/22/K277/I_S |  |  |  | CDC | 96 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七七線 | 科七七線 |  | 科七七線A3 | [17 empty] | 2-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七七線A3 | 23KV科七七線 T相AMP | FEEDER | E02/22/K277/I_T |  |  |  | CDC | 97 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七七線 | 科七七線 |  | 科七七線A0 | [17 empty] | 2-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七七線A0 | 23KV科七七線 N相AMP | FEEDER | E02/22/K277/I_N |  |  |  | CDC | 98 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七二線 | 科七二線 |  | 科七二線KVAR | [17 empty] | 2-CE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七二線KVAR | 23KV科七二線 KVAR | FEEDER | E02/22/K272/KVAR |  |  |  | CDC | 99 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七二線 | 科七二線 |  | 科七二線A1 | [17 empty] | 2-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七二線A1 | 23KV科七二線 R相AMP | FEEDER | E02/22/K272/I_R |  |  |  | CDC | 100 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七二線 | 科七二線 |  | 科七二線A2 | [17 empty] | 2-D0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七二線A2 | 23KV科七二線 S相AMP | FEEDER | E02/22/K272/I_S |  |  |  | CDC | 101 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七二線 | 科七二線 |  | 科七二線A3 | [17 empty] | 2-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七二線A3 | 23KV科七二線 T相AMP | FEEDER | E02/22/K272/I_T |  |  |  | CDC | 102 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七二線 | 科七二線 |  | 科七二線A0 | [17 empty] | 2-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七二線A0 | 23KV科七二線 N相AMP | FEEDER | E02/22/K272/I_N |  |  |  | CDC | 103 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七八線 | 科七八線 |  | 科七八線KVAR | [17 empty] | 2-F2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七八線KVAR | 23KV科七八線 KVAR | FEEDER | E02/22/K278/KVAR |  |  |  | CDC | 104 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七八線 | 科七八線 |  | 科七八線A1 | [17 empty] | 2-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七八線A1 | 23KV科七八線 R相AMP | FEEDER | E02/22/K278/I_R |  |  |  | CDC | 105 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七八線 | 科七八線 |  | 科七八線A2 | [17 empty] | 2-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七八線A2 | 23KV科七八線 S相AMP | FEEDER | E02/22/K278/I_S |  |  |  | CDC | 106 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七八線 | 科七八線 |  | 科七八線A3 | [17 empty] | 2-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七八線A3 | 23KV科七八線 T相AMP | FEEDER | E02/22/K278/I_T |  |  |  | CDC | 107 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七八線 | 科七八線 |  | 科七八線A0 | [17 empty] | 2-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七八線A0 | 23KV科七八線 N相AMP | FEEDER | E02/22/K278/I_N |  |  |  | CDC | 108 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七三線 | 科七三線 |  | 科七三線KVAR | [17 empty] | 2-D3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七三線KVAR | 23KV科七三線 KVAR | FEEDER | E02/22/K273/KVAR |  |  |  | CDC | 109 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七三線 | 科七三線 |  | 科七三線A1 | [17 empty] | 2-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七三線A1 | 23KV科七三線 R相AMP | FEEDER | E02/22/K273/I_R |  |  |  | CDC | 110 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七三線 | 科七三線 |  | 科七三線A2 | [17 empty] | 2-D5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七三線A2 | 23KV科七三線 S相AMP | FEEDER | E02/22/K273/I_S |  |  |  | CDC | 111 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七三線 | 科七三線 |  | 科七三線A3 | [17 empty] | 2-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七三線A3 | 23KV科七三線 T相AMP | FEEDER | E02/22/K273/I_T |  |  |  | CDC | 112 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七三線 | 科七三線 |  | 科七三線A0 | [17 empty] | 2-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七三線A0 | 23KV科七三線 N相AMP | FEEDER | E02/22/K273/I_N |  |  |  | CDC | 113 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七五線 | 科七五線 |  | 科七五線KVAR | [17 empty] | 2-E3 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七五線KVAR | 23KV科七五線 KVAR | FEEDER | E02/22/K275/KVAR |  |  |  | CDC | 114 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七五線 | 科七五線 |  | 科七五線A1 | [17 empty] | 2-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七五線A1 | 23KV科七五線 R相AMP | FEEDER | E02/22/K275/I_R |  |  |  | CDC | 115 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七五線 | 科七五線 |  | 科七五線A2 | [17 empty] | 2-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七五線A2 | 23KV科七五線 S相AMP | FEEDER | E02/22/K275/I_S |  |  |  | CDC | 116 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七五線 | 科七五線 |  | 科七五線A3 | [17 empty] | 2-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七五線A3 | 23KV科七五線 T相AMP | FEEDER | E02/22/K275/I_T |  |  |  | CDC | 117 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七五線 | 科七五線 |  | 科七五線A0 | [17 empty] | 2-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七五線A0 | 23KV科七五線 N相AMP | FEEDER | E02/22/K275/I_N |  |  |  | CDC | 118 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七六線 | 科七六線 |  | 科七六線KVAR | [17 empty] | 2-E8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七六線KVAR | 23KV科七六線 KVAR | FEEDER | E02/22/K276/KVAR |  |  |  | CDC | 119 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七六線 | 科七六線 |  | 科七六線A1 | [17 empty] | 2-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七六線A1 | 23KV科七六線 R相AMP | FEEDER | E02/22/K276/I_R |  |  |  | CDC | 120 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七六線 | 科七六線 |  | 科七六線A2 | [17 empty] | 2-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七六線A2 | 23KV科七六線 S相AMP | FEEDER | E02/22/K276/I_S |  |  |  | CDC | 121 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七六線 | 科七六線 |  | 科七六線A3 | [17 empty] | 2-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七六線A3 | 23KV科七六線 T相AMP | FEEDER | E02/22/K276/I_T |  |  |  | CDC | 122 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七六線 | 科七六線 |  | 科七六線A0 | [17 empty] | 2-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七六線A0 | 23KV科七六線 N相AMP | FEEDER | E02/22/K276/I_N |  |  |  | CDC | 123 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七四線 | 科七四線 |  | 科七四線KVAR | [17 empty] | 2-D8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七四線KVAR | 23KV科七四線 KVAR | FEEDER | E02/22/K274/KVAR |  |  |  | CDC | 124 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七四線 | 科七四線 |  | 科七四線A1 | [17 empty] | 2-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七四線A1 | 23KV科七四線 R相AMP | FEEDER | E02/22/K274/I_R |  |  |  | CDC | 125 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七四線 | 科七四線 |  | 科七四線A2 | [17 empty] | 2-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七四線A2 | 23KV科七四線 S相AMP | FEEDER | E02/22/K274/I_S |  |  |  | CDC | 126 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七四線 | 科七四線 |  | 科七四線A3 | [17 empty] | 2-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七四線A3 | 23KV科七四線 T相AMP | FEEDER | E02/22/K274/I_T |  |  |  | CDC | 127 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科七四線 | 科七四線 |  | 科七四線A0 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科七四線A0 | 23KV科七四線 N相AMP | FEEDER | E02/22/K274/I_N |  |  |  | CDC | 128 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六一線 | 科六一線 |  | 科六一線KVAR | [17 empty] | 2-90 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六一線KVAR | 23KV科六一線 KVAR | FEEDER | E02/22/K261/KVAR |  |  |  | CDC | 129 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六一線 | 科六一線 |  | 科六一線A1 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六一線A1 | 23KV科六一線 R相AMP | FEEDER | E02/22/K261/I_R |  |  |  | CDC | 130 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六一線 | 科六一線 |  | 科六一線A2 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六一線A2 | 23KV科六一線 S相AMP | FEEDER | E02/22/K261/I_S |  |  |  | CDC | 131 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六一線 | 科六一線 |  | 科六一線A3 | [17 empty] | 2-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六一線A3 | 23KV科六一線 T相AMP | FEEDER | E02/22/K261/I_T |  |  |  | CDC | 132 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六一線 | 科六一線 |  | 科六一線A0 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六一線A0 | 23KV科六一線 N相AMP | FEEDER | E02/22/K261/I_N |  |  |  | CDC | 133 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六七線 | 科六七線 |  | 科六七線KVAR | [17 empty] | 2-B4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六七線KVAR | 23KV科六七線 KVAR | FEEDER | E02/22/K267/KVAR |  |  |  | CDC | 134 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六七線 | 科六七線 |  | 科六七線A1 | [17 empty] | 2-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六七線A1 | 23KV科六七線 R相AMP | FEEDER | E02/22/K267/I_R |  |  |  | CDC | 135 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六七線 | 科六七線 |  | 科六七線A2 | [17 empty] | 2-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六七線A2 | 23KV科六七線 S相AMP | FEEDER | E02/22/K267/I_S |  |  |  | CDC | 136 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六七線 | 科六七線 |  | 科六七線A3 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六七線A3 | 23KV科六七線 T相AMP | FEEDER | E02/22/K267/I_T |  |  |  | CDC | 137 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六七線 | 科六七線 |  | 科六七線A0 | [17 empty] | 2-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六七線A0 | 23KV科六七線 N相AMP | FEEDER | E02/22/K267/I_N |  |  |  | CDC | 138 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六二線 | 科六二線 |  | 科六二線KVAR | [17 empty] | 2-95 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六二線KVAR | 23KV科六二線 KVAR | FEEDER | E02/22/K262/KVAR |  |  |  | CDC | 139 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六二線 | 科六二線 |  | 科六二線A1 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六二線A1 | 23KV科六二線 R相AMP | FEEDER | E02/22/K262/I_R |  |  |  | CDC | 140 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六二線 | 科六二線 |  | 科六二線A2 | [17 empty] | 2-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六二線A2 | 23KV科六二線 S相AMP | FEEDER | E02/22/K262/I_S |  |  |  | CDC | 141 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六二線 | 科六二線 |  | 科六二線A3 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六二線A3 | 23KV科六二線 T相AMP | FEEDER | E02/22/K262/I_T |  |  |  | CDC | 142 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六二線 | 科六二線 |  | 科六二線A0 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六二線A0 | 23KV科六二線 N相AMP | FEEDER | E02/22/K262/I_N |  |  |  | CDC | 143 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六八線 | 科六八線 |  | 科六八線KVAR | [17 empty] | 2-B9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六八線KVAR | 23KV科六八線 KVAR | FEEDER | E02/22/K268/KVAR |  |  |  | CDC | 144 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六八線 | 科六八線 |  | 科六八線A1 | [17 empty] | 2-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六八線A1 | 23KV科六八線 R相AMP | FEEDER | E02/22/K268/I_R |  |  |  | CDC | 145 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六八線 | 科六八線 |  | 科六八線A2 | [17 empty] | 2-BB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六八線A2 | 23KV科六八線 S相AMP | FEEDER | E02/22/K268/I_S |  |  |  | CDC | 146 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六八線 | 科六八線 |  | 科六八線A3 | [17 empty] | 2-BC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六八線A3 | 23KV科六八線 T相AMP | FEEDER | E02/22/K268/I_T |  |  |  | CDC | 147 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六八線 | 科六八線 |  | 科六八線A0 | [17 empty] | 2-BD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六八線A0 | 23KV科六八線 N相AMP | FEEDER | E02/22/K268/I_N |  |  |  | CDC | 148 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六三線 | 科六三線 |  | 科六三線KVAR | [17 empty] | 2-9A | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六三線KVAR | 23KV科六三線 KVAR | FEEDER | E02/22/K263/KVAR |  |  |  | CDC | 149 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六三線 | 科六三線 |  | 科六三線A1 | [17 empty] | 2-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六三線A1 | 23KV科六三線 R相AMP | FEEDER | E02/22/K263/I_R |  |  |  | CDC | 150 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六三線 | 科六三線 |  | 科六三線A2 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六三線A2 | 23KV科六三線 S相AMP | FEEDER | E02/22/K263/I_S |  |  |  | CDC | 151 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六三線 | 科六三線 |  | 科六三線A3 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六三線A3 | 23KV科六三線 T相AMP | FEEDER | E02/22/K263/I_T |  |  |  | CDC | 152 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六三線 | 科六三線 |  | 科六三線A0 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六三線A0 | 23KV科六三線 N相AMP | FEEDER | E02/22/K263/I_N |  |  |  | CDC | 153 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六五線 | 科六五線 |  | 科六五線KVAR | [17 empty] | 2-AA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六五線KVAR | 23KV科六五線 KVAR | FEEDER | E02/22/K265/KVAR |  |  |  | CDC | 154 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六五線 | 科六五線 |  | 科六五線A1 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六五線A1 | 23KV科六五線 R相AMP | FEEDER | E02/22/K265/I_R |  |  |  | CDC | 155 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六五線 | 科六五線 |  | 科六五線A2 | [17 empty] | 2-AC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六五線A2 | 23KV科六五線 S相AMP | FEEDER | E02/22/K265/I_S |  |  |  | CDC | 156 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六五線 | 科六五線 |  | 科六五線A3 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六五線A3 | 23KV科六五線 T相AMP | FEEDER | E02/22/K265/I_T |  |  |  | CDC | 157 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六五線 | 科六五線 |  | 科六五線A0 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六五線A0 | 23KV科六五線 N相AMP | FEEDER | E02/22/K265/I_N |  |  |  | CDC | 158 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六六線 | 科六六線 |  | 科六六線KVAR | [17 empty] | 2-AF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六六線KVAR | 23KV科六六線 KVAR | FEEDER | E02/22/K266/KVAR |  |  |  | CDC | 159 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六六線 | 科六六線 |  | 科六六線A1 | [17 empty] | 2-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六六線A1 | 23KV科六六線 R相AMP | FEEDER | E02/22/K266/I_R |  |  |  | CDC | 160 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六六線 | 科六六線 |  | 科六六線A2 | [17 empty] | 2-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六六線A2 | 23KV科六六線 S相AMP | FEEDER | E02/22/K266/I_S |  |  |  | CDC | 161 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六六線 | 科六六線 |  | 科六六線A3 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六六線A3 | 23KV科六六線 T相AMP | FEEDER | E02/22/K266/I_T |  |  |  | CDC | 162 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六六線 | 科六六線 |  | 科六六線A0 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六六線A0 | 23KV科六六線 N相AMP | FEEDER | E02/22/K266/I_N |  |  |  | CDC | 163 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六四線 | 科六四線 |  | 科六四線KVAR | [17 empty] | 2-9F | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六四線KVAR | 23KV科六四線 KVAR | FEEDER | E02/22/K264/KVAR |  |  |  | CDC | 164 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六四線 | 科六四線 |  | 科六四線A1 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六四線A1 | 23KV科六四線 R相AMP | FEEDER | E02/22/K264/I_R |  |  |  | CDC | 165 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六四線 | 科六四線 |  | 科六四線A2 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六四線A2 | 23KV科六四線 S相AMP | FEEDER | E02/22/K264/I_S |  |  |  | CDC | 166 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六四線 | 科六四線 |  | 科六四線A3 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六四線A3 | 23KV科六四線 T相AMP | FEEDER | E02/22/K264/I_T |  |  |  | CDC | 167 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科六四線 | 科六四線 |  | 科六四線A0 | [17 empty] | 2-A3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科六四線A0 | 23KV科六四線 N相AMP | FEEDER | E02/22/K264/I_N |  |  |  | CDC | 168 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LGA0_120 | 96.000000 | 108.000000 | 114.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1500TIE_AMP | 1500TIE AMP | TIE | E02/161/1500/I |  |  |  | CDC | 169 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1700TIE | 1700TIE |  | I | [17 empty] | 1-B1 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1700TIE_AMP | 1700TIE AMP | TIE | E02/161/1700/I |  |  |  | CDC | 170 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C30R2020 | 1818.000000 | 1818.000000 | 2020.000000 | 3000.000000 | 1.560000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1800TIE | 1800TIE |  | I | [17 empty] | 1-B2 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1800TIE_AMP | 1800TIE AMP | TIE | E02/161/1800/I |  |  |  | CDC | 171 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C30R2020 | 1818.000000 | 1818.000000 | 2020.000000 | 3000.000000 | 1.560000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 2-87 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.11KV_200_A1 | 11KV 200 R相AMP | TIE | E02/11/200/I_R |  |  |  | CDC | 172 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 2-88 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.11KV_200_A2 | 11KV 200 S相AMP | TIE | E02/11/200/I_S |  |  |  | CDC | 173 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 2-89 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.11KV_200_A3 | 11KV 200 T相AMP | TIE | E02/11/200/I_T |  |  |  | CDC | 174 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 2-BE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_300_A1 | 23KV 300 R相AMP | TIE | E02/22/300/I_R |  |  |  | CDC | 175 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 2-BF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_300_A2 | 23KV 300 S相AMP | TIE | E02/22/300/I_S |  |  |  | CDC | 176 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 2-C2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_300_A3 | 23KV 300 T相AMP | TIE | E02/22/300/I_T |  |  |  | CDC | 177 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _400 | 400 |  | I_R | [17 empty] | 2-F7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_400_A1 | 23KV 400 R相AMP | TIE | E02/22/400/I_R |  |  |  | CDC | 178 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _400 | 400 |  | I_S | [17 empty] | 2-F8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_400_A2 | 23KV 400 S相AMP | TIE | E02/22/400/I_S |  |  |  | CDC | 179 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _400 | 400 |  | I_T | [17 empty] | 2-F9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_400_A3 | 23KV 400 T相AMP | TIE | E02/22/400/I_T |  |  |  | CDC | 180 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-C5 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | E02/22/310/MW |  |  |  | CDC | 181 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-C6 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | E02/22/310/MVAR |  |  |  | CDC | 182 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-C7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | E02/22/310/I_R |  |  |  | CDC | 183 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-C8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | E02/22/310/I_S |  |  |  | CDC | 184 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-C9 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | E02/22/310/I_T |  |  |  | CDC | 185 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 1-B3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR_OIL | #1DTR 油溫 | MTR | E02//1DTR(A)/OilTemp |  |  |  | CDC | 186 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 1-B4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | E02//1DTR(A)/CoilTemp |  |  |  | CDC | 187 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 1-B6 |  | 1-1D |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | E02//1DTR(A)/TapPosMv |  |  |  | CDC | 188 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-E4 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | E02/11/320/MW |  |  |  | CDC | 189 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-E5 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | E02/11/320/MVAR |  |  |  | CDC | 190 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-E6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | E02/11/320/I_R |  |  |  | CDC | 191 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-E7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | E02/11/320/I_S |  |  |  | CDC | 192 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-E8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | E02/11/320/I_T |  |  |  | CDC | 193 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 1-B5 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | E02//1DTR(B)/CoilTemp |  |  |  | CDC | 194 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 1-B7 |  | 1-1F |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | E02//1DTR(B)/TapPosMv |  |  |  | CDC | 195 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-B8 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_OIL | #2DTR 油溫 | MTR | E02//2DTR/OilTemp |  |  |  | CDC | 196 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | CoilTemp | [17 empty] | 1-B9 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_COIL | #2DTR 線溫 | MTR | E02//2DTR/CoilTemp |  |  |  | CDC | 197 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | TapPosMv | [17 empty] | 1-BA |  | 1-21 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_TAP | #2DTR OLTC TAP | MTR | E02//2DTR/TapPosMv |  |  |  | CDC | 198 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-BB | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_OIL | #3DTR 油溫 | MTR | E02//3DTR/OilTemp |  |  |  | CDC | 199 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | CoilTemp | [17 empty] | 1-BC | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_COIL | #3DTR 線溫 | MTR | E02//3DTR/CoilTemp |  |  |  | CDC | 200 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | TapPosMv | [17 empty] | 1-BD |  | 1-23 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_TAP | #3DTR OLTC TAP | MTR | E02//3DTR/TapPosMv |  |  |  | CDC | 201 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MW | [17 empty] | 3-82 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_MW | #4DTR二次側(A) MW | MTR | E02/22/370/MW |  |  |  | CDC | 202 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | MVAR | [17 empty] | 3-83 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_MVAR | #4DTR二次側(A) MVAR | MTR | E02/22/370/MVAR |  |  |  | CDC | 203 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_R | [17 empty] | 3-84 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_A1 | #4DTR二次側(A) R相AMP | MTR | E02/22/370/I_R |  |  |  | CDC | 204 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_S | [17 empty] | 3-85 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_A2 | #4DTR二次側(A) S相AMP | MTR | E02/22/370/I_S |  |  |  | CDC | 205 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR二次側(A) |  | I_T | [17 empty] | 3-86 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_A3 | #4DTR二次側(A) T相AMP | MTR | E02/22/370/I_T |  |  |  | CDC | 206 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | OilTemp | [17 empty] | 1-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR_OIL | #4DTR 油溫 | MTR | E02//4DTR(A)/OilTemp |  |  |  | CDC | 207 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | CoilTemp | [17 empty] | 1-BF | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_COIL | #4DTR(A) 線溫 | MTR | E02//4DTR(A)/CoilTemp |  |  |  | CDC | 208 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | TapPosMv | [17 empty] | 1-C3 |  | 1-25 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_TAP | #4DTR(A) OLTC TAP | MTR | E02//4DTR(A)/TapPosMv |  |  |  | CDC | 209 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MW | [17 empty] | 3-A1 | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_MW | #4DTR二次側(B) MW | MTR | E02/11/380/MW |  |  |  | CDC | 210 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | MVAR | [17 empty] | 3-A2 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_MVAR | #4DTR二次側(B) MVAR | MTR | E02/11/380/MVAR |  |  |  | CDC | 211 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_R | [17 empty] | 3-A3 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_A1 | #4DTR二次側(B) R相AMP | MTR | E02/11/380/I_R |  |  |  | CDC | 212 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_S | [17 empty] | 3-A4 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_A2 | #4DTR二次側(B) S相AMP | MTR | E02/11/380/I_S |  |  |  | CDC | 213 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR二次側(B) |  | I_T | [17 empty] | 3-A5 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_A3 | #4DTR二次側(B) T相AMP | MTR | E02/11/380/I_T |  |  |  | CDC | 214 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR(B) |  | CoilTemp | [17 empty] | 1-C2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_COIL | #4DTR(B) 線溫 | MTR | E02//4DTR(B)/CoilTemp |  |  |  | CDC | 215 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR(B) |  | TapPosMv | [17 empty] | 1-C4 |  | 1-27 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_TAP | #4DTR(B) OLTC TAP | MTR | E02//4DTR(B)/TapPosMv |  |  |  | CDC | 216 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
E02 | 南科ES | 0 |  | 2DTR | #2DTR二次側 |  | MW | [17 empty] | 2-A4 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_MW | #2DTR二次側 MW | MTR | E02/22/330/MW |  |  |  | CDC | 217 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 0 |  | 2DTR | #2DTR二次側 |  | MVAR | [17 empty] | 2-A5 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_MVAR | #2DTR二次側 MVAR | MTR | E02/22/330/MVAR |  |  |  | CDC | 218 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 0 |  | 3DTR | #3DTR二次側 |  | MW | [17 empty] | 2-C3 | [5 empty] | MW_-108_108(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_MW | #3DTR二次側 MW | MTR | E02/22/350/MW |  |  |  | CDC | 219 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.216000 | 0.010000
E02 | 南科ES | 0 |  | 3DTR | #3DTR二次側 |  | MVAR | [17 empty] | 2-C4 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_MVAR | #3DTR二次側 MVAR | MTR | E02/22/350/MVAR |  |  |  | CDC | 220 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
E02 | 南科ES | 0 |  |  |  |  | DCV_N | [17 empty] | 1-FF | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.直流N電源電壓 | 直流N電源電壓 | OTHER | E02/0/StaDev/DCV_N |  |  |  | CDC | 221 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
E02 | 南科ES | 0 |  |  |  |  | DCV_P | [17 empty] | 1-FE | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.直流P電源電壓 | 直流P電源電壓 | OTHER | E02/0/StaDev/DCV_P |  |  |  | CDC | 222 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
E02 | 南科ES | 0 |  | 2DTR | #2DTR二次側 |  | I_R | [17 empty] | 2-A6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_A1 | #2DTR二次側 R相AMP | MTR | E02/22/330/I_R |  |  |  | CDC | 223 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 2DTR | #2DTR二次側 |  | I_S | [17 empty] | 2-A7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_A2 | #2DTR二次側 S相AMP | MTR | E02/22/330/I_S |  |  |  | CDC | 224 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 2DTR | #2DTR二次側 |  | I_T | [17 empty] | 2-A8 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#2DTR_A3 | #2DTR二次側 T相AMP | MTR | E02/22/330/I_T |  |  |  | CDC | 225 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 3DTR | #3DTR二次側 |  | I_R | [17 empty] | 2-C5 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_A1 | #3DTR二次側 R相AMP | MTR | E02/22/350/I_R |  |  |  | CDC | 226 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 3DTR | #3DTR二次側 |  | I_S | [17 empty] | 2-C6 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_A2 | #3DTR二次側 S相AMP | MTR | E02/22/350/I_S |  |  |  | CDC | 227 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 0 |  | 3DTR | #3DTR二次側 |  | I_T | [17 empty] | 2-C7 | [5 empty] | A_-3000_3000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.#3DTR_A3 | #3DTR二次側 T相AMP | MTR | E02/22/350/I_T |  |  |  | CDC | 228 | GENERICAIPoint | ES002_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | MW | [17 empty] | 1-91 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1570_MW | 南科道爺三路 MW | LINE161 | E02/161/1570/MW |  |  |  | CDC | 229 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | MVAR | [17 empty] | 1-92 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1570_MVAR | 南科道爺三路 MVAR | LINE161 | E02/161/1570/MVAR |  |  |  | CDC | 230 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1570LPD | 南科道爺三路(1570) |  | V | [17 empty] | 3-C3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1570LPD_KV | 南科道爺三路(1570) LPD KV | LINE161 | E02/161/1570/V |  |  |  | CDC | 231 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1680LPD | 康寧線(1680) |  | V | [17 empty] | 3-D1 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1680LPD_KV | 康寧線(1680) LPD KV | LINE161 | E02/161/1680/V |  |  |  | CDC | 232 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | MW | [17 empty] | 1-8B | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1540_MW | 南科積E六線 MW | LINE161 | E02/161/1540/MW |  |  |  | CDC | 233 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | MVAR | [17 empty] | 1-8C | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1540_MVAR | 南科積E六線 MVAR | LINE161 | E02/161/1540/MVAR |  |  |  | CDC | 234 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 11 | 11kV | 4BBUS | #4BBUS |  | V | [17 empty] | 3-A6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.11KV#4BBUS_KV | 11KV #4BBUS KV | BUS | E02/11/4BBUS/V |  |  |  | CDC | 235 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
E02 | 南科ES | 11 | 11kV | 科21線 | 科21線 |  | 科21線KVAR | [17 empty] | 3-9C | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科21線KVAR | 11KV科21線 KVAR | FEEDER | E02/11/K221/KVAR |  |  |  | CDC | 236 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科21線 | 科21線 |  | 科21線A1 | [17 empty] | 3-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科21線A1 | 11KV科21線 R相AMP | FEEDER | E02/11/K221/I_R |  |  |  | CDC | 237 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科21線 | 科21線 |  | 科21線A2 | [17 empty] | 3-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科21線A2 | 11KV科21線 S相AMP | FEEDER | E02/11/K221/I_S |  |  |  | CDC | 238 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科21線 | 科21線 |  | 科21線A3 | [17 empty] | 3-9F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科21線A3 | 11KV科21線 T相AMP | FEEDER | E02/11/K221/I_T |  |  |  | CDC | 239 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科21線 | 科21線 |  | 科21線A0 | [17 empty] | 3-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科21線A0 | 11KV科21線 N相AMP | FEEDER | E02/11/K221/I_N |  |  |  | CDC | 240 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科22線 | 科22線 |  | 科22線KVAR | [17 empty] | 3-A7 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科22線KVAR | 11KV科22線 KVAR | FEEDER | E02/11/K222/KVAR |  |  |  | CDC | 241 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科22線 | 科22線 |  | 科22線A1 | [17 empty] | 3-A8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科22線A1 | 11KV科22線 R相AMP | FEEDER | E02/11/K222/I_R |  |  |  | CDC | 242 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科22線 | 科22線 |  | 科22線A2 | [17 empty] | 3-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科22線A2 | 11KV科22線 S相AMP | FEEDER | E02/11/K222/I_S |  |  |  | CDC | 243 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科22線 | 科22線 |  | 科22線A3 | [17 empty] | 3-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科22線A3 | 11KV科22線 T相AMP | FEEDER | E02/11/K222/I_T |  |  |  | CDC | 244 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科22線 | 科22線 |  | 科22線A0 | [17 empty] | 3-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科22線A0 | 11KV科22線 N相AMP | FEEDER | E02/11/K222/I_N |  |  |  | CDC | 245 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科23線 | 科23線 |  | 科23線KVAR | [17 empty] | 3-AC | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科23線KVAR | 11KV科23線 KVAR | FEEDER | E02/11/K223/KVAR |  |  |  | CDC | 246 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科23線 | 科23線 |  | 科23線A1 | [17 empty] | 3-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科23線A1 | 11KV科23線 R相AMP | FEEDER | E02/11/K223/I_R |  |  |  | CDC | 247 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科23線 | 科23線 |  | 科23線A2 | [17 empty] | 3-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科23線A2 | 11KV科23線 S相AMP | FEEDER | E02/11/K223/I_S |  |  |  | CDC | 248 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科23線 | 科23線 |  | 科23線A3 | [17 empty] | 3-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科23線A3 | 11KV科23線 T相AMP | FEEDER | E02/11/K223/I_T |  |  |  | CDC | 249 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科23線 | 科23線 |  | 科23線A0 | [17 empty] | 3-B0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科23線A0 | 11KV科23線 N相AMP | FEEDER | E02/11/K223/I_N |  |  |  | CDC | 250 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科24線 | 科24線 |  | 科24線KVAR | [17 empty] | 3-B1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科24線KVAR | 11KV科24線 KVAR | FEEDER | E02/11/K224/KVAR |  |  |  | CDC | 251 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科24線 | 科24線 |  | 科24線A1 | [17 empty] | 3-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科24線A1 | 11KV科24線 R相AMP | FEEDER | E02/11/K224/I_R |  |  |  | CDC | 252 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科24線 | 科24線 |  | 科24線A2 | [17 empty] | 3-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科24線A2 | 11KV科24線 S相AMP | FEEDER | E02/11/K224/I_S |  |  |  | CDC | 253 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科24線 | 科24線 |  | 科24線A3 | [17 empty] | 3-B4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科24線A3 | 11KV科24線 T相AMP | FEEDER | E02/11/K224/I_T |  |  |  | CDC | 254 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科24線 | 科24線 |  | 科24線A0 | [17 empty] | 3-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科24線A0 | 11KV科24線 N相AMP | FEEDER | E02/11/K224/I_N |  |  |  | CDC | 255 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科25線 | 科25線 |  | 科25線KVAR | [17 empty] | 3-B6 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科25線KVAR | 11KV科25線 KVAR | FEEDER | E02/11/K225/KVAR |  |  |  | CDC | 256 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科25線 | 科25線 |  | 科25線A1 | [17 empty] | 3-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科25線A1 | 11KV科25線 R相AMP | FEEDER | E02/11/K225/I_R |  |  |  | CDC | 257 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科25線 | 科25線 |  | 科25線A2 | [17 empty] | 3-B8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科25線A2 | 11KV科25線 S相AMP | FEEDER | E02/11/K225/I_S |  |  |  | CDC | 258 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科25線 | 科25線 |  | 科25線A3 | [17 empty] | 3-B9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科25線A3 | 11KV科25線 T相AMP | FEEDER | E02/11/K225/I_T |  |  |  | CDC | 259 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 11 | 11kV | 科25線 | 科25線 |  | 科25線A0 | [17 empty] | 3-BA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科25線A0 | 11KV科25線 N相AMP | FEEDER | E02/11/K225/I_N |  |  |  | CDC | 260 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7A線 | 科7A線 |  | 科7A線KVAR | [17 empty] | 3-88 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7A線KVAR | 23KV科7A線 KVAR | FEEDER | E02/22/K27A/KVAR |  |  |  | CDC | 261 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7A線 | 科7A線 |  | 科7A線A1 | [17 empty] | 3-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7A線A1 | 23KV科7A線 R相AMP | FEEDER | E02/22/K27A/I_R |  |  |  | CDC | 262 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7A線 | 科7A線 |  | 科7A線A2 | [17 empty] | 3-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7A線A2 | 23KV科7A線 S相AMP | FEEDER | E02/22/K27A/I_S |  |  |  | CDC | 263 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7A線 | 科7A線 |  | 科7A線A3 | [17 empty] | 3-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7A線A3 | 23KV科7A線 T相AMP | FEEDER | E02/22/K27A/I_T |  |  |  | CDC | 264 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7A線 | 科7A線 |  | 科7A線A0 | [17 empty] | 3-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7A線A0 | 23KV科7A線 N相AMP | FEEDER | E02/22/K27A/I_N |  |  |  | CDC | 265 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7B線 | 科7B線 |  | 科7B線KVAR | [17 empty] | 3-8D | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7B線KVAR | 23KV科7B線 KVAR | FEEDER | E02/22/K27B/KVAR |  |  |  | CDC | 266 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7B線 | 科7B線 |  | 科7B線A1 | [17 empty] | 3-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7B線A1 | 23KV科7B線 R相AMP | FEEDER | E02/22/K27B/I_R |  |  |  | CDC | 267 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7B線 | 科7B線 |  | 科7B線A2 | [17 empty] | 3-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7B線A2 | 23KV科7B線 S相AMP | FEEDER | E02/22/K27B/I_S |  |  |  | CDC | 268 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7B線 | 科7B線 |  | 科7B線A3 | [17 empty] | 3-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7B線A3 | 23KV科7B線 T相AMP | FEEDER | E02/22/K27B/I_T |  |  |  | CDC | 269 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7B線 | 科7B線 |  | 科7B線A0 | [17 empty] | 3-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7B線A0 | 23KV科7B線 N相AMP | FEEDER | E02/22/K27B/I_N |  |  |  | CDC | 270 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7C線 | 科7C線 |  | 科7C線KVAR | [17 empty] | 3-92 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7C線KVAR | 23KV科7C線 KVAR | FEEDER | E02/22/K27C/KVAR |  |  |  | CDC | 271 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7C線 | 科7C線 |  | 科7C線A1 | [17 empty] | 3-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7C線A1 | 23KV科7C線 R相AMP | FEEDER | E02/22/K27C/I_R |  |  |  | CDC | 272 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7C線 | 科7C線 |  | 科7C線A2 | [17 empty] | 3-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7C線A2 | 23KV科7C線 S相AMP | FEEDER | E02/22/K27C/I_S |  |  |  | CDC | 273 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7C線 | 科7C線 |  | 科7C線A3 | [17 empty] | 3-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7C線A3 | 23KV科7C線 T相AMP | FEEDER | E02/22/K27C/I_T |  |  |  | CDC | 274 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7C線 | 科7C線 |  | 科7C線A0 | [17 empty] | 3-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7C線A0 | 23KV科7C線 N相AMP | FEEDER | E02/22/K27C/I_N |  |  |  | CDC | 275 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7D線 | 科7D線 |  | 科7D線KVAR | [17 empty] | 3-97 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7D線KVAR | 23KV科7D線 KVAR | FEEDER | E02/22/K27D/KVAR |  |  |  | CDC | 276 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7D線 | 科7D線 |  | 科7D線A1 | [17 empty] | 3-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7D線A1 | 23KV科7D線 R相AMP | FEEDER | E02/22/K27D/I_R |  |  |  | CDC | 277 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7D線 | 科7D線 |  | 科7D線A2 | [17 empty] | 3-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7D線A2 | 23KV科7D線 S相AMP | FEEDER | E02/22/K27D/I_S |  |  |  | CDC | 278 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7D線 | 科7D線 |  | 科7D線A3 | [17 empty] | 3-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7D線A3 | 23KV科7D線 T相AMP | FEEDER | E02/22/K27D/I_T |  |  |  | CDC | 279 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科7D線 | 科7D線 |  | 科7D線A0 | [17 empty] | 3-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科7D線A0 | 23KV科7D線 N相AMP | FEEDER | E02/22/K27D/I_N |  |  |  | CDC | 280 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-CA | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV#1ABUS_KV | 23KV #1ABUS KV | BUS | E02/22/1ABUS/V |  |  |  | CDC | 281 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
E02 | 南科ES | 22 | 22kV | 科51線 | 科51線 |  | 科51線KVAR | [17 empty] | 1-D0 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科51線KVAR | 23KV科51線 KVAR | FEEDER | E02/22/K251/KVAR |  |  |  | CDC | 282 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科51線 | 科51線 |  | 科51線A1 | [17 empty] | 1-D1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科51線A1 | 23KV科51線 R相AMP | FEEDER | E02/22/K251/I_R |  |  |  | CDC | 283 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科51線 | 科51線 |  | 科51線A2 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科51線A2 | 23KV科51線 S相AMP | FEEDER | E02/22/K251/I_S |  |  |  | CDC | 284 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科51線 | 科51線 |  | 科51線A3 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科51線A3 | 23KV科51線 T相AMP | FEEDER | E02/22/K251/I_T |  |  |  | CDC | 285 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科51線 | 科51線 |  | 科51線A0 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科51線A0 | 23KV科51線 N相AMP | FEEDER | E02/22/K251/I_N |  |  |  | CDC | 286 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科52線 | 科52線 |  | 科52線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科52線KVAR | 23KV科52線 KVAR | FEEDER | E02/22/K252/KVAR |  |  |  | CDC | 287 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科52線 | 科52線 |  | 科52線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科52線A1 | 23KV科52線 R相AMP | FEEDER | E02/22/K252/I_R |  |  |  | CDC | 288 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科52線 | 科52線 |  | 科52線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科52線A2 | 23KV科52線 S相AMP | FEEDER | E02/22/K252/I_S |  |  |  | CDC | 289 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科52線 | 科52線 |  | 科52線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科52線A3 | 23KV科52線 T相AMP | FEEDER | E02/22/K252/I_T |  |  |  | CDC | 290 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科52線 | 科52線 |  | 科52線A0 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科52線A0 | 23KV科52線 N相AMP | FEEDER | E02/22/K252/I_N |  |  |  | CDC | 291 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科53線 | 科53線 |  | 科53線KVAR | [17 empty] | 1-DA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科53線KVAR | 23KV科53線 KVAR | FEEDER | E02/22/K253/KVAR |  |  |  | CDC | 292 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科53線 | 科53線 |  | 科53線A1 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科53線A1 | 23KV科53線 R相AMP | FEEDER | E02/22/K253/I_R |  |  |  | CDC | 293 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科53線 | 科53線 |  | 科53線A2 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科53線A2 | 23KV科53線 S相AMP | FEEDER | E02/22/K253/I_S |  |  |  | CDC | 294 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科53線 | 科53線 |  | 科53線A3 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科53線A3 | 23KV科53線 T相AMP | FEEDER | E02/22/K253/I_T |  |  |  | CDC | 295 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科53線 | 科53線 |  | 科53線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科53線A0 | 23KV科53線 N相AMP | FEEDER | E02/22/K253/I_N |  |  |  | CDC | 296 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科54線 | 科54線 |  | 科54線KVAR | [17 empty] | 1-DF | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科54線KVAR | 23KV科54線 KVAR | FEEDER | E02/22/K254/KVAR |  |  |  | CDC | 297 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科54線 | 科54線 |  | 科54線A1 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科54線A1 | 23KV科54線 R相AMP | FEEDER | E02/22/K254/I_R |  |  |  | CDC | 298 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科54線 | 科54線 |  | 科54線A2 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科54線A2 | 23KV科54線 S相AMP | FEEDER | E02/22/K254/I_S |  |  |  | CDC | 299 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科54線 | 科54線 |  | 科54線A3 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科54線A3 | 23KV科54線 T相AMP | FEEDER | E02/22/K254/I_T |  |  |  | CDC | 300 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | 科54線 | 科54線 |  | 科54線A0 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_2 | [8 empty] | 南科ES.科54線A0 | 23KV科54線 N相AMP | FEEDER | E02/22/K254/I_N |  |  |  | CDC | 301 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _100 | 100 |  | I_R | [17 empty] | 3-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_100_A1 | 23KV 100 R相AMP | TIE | E02/22/100/I_R |  |  |  | CDC | 302 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _100 | 100 |  | I_S | [17 empty] | 3-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_100_A2 | 23KV 100 S相AMP | TIE | E02/22/100/I_S |  |  |  | CDC | 303 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 22 | 22kV | _100 | 100 |  | I_T | [17 empty] | 3-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.23KV_100_A3 | 23KV 100 T相AMP | TIE | E02/22/100/I_T |  |  |  | CDC | 304 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1720LPD | 南科積P3線(1720) |  | V | [17 empty] | 3-D7 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1720LPD_KV | 南科積P3線(1720) LPD KV | LINE161 | E02/161/1720/V |  |  |  | CDC | 305 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | MW | [17 empty] | 1-8F | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1580_MW | 南科道爺四路 MW | LINE161 | E02/161/1580/MW |  |  |  | CDC | 306 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | MVAR | [17 empty] | 1-90 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1580_MVAR | 南科道爺四路 MVAR | LINE161 | E02/161/1580/MVAR |  |  |  | CDC | 307 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1580LPD | 南科道爺四路(1580) |  | V | [17 empty] | 3-D8 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1580LPD_KV | 南科道爺四路(1580) LPD KV | LINE161 | E02/161/1580/V |  |  |  | CDC | 308 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1550LPD | 三福科線(1550) |  | V | [17 empty] | 3-D9 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1550LPD_KV | 三福科線(1550) LPD KV | LINE161 | E02/161/1550/V |  |  |  | CDC | 309 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | MW | [17 empty] | 1-85 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1530_MW | 南科三福一線 MW | LINE161 | E02/161/1530/MW |  |  |  | CDC | 310 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | MVAR | [17 empty] | 1-86 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1530_MVAR | 南科三福一線 MVAR | LINE161 | E02/161/1530/MVAR |  |  |  | CDC | 311 | GENERICAIPoint | ES002_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
E02 | 南科ES | 161 | 161kV | 1530LPD | 南科三福一線(1530) |  | V | [17 empty] | 3-DA | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1530LPD_KV | 南科三福一線(1530) LPD KV | LINE161 | E02/161/1530/V |  |  |  | CDC | 312 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1540LPD | 南科積E六線(1540) |  | V | [17 empty] | 3-DB | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 南科ES.1540LPD_KV | 南科積E六線(1540) LPD KV | LINE161 | E02/161/1540/V |  |  |  | CDC | 313 | GENERICAIPoint | ES002_L3 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | PHA | [17 empty] | 1-01-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1510_PHA | 南科道爺ㄧ路(1510) 相間RY | LINE161 | E02/161/1510/PHA |  |  |  | CDC | 314 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | GDA | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1510_GDA | 南科道爺ㄧ路(1510) 接地RY | LINE161 | E02/161/1510/GDA |  |  |  | CDC | 315 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | CB | [17 empty] | 1-01-00 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1510_CB | 1510(南科道爺ㄧ路) CB | LINE161 | E02/161/1510/CB |  |  |  | CDC | 316 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | 79UL | [17 empty] | 1-30-07 |  | 1-6B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1510_79UL | 南科道爺ㄧ路(1510) 79RY U/L | LINE161 | E02/161/1510/79UL |  |  |  | CDC | 317 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | DS1 | 1511 | [16 empty] | 1-38-08 | 1-38-09 | 1-2C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1511_DS | 1511(南科道爺ㄧ路) DS | LINE161 | E02/161/1510/DS1 |  |  |  | CDC | 318 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | DS2 | 1512 | [16 empty] | 1-38-10 | 1-38-11 | 1-2D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1512_DS | 1512(南科道爺ㄧ路) DS | LINE161 | E02/161/1510/DS2 |  |  |  | CDC | 319 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | DS3 | 1513 | [16 empty] | 1-38-12 | 1-38-13 | 1-2E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1513_DS | 1513(南科道爺ㄧ路) DS | LINE161 | E02/161/1510/DS3 |  |  |  | CDC | 320 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | E3 | 1513E | [16 empty] | 1-38-14 | 1-38-15 | 1-2F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1513E_ES | 1513E(南科道爺ㄧ路) ES | LINE161 | E02/161/1510/E3 |  |  |  | CDC | 321 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | PHA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1520_PHA | 南科道爺二路(1520) 相間RY | LINE161 | E02/161/1520/PHA |  |  |  | CDC | 322 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | GDA | [17 empty] | 1-01-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1520_GDA | 南科道爺二路(1520) 接地RY | LINE161 | E02/161/1520/GDA |  |  |  | CDC | 323 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | CB | [17 empty] | 1-01-04 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1520_CB | 1520(南科道爺二路) CB | LINE161 | E02/161/1520/CB |  |  |  | CDC | 324 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | 79UL | [17 empty] | 1-30-11 |  | 1-6D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1520_79UL | 南科道爺二路(1520) 79RY U/L | LINE161 | E02/161/1520/79UL |  |  |  | CDC | 325 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | DS1 | 1521 | [16 empty] | 1-39-00 | 1-39-01 | 1-30 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1521_DS | 1521(南科道爺二路) DS | LINE161 | E02/161/1520/DS1 |  |  |  | CDC | 326 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | DS2 | 1522 | [16 empty] | 1-39-02 | 1-39-03 | 1-31 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1522_DS | 1522(南科道爺二路) DS | LINE161 | E02/161/1520/DS2 |  |  |  | CDC | 327 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | DS3 | 1523 | [16 empty] | 1-39-04 | 1-39-05 | 1-32 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1523_DS | 1523(南科道爺二路) DS | LINE161 | E02/161/1520/DS3 |  |  |  | CDC | 328 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | E3 | 1523E | [16 empty] | 1-39-06 | 1-39-07 | 1-33 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1523E_ES | 1523E(南科道爺二路) ES | LINE161 | E02/161/1520/E3 |  |  |  | CDC | 329 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | PHA | [17 empty] | 1-02-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1550_PHA | 三福科線(1550) 相間RY | LINE161 | E02/161/1550/PHA |  |  |  | CDC | 330 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | GDA | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1550_GDA | 三福科線(1550) 接地RY | LINE161 | E02/161/1550/GDA |  |  |  | CDC | 331 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | 85A | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1550_85A | 三福科線(1550) 85RY | LINE161 | E02/161/1550/85A |  |  |  | CDC | 332 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | CB | [17 empty] | 1-02-04 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1550_CB | 1550(三福科線) CB | LINE161 | E02/161/1550/CB |  |  |  | CDC | 333 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | DS1 | 1551 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-3A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1551_DS | 1551(三福科線) DS | LINE161 | E02/161/1550/DS1 |  |  |  | CDC | 334 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | DS2 | 1552 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-3B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1552_DS | 1552(三福科線) DS | LINE161 | E02/161/1550/DS2 |  |  |  | CDC | 335 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | DS3 | 1553 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-3C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1553_DS | 1553(三福科線) DS | LINE161 | E02/161/1550/DS3 |  |  |  | CDC | 336 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1550 | 三福科線(1550) |  | E3 | 1553E | [16 empty] | 1-3A-10 | 1-3A-11 | 1-3D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1553E_ES | 1553E(三福科線) ES | LINE161 | E02/161/1550/E3 |  |  |  | CDC | 337 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | PHA | [17 empty] | 1-04-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1610_PHA | 麻工ㄧ路(1610) 相間RY | LINE161 | E02/161/1610/PHA |  |  |  | CDC | 338 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | GDA | [17 empty] | 1-04-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1610_GDA | 麻工ㄧ路(1610) 接地RY | LINE161 | E02/161/1610/GDA |  |  |  | CDC | 339 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | 85A | [17 empty] | 1-04-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1610_85A | 麻工ㄧ路(1610) 85RY | LINE161 | E02/161/1610/85A |  |  |  | CDC | 340 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | 85UL | [17 empty] | 1-32-02 |  | 1-78 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1610_85UL | 麻工ㄧ路(1610) 85RY U/L | LINE161 | E02/161/1610/85UL |  |  |  | CDC | 341 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | CB | [17 empty] | 1-04-04 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 南科ES.1610_CB | 1610(麻工ㄧ路) CB | LINE161 | E02/161/1610/CB |  |  |  | CDC | 342 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | 79UL | [17 empty] | 1-32-03 |  | 1-79 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1610_79UL | 麻工ㄧ路(1610) 79RY U/L | LINE161 | E02/161/1610/79UL |  |  |  | CDC | 343 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | DS1 | 1611 | [16 empty] | 1-3C-04 | 1-3C-05 | 1-4A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1611_DS | 1611(麻工ㄧ路) DS | LINE161 | E02/161/1610/DS1 |  |  |  | CDC | 344 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | DS2 | 1612 | [16 empty] | 1-3C-06 | 1-3C-07 | 1-4B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1612_DS | 1612(麻工ㄧ路) DS | LINE161 | E02/161/1610/DS2 |  |  |  | CDC | 345 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | DS3 | 1613 | [16 empty] | 1-3C-08 | 1-3C-09 | 1-4C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1613_DS | 1613(麻工ㄧ路) DS | LINE161 | E02/161/1610/DS3 |  |  |  | CDC | 346 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | E3 | 1613E | [16 empty] | 1-3C-10 | 1-3C-11 | 1-4D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1613E_ES | 1613E(麻工ㄧ路) ES | LINE161 | E02/161/1610/E3 |  |  |  | CDC | 347 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | 85FA | [17 empty] | 1-32-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1610_85FA | 麻工ㄧ路(1610) 85FA | LINE161 | E02/161/1610/2A5Other |  |  |  | CDC | 348 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1610 | 麻工ㄧ路(1610) |  | RYFA | [17 empty] | 1-32-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1610_85UA | 麻工ㄧ路(1610) 85uA | LINE161 | E02/161/1610/RYFA |  |  |  | CDC | 349 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | PHA | [17 empty] | 1-05-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1620_PHA | 麻工二路(1620) 相間RY | LINE161 | E02/161/1620/PHA |  |  |  | CDC | 350 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | GDA | [17 empty] | 1-05-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1620_GDA | 麻工二路(1620) 接地RY | LINE161 | E02/161/1620/GDA |  |  |  | CDC | 351 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | 85A | [17 empty] | 1-05-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1620_85A | 麻工二路(1620) 85RY | LINE161 | E02/161/1620/85A |  |  |  | CDC | 352 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | 85UL | [17 empty] | 1-32-06 |  | 1-7A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1620_85UL | 麻工二路(1620) 85RY U/L | LINE161 | E02/161/1620/85UL |  |  |  | CDC | 353 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | CB | [17 empty] | 1-05-00 |  | 1-0B | [5 empty] | 161KV_S | [8 empty] | 南科ES.1620_CB | 1620(麻工二路) CB | LINE161 | E02/161/1620/CB |  |  |  | CDC | 354 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | 79UL | [17 empty] | 1-32-07 |  | 1-7B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1620_79UL | 麻工二路(1620) 79RY U/L | LINE161 | E02/161/1620/79UL |  |  |  | CDC | 355 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | DS1 | 1621 | [16 empty] | 1-3C-12 | 1-3C-13 | 1-4E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1621_DS | 1621(麻工二路) DS | LINE161 | E02/161/1620/DS1 |  |  |  | CDC | 356 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | DS2 | 1622 | [16 empty] | 1-3C-14 | 1-3C-15 | 1-4F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1622_DS | 1622(麻工二路) DS | LINE161 | E02/161/1620/DS2 |  |  |  | CDC | 357 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | DS3 | 1623 | [16 empty] | 1-3D-00 | 1-3D-01 | 1-50 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1623_DS | 1623(麻工二路) DS | LINE161 | E02/161/1620/DS3 |  |  |  | CDC | 358 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | E3 | 1623E | [16 empty] | 1-3D-02 | 1-3D-03 | 1-51 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1623E_ES | 1623E(麻工二路) ES | LINE161 | E02/161/1620/E3 |  |  |  | CDC | 359 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | 85FA | [17 empty] | 1-32-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1620_85FA | 麻工二路(1620) 85FA | LINE161 | E02/161/1620/2A5Other |  |  |  | CDC | 360 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1620 | 麻工二路(1620) |  | RYFA | [17 empty] | 1-32-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1620_85UA | 麻工二路(1620) 85uA | LINE161 | E02/161/1620/RYFA |  |  |  | CDC | 361 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | PHA | [17 empty] | 1-06-04 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1630_PHA | 南科豐華紅線(1630) 相間RY | LINE161 | E02/161/1630/PHA |  |  |  | CDC | 362 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | GDA | [17 empty] | 1-06-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1630_GDA | 南科豐華紅線(1630) 接地RY | LINE161 | E02/161/1630/GDA |  |  |  | CDC | 363 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | CB | [17 empty] | 1-06-02 |  | 1-0E | [5 empty] | 161KV_S | [8 empty] | 南科ES.1630_CB | 1630(南科豐華紅線) CB | LINE161 | E02/161/1630/CB |  |  |  | CDC | 364 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | 79UL | [17 empty] | 1-32-11 |  | 1-7D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1630_79UL | 南科豐華紅線(1630) 79RY U/L | LINE161 | E02/161/1630/79UL |  |  |  | CDC | 365 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | DS1 | 1631 | [16 empty] | 1-3D-12 | 1-3D-13 | 1-56 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1631_DS | 1631(南科豐華紅線) DS | LINE161 | E02/161/1630/DS1 |  |  |  | CDC | 366 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | DS2 | 1632 | [16 empty] | 1-3D-14 | 1-3D-15 | 1-57 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1632_DS | 1632(南科豐華紅線) DS | LINE161 | E02/161/1630/DS2 |  |  |  | CDC | 367 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | DS3 | 1633 | [16 empty] | 1-3E-00 | 1-3E-01 | 1-58 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1633_DS | 1633(南科豐華紅線) DS | LINE161 | E02/161/1630/DS3 |  |  |  | CDC | 368 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | E3 | 1633E | [16 empty] | 1-3E-02 | 1-3E-03 | 1-59 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1633E_ES | 1633E(南科豐華紅線) ES | LINE161 | E02/161/1630/E3 |  |  |  | CDC | 369 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | PHA | [17 empty] | 1-07-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1640_PHA | 南科豐華白線(1640) 相間RY | LINE161 | E02/161/1640/PHA |  |  |  | CDC | 370 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | GDA | [17 empty] | 1-07-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1640_GDA | 南科豐華白線(1640) 接地RY | LINE161 | E02/161/1640/GDA |  |  |  | CDC | 371 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | CB | [17 empty] | 1-06-06 |  | 1-0F | [5 empty] | 161KV_S | [8 empty] | 南科ES.1640_CB | 1640(南科豐華白線) CB | LINE161 | E02/161/1640/CB |  |  |  | CDC | 372 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | 79UL | [17 empty] | 1-32-15 |  | 1-7F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1640_79UL | 南科豐華白線(1640) 79RY U/L | LINE161 | E02/161/1640/79UL |  |  |  | CDC | 373 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | DS1 | 1641 | [16 empty] | 1-3E-04 | 1-3E-05 | 1-5A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1641_DS | 1641(南科豐華白線) DS | LINE161 | E02/161/1640/DS1 |  |  |  | CDC | 374 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | DS2 | 1642 | [16 empty] | 1-3E-06 | 1-3E-07 | 1-5B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1642_DS | 1642(南科豐華白線) DS | LINE161 | E02/161/1640/DS2 |  |  |  | CDC | 375 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | DS3 | 1643 | [16 empty] | 1-3E-08 | 1-3E-09 | 1-5C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1643_DS | 1643(南科豐華白線) DS | LINE161 | E02/161/1640/DS3 |  |  |  | CDC | 376 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1640 | 南科豐華白線(1640) |  | E3 | 1643E | [16 empty] | 1-3E-10 | 1-3E-11 | 1-5D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1643E_ES | 1643E(南科豐華白線) ES | LINE161 | E02/161/1640/E3 |  |  |  | CDC | 377 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | PHA | [17 empty] | 3-00-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1650_PHA | 三竹ㄧ路(1650) 相間RY | LINE161 | E02/161/1650/PHA |  |  |  | CDC | 378 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | GDA | [17 empty] | 3-00-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1650_GDA | 三竹ㄧ路(1650) 接地RY | LINE161 | E02/161/1650/GDA |  |  |  | CDC | 379 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | CB | [17 empty] | 3-00-04 |  | 3-01 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1650_CB | 1650(三竹ㄧ路) CB | LINE161 | E02/161/1650/CB |  |  |  | CDC | 380 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | 79UL | [17 empty] | 3-38-05 |  | 2-73 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1650_79UL | 三竹ㄧ路(1650) 79RY U/L | LINE161 | E02/161/1650/79UL |  |  |  | CDC | 381 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | DS1 | 1651 | [16 empty] | 3-30-08 | 3-30-09 | 3-0C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1651_DS | 1651(三竹ㄧ路) DS | LINE161 | E02/161/1650/DS1 |  |  |  | CDC | 382 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | DS2 | 1652 | [16 empty] | 3-30-10 | 3-30-11 | 3-0D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1652_DS | 1652(三竹ㄧ路) DS | LINE161 | E02/161/1650/DS2 |  |  |  | CDC | 383 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | DS3 | 1653 | [16 empty] | 3-30-12 | 3-30-13 | 3-0E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1653_DS | 1653(三竹ㄧ路) DS | LINE161 | E02/161/1650/DS3 |  |  |  | CDC | 384 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1650 | 三竹ㄧ路(1650) |  | E3 | 1653E | [16 empty] | 3-30-14 | 3-30-15 | 3-0F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1653E_ES | 1653E(三竹ㄧ路) ES | LINE161 | E02/161/1650/E3 |  |  |  | CDC | 385 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | PHA | [17 empty] | 3-00-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1660_PHA | 三竹二路(1660) 相間RY | LINE161 | E02/161/1660/PHA |  |  |  | CDC | 386 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | GDA | [17 empty] | 3-00-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1660_GDA | 三竹二路(1660) 接地RY | LINE161 | E02/161/1660/GDA |  |  |  | CDC | 387 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | CB | [17 empty] | 3-00-00 |  | 3-00 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1660_CB | 1660(三竹二路) CB | LINE161 | E02/161/1660/CB |  |  |  | CDC | 388 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | 79UL | [17 empty] | 3-38-01 |  | 2-71 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1660_79UL | 三竹二路(1660) 79RY U/L | LINE161 | E02/161/1660/79UL |  |  |  | CDC | 389 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | DS1 | 1661 | [16 empty] | 3-30-00 | 3-30-01 | 3-08 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1661_DS | 1661(三竹二路) DS | LINE161 | E02/161/1660/DS1 |  |  |  | CDC | 390 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | DS2 | 1662 | [16 empty] | 3-30-02 | 3-30-03 | 3-09 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1662_DS | 1662(三竹二路) DS | LINE161 | E02/161/1660/DS2 |  |  |  | CDC | 391 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | DS3 | 1663 | [16 empty] | 3-30-04 | 3-30-05 | 3-0A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1663_DS | 1663(三竹二路) DS | LINE161 | E02/161/1660/DS3 |  |  |  | CDC | 392 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1660 | 三竹二路(1660) |  | E3 | 1663E | [16 empty] | 3-30-06 | 3-30-07 | 3-0B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1663E_ES | 1663E(三竹二路) ES | LINE161 | E02/161/1660/E3 |  |  |  | CDC | 393 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | PHA | [17 empty] | 3-01-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1670_PHA | 積六線(1670) 相間RY | LINE161 | E02/161/1670/PHA |  |  |  | CDC | 394 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | GDA | [17 empty] | 3-01-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1670_GDA | 積六線(1670) 接地RY | LINE161 | E02/161/1670/GDA |  |  |  | CDC | 395 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | 85A | [17 empty] | 3-01-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1670_85A | 積六線(1670) 85RY | LINE161 | E02/161/1670/85A |  |  |  | CDC | 396 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | CB | [17 empty] | 3-01-00 |  | 3-02 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1670_CB | 1670(積六線) CB | LINE161 | E02/161/1670/CB |  |  |  | CDC | 397 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | 79UL | [17 empty] | 3-38-09 |  | 2-75 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1670_79UL | 積六線(1670) 79RY U/L | LINE161 | E02/161/1670/79UL |  |  |  | CDC | 398 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | DS1 | 1671 | [16 empty] | 3-31-00 | 3-31-01 | 3-10 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1671_DS | 1671(積六線) DS | LINE161 | E02/161/1670/DS1 |  |  |  | CDC | 399 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | DS2 | 1672 | [16 empty] | 3-31-02 | 3-31-03 | 3-11 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1672_DS | 1672(積六線) DS | LINE161 | E02/161/1670/DS2 |  |  |  | CDC | 400 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | DS3 | 1673 | [16 empty] | 3-31-04 | 3-31-05 | 3-12 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1673_DS | 1673(積六線) DS | LINE161 | E02/161/1670/DS3 |  |  |  | CDC | 401 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1670 | 積六線(1670) |  | E3 | 1673E | [16 empty] | 3-31-06 | 3-31-07 | 3-13 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1673E_ES | 1673E(積六線) ES | LINE161 | E02/161/1670/E3 |  |  |  | CDC | 402 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | PHA | [17 empty] | 3-02-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1680_PHA | 康寧線(1680) 相間RY | LINE161 | E02/161/1680/PHA |  |  |  | CDC | 403 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | GDA | [17 empty] | 3-02-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1680_GDA | 康寧線(1680) 接地RY | LINE161 | E02/161/1680/GDA |  |  |  | CDC | 404 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | 87L1TA | [17 empty] | 3-02-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1680_87L1TA | 康寧線(1680) 87L1TA RY | LINE161 | E02/161/1680/21A |  |  |  | CDC | 405 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | 87L2TA | [17 empty] | 3-02-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1680_87L2TA | 康寧線(1680) 87L2TA | LINE161 | E02/161/1680/1A5Other |  |  |  | CDC | 406 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | CB | [17 empty] | 3-01-06 |  | 3-03 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1680_CB | 1680(康寧線) CB | LINE161 | E02/161/1680/CB |  |  |  | CDC | 407 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | DS1 | 1681 | [16 empty] | 3-31-08 | 3-31-09 | 3-14 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1681_DS | 1681(康寧線) DS | LINE161 | E02/161/1680/DS1 |  |  |  | CDC | 408 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | DS2 | 1682 | [16 empty] | 3-31-10 | 3-31-11 | 3-15 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1682_DS | 1682(康寧線) DS | LINE161 | E02/161/1680/DS2 |  |  |  | CDC | 409 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | DS3 | 1683 | [16 empty] | 3-31-12 | 3-31-13 | 3-16 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1683_DS | 1683(康寧線) DS | LINE161 | E02/161/1680/DS3 |  |  |  | CDC | 410 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1680 | 康寧線(1680) |  | E3 | 1683E | [16 empty] | 3-31-14 | 3-31-15 | 3-17 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1683E_ES | 1683E(康寧線) ES | LINE161 | E02/161/1680/E3 |  |  |  | CDC | 411 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | PHA | [17 empty] | 3-02-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1710_PHA | 南科和鑫二線(1710) 相間RY | LINE161 | E02/161/1710/PHA |  |  |  | CDC | 412 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | GDA | [17 empty] | 3-02-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1710_GDA | 南科和鑫二線(1710) 接地RY | LINE161 | E02/161/1710/GDA |  |  |  | CDC | 413 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | 87L1TA | [17 empty] | 3-03-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1710_87L1TA | 南科和鑫二線(1710) 87L1TA RY | LINE161 | E02/161/1710/21A |  |  |  | CDC | 414 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | 87L2TA | [17 empty] | 3-03-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1710_87L2TA | 南科和鑫二線(1710) 87L2TA | LINE161 | E02/161/1710/1A5Other |  |  |  | CDC | 415 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | CB | [17 empty] | 3-02-04 |  | 3-04 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1710_CB | 1710(南科和鑫二線) CB | LINE161 | E02/161/1710/CB |  |  |  | CDC | 416 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | DS1 | 1711 | [16 empty] | 3-32-00 | 3-32-01 | 3-18 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1711_DS | 1711(南科和鑫二線) DS | LINE161 | E02/161/1710/DS1 |  |  |  | CDC | 417 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | DS2 | 1712 | [16 empty] | 3-32-02 | 3-32-03 | 3-19 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1712_DS | 1712(南科和鑫二線) DS | LINE161 | E02/161/1710/DS2 |  |  |  | CDC | 418 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | DS3 | 1713 | [16 empty] | 3-32-04 | 3-32-05 | 3-1A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1713_DS | 1713(南科和鑫二線) DS | LINE161 | E02/161/1710/DS3 |  |  |  | CDC | 419 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | E3 | 1713E | [16 empty] | 3-32-06 | 3-32-07 | 3-1B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1713E_ES | 1713E(南科和鑫二線) ES | LINE161 | E02/161/1710/E3 |  |  |  | CDC | 420 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | PHA | [17 empty] | 3-03-04 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1720_PHA | 南科積P3線(1720) 相間RY | LINE161 | E02/161/1720/PHA |  |  |  | CDC | 421 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | GDA | [17 empty] | 3-03-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1720_GDA | 南科積P3線(1720) 接地RY | LINE161 | E02/161/1720/GDA |  |  |  | CDC | 422 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | 87L1TA | [17 empty] | 3-03-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1720_87L1TA | 南科積P3線(1720) 87L1TA RY | LINE161 | E02/161/1720/21A |  |  |  | CDC | 423 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | 87L2TA | [17 empty] | 3-03-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1720_87L2TA | 南科積P3線(1720) 87L2TA | LINE161 | E02/161/1720/1A5Other |  |  |  | CDC | 424 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | CB | [17 empty] | 3-03-02 |  | 3-05 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1720_CB | 1720(南科積P3線) CB | LINE161 | E02/161/1720/CB |  |  |  | CDC | 425 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | DS1 | 1721 | [16 empty] | 3-32-08 | 3-32-09 | 3-1C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1721_DS | 1721(南科積P3線) DS | LINE161 | E02/161/1720/DS1 |  |  |  | CDC | 426 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | DS2 | 1722 | [16 empty] | 3-32-10 | 3-32-11 | 3-1D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1722_DS | 1722(南科積P3線) DS | LINE161 | E02/161/1720/DS2 |  |  |  | CDC | 427 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | DS3 | 1723 | [16 empty] | 3-32-12 | 3-32-13 | 3-1E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1723_DS | 1723(南科積P3線) DS | LINE161 | E02/161/1720/DS3 |  |  |  | CDC | 428 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | E3 | 1723E | [16 empty] | 3-32-14 | 3-32-15 | 3-1F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1723E_ES | 1723E(南科積P3線) ES | LINE161 | E02/161/1720/E3 |  |  |  | CDC | 429 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | PHA | [17 empty] | 3-04-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1730_PHA | 積十八線(1730) 相間RY | LINE161 |  |  |  |  | CDC | 430 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | GDA | [17 empty] | 3-04-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1730_GDA | 積十八線(1730) 接地RY | LINE161 |  |  |  |  | CDC | 431 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | 85A | [17 empty] | 3-04-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1730_85A | 積十八線(1730) 85RY | LINE161 |  |  |  |  | CDC | 432 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | 85UL | [17 empty] | 3-39-08 |  | 2-7C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1730_85UL | 積十八線(1730) 85RY U/L | LINE161 |  |  |  |  | CDC | 433 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | 87L1TA | [17 empty] | 3-04-04 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1730_87L1TA | 積十八線(1730) 87L1TA RY | LINE161 |  |  |  |  | CDC | 434 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | 87L2TA | [17 empty] | 3-04-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1730_87L2TA | 積十八線(1730) 87L2TA | LINE161 |  |  |  |  | CDC | 435 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | CB | [17 empty] | 3-04-00 |  | 3-06 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1730_CB | 1730(積十八線) CB | LINE161 |  |  |  |  | CDC | 436 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | 79UL | [17 empty] | 3-39-09 |  | 2-7D | [5 empty] | ADCS_S | [8 empty] | 南科ES.1730_79UL | 積十八線(1730) 79RY U/L | LINE161 |  |  |  |  | CDC | 437 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | DS1 | 1731 | [16 empty] | 3-33-00 | 3-33-01 | 3-20 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1731_DS | 1731(積十八線) DS | LINE161 |  |  |  |  | CDC | 438 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | DS2 | 1732 | [16 empty] | 3-33-02 | 3-33-03 | 3-21 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1732_DS | 1732(積十八線) DS | LINE161 |  |  |  |  | CDC | 439 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | DS3 | 1733 | [16 empty] | 3-33-04 | 3-33-05 | 3-22 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1733_DS | 1733(積十八線) DS | LINE161 |  |  |  |  | CDC | 440 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | E3 | 1733E | [16 empty] | 3-33-06 | 3-33-07 | 3-23 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1733E_ES | 1733E(積十八線) ES | LINE161 |  |  |  |  | CDC | 441 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | 85FA | [17 empty] | 3-39-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1730_85FA | 積十八線(1730) 85FA | LINE161 |  |  |  |  | CDC | 442 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1730 | 積十八線(1730) |  | RYFA | [17 empty] | 3-39-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1730_85UA | 積十八線(1730) 85uA | LINE161 |  |  |  |  | CDC | 443 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | PHA | [17 empty] | 3-05-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1740_PHA | 積十九線(1740) 相間RY | LINE161 |  |  |  |  | CDC | 444 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | GDA | [17 empty] | 3-05-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1740_GDA | 積十九線(1740) 接地RY | LINE161 |  |  |  |  | CDC | 445 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | 85A | [17 empty] | 3-04-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1740_85A | 積十九線(1740) 85RY | LINE161 |  |  |  |  | CDC | 446 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | 85UL | [17 empty] | 3-39-12 |  | 2-7E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1740_85UL | 積十九線(1740) 85RY U/L | LINE161 |  |  |  |  | CDC | 447 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | 87L1TA | [17 empty] | 3-05-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1740_87L1TA | 積十九線(1740) 87L1TA RY | LINE161 |  |  |  |  | CDC | 448 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | 87L2TA | [17 empty] | 3-05-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1740_87L2TA | 積十九線(1740) 87L2TA | LINE161 |  |  |  |  | CDC | 449 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | CB | [17 empty] | 3-04-06 |  | 3-07 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1740_CB | 1740(積十九線) CB | LINE161 |  |  |  |  | CDC | 450 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | 79UL | [17 empty] | 3-39-13 |  | 2-7F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1740_79UL | 積十九線(1740) 79RY U/L | LINE161 |  |  |  |  | CDC | 451 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | DS1 | 1741 | [16 empty] | 3-33-08 | 3-33-09 | 3-24 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1741_DS | 1741(積十九線) DS | LINE161 |  |  |  |  | CDC | 452 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | DS2 | 1742 | [16 empty] | 3-33-10 | 3-33-11 | 3-25 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1742_DS | 1742(積十九線) DS | LINE161 |  |  |  |  | CDC | 453 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | DS3 | 1743 | [16 empty] | 3-33-12 | 3-33-13 | 3-26 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1743_DS | 1743(積十九線) DS | LINE161 |  |  |  |  | CDC | 454 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | E3 | 1743E | [16 empty] | 3-33-14 | 3-33-15 | 3-27 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1743E_ES | 1743E(積十九線) ES | LINE161 |  |  |  |  | CDC | 455 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | 85FA | [17 empty] | 3-39-14 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1740_85FA | 積十九線(1740) 85FA | LINE161 |  |  |  |  | CDC | 456 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1740 | 積十九線(1740) |  | RYFA | [17 empty] | 3-39-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1740_85UA | 積十九線(1740) 85uA | LINE161 |  |  |  |  | CDC | 457 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K216 | 科十六線(K216) |  | PHA | [17 empty] | 2-02-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_PHA | 11KV科十六線(K216) 相間RY | FEEDER | E02/11/K216/PHA |  |  |  | CDC | 458 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K216 | 科十六線(K216) |  | GDA | [17 empty] | 2-02-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_GDA | 11KV科十六線(K216) 接地RY | FEEDER | E02/11/K216/GDA |  |  |  | CDC | 459 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K216 | 科十六線(K216) 79RY |  | 79UL | [17 empty] | 2-38-13 |  | 2-3A | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_79UL | 11KV科十六線(K216) 79RY U/L | FEEDER | E02/11/K216/79UL |  |  |  | CDC | 460 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K216_LCO | 科十六線(K216) LCO |  | TapPosMv | [17 empty] | 2-38-14 |  | 2-3B | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_LCO_TAP | 11KV科十六線(K216) LCO TAP | FEEDER | E02/11/K216/IED_ADJ |  |  |  | CDC | 461 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K216 | K216(11KV科十六線) |  | CB | [17 empty] | 2-02-02 |  | 2-07 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K216_CB | K216(11KV科十六線) CB | FEEDER | E02/11/K216/CB |  |  |  | CDC | 462 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K217 | 科十七線(K217) |  | PHA | [17 empty] | 2-02-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_PHA | 11KV科十七線(K217) 相間RY | FEEDER | E02/11/K217/PHA |  |  |  | CDC | 463 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K217 | 科十七線(K217) |  | GDA | [17 empty] | 2-02-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_GDA | 11KV科十七線(K217) 接地RY | FEEDER | E02/11/K217/GDA |  |  |  | CDC | 464 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K217 | 科十七線(K217) 79RY |  | 79UL | [17 empty] | 2-38-15 |  | 2-3C | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_79UL | 11KV科十七線(K217) 79RY U/L | FEEDER | E02/11/K217/79UL |  |  |  | CDC | 465 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K217_LCO | 科十七線(K217) LCO |  | TapPosMv | [17 empty] | 2-39-00 |  | 2-3D | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_LCO_TAP | 11KV科十七線(K217) LCO TAP | FEEDER | E02/11/K217/IED_ADJ |  |  |  | CDC | 466 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K217 | K217(11KV科十七線) |  | CB | [17 empty] | 2-02-05 |  | 2-08 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K217_CB | K217(11KV科十七線) CB | FEEDER | E02/11/K217/CB |  |  |  | CDC | 467 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K218 | 科十八線(K218) |  | PHA | [17 empty] | 2-03-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_PHA | 11KV科十八線(K218) 相間RY | FEEDER | E02/11/K218/PHA |  |  |  | CDC | 468 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K218 | 科十八線(K218) |  | GDA | [17 empty] | 2-03-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_GDA | 11KV科十八線(K218) 接地RY | FEEDER | E02/11/K218/GDA |  |  |  | CDC | 469 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K218 | 科十八線(K218) 79RY |  | 79UL | [17 empty] | 2-39-01 |  | 2-3E | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_79UL | 11KV科十八線(K218) 79RY U/L | FEEDER | E02/11/K218/79UL |  |  |  | CDC | 470 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K218_LCO | 科十八線(K218) LCO |  | TapPosMv | [17 empty] | 2-39-02 |  | 2-3F | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_LCO_TAP | 11KV科十八線(K218) LCO TAP | FEEDER | E02/11/K218/IED_ADJ |  |  |  | CDC | 471 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K218 | K218(11KV科十八線) |  | CB | [17 empty] | 2-03-00 |  | 2-09 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K218_CB | K218(11KV科十八線) CB | FEEDER | E02/11/K218/CB |  |  |  | CDC | 472 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K219 | 科十九線(K219) |  | PHA | [17 empty] | 2-03-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_PHA | 11KV科十九線(K219) 相間RY | FEEDER | E02/11/K219/PHA |  |  |  | CDC | 473 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K219 | 科十九線(K219) |  | GDA | [17 empty] | 2-03-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_GDA | 11KV科十九線(K219) 接地RY | FEEDER | E02/11/K219/GDA |  |  |  | CDC | 474 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K219 | 科十九線(K219) 79RY |  | 79UL | [17 empty] | 2-39-03 |  | 2-40 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_79UL | 11KV科十九線(K219) 79RY U/L | FEEDER | E02/11/K219/79UL |  |  |  | CDC | 475 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K219_LCO | 科十九線(K219) LCO |  | TapPosMv | [17 empty] | 2-39-04 |  | 2-41 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_LCO_TAP | 11KV科十九線(K219) LCO TAP | FEEDER | E02/11/K219/IED_ADJ |  |  |  | CDC | 476 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K219 | K219(11KV科十九線) |  | CB | [17 empty] | 2-03-03 |  | 2-0A | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K219_CB | K219(11KV科十九線) CB | FEEDER | E02/11/K219/CB |  |  |  | CDC | 477 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K220 | 科二十線(K220) |  | PHA | [17 empty] | 2-03-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_PHA | 11KV科二十線(K220) 相間RY | FEEDER | E02/11/K220/PHA |  |  |  | CDC | 478 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K220 | 科二十線(K220) |  | GDA | [17 empty] | 2-04-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_GDA | 11KV科二十線(K220) 接地RY | FEEDER | E02/11/K220/GDA |  |  |  | CDC | 479 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K220 | 科二十線(K220) 79RY |  | 79UL | [17 empty] | 2-39-05 |  | 2-42 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_79UL | 11KV科二十線(K220) 79RY U/L | FEEDER | E02/11/K220/79UL |  |  |  | CDC | 480 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K220_LCO | 科二十線(K220) LCO |  | TapPosMv | [17 empty] | 2-39-06 |  | 2-43 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_LCO_TAP | 11KV科二十線(K220) LCO TAP | FEEDER | E02/11/K220/IED_ADJ |  |  |  | CDC | 481 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K220 | K220(11KV科二十線) |  | CB | [17 empty] | 2-03-06 |  | 2-0B | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K220_CB | K220(11KV科二十線) CB | FEEDER | E02/11/K220/CB |  |  |  | CDC | 482 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K261 | 科六一線(K261) |  | PHA | [17 empty] | 2-05-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_PHA | 23KV科六一線(K261) 相間RY | FEEDER | E02/22/K261/PHA |  |  |  | CDC | 483 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K261 | 科六一線(K261) |  | GDA | [17 empty] | 2-05-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_GDA | 23KV科六一線(K261) 接地RY | FEEDER | E02/22/K261/GDA |  |  |  | CDC | 484 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K261 | 科六一線(K261) 79RY |  | 79UL | [17 empty] | 2-39-07 |  | 2-44 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_79UL | 23KV科六一線(K261) 79RY U/L | FEEDER | E02/22/K261/79UL |  |  |  | CDC | 485 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K261_LCO | 科六一線(K261) LCO |  | TapPosMv | [17 empty] | 2-39-08 |  | 2-45 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_LCO_TAP | 23KV科六一線(K261) LCO TAP | FEEDER | E02/22/K261/IED_ADJ |  |  |  | CDC | 486 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K261 | K261(23KV科六一線) |  | CB | [17 empty] | 2-04-07 |  | 2-0F | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K261_CB | K261(23KV科六一線) CB | FEEDER | E02/22/K261/CB |  |  |  | CDC | 487 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K262 | 科六二線(K262) |  | PHA | [17 empty] | 2-05-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_PHA | 23KV科六二線(K262) 相間RY | FEEDER | E02/22/K262/PHA |  |  |  | CDC | 488 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K262 | 科六二線(K262) |  | GDA | [17 empty] | 2-05-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_GDA | 23KV科六二線(K262) 接地RY | FEEDER | E02/22/K262/GDA |  |  |  | CDC | 489 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K262 | 科六二線(K262) 79RY |  | 79UL | [17 empty] | 2-39-09 |  | 2-46 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_79UL | 23KV科六二線(K262) 79RY U/L | FEEDER | E02/22/K262/79UL |  |  |  | CDC | 490 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K262_LCO | 科六二線(K262) LCO |  | TapPosMv | [17 empty] | 2-39-10 |  | 2-47 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_LCO_TAP | 23KV科六二線(K262) LCO TAP | FEEDER | E02/22/K262/IED_ADJ |  |  |  | CDC | 491 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K262 | K262(23KV科六二線) |  | CB | [17 empty] | 2-05-02 |  | 2-10 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K262_CB | K262(23KV科六二線) CB | FEEDER | E02/22/K262/CB |  |  |  | CDC | 492 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K263 | 科六三線(K263) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_PHA | 23KV科六三線(K263) 相間RY | FEEDER | E02/22/K263/PHA |  |  |  | CDC | 493 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K263 | 科六三線(K263) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_GDA | 23KV科六三線(K263) 接地RY | FEEDER | E02/22/K263/GDA |  |  |  | CDC | 494 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K263 | 科六三線(K263) 79RY |  | 79UL | [17 empty] | 2-39-11 |  | 2-48 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_79UL | 23KV科六三線(K263) 79RY U/L | FEEDER | E02/22/K263/79UL |  |  |  | CDC | 495 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K263_LCO | 科六三線(K263) LCO |  | TapPosMv | [17 empty] | 2-39-12 |  | 2-49 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_LCO_TAP | 23KV科六三線(K263) LCO TAP | FEEDER | E02/22/K263/IED_ADJ |  |  |  | CDC | 496 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K263 | K263(23KV科六三線) |  | CB | [17 empty] | 2-05-05 |  | 2-11 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K263_CB | K263(23KV科六三線) CB | FEEDER | E02/22/K263/CB |  |  |  | CDC | 497 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K264 | 科六四線(K264) |  | PHA | [17 empty] | 2-06-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_PHA | 23KV科六四線(K264) 相間RY | FEEDER | E02/22/K264/PHA |  |  |  | CDC | 498 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K264 | 科六四線(K264) |  | GDA | [17 empty] | 2-06-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_GDA | 23KV科六四線(K264) 接地RY | FEEDER | E02/22/K264/GDA |  |  |  | CDC | 499 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K264 | 科六四線(K264) 79RY |  | 79UL | [17 empty] | 2-39-13 |  | 2-4A | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_79UL | 23KV科六四線(K264) 79RY U/L | FEEDER | E02/22/K264/79UL |  |  |  | CDC | 500 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K264_LCO | 科六四線(K264) LCO |  | TapPosMv | [17 empty] | 2-39-14 |  | 2-4B | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_LCO_TAP | 23KV科六四線(K264) LCO TAP | FEEDER | E02/22/K264/IED_ADJ |  |  |  | CDC | 501 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K264 | K264(23KV科六四線) |  | CB | [17 empty] | 2-06-00 |  | 2-12 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K264_CB | K264(23KV科六四線) CB | FEEDER | E02/22/K264/CB |  |  |  | CDC | 502 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K265 | 科六五線(K265) |  | PHA | [17 empty] | 2-07-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_PHA | 23KV科六五線(K265) 相間RY | FEEDER | E02/22/K265/PHA |  |  |  | CDC | 503 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K265 | 科六五線(K265) |  | GDA | [17 empty] | 2-07-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_GDA | 23KV科六五線(K265) 接地RY | FEEDER | E02/22/K265/GDA |  |  |  | CDC | 504 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K265 | 科六五線(K265) 79RY |  | 79UL | [17 empty] | 2-39-15 |  | 2-4C | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_79UL | 23KV科六五線(K265) 79RY U/L | FEEDER | E02/22/K265/79UL |  |  |  | CDC | 505 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K265_LCO | 科六五線(K265) LCO |  | TapPosMv | [17 empty] | 2-3A-00 |  | 2-4D | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_LCO_TAP | 23KV科六五線(K265) LCO TAP | FEEDER | E02/22/K265/IED_ADJ |  |  |  | CDC | 506 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K265 | K265(23KV科六五線) |  | CB | [17 empty] | 2-07-01 |  | 2-15 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K265_CB | K265(23KV科六五線) CB | FEEDER | E02/22/K265/CB |  |  |  | CDC | 507 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K266 | 科六六線(K266) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_PHA | 23KV科六六線(K266) 相間RY | FEEDER | E02/22/K266/PHA |  |  |  | CDC | 508 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K266 | 科六六線(K266) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_GDA | 23KV科六六線(K266) 接地RY | FEEDER | E02/22/K266/GDA |  |  |  | CDC | 509 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K266 | 科六六線(K266) 79RY |  | 79UL | [17 empty] | 2-3A-01 |  | 2-4E | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_79UL | 23KV科六六線(K266) 79RY U/L | FEEDER | E02/22/K266/79UL |  |  |  | CDC | 510 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K266_LCO | 科六六線(K266) LCO |  | TapPosMv | [17 empty] | 2-3A-02 |  | 2-4F | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_LCO_TAP | 23KV科六六線(K266) LCO TAP | FEEDER | E02/22/K266/IED_ADJ |  |  |  | CDC | 511 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K266 | K266(23KV科六六線) |  | CB | [17 empty] | 2-07-04 |  | 2-16 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K266_CB | K266(23KV科六六線) CB | FEEDER | E02/22/K266/CB |  |  |  | CDC | 512 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K267 | 科六七線(K267) |  | PHA | [17 empty] | 2-08-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_PHA | 23KV科六七線(K267) 相間RY | FEEDER | E02/22/K267/PHA |  |  |  | CDC | 513 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K267 | 科六七線(K267) |  | GDA | [17 empty] | 2-08-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_GDA | 23KV科六七線(K267) 接地RY | FEEDER | E02/22/K267/GDA |  |  |  | CDC | 514 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K267 | 科六七線(K267) 79RY |  | 79UL | [17 empty] | 2-3A-03 |  | 2-50 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_79UL | 23KV科六七線(K267) 79RY U/L | FEEDER | E02/22/K267/79UL |  |  |  | CDC | 515 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K267_LCO | 科六七線(K267) LCO |  | TapPosMv | [17 empty] | 2-3A-04 |  | 2-51 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_LCO_TAP | 23KV科六七線(K267) LCO TAP | FEEDER | E02/22/K267/IED_ADJ |  |  |  | CDC | 516 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K267 | K267(23KV科六七線) |  | CB | [17 empty] | 2-07-07 |  | 2-17 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K267_CB | K267(23KV科六七線) CB | FEEDER | E02/22/K267/CB |  |  |  | CDC | 517 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K268 | 科六八線(K268) |  | PHA | [17 empty] | 2-08-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_PHA | 23KV科六八線(K268) 相間RY | FEEDER | E02/22/K268/PHA |  |  |  | CDC | 518 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K268 | 科六八線(K268) |  | GDA | [17 empty] | 2-08-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_GDA | 23KV科六八線(K268) 接地RY | FEEDER | E02/22/K268/GDA |  |  |  | CDC | 519 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K268 | 科六八線(K268) 79RY |  | 79UL | [17 empty] | 2-3A-05 |  | 2-52 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_79UL | 23KV科六八線(K268) 79RY U/L | FEEDER | E02/22/K268/79UL |  |  |  | CDC | 520 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K268_LCO | 科六八線(K268) LCO |  | TapPosMv | [17 empty] | 2-3A-06 |  | 2-53 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_LCO_TAP | 23KV科六八線(K268) LCO TAP | FEEDER | E02/22/K268/IED_ADJ |  |  |  | CDC | 521 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K268 | K268(23KV科六八線) |  | CB | [17 empty] | 2-08-02 |  | 2-18 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K268_CB | K268(23KV科六八線) CB | FEEDER | E02/22/K268/CB |  |  |  | CDC | 522 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K271 | 科七一線(K271) |  | PHA | [17 empty] | 2-09-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_PHA | 23KV科七一線(K271) 相間RY | FEEDER | E02/22/K271/PHA |  |  |  | CDC | 523 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K271 | 科七一線(K271) |  | GDA | [17 empty] | 2-0A-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_GDA | 23KV科七一線(K271) 接地RY | FEEDER | E02/22/K271/GDA |  |  |  | CDC | 524 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K271 | 科七一線(K271) 79RY |  | 79UL | [17 empty] | 2-3A-07 |  | 2-54 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_79UL | 23KV科七一線(K271) 79RY U/L | FEEDER | E02/22/K271/79UL |  |  |  | CDC | 525 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K271_LCO | 科七一線(K271) LCO |  | TapPosMv | [17 empty] | 2-3A-08 |  | 2-55 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_LCO_TAP | 23KV科七一線(K271) LCO TAP | FEEDER | E02/22/K271/IED_ADJ |  |  |  | CDC | 526 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K271 | K271(23KV科七一線) |  | CB | [17 empty] | 2-09-06 |  | 2-1C | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K271_CB | K271(23KV科七一線) CB | FEEDER | E02/22/K271/CB |  |  |  | CDC | 527 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K272 | 科七二線(K272) |  | PHA | [17 empty] | 2-0A-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_PHA | 23KV科七二線(K272) 相間RY | FEEDER | E02/22/K272/PHA |  |  |  | CDC | 528 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K272 | 科七二線(K272) |  | GDA | [17 empty] | 2-0A-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_GDA | 23KV科七二線(K272) 接地RY | FEEDER | E02/22/K272/GDA |  |  |  | CDC | 529 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K272 | 科七二線(K272) 79RY |  | 79UL | [17 empty] | 2-3A-09 |  | 2-56 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_79UL | 23KV科七二線(K272) 79RY U/L | FEEDER | E02/22/K272/79UL |  |  |  | CDC | 530 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K272_LCO | 科七二線(K272) LCO |  | TapPosMv | [17 empty] | 2-3A-10 |  | 2-57 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_LCO_TAP | 23KV科七二線(K272) LCO TAP | FEEDER | E02/22/K272/IED_ADJ |  |  |  | CDC | 531 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K272 | K272(23KV科七二線) |  | CB | [17 empty] | 2-0A-01 |  | 2-1D | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K272_CB | K272(23KV科七二線) CB | FEEDER | E02/22/K272/CB |  |  |  | CDC | 532 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K273 | 科七三線(K273) |  | PHA | [17 empty] | 2-0A-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_PHA | 23KV科七三線(K273) 相間RY | FEEDER | E02/22/K273/PHA |  |  |  | CDC | 533 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K273 | 科七三線(K273) |  | GDA | [17 empty] | 2-0A-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_GDA | 23KV科七三線(K273) 接地RY | FEEDER | E02/22/K273/GDA |  |  |  | CDC | 534 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K273 | 科七三線(K273) 79RY |  | 79UL | [17 empty] | 2-3A-11 |  | 2-58 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_79UL | 23KV科七三線(K273) 79RY U/L | FEEDER | E02/22/K273/79UL |  |  |  | CDC | 535 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K273_LCO | 科七三線(K273) LCO |  | TapPosMv | [17 empty] | 2-3A-12 |  | 2-59 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_LCO_TAP | 23KV科七三線(K273) LCO TAP | FEEDER | E02/22/K273/IED_ADJ |  |  |  | CDC | 536 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K273 | K273(23KV科七三線) |  | CB | [17 empty] | 2-0A-04 |  | 2-1E | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K273_CB | K273(23KV科七三線) CB | FEEDER | E02/22/K273/CB |  |  |  | CDC | 537 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K274 | 科七四線(K274) |  | PHA | [17 empty] | 2-0B-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_PHA | 23KV科七四線(K274) 相間RY | FEEDER | E02/22/K274/PHA |  |  |  | CDC | 538 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K274 | 科七四線(K274) |  | GDA | [17 empty] | 2-0B-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_GDA | 23KV科七四線(K274) 接地RY | FEEDER | E02/22/K274/GDA |  |  |  | CDC | 539 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K274 | 科七四線(K274) 79RY |  | 79UL | [17 empty] | 2-3A-13 |  | 2-5A | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_79UL | 23KV科七四線(K274) 79RY U/L | FEEDER | E02/22/K274/79UL |  |  |  | CDC | 540 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K274_LCO | 科七四線(K274) LCO |  | TapPosMv | [17 empty] | 2-3A-14 |  | 2-5B | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_LCO_TAP | 23KV科七四線(K274) LCO TAP | FEEDER | E02/22/K274/IED_ADJ |  |  |  | CDC | 541 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K274 | K274(23KV科七四線) |  | CB | [17 empty] | 2-0A-07 |  | 2-1F | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K274_CB | K274(23KV科七四線) CB | FEEDER | E02/22/K274/CB |  |  |  | CDC | 542 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K275 | 科七五線(K275) |  | PHA | [17 empty] | 2-0C-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_PHA | 23KV科七五線(K275) 相間RY | FEEDER | E02/22/K275/PHA |  |  |  | CDC | 543 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K275 | 科七五線(K275) |  | GDA | [17 empty] | 2-0C-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_GDA | 23KV科七五線(K275) 接地RY | FEEDER | E02/22/K275/GDA |  |  |  | CDC | 544 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K275 | 科七五線(K275) 79RY |  | 79UL | [17 empty] | 2-3A-15 |  | 2-5C | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_79UL | 23KV科七五線(K275) 79RY U/L | FEEDER | E02/22/K275/79UL |  |  |  | CDC | 545 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K275_LCO | 科七五線(K275) LCO |  | TapPosMv | [17 empty] | 2-3B-00 |  | 2-5D | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_LCO_TAP | 23KV科七五線(K275) LCO TAP | FEEDER | E02/22/K275/IED_ADJ |  |  |  | CDC | 546 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K275 | K275(23KV科七五線) |  | CB | [17 empty] | 2-0C-00 |  | 2-23 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K275_CB | K275(23KV科七五線) CB | FEEDER | E02/22/K275/CB |  |  |  | CDC | 547 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K276 | 科七六線(K276) |  | PHA | [17 empty] | 2-0C-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_PHA | 23KV科七六線(K276) 相間RY | FEEDER | E02/22/K276/PHA |  |  |  | CDC | 548 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K276 | 科七六線(K276) |  | GDA | [17 empty] | 2-0C-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_GDA | 23KV科七六線(K276) 接地RY | FEEDER | E02/22/K276/GDA |  |  |  | CDC | 549 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K276 | 科七六線(K276) 79RY |  | 79UL | [17 empty] | 2-3B-01 |  | 2-5E | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_79UL | 23KV科七六線(K276) 79RY U/L | FEEDER | E02/22/K276/79UL |  |  |  | CDC | 550 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K276_LCO | 科七六線(K276) LCO |  | TapPosMv | [17 empty] | 2-3B-02 |  | 2-5F | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_LCO_TAP | 23KV科七六線(K276) LCO TAP | FEEDER | E02/22/K276/IED_ADJ |  |  |  | CDC | 551 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K276 | K276(23KV科七六線) |  | CB | [17 empty] | 2-0C-03 |  | 2-24 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K276_CB | K276(23KV科七六線) CB | FEEDER | E02/22/K276/CB |  |  |  | CDC | 552 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K277 | 科七七線(K277) |  | PHA | [17 empty] | 2-0C-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_PHA | 23KV科七七線(K277) 相間RY | FEEDER | E02/22/K277/PHA |  |  |  | CDC | 553 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K277 | 科七七線(K277) |  | GDA | [17 empty] | 2-0D-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_GDA | 23KV科七七線(K277) 接地RY | FEEDER | E02/22/K277/GDA |  |  |  | CDC | 554 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K277 | 科七七線(K277) 79RY |  | 79UL | [17 empty] | 2-3B-03 |  | 2-60 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_79UL | 23KV科七七線(K277) 79RY U/L | FEEDER | E02/22/K277/79UL |  |  |  | CDC | 555 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K277_LCO | 科七七線(K277) LCO |  | TapPosMv | [17 empty] | 2-3B-04 |  | 2-61 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_LCO_TAP | 23KV科七七線(K277) LCO TAP | FEEDER | E02/22/K277/IED_ADJ |  |  |  | CDC | 556 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K277 | K277(23KV科七七線) |  | CB | [17 empty] | 2-0C-06 |  | 2-25 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K277_CB | K277(23KV科七七線) CB | FEEDER | E02/22/K277/CB |  |  |  | CDC | 557 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K278 | 科七八線(K278) |  | PHA | [17 empty] | 2-0D-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_PHA | 23KV科七八線(K278) 相間RY | FEEDER | E02/22/K278/PHA |  |  |  | CDC | 558 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K278 | 科七八線(K278) |  | GDA | [17 empty] | 2-0D-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_GDA | 23KV科七八線(K278) 接地RY | FEEDER | E02/22/K278/GDA |  |  |  | CDC | 559 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K278 | 科七八線(K278) 79RY |  | 79UL | [17 empty] | 2-3B-05 |  | 2-62 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_79UL | 23KV科七八線(K278) 79RY U/L | FEEDER | E02/22/K278/79UL |  |  |  | CDC | 560 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K278_LCO | 科七八線(K278) LCO |  | TapPosMv | [17 empty] | 2-3B-06 |  | 2-63 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_LCO_TAP | 23KV科七八線(K278) LCO TAP | FEEDER | E02/22/K278/IED_ADJ |  |  |  | CDC | 561 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K278 | K278(23KV科七八線) |  | CB | [17 empty] | 2-0D-01 |  | 2-26 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K278_CB | K278(23KV科七八線) CB | FEEDER | E02/22/K278/CB |  |  |  | CDC | 562 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 2-0E-05 |  | 2-27 | [5 empty] | ADCS_S | [8 empty] | 南科ES.100_CB | 100(TIE) CB | TIE | E02/22/100/CB |  |  |  | CDC | 563 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E02 | 南科ES | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 2-0E-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.100_51A | 23KV TIE(100) 51RY | TIE | E02/22/100/51A |  |  |  | CDC | 564 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 2-0E-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.100_51NA | 23KV TIE(100) 51N RY | TIE | E02/22/100/51NA |  |  |  | CDC | 565 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-00-00 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1500_CB | 1500(TIE) CB | TIE | E02/161/1500/CB |  |  |  | CDC | 566 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-00-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1500_50A | 161KV TIE(1500) 50RY | TIE | E02/161/1500/50A |  |  |  | CDC | 567 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-38 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1501_DS | 1501(TIE) DS | TIE | E02/161/1500/DS1 |  |  |  | CDC | 568 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-39 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1502_DS | 1502(TIE) DS | TIE | E02/161/1500/DS2 |  |  |  | CDC | 569 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | CB | [17 empty] | 1-05-04 |  | 1-0C | [5 empty] | 161KV_S | [8 empty] | 南科ES.1700_CB | 1700(TIE) CB | TIE | E02/161/1700/CB |  |  |  | CDC | 570 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 | [16 empty] | 1-3D-04 | 1-3D-05 | 1-52 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1701_DS | 1701(TIE) DS | TIE | E02/161/1700/DS1 |  |  |  | CDC | 571 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1700 | TIE(1700) |  | DS3 | 1703 | [16 empty] | 1-3D-06 | 1-3D-07 | 1-53 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1703_DS | 1703(TIE) DS | TIE | E02/161/1700/DS2 |  |  |  | CDC | 572 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | CB | [17 empty] | 1-05-06 |  | 1-0D | [5 empty] | 161KV_S | [8 empty] | 南科ES.1800_CB | 1800(TIE) CB | TIE | E02/161/1800/CB |  |  |  | CDC | 573 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1802 | [16 empty] | 1-3D-08 | 1-3D-09 | 1-54 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1802_DS | 1802(TIE) DS | TIE | E02/161/1800/DS1 |  |  |  | CDC | 574 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1800 | TIE(1800) |  | DS4 | 1804 | [16 empty] | 1-3D-10 | 1-3D-11 | 1-55 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1804_DS | 1804(TIE) DS | TIE | E02/161/1800/DS2 |  |  |  | CDC | 575 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-04-04 |  | 2-0C | [5 empty] | ADCS_S | [8 empty] | 南科ES.200_CB | 200(TIE) CB | TIE | E02/11/200/CB |  |  |  | CDC | 576 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E02 | 南科ES | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-04-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.200_51A | 11KV TIE(200) 51RY | TIE | E02/11/200/51A |  |  |  | CDC | 577 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-04-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.200_51NA | 11KV TIE(200) 51N RY | TIE | E02/11/200/51NA |  |  |  | CDC | 578 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 2-09-03 |  | 2-19 | [5 empty] | ADCS_S | [8 empty] | 南科ES.300_CB | 300(TIE) CB | TIE | E02/22/300/CB |  |  |  | CDC | 579 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E02 | 南科ES | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 2-09-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.300_51A | 11KV TIE(300) 51RY | TIE | E02/22/300/51A |  |  |  | CDC | 580 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 2-09-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.300_51NA | 11KV TIE(300) 51N RY | TIE | E02/22/300/51NA |  |  |  | CDC | 581 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 400 | TIE(400) |  | CB | [17 empty] | 2-0E-02 |  | 2-20 | [5 empty] | ADCS_S | [8 empty] | 南科ES.400_CB | 400(TIE) CB | TIE | E02/22/400/CB |  |  |  | CDC | 582 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E02 | 南科ES | 0 |  | 400 | TIE(400) |  | 51A | [17 empty] | 2-0E-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.400_51A | 23KV TIE(400) 51RY | TIE | E02/22/400/51A |  |  |  | CDC | 583 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 400 | TIE(400) |  | 51NA | [17 empty] | 2-0E-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.400_51NA | 23KV TIE(400) 51N RY | TIE | E02/22/400/51NA |  |  |  | CDC | 584 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 190 | #1SSTR(190) |  | CB | [17 empty] | 2-00-00 |  | 2-01 | [5 empty] | 161KV_S | [8 empty] | 南科ES.190_CB | 190(#1SSTR) CB | OTHER | E02/22/190/CB |  |  |  | CDC | 585 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 2-00-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1SSTR_51A | #1SSTR 51RY | OTHER | E02/22/190/PHA |  |  |  | CDC | 586 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1SSTR | #1SSTR |  | 51NA | [17 empty] | 2-00-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1SSTR_51NA | #1SSTR 51N RY | OTHER | E02/22/190/GDA |  |  |  | CDC | 587 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 290 | #2SSTR(290) |  | CB | [17 empty] | 2-0D-07 |  | 2-22 | [5 empty] | 161KV_S | [8 empty] | 南科ES.290_CB | 290(#2SSTR) CB | OTHER | E02/22/290/CB |  |  |  | CDC | 588 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 2-0E-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2SSTR_51A | #2SSTR 51RY | OTHER | E02/22/290/PHA |  |  |  | CDC | 589 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2SSTR | #2SSTR |  | 51NA | [17 empty] | 2-0E-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2SSTR_51NA | #2SSTR 51N RY | OTHER | E02/22/290/GDA |  |  |  | CDC | 590 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 390 | #3SSTR(390) |  | CB | [17 empty] | 2-09-00 |  | 2-14 | [5 empty] | 161KV_S | [8 empty] | 南科ES.390_CB | 390(#3SSTR) CB | OTHER | E02/22/390/CB |  |  |  | CDC | 591 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 2-09-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3SSTR_51A | #3SSTR 51RY | OTHER | E02/22/390/PHA |  |  |  | CDC | 592 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3SSTR | #3SSTR |  | 51NA | [17 empty] | 2-09-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3SSTR_51NA | #3SSTR 51N RY | OTHER | E02/22/390/GDA |  |  |  | CDC | 593 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 490 | #4SSTR(490) |  | CB | [17 empty] | 3-10-00 |  | 3-30 | [5 empty] | 161KV_S | [8 empty] | 南科ES.490_CB | 490(#4SSTR) CB | OTHER | E02/22/490/CB |  |  |  | CDC | 594 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 4SSTR | #4SSTR |  | 51A | [17 empty] | 3-10-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4SSTR_51A | #4SSTR 51RY | OTHER | E02/22/490/PHA |  |  |  | CDC | 595 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4SSTR | #4SSTR |  | 51NA | [17 empty] | 3-10-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4SSTR_51NA | #4SSTR 51N RY | OTHER | E02/22/490/GDA |  |  |  | CDC | 596 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-07-02 |  | 1-10 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1750_CB | 1750(#1DTR) CB | MTR | E02/161/1750/CB |  |  |  | CDC | 597 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-08-02 |  | 1-11 | [5 empty] | ADCS_S | [8 empty] | 南科ES.310_CB | 310(#1DTR) CB | MTR | E02/22/310/CB |  |  |  | CDC | 598 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-08-05 |  | 1-12 | [5 empty] | ADCS_S | [8 empty] | 南科ES.320_CB | 320(#1DTR) CB | MTR | E02/11/320/CB |  |  |  | CDC | 599 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 51A | [17 empty] | 1-07-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1DTR_51A | #1DTR 51RY | MTR | E02//1DTR/51A |  |  |  | CDC | 600 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 51NA | [17 empty] | 1-07-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1DTR_51NA | #1DTR 51N RY | MTR | E02//1DTR/51NA |  |  |  | CDC | 601 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-07-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1DTR_51ZA | #1DTR 51Z RY | MTR | E02//1DTR/51ZA |  |  |  | CDC | 602 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-07-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1DTR_87A | #1DTR 87RY | MTR | E02//1DTR/87A |  |  |  | CDC | 603 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-08-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.310_51A | #1DTR二次側(310) 51RY | MTR | E02/22/310/PHA |  |  |  | CDC | 604 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-08-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.320_51A | #1DTR二次側(320) 51RY | MTR | E02/11/320/PHA |  |  |  | CDC | 605 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-07-04 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#1DTR_96PA | #1DTR 機械保護動作 | MTR | E02//1DTR/96PA |  |  |  | CDC | 606 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-33-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_96D | #1DTR 96D RY | MTR | E02//1DTR/96D |  |  |  | CDC | 607 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-33-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_96P | #1DTR 96P RY | MTR | E02//1DTR/96P |  |  |  | CDC | 608 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-33-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_63Q | #1DTR 63Q RY | MTR | E02//1DTR/63Q |  |  |  | CDC | 609 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-33-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_96B1 | #1DTR 96B1 RY | MTR | E02//1DTR/96B1 |  |  |  | CDC | 610 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-33-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_96B2 | #1DTR 96B2 RY | MTR | E02//1DTR/96B2 |  |  |  | CDC | 611 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-33-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_TRA | #1DTR 重故障 | MTR | E02//1DTR/TRA |  |  |  | CDC | 612 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-33-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR_TRF | #1DTR 輕故障 | MTR | E02//1DTR/TRF |  |  |  | CDC | 613 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-33-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | E02//1DTR(A)/SupLocal |  |  |  | CDC | 614 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-33-04 |  | 1-1C | [5 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | E02//1DTR(A)/Tap Chan |  |  |  | CDC | 615 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | E02//1DTR(B)/SupLocal |  |  |  | CDC | 616 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-33-06 |  | 1-1E | [5 empty] | ADCS_S | [8 empty] | 南科ES.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | E02//1DTR(B)/Tap Chan |  |  |  | CDC | 617 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3E-12 | 1-3E-13 | 1-60 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1751_DS | 1751(#1DTR) DS | MTR | E02/161/1750/DS1 |  |  |  | CDC | 618 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3E-14 | 1-3E-15 | 1-61 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1752_DS | 1752(#1DTR) DS | MTR | E02/161/1750/DS2 |  |  |  | CDC | 619 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-09-00 |  | 1-13 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1760_CB | 1760(#2DTR) CB | MTR | E02/161/1760/CB |  |  |  | CDC | 620 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-0A-00 |  | 1-14 | [5 empty] | ADCS_S | [8 empty] | 南科ES.330_CB | 330(#2DTR) CB | MTR | E02/22/330/CB |  |  |  | CDC | 621 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0A-03 |  | 1-15 | [5 empty] | ADCS_S | [8 empty] | 南科ES.340_CB | 340(#2DTR) CB | MTR | E02/22/340/CB |  |  |  | CDC | 622 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-09-04 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2DTR_51A | #2DTR 51RY | MTR | E02//2DTR/51A |  |  |  | CDC | 623 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-09-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2DTR_51NA | #2DTR 51N RY | MTR | E02//2DTR/51NA |  |  |  | CDC | 624 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-09-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2DTR_51ZA | #2DTR 51Z RY | MTR | E02//2DTR/51ZA |  |  |  | CDC | 625 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-09-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2DTR_87A | #2DTR 87RY | MTR | E02//2DTR/87A |  |  |  | CDC | 626 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-09-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.330_51A | #2DTR二次側(330) 51RY | MTR | E02/22/330/PHA |  |  |  | CDC | 627 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-09-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.340_51A | #2DTR二次側(340) 51RY | MTR | E02/22/340/PHA |  |  |  | CDC | 628 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-09-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#2DTR_96PA | #2DTR 機械保護動作 | MTR | E02//2DTR/96PA |  |  |  | CDC | 629 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-34-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_96D | #2DTR 96D RY | MTR | E02//2DTR/96D |  |  |  | CDC | 630 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-34-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_96P | #2DTR 96P RY | MTR | E02//2DTR/96P |  |  |  | CDC | 631 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-34-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_63Q | #2DTR 63Q RY | MTR | E02//2DTR/63Q |  |  |  | CDC | 632 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-34-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_96B1 | #2DTR 96B1 RY | MTR | E02//2DTR/96B1 |  |  |  | CDC | 633 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-34-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_96B2 | #2DTR 96B2 RY | MTR | E02//2DTR/96B2 |  |  |  | CDC | 634 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-34-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_TRA | #2DTR 重故障 | MTR | E02//2DTR/TRA |  |  |  | CDC | 635 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-34-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_TRF | #2DTR 輕故障 | MTR | E02//2DTR/TRF |  |  |  | CDC | 636 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | SupLocal | [17 empty] | 1-33-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_S/L | #2DTR OLTC S/L | MTR | E02//2DTR/SupLocal |  |  |  | CDC | 637 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES | 0 |  | 2DTR | #2DTR |  | A_M | [17 empty] | 1-34-00 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#2DTR_A/M | #2DTR OLTC A/M | MTR | E02//2DTR/Tap Chan |  |  |  | CDC | 638 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3F-00 | 1-3F-01 | 1-62 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1761_DS | 1761(#2DTR) DS | MTR | E02/161/1760/DS1 |  |  |  | CDC | 639 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3F-02 | 1-3F-03 | 1-63 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1762_DS | 1762(#2DTR) DS | MTR | E02/161/1760/DS2 |  |  |  | CDC | 640 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-0A-06 |  | 1-16 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1770_CB | 1770(#3DTR) CB | MTR | E02/161/1770/CB |  |  |  | CDC | 641 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-0B-06 |  | 1-17 | [5 empty] | ADCS_S | [8 empty] | 南科ES.350_CB | 350(#3DTR) CB | MTR | E02/22/350/CB |  |  |  | CDC | 642 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 360 | #3DTR(360) |  | CB | [17 empty] | 1-0C-01 |  | 1-18 | [5 empty] | ADCS_S | [8 empty] | 南科ES.360_CB | 360(#3DTR) CB | MTR | E02/22/360/CB |  |  |  | CDC | 643 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0B-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3DTR_51A | #3DTR 51RY | MTR | E02//3DTR/51A |  |  |  | CDC | 644 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0B-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3DTR_51NA | #3DTR 51N RY | MTR | E02//3DTR/51NA |  |  |  | CDC | 645 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-0B-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3DTR_51ZA | #3DTR 51Z RY | MTR | E02//3DTR/51ZA |  |  |  | CDC | 646 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-0A-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3DTR_87A | #3DTR 87RY | MTR | E02//3DTR/87A |  |  |  | CDC | 647 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0B-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.350_51A | #3DTR二次側(350) 51RY | MTR | E02/22/350/PHA |  |  |  | CDC | 648 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 360 | #3DTR(360) |  | 51A | [17 empty] | 1-0B-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.360_51A | #3DTR二次側(360) 51RY | MTR | E02/22/360/PHA |  |  |  | CDC | 649 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-0B-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#3DTR_96PA | #3DTR 機械保護動作 | MTR | E02//3DTR/96PA |  |  |  | CDC | 650 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-34-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_96D | #3DTR 96D RY | MTR | E02//3DTR/96D |  |  |  | CDC | 651 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-35-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_96P | #3DTR 96P RY | MTR | E02//3DTR/96P |  |  |  | CDC | 652 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-35-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_63Q | #3DTR 63Q RY | MTR | E02//3DTR/63Q |  |  |  | CDC | 653 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-34-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_96B1 | #3DTR 96B1 RY | MTR | E02//3DTR/96B1 |  |  |  | CDC | 654 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-34-14 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_96B2 | #3DTR 96B2 RY | MTR | E02//3DTR/96B2 |  |  |  | CDC | 655 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-34-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_TRA | #3DTR 重故障 | MTR | E02//3DTR/TRA |  |  |  | CDC | 656 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-34-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_TRF | #3DTR 輕故障 | MTR | E02//3DTR/TRF |  |  |  | CDC | 657 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | SupLocal | [17 empty] | 1-34-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_S/L | #3DTR OLTC S/L | MTR | E02//3DTR/SupLocal |  |  |  | CDC | 658 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES | 0 |  | 3DTR | #3DTR |  | A_M | [17 empty] | 1-34-12 |  | 1-22 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#3DTR_A/M | #3DTR OLTC A/M | MTR | E02//3DTR/Tap Chan |  |  |  | CDC | 659 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3F-04 | 1-3F-05 | 1-64 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1771_DS | 1771(#3DTR) DS | MTR | E02/161/1770/DS1 |  |  |  | CDC | 660 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3F-06 | 1-3F-07 | 1-65 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1772_DS | 1772(#3DTR) DS | MTR | E02/161/1770/DS2 |  |  |  | CDC | 661 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | CB | [17 empty] | 1-0C-04 |  | 1-19 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1780_CB | 1780(#4DTR) CB | MTR | E02/161/1780/CB |  |  |  | CDC | 662 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 370 | #4DTR(370) |  | CB | [17 empty] | 1-0D-04 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 南科ES.370_CB | 370(#4DTR) CB | MTR | E02/22/370/CB |  |  |  | CDC | 663 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 380 | #4DTR(380) |  | CB | [17 empty] | 1-0D-07 |  | 1-1B | [5 empty] | ADCS_S | [8 empty] | 南科ES.380_CB | 380(#4DTR) CB | MTR | E02/11/380/CB |  |  |  | CDC | 664 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 51A | [17 empty] | 1-0D-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4DTR_51A | #4DTR 51RY | MTR | E02//4DTR/51A |  |  |  | CDC | 665 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 51NA | [17 empty] | 1-0D-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4DTR_51NA | #4DTR 51N RY | MTR | E02//4DTR/51NA |  |  |  | CDC | 666 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 51ZA | [17 empty] | 1-0C-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4DTR_51ZA | #4DTR 51Z RY | MTR | E02//4DTR/51ZA |  |  |  | CDC | 667 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 87A | [17 empty] | 1-0C-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4DTR_87A | #4DTR 87RY | MTR | E02//4DTR/87A |  |  |  | CDC | 668 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 370 | #4DTR(370) |  | 51A | [17 empty] | 1-0D-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.370_51A | #4DTR二次側(370) 51RY | MTR | E02/22/370/PHA |  |  |  | CDC | 669 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 380 | #4DTR(380) |  | 51A | [17 empty] | 1-0D-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.380_51A | #4DTR二次側(380) 51RY | MTR | E02/11/380/GDA |  |  |  | CDC | 670 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 96PA | [17 empty] | 1-0C-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.#4DTR_96PA | #4DTR 機械保護動作 | MTR | E02//4DTR/96PA |  |  |  | CDC | 671 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 96D | [17 empty] | 1-35-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_96D | #4DTR 96D RY | MTR | E02//4DTR/96D |  |  |  | CDC | 672 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 96P | [17 empty] | 1-35-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_96P | #4DTR 96P RY | MTR | E02//4DTR/96P |  |  |  | CDC | 673 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 63Q | [17 empty] | 1-35-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_63Q | #4DTR 63Q RY | MTR | E02//4DTR/63Q |  |  |  | CDC | 674 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 96B1 | [17 empty] | 1-35-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_96B1 | #4DTR 96B1 RY | MTR | E02//4DTR/96B1 |  |  |  | CDC | 675 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | 96B2 | [17 empty] | 1-35-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_96B2 | #4DTR 96B2 RY | MTR | E02//4DTR/96B2 |  |  |  | CDC | 676 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | TRA | [17 empty] | 1-35-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_TRA | #4DTR 重故障 | MTR | E02//4DTR/TRA |  |  |  | CDC | 677 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR | #4DTR |  | TRF | [17 empty] | 1-35-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR_TRF | #4DTR 輕故障 | MTR | E02//4DTR/TRF |  |  |  | CDC | 678 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | SupLocal | [17 empty] | 1-35-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_S/L | #4DTR(A) OLTC S/L | MTR | E02//4DTR(A)/SupLocal |  |  |  | CDC | 679 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES | 0 |  | 4DTR(A) | #4DTR(A) |  | A_M | [17 empty] | 1-35-04 |  | 1-24 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(A)_A/M | #4DTR(A) OLTC A/M | MTR | E02//4DTR(A)/Tap Chan |  |  |  | CDC | 680 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR(B) |  | SupLocal | [17 empty] | 1-35-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_S/L | #4DTR(B) OLTC S/L | MTR | E02//4DTR(B)/SupLocal |  |  |  | CDC | 681 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E02 | 南科ES | 0 |  | 4DTR(B) | #4DTR(B) |  | A_M | [17 empty] | 1-35-06 |  | 1-26 | [5 empty] | ADCS_S | [8 empty] | 南科ES.#4DTR(B)_A/M | #4DTR(B) OLTC A/M | MTR | E02//4DTR(B)/Tap Chan |  |  |  | CDC | 682 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | DS1 | 1781 | [16 empty] | 1-3F-08 | 1-3F-09 | 1-66 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1781_DS | 1781(#4DTR) DS | MTR | E02/161/1780/DS1 |  |  |  | CDC | 683 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1780 | #4DTR(1780) |  | DS2 | 1782 | [16 empty] | 1-3F-10 | 1-3F-11 | 1-67 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1782_DS | 1782(#4DTR) DS | MTR | E02/161/1780/DS2 |  |  |  | CDC | 684 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | CB | [17 empty] | 2-01-07 |  | 2-00 | [5 empty] | ADCS_S | [8 empty] | 南科ES.210_CB | 210(23KV #1SC) CB | SC | E02/22/210/CB |  |  |  | CDC | 685 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | SCA | [17 empty] | 2-02-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.210_SCA | 23KV #1SC 51,51N RY | SC | E02/22/210/SCA |  |  |  | CDC | 686 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 210 | #1SC(210) |  | UVA | [17 empty] | 2-02-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.210_UVA | 23KV #1SC 27RY(欠壓) | SC | E02/22/210/UVA |  |  |  | CDC | 687 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 2-04-01 |  | 2-06 | [5 empty] | ADCS_S | [8 empty] | 南科ES.220_CB | 220(11KV #2SC) CB | SC | E02/11/220/CB |  |  |  | CDC | 688 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 2-04-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.220_SCA | 11KV #2SC 51,51N RY | SC | E02/11/220/SCA |  |  |  | CDC | 689 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 2-04-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.220_UVA | 11KV #2SC 27RY(欠壓) | SC | E02/11/220/UVA |  |  |  | CDC | 690 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 220 | #2SC(220) |  | LBS | [17 empty] | 3-35-02 | 3-35-03 | 3-2D | [5 empty] | ADCS_S | [8 empty] | 南科ES.220_LBS | 220(11KV #2SC) LBS | SC | E02/11/220/DS2 |  |  |  | CDC | 691 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-06-03 |  | 2-0D | [5 empty] | ADCS_S | [8 empty] | 南科ES.230_CB | 230(23KV #3SC) CB | SC | E02/22/230/CB |  |  |  | CDC | 692 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-06-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.230_SCA | 23KV #3SC 51,51N RY | SC | E02/22/230/SCA |  |  |  | CDC | 693 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-06-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.230_UVA | 23KV #3SC 27RY(欠壓) | SC | E02/22/230/UVA |  |  |  | CDC | 694 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-08-05 |  | 2-13 | [5 empty] | ADCS_S | [8 empty] | 南科ES.240_CB | 240(23KV #4SC) CB | SC | E02/22/240/CB |  |  |  | CDC | 695 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-08-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.240_SCA | 23KV #4SC 51,51N RY | SC | E02/22/240/SCA |  |  |  | CDC | 696 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-08-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.240_UVA | 23KV #4SC 27RY(欠壓) | SC | E02/22/240/UVA |  |  |  | CDC | 697 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-0B-02 |  | 2-1A | [5 empty] | ADCS_S | [8 empty] | 南科ES.250_CB | 250(23KV #5SC) CB | SC | E02/22/250/CB |  |  |  | CDC | 698 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-0B-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.250_SCA | 23KV #5SC 51,51N RY | SC | E02/22/250/SCA |  |  |  | CDC | 699 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-0B-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.250_UVA | 23KV #5SC 27RY(欠壓) | SC | E02/22/250/UVA |  |  |  | CDC | 700 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-0D-04 |  | 2-21 | [5 empty] | ADCS_S | [8 empty] | 南科ES.260_CB | 260(23KV #6SC) CB | SC | E02/22/260/CB |  |  |  | CDC | 701 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-0D-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.260_SCA | 23KV #6SC 51,51N RY | SC | E02/22/260/SCA |  |  |  | CDC | 702 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-0D-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.260_UVA | 23KV #6SC 27RY(欠壓) | SC | E02/22/260/UVA |  |  |  | CDC | 703 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-36-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | E02/161/1BUS/BUS_VUA |  |  |  | CDC | 704 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-00-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.161#1BUS_87A | 161KV #1BUS 87RY | BUS | E02/161/1BUS/87A |  |  |  | CDC | 705 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-36-00 |  | 1-74 | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | E02/161/1BUS/87UL |  |  |  | CDC | 706 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-36-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | E02/161/2BUS/BUS_VUA |  |  |  | CDC | 707 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-00-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.161#2BUS_87A | 161KV #2BUS 87RY | BUS | E02/161/2BUS/87A |  |  |  | CDC | 708 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-36-01 |  | 1-75 | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | E02/161/2BUS/87UL |  |  |  | CDC | 709 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1613BUS | #3BUS |  | VUA | [17 empty] | 1-36-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS | E02/161/3BUS/BUS_VUA |  |  |  | CDC | 710 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1613BUS | #3BUS |  | 87A | [17 empty] | 1-06-00 | [7 empty] | 161KV_S | [8 empty] | 南科ES.161#3BUS_87A | 161KV #3BUS 87RY | BUS | E02/161/3BUS/87A |  |  |  | CDC | 711 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1613BUS | #3BUS |  | 87UL | [17 empty] | 1-36-02 |  | 1-76 | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER | E02/161/3BUS/87UL |  |  |  | CDC | 712 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1614BUS | #4BUS |  | VUA | [17 empty] | 1-36-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS | E02/161/4BUS/BUS_VUA |  |  |  | CDC | 713 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1614BUS | #4BUS |  | 87A | [17 empty] | 1-06-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.161#4BUS_87A | 161KV #4BUS 87RY | BUS | E02/161/4BUS/87A |  |  |  | CDC | 714 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1614BUS | #4BUS |  | 87UL | [17 empty] | 1-36-03 |  | 1-77 | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER | E02/161/4BUS/87UL |  |  |  | CDC | 715 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | 11_ | 11/ |  | CBA | [17 empty] | 2-38-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.11/23KV_CBA | 11/23KV斷路器重故障 | OTHER | E02/22/ComPoint/CBA |  |  |  | CDC | 716 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 11_ | 11/ |  | CBF | [17 empty] | 2-38-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.11/23KV_CBF | 11/23KV斷路器輕故障 | OTHER | E02/22/ComPoint/CBF |  |  |  | CDC | 717 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV |  |  |  | BFA | [17 empty] | 1-0E-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_BFA | 161KV斷路器失靈(BF)RY | OTHER | E02/161/ComPoint/BFA |  |  |  | CDC | 718 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-36-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_CBA | 161KV斷路器重故障 | OTHER | E02/161/ComPoint/CBA |  |  |  | CDC | 719 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-36-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_CBF | 161KV斷路器輕故障 | OTHER | E02/161/ComPoint/CBF |  |  |  | CDC | 720 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-0E-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_OSCA | 161KV示波器啟動警報 | OTHER | E02/161/ComPoint/OSCA |  |  |  | CDC | 721 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0E-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | E02/161/ComPoint/RCA |  |  |  | CDC | 722 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-36-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | E02/161/ComPoint/COMT |  |  |  | CDC | 723 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 1-37-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.23KV_SC_60A | 23/11KV SC 60A | OTHER | E02/22/ComPoint/FDR_60A |  |  |  | CDC | 724 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | FEEDER | FEEDER |  | RCA | [17 empty] | 2-38-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.FEEDER_RCA | 饋線復閉電驛動作(23KV) | FEEDER | E02/0/StaDev/FDR_RCA |  |  |  | CDC | 725 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.RTU_S/L | RTU SUPY/LOCAL | OTHER | E02/0/StaDev/RTU_R_L |  |  |  | CDC | 726 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E02 | 南科ES | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 南科ES.TEST_CB | TEST CB | OTHER | E02/0/StaDev/Test_CB |  |  |  | CDC | 727 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  |  |  |  | Fire1 | [17 empty] | 2-3D-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.火災警報(1) | 火災警報(1)受信總機 | OTHER | E02/0/StaDev/Fire1 |  |  |  | CDC | 728 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | Fire2 | [17 empty] | 2-3D-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.火災警報(2) | 火災警報(2)建物B棟 | OTHER | E02/0/StaDev/Fire2 |  |  |  | CDC | 729 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | Fire3 | [17 empty] | 2-3D-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.火災警報(3) | 火災警報(3)消防閘門動作 | OTHER | E02/0/StaDev/Fire3 |  |  |  | CDC | 730 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | OPA | [17 empty] | 1-37-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.充油電纜OPA | 充油電纜低油壓警報 | OTHER | E02/0/StaDev/OPA |  |  |  | CDC | 731 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | 25PFA | [17 empty] | 2-3C-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | E02/0/StaDev/25PFA |  |  |  | CDC | 732 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | 25TA | [17 empty] | 2-3C-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | E02/0/StaDev/25TA |  |  |  | CDC | 733 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | SUBA | [17 empty] | 2-3D-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.其他重故障 | 變電所內其他重故障 | OTHER | E02/0/StaDev/PSA |  |  |  | CDC | 734 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | SUBF | [17 empty] | 2-3D-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.其他輕故障 | 變電所內其他輕故障 | OTHER | E02/0/StaDev/PSF |  |  |  | CDC | 735 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | ACB1 | [17 empty] | 2-3C-07 |  | 2-28 | [5 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACB1 | 所內電源開關ACB1 | OTHER | E02/0/StaDev/ACB1 |  |  |  | CDC | 736 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E02 | 南科ES | 0 |  |  |  |  | ACB2 | [17 empty] | 2-3C-09 |  | 2-2A | [5 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACB2 | 所內電源開關ACB2 | OTHER | E02/0/StaDev/ACB2 |  |  |  | CDC | 737 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E02 | 南科ES | 0 |  |  |  |  | ACBA | [17 empty] | 1-36-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACBA | 所內電源故障警報 | OTHER | E02/0/StaDev/ACBA |  |  |  | CDC | 738 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 2-3C-08 |  | 2-29 | [5 empty] | ADCS_S | [8 empty] | 南科ES.所內電源ACBT | 所內電源開關ACB TIE | OTHER | E02/0/StaDev/ACBT |  |  |  | CDC | 739 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E02 | 南科ES | 0 |  |  |  |  | STUV | [17 empty] | 2-3C-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.所內電源欠壓 | 所內電源欠壓警報 | OTHER | E02/0/StaDev/STUV |  |  |  | CDC | 740 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | DCA | [17 empty] | 1-36-14 | [7 empty] | ADCS_S | [8 empty] | 南科ES.直流電源DCA | 直流電源故障警報 | OTHER | E02/0/StaDev/DCA |  |  |  | CDC | 741 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | DCE | [17 empty] | 1-36-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.直流電源DCE | 直流電源接地故障警報 | OTHER | E02/0/StaDev/DCE |  |  |  | CDC | 742 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | OilLeak | [17 empty] | 1-37-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.洩油池水位警報 | 洩油池水位警報 | OTHER | E02/0/StaDev/OilLeak |  |  |  | CDC | 743 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-3D-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | E02/0/StaDev/Burglar1 |  |  |  | CDC | 744 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | Burglar2 | [17 empty] | 2-3D-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.無人化防盜(2) | 無人化防盜(2)sp | OTHER | E02/0/StaDev/Burglar2 |  |  |  | CDC | 745 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | Burglar3 | [17 empty] | 2-3D-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.無人化防盜(3) | 無人化防盜(3)sp | OTHER | E02/0/StaDev/Burglar3 |  |  |  | CDC | 746 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | Door1 | [17 empty] | 2-3D-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.無人化門禁(1) | 無人化門禁(1)建築物大門 | OTHER | E02/0/StaDev/Door1 |  |  |  | CDC | 747 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  |  |  |  | Door2 | [17 empty] | 2-3D-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | E02/0/StaDev/Door2 |  |  |  | CDC | 748 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  |  |  |  | Door3 | [17 empty] | 2-3D-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.無人化門禁(3) | 無人化門禁(3) | OTHER | E02/0/StaDev/Door3 |  |  |  | CDC | 749 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  |  |  |  | Lights1 | [17 empty] | 3-3B-14 |  | 3-2E | [5 empty] | ADCS_S | [8 empty] | 南科ES.開關場照明(A) | 開關場照明(A) | OTHER | E02/0/StaDev/Lights1 |  |  |  | CDC | 750 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E02 | 南科ES | 0 |  |  |  |  | Lights2 | [17 empty] | 3-3B-15 |  | 3-2F | [5 empty] | ADCS_S | [8 empty] | 南科ES.開關場照明(B) | 開關場照明(B) | OTHER | E02/0/StaDev/Lights2 |  |  |  | CDC | 751 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E02 | 南科ES | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.310_GDA | 310開關箱IED RY GDA | OTHER | E02/22/310/GDA |  |  |  | CDC | 752 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 310 | #1DTR(310) |  | PHA2 | [17 empty] | 1-08-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.310_PHA2 | 310開關箱IED RY PHA | OTHER | E02/22/310/PHA2 |  |  |  | CDC | 753 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.320_GDA | 320開關箱IED RY GDA | OTHER | E02/11/320/GDA |  |  |  | CDC | 754 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 320 | #1DTR(320) |  | PHA2 | [17 empty] | 1-08-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.320_PHA2 | 320開關箱IED RY PHA | OTHER | E02/11/320/PHA2 |  |  |  | CDC | 755 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-0A-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.330_GDA | 330開關箱IED RY GDA | OTHER | E02/22/330/GDA |  |  |  | CDC | 756 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 330 | #2DTR(330) |  | PHA2 | [17 empty] | 1-0A-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.330_PHA2 | 330開關箱IED RY PHA | OTHER | E02/22/330/PHA2 |  |  |  | CDC | 757 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.340_GDA | 340開關箱IED RY GDA | OTHER | E02/22/340/GDA |  |  |  | CDC | 758 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 340 | #2DTR(340) |  | PHA2 | [17 empty] | 1-0A-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.340_PHA2 | 340開關箱IED RY PHA | OTHER | E02/22/340/PHA2 |  |  |  | CDC | 759 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0C-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.350_GDA | 350開關箱IED RY GDA | OTHER | E02/22/350/GDA |  |  |  | CDC | 760 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 350 | #3DTR(350) |  | PHA2 | [17 empty] | 1-0B-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.350_PHA2 | 350開關箱IED RY PHA | OTHER | E02/22/350/PHA2 |  |  |  | CDC | 761 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 360 | #3DTR(360) |  | GDA | [17 empty] | 1-0C-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.360_GDA | 360開關箱IED RY GDA | OTHER | E02/22/360/GDA |  |  |  | CDC | 762 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 360 | #3DTR(360) |  | PHA2 | [17 empty] | 1-0C-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.360_PHA2 | 360開關箱IED RY PHA | OTHER | E02/22/360/PHA2 |  |  |  | CDC | 763 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 370 | #4DTR(370) |  | GDA | [17 empty] | 1-0D-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.370_GDA | 370開關箱IED RY GDA | OTHER | E02/22/370/GDA |  |  |  | CDC | 764 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 370 | #4DTR(370) |  | PHA2 | [17 empty] | 1-0D-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.370_PHA2 | 370開關箱IED RY PHA | OTHER | E02/22/370/PHA2 |  |  |  | CDC | 765 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 380 | #4DTR(380) |  | GDA | [17 empty] | 1-0E-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.380_GDA | 380開關箱IED RY GDA | OTHER |  |  |  |  | CDC | 766 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 380 | #4DTR(380) |  | PHA2 | [17 empty] | 1-0E-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.380_PHA2 | 380開關箱IED RY PHA | OTHER | E02/11/380/PHA2 |  |  |  | CDC | 767 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | OilLeak1 | [17 empty] | 2-3C-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.OW1 | 水位警報1 | OTHER | E02/0/StaDev/OilLeak1 |  |  |  | CDC | 768 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | OilLeak2 | [17 empty] | 2-3C-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.OW2 | 水位警報2 | OTHER | E02/0/StaDev/OilLeak2 |  |  |  | CDC | 769 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | ㄧ號充電機故障 | [17 empty] | 1-36-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.ㄧ號充電機故障 | ㄧ號充電機故障 | OTHER | E02/0/StaDev/5A5Other |  |  |  | CDC | 770 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | 二號充電機故障 | [17 empty] | 1-37-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.二號充電機故障 | 二號充電機故障 | OTHER | E02/0/StaDev/6A5Other |  |  |  | CDC | 771 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | 空調機故障 | [17 empty] | 1-37-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.空調機故障 | 空調機故障或電源跳脫 | OTHER | E02/0/StaDev/7A5Other |  |  |  | CDC | 772 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | PHA | [17 empty] | 1-03-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1570_PHA | 南科道爺三路(1570) 相間RY | LINE161 | E02/161/1570/PHA |  |  |  | CDC | 773 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | GDA | [17 empty] | 1-03-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1570_GDA | 南科道爺三路(1570) 接地RY | LINE161 | E02/161/1570/GDA |  |  |  | CDC | 774 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | CB | [17 empty] | 1-03-00 |  | 1-07 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1570_CB | 1570(南科道爺三路) CB | LINE161 | E02/161/1570/CB |  |  |  | CDC | 775 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | 79UL | [17 empty] | 1-31-07 |  | 1-71 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1570_79UL | 南科道爺三路(1570) 79RY U/L | LINE161 | E02/161/1570/79UL |  |  |  | CDC | 776 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | DS1 | 1571 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-3E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1571_DS | 1571(南科道爺三路) DS | LINE161 | E02/161/1570/DS1 |  |  |  | CDC | 777 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | DS2 | 1572 | [16 empty] | 1-3A-14 | 1-3A-15 | 1-3F | [5 empty] | ADCS_S | [8 empty] | 南科ES.1572_DS | 1572(南科道爺三路) DS | LINE161 | E02/161/1570/DS2 |  |  |  | CDC | 778 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | DS3 | 1573 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-40 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1573_DS | 1573(南科道爺三路) DS | LINE161 | E02/161/1570/DS3 |  |  |  | CDC | 779 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | E3 | 1573E | [16 empty] | 1-3B-02 | 1-3B-03 | 1-41 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1573E_ES | 1573E(南科道爺三路) ES | LINE161 | E02/161/1570/E3 |  |  |  | CDC | 780 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-37-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | E02/161/1500/50SA |  |  |  | CDC | 781 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | 87A | [17 empty] | 1-03-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1570_87A | 南科道爺三路(1570) 87RY | LINE161 | E02/161/1570/85A |  |  |  | CDC | 782 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1570 | 南科道爺三路(1570) |  | 87UL | [17 empty] | 1-31-06 |  | 1-70 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1570_87UL | 南科道爺三路(1570) 87RY U/L | LINE161 | E02/161/1570/85UL2 |  |  |  | CDC | 783 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1570 | 南科道爺三路(1570) |  | 87CFA | [17 empty] | 1-31-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1570_87CFA | 南科道爺三路(1570)87RY通訊故障 | OTHER | E02/161/1570/87CFA |  |  |  | CDC | 784 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-3D-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | E02/161/ComPoint/OSCF |  |  |  | CDC | 785 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | PHA | [17 empty] | 1-02-02 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1540_PHA | 南科積E六線(1540) 相間RY | LINE161 | E02/161/1540/PHA |  |  |  | CDC | 786 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | GDA | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1540_GDA | 南科積E六線(1540) 接地RY | LINE161 | E02/161/1540/GDA |  |  |  | CDC | 787 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | CB | [17 empty] | 1-02-00 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1540_CB | 1540(南科積E六線) CB | LINE161 | E02/161/1540/CB |  |  |  | CDC | 788 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | 79UL | [17 empty] | 1-30-15 |  | 2-6C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1540_79UL | 南科積E六線(1540) 79RY U/L | LINE161 | E02/161/1540/79UL |  |  |  | CDC | 789 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | DS1 | 1541 | [16 empty] | 1-39-08 | 1-39-09 | 1-34 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1541_DS | 1541(南科積E六線) DS | LINE161 | E02/161/1540/DS1 |  |  |  | CDC | 790 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | DS2 | 1542 | [16 empty] | 1-39-10 | 1-39-11 | 1-35 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1542_DS | 1542(南科積E六線) DS | LINE161 | E02/161/1540/DS2 |  |  |  | CDC | 791 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | DS3 | 1543 | [16 empty] | 1-39-12 | 1-39-13 | 1-36 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1543_DS | 1543(南科積E六線) DS | LINE161 | E02/161/1540/DS3 |  |  |  | CDC | 792 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1540 | 南科積E六線(1540) |  | E3 | 1543E | [16 empty] | 1-39-14 | 1-39-15 | 1-37 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1543E_ES | 1543E(南科積E六線) ES | LINE161 | E02/161/1540/E3 |  |  |  | CDC | 793 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | 87CFA | [17 empty] | 1-31-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1540_87CFA | 南科積E六線1540 87RY通訊故障 | OTHER | E02/161/1540/87CFA |  |  |  | CDC | 794 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | RYFA | [17 empty] | 1-31-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1540_RYFA | 南科積E六線1540 數位電驛故障 | OTHER | E02/161/1540/RYFA |  |  |  | CDC | 795 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K221 | 科21線(K221) |  | PHA | [17 empty] | 3-12-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_PHA | 11KV科21線(K221) 相間RY | FEEDER | E02/11/K221/PHA |  |  |  | CDC | 796 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K221 | 科21線(K221) |  | GDA | [17 empty] | 3-13-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_GDA | 11KV科21線(K221) 接地RY | FEEDER | E02/11/K221/GDA |  |  |  | CDC | 797 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K221 | 科21線(K221) 79RY |  | 79UL | [17 empty] | 3-36-10 |  | 3-4A | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_79UL | 11KV科21線(K221) 79RY U/L | FEEDER | E02/11/K221/79UL |  |  |  | CDC | 798 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K221_LCO | 科21線(K221) LCO |  | TapPosMv | [17 empty] | 3-36-11 |  | 3-4B | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_LCO_TAP | 11KV科21線(K221) LCO TAP | FEEDER | E02/11/K221/IED_ADJ |  |  |  | CDC | 799 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K221 | K221(11KV科21線) |  | CB | [17 empty] | 3-12-06 |  | 3-36 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_CB | K221(11KV科21線) CB | FEEDER | E02/11/K221/CB |  |  |  | CDC | 800 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K222 | 科22線(K222) |  | PHA | [17 empty] | 3-13-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_PHA | 11KV科22線(K222) 相間RY | FEEDER | E02/11/K222/PHA |  |  |  | CDC | 801 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K222 | 科22線(K222) |  | GDA | [17 empty] | 3-13-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_GDA | 11KV科22線(K222) 接地RY | FEEDER | E02/11/K222/GDA |  |  |  | CDC | 802 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K222 | 科22線(K222) 79RY |  | 79UL | [17 empty] | 3-36-12 |  | 3-4C | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_79UL | 11KV科22線(K222) 79RY U/L | FEEDER | E02/11/K222/79UL |  |  |  | CDC | 803 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K222_LCO | 科22線(K222) LCO |  | TapPosMv | [17 empty] | 3-36-13 |  | 3-4D | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_LCO_TAP | 11KV科22線(K222) LCO TAP | FEEDER | E02/11/K222/IED_ADJ |  |  |  | CDC | 804 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K222 | K222(11KV科22線) |  | CB | [17 empty] | 3-13-02 |  | 3-37 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_CB | K222(11KV科22線) CB | FEEDER | E02/11/K222/CB |  |  |  | CDC | 805 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K223 | 科23線(K223) |  | PHA | [17 empty] | 3-13-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_PHA | 11KV科23線(K223) 相間RY | FEEDER | E02/11/K223/PHA |  |  |  | CDC | 806 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K223 | 科23線(K223) |  | GDA | [17 empty] | 3-14-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_GDA | 11KV科23線(K223) 接地RY | FEEDER | E02/11/K223/GDA |  |  |  | CDC | 807 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K223 | 科23線(K223) 79RY |  | 79UL | [17 empty] | 3-36-14 |  | 3-4E | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_79UL | 11KV科23線(K223) 79RY U/L | FEEDER | E02/11/K223/79UL |  |  |  | CDC | 808 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K223_LCO | 科23線(K223) LCO |  | TapPosMv | [17 empty] | 3-36-15 |  | 3-4F | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_LCO_TAP | 11KV科23線(K223) LCO TAP | FEEDER | E02/11/K223/IED_ADJ |  |  |  | CDC | 809 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K223 | K223(11KV科23線) |  | CB | [17 empty] | 3-13-06 |  | 3-38 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_CB | K223(11KV科23線) CB | FEEDER | E02/11/K223/CB |  |  |  | CDC | 810 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K224 | 科24線(K224) |  | PHA | [17 empty] | 3-14-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_PHA | 11KV科24線(K224) 相間RY | FEEDER | E02/11/K224/PHA |  |  |  | CDC | 811 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K224 | 科24線(K224) |  | GDA | [17 empty] | 3-14-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_GDA | 11KV科24線(K224) 接地RY | FEEDER | E02/11/K224/GDA |  |  |  | CDC | 812 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K224 | 科24線(K224) 79RY |  | 79UL | [17 empty] | 3-37-00 |  | 3-50 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_79UL | 11KV科24線(K224) 79RY U/L | FEEDER | E02/11/K224/79UL |  |  |  | CDC | 813 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K224_LCO | 科24線(K224) LCO |  | TapPosMv | [17 empty] | 3-37-01 |  | 3-51 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_LCO_TAP | 11KV科24線(K224) LCO TAP | FEEDER | E02/11/K224/IED_ADJ |  |  |  | CDC | 814 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K224 | K224(11KV科24線) |  | CB | [17 empty] | 3-14-02 |  | 3-39 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_CB | K224(11KV科24線) CB | FEEDER | E02/11/K224/CB |  |  |  | CDC | 815 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | K225 | 科25線(K225) |  | PHA | [17 empty] | 3-14-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_PHA | 11KV科25線(K225) 相間RY | FEEDER | E02/11/K225/PHA |  |  |  | CDC | 816 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K225 | 科25線(K225) |  | GDA | [17 empty] | 3-15-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_GDA | 11KV科25線(K225) 接地RY | FEEDER | E02/11/K225/GDA |  |  |  | CDC | 817 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | K225 | 科25線(K225) 79RY |  | 79UL | [17 empty] | 3-37-02 |  | 3-52 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_79UL | 11KV科25線(K225) 79RY U/L | FEEDER | E02/11/K225/79UL |  |  |  | CDC | 818 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 11 | 11kV | K225_LCO | 科25線(K225) LCO |  | TapPosMv | [17 empty] | 3-37-03 |  | 3-53 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_LCO_TAP | 11KV科25線(K225) LCO TAP | FEEDER | E02/11/K225/IED_ADJ |  |  |  | CDC | 819 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 11 | 11kV | K225 | K225(11KV科25線) |  | CB | [17 empty] | 3-14-06 |  | 3-3A | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_CB | K225(11KV科25線) CB | FEEDER | E02/11/K225/CB |  |  |  | CDC | 820 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27A | 科7A線(K27A) |  | PHA | [17 empty] | 3-10-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_PHA | 23KV科7A線(K27A) 相間RY | FEEDER | E02/22/K27A/PHA |  |  |  | CDC | 821 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27A | 科7A線(K27A) |  | GDA | [17 empty] | 3-10-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_GDA | 23KV科7A線(K27A) 接地RY | FEEDER | E02/22/K27A/GDA |  |  |  | CDC | 822 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27A | 科7A線(K27A) 79RY |  | 79UL | [17 empty] | 3-36-02 |  | 3-42 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_79UL | 23KV科7A線(K27A) 79RY U/L | FEEDER | E02/22/K27A/79UL |  |  |  | CDC | 823 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27A_LCO | 科7A線(K27A) LCO |  | TapPosMv | [17 empty] | 3-36-03 |  | 3-43 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_LCO_TAP | 23KV科7A線(K27A) LCO TAP | FEEDER | E02/22/K27A/IED_ADJ |  |  |  | CDC | 824 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27A | K27A(23KV科7A線) |  | CB | [17 empty] | 3-10-03 |  | 3-31 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_CB | K27A(23KV科7A線) CB | FEEDER | E02/22/K27A/CB |  |  |  | CDC | 825 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27B | 科7B線(K27B) |  | PHA | [17 empty] | 3-11-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_PHA | 23KV科7B線(K27B) 相間RY | FEEDER | E02/22/K27B/PHA |  |  |  | CDC | 826 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27B | 科7B線(K27B) |  | GDA | [17 empty] | 3-11-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_GDA | 23KV科7B線(K27B) 接地RY | FEEDER | E02/22/K27B/GDA |  |  |  | CDC | 827 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27B | 科7B線(K27B) 79RY |  | 79UL | [17 empty] | 3-36-04 |  | 3-44 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_79UL | 23KV科7B線(K27B) 79RY U/L | FEEDER | E02/22/K27B/79UL |  |  |  | CDC | 828 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27B_LCO | 科7B線(K27B) LCO |  | TapPosMv | [17 empty] | 3-36-05 |  | 3-45 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_LCO_TAP | 23KV科7B線(K27B) LCO TAP | FEEDER | E02/22/K27B/IED_ADJ |  |  |  | CDC | 829 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27B | K27B(23KV科7B線) |  | CB | [17 empty] | 3-10-07 |  | 3-32 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_CB | K27B(23KV科7B線) CB | FEEDER | E02/22/K27B/CB |  |  |  | CDC | 830 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27C | 科7C線(K27C) |  | PHA | [17 empty] | 3-11-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_PHA | 23KV科7C線(K27C) 相間RY | FEEDER | E02/22/K27C/PHA |  |  |  | CDC | 831 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27C | 科7C線(K27C) |  | GDA | [17 empty] | 3-11-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_GDA | 23KV科7C線(K27C) 接地RY | FEEDER | E02/22/K27C/GDA |  |  |  | CDC | 832 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27C | 科7C線(K27C) 79RY |  | 79UL | [17 empty] | 3-36-06 |  | 3-46 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_79UL | 23KV科7C線(K27C) 79RY U/L | FEEDER | E02/22/K27C/79UL |  |  |  | CDC | 833 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27C_LCO | 科7C線(K27C) LCO |  | TapPosMv | [17 empty] | 3-36-07 |  | 3-47 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_LCO_TAP | 23KV科7C線(K27C) LCO TAP | FEEDER | E02/22/K27C/IED_ADJ |  |  |  | CDC | 834 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27C | K27C(23KV科7C線) |  | CB | [17 empty] | 3-11-03 |  | 3-33 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_CB | K27C(23KV科7C線) CB | FEEDER | E02/22/K27C/CB |  |  |  | CDC | 835 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K27D | 科7D線(K27D) |  | PHA | [17 empty] | 3-12-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_PHA | 23KV科7D線(K27D) 相間RY | FEEDER | E02/22/K27D/PHA |  |  |  | CDC | 836 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27D | 科7D線(K27D) |  | GDA | [17 empty] | 3-12-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_GDA | 23KV科7D線(K27D) 接地RY | FEEDER | E02/22/K27D/GDA |  |  |  | CDC | 837 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K27D | 科7D線(K27D) 79RY |  | 79UL | [17 empty] | 3-36-08 |  | 3-48 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_79UL | 23KV科7D線(K27D) 79RY U/L | FEEDER | E02/22/K27D/79UL |  |  |  | CDC | 838 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K27D_LCO | 科7D線(K27D) LCO |  | TapPosMv | [17 empty] | 3-36-09 |  | 3-49 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_LCO_TAP | 23KV科7D線(K27D) LCO TAP | FEEDER | E02/22/K27D/IED_ADJ |  |  |  | CDC | 839 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K27D | K27D(23KV科7D線) |  | CB | [17 empty] | 3-11-07 |  | 3-34 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_CB | K27D(23KV科7D線) CB | FEEDER | E02/22/K27D/CB |  |  |  | CDC | 840 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | CB | [17 empty] | 3-15-02 |  | 3-3B | [5 empty] | ADCS_S | [8 empty] | 南科ES.280_CB | 280(11KV #8SC) CB | SC | E02/11/280/CB |  |  |  | CDC | 841 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | SCA | [17 empty] | 3-15-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.280_SCA | 11KV #8SC 51,51N RY | SC | E02/11/280/SCA |  |  |  | CDC | 842 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | UVA | [17 empty] | 3-15-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.280_UVA | 11KV #8SC 27RY(欠壓) | SC | E02/11/280/UVA |  |  |  | CDC | 843 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 11 | 11kV | 280 | #8SC(280) |  | LBS | [17 empty] | 3-35-04 | 3-35-05 | 3-3C | [5 empty] | ADCS_S | [8 empty] | 南科ES.280_LBS | 280(11KV #8SC) LBS | SC | E02/11/280/DS2 |  |  |  | CDC | 844 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 3-12-03 |  | 3-35 | [5 empty] | ADCS_S | [8 empty] | 南科ES.270_CB | 270(23KV #7SC) CB | SC | E02/22/270/CB |  |  |  | CDC | 845 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 3-12-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.270_SCA | 23KV #7SC 51,51N RY | SC | E02/22/270/SCA |  |  |  | CDC | 846 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 3-12-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.270_UVA | 23KV #7SC 27RY(欠壓) | SC | E02/22/270/UVA |  |  |  | CDC | 847 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 370 | #4DTR(370) |  | 81A | [17 empty] | 1-0E-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.370_81A | #4DTR 370CB 81RY | OTHER | E02/22/370/81A |  |  |  | CDC | 848 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 370_81RY | #4DTR |  | U/L | [17 empty] | 3-36-00 |  | 3-40 | [5 empty] | ADCS_S | [8 empty] | 南科ES.370_81RY_U/L | #4DTR 370CB 81RY U/L | OTHER | E02/22/370/81UL |  |  |  | CDC | 849 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 380 | #4DTR(380) |  | 81A | [17 empty] | 1-0F-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.380_81A | #4DTR 380CB 81RY | OTHER | E02/11/380/81A |  |  |  | CDC | 850 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 380_81RY | #4DTR |  | U/L | [17 empty] | 3-36-01 |  | 3-41 | [5 empty] | ADCS_S | [8 empty] | 南科ES.380_81RY_U/L | #4DTR 380CB 81RY U/L | OTHER | E02/11/380/81UL |  |  |  | CDC | 851 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | K221 | 科21線CB |  | 81A | [17 empty] | 3-13-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K221_81A | 科21線CB 81RY | OTHER | E02/11/K221/81A |  |  |  | CDC | 852 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K222 | 科22線CB |  | 81A | [17 empty] | 3-13-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K222_81A | 科22線CB 81RY | OTHER | E02/11/K222/81A |  |  |  | CDC | 853 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K223 | 科23線CB |  | 81A | [17 empty] | 3-14-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K223_81A | 科23線CB 81RY | OTHER | E02/11/K223/81A |  |  |  | CDC | 854 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K224 | 科24線CB |  | 81A | [17 empty] | 3-14-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K224_81A | 科24線CB 81RY | OTHER | E02/11/K224/81A |  |  |  | CDC | 855 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K225 | 科25線CB |  | 81A | [17 empty] | 3-15-01 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K225_81A | 科25線CB 81RY | OTHER | E02/11/K225/81A |  |  |  | CDC | 856 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K27A | 科7A線CB |  | 81A | [17 empty] | 3-10-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27A_81A | 科7A線CB 81RY | OTHER | E02/22/K27A/81A |  |  |  | CDC | 857 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K27B | 科7B線CB |  | 81A | [17 empty] | 3-11-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27B_81A | 科7B線CB 81RY | OTHER | E02/22/K27B/81A |  |  |  | CDC | 858 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K27C | 科7C線CB |  | 81A | [17 empty] | 3-11-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27C_81A | 科7C線CB 81RY | OTHER | E02/22/K27C/81A |  |  |  | CDC | 859 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | K27D | 科7D線CB |  | 81A | [17 empty] | 3-12-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K27D_81A | 科7D線CB 81RY | OTHER | E02/22/K27D/81A |  |  |  | CDC | 860 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | PMA | [17 empty] | 2-3E-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.PMA | 電力量測表計故障(#4DTR) | OTHER | E02/0/StaDev/PMA |  |  |  | CDC | 861 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K251 | 科51線(K251) |  | PHA | [17 empty] | 2-00-04 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_PHA | 23KV科51線(K251) 相間RY | FEEDER | E02/22/K251/PHA |  |  |  | CDC | 862 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K251 | 科51線(K251) |  | GDA | [17 empty] | 2-00-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_GDA | 23KV科51線(K251) 接地RY | FEEDER | E02/22/K251/GDA |  |  |  | CDC | 863 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K251 | 科51線(K251) 79RY |  | 79UL | [17 empty] | 2-38-05 |  | 2-32 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_79UL | 23KV科51線(K251) 79RY U/L | FEEDER | E02/22/K251/79UL |  |  |  | CDC | 864 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K251_LCO | 科51線(K251) LCO |  | TapPosMv | [17 empty] | 2-38-06 |  | 2-33 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_LCO_TAP | 23KV科51線(K251) LCO TAP | FEEDER | E02/22/K251/IED_ADJ |  |  |  | CDC | 865 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K251 | K251(23KV科51線) |  | CB | [17 empty] | 2-00-03 |  | 2-02 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K251_CB | K251(23KV科51線) CB | FEEDER | E02/22/K251/CB |  |  |  | CDC | 866 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K252 | 科52線(K252) |  | PHA | [17 empty] | 2-00-07 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_PHA | 23KV科52線(K252) 相間RY | FEEDER | E02/22/K252/PHA |  |  |  | CDC | 867 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K252 | 科52線(K252) |  | GDA | [17 empty] | 2-01-00 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_GDA | 23KV科52線(K252) 接地RY | FEEDER | E02/22/K252/GDA |  |  |  | CDC | 868 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K252 | 科52線(K252) 79RY |  | 79UL | [17 empty] | 2-38-07 |  | 2-34 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_79UL | 23KV科52線(K252) 79RY U/L | FEEDER | E02/22/K252/79UL |  |  |  | CDC | 869 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K252_LCO | 科52線(K252) LCO |  | TapPosMv | [17 empty] | 2-38-08 |  | 2-35 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_LCO_TAP | 23KV科52線(K252) LCO TAP | FEEDER | E02/22/K252/IED_ADJ |  |  |  | CDC | 870 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K252 | K252(23KV科52線) |  | CB | [17 empty] | 2-00-06 |  | 2-03 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K252_CB | K252(23KV科52線) CB | FEEDER | E02/22/K252/CB |  |  |  | CDC | 871 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K253 | 科53線(K253) |  | PHA | [17 empty] | 2-01-02 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_PHA | 23KV科53線(K253) 相間RY | FEEDER | E02/22/K253/PHA |  |  |  | CDC | 872 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K253 | 科53線(K253) |  | GDA | [17 empty] | 2-01-03 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_GDA | 23KV科53線(K253) 接地RY | FEEDER | E02/22/K253/GDA |  |  |  | CDC | 873 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K253 | 科53線(K253) 79RY |  | 79UL | [17 empty] | 2-38-09 |  | 2-36 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_79UL | 23KV科53線(K253) 79RY U/L | FEEDER | E02/22/K253/79UL |  |  |  | CDC | 874 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K253_LCO | 科53線(K253) LCO |  | TapPosMv | [17 empty] | 2-38-10 |  | 2-37 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_LCO_TAP | 23KV科53線(K253) LCO TAP | FEEDER | E02/22/K253/IED_ADJ |  |  |  | CDC | 875 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K253 | K253(23KV科53線) |  | CB | [17 empty] | 2-01-01 |  | 2-04 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K253_CB | K253(23KV科53線) CB | FEEDER | E02/22/K253/CB |  |  |  | CDC | 876 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 22 | 22kV | K254 | 科54線(K254) |  | PHA | [17 empty] | 2-01-05 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_PHA | 23KV科54線(K254) 相間RY | FEEDER | E02/22/K254/PHA |  |  |  | CDC | 877 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K254 | 科54線(K254) |  | GDA | [17 empty] | 2-01-06 | [7 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_GDA | 23KV科54線(K254) 接地RY | FEEDER | E02/22/K254/GDA |  |  |  | CDC | 878 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | K254 | 科54線(K254) 79RY |  | 79UL | [17 empty] | 2-38-11 |  | 2-38 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_79UL | 23KV科54線(K254) 79RY U/L | FEEDER | E02/22/K254/79UL |  |  |  | CDC | 879 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 22 | 22kV | K254_LCO | 科54線(K254) LCO |  | TapPosMv | [17 empty] | 2-38-12 |  | 2-39 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_LCO_TAP | 23KV科54線(K254) LCO TAP | FEEDER | E02/22/K254/IED_ADJ |  |  |  | CDC | 880 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
E02 | 南科ES | 22 | 22kV | K254 | K254(23KV科54線) |  | CB | [17 empty] | 2-01-04 |  | 2-05 | [5 empty] | DDCS4_2 | [8 empty] | 南科ES.K254_CB | K254(23KV科54線) CB | FEEDER | E02/22/K254/CB |  |  |  | CDC | 881 | GENERICDIPoint | ES002_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 0 |  | 1510 | 南科道爺ㄧ路(1510) |  | RYFA | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1510_RYFA | 南科道爺ㄧ路(1510)數位電驛故障 | OTHER | E02/161/1510/RYFA |  |  |  | CDC | 882 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1520 | 南科道爺二路(1520) |  | RYFA | [17 empty] | 1-30-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1520_RYFA | 南科道爺二路(1520)數位電驛故障 | OTHER | E02/161/1520/RYFA |  |  |  | CDC | 883 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1710 | 南科和鑫二線(1710) |  | 87CFA | [17 empty] | 3-39-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1710_87CFA | 南科和鑫二線(1710)電驛通訊故障 | OTHER | E02/161/1710/87CFA |  |  |  | CDC | 884 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1710 | 南科和鑫二線(1710) |  | RYFA | [17 empty] | 3-39-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1710_RYFA | 南科和鑫二線(1710)數位電驛故障 | OTHER | E02/161/1710/RYFA |  |  |  | CDC | 885 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1720 | 南科積P3線(1720) |  | 87CFA | [17 empty] | 3-39-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1720_87CFA | 南科積P3線(1720)電驛通訊故障 | OTHER | E02/161/1720/87CFA |  |  |  | CDC | 886 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1720 | 南科積P3線(1720) |  | RYFA | [17 empty] | 3-39-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1720_RYFA | 南科積P3線(1720)數位電驛故障 | OTHER | E02/161/1720/RYFA |  |  |  | CDC | 887 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | 87A | [17 empty] | 1-06-03 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1630_87A | 南科豐華紅線(1630) 87RY | LINE161 | E02/161/1630/85A |  |  |  | CDC | 888 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1630 | 南科豐華紅線(1630) |  | 87UL | [17 empty] | 1-32-10 |  | 1-7C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1630_87UL | 南科豐華紅線(1630) 87RY U/L | LINE161 | E02/161/1630/85UL2 |  |  |  | CDC | 889 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1630 | 南科豐華紅線(1630) |  | 87CFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1630_87CFA | 南科豐華紅線(1630)電驛通訊故障 | OTHER | E02/161/1630/87CFA |  |  |  | CDC | 890 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1630 | 南科豐華紅線(1630) |  | 87FA | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1630_87FA | 南科豐華紅線(1630)數位電驛故障 | OTHER | E02/161/1630/RYFA |  |  |  | CDC | 891 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | 1_87UL1 | [17 empty] | 3-39-00 |  | 2-78 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1710_87UL1 | 南科和鑫二線(1710) #1_87RY U/L | LINE161 | E02/161/1710/85UL2 |  |  |  | CDC | 892 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1710 | 南科和鑫二線(1710) |  | 1_87UL2 | [17 empty] | 3-39-01 |  | 2-79 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1710_87UL2 | 南科和鑫二線(1710) #2_87RY U/L | LINE161 | E02/161/1710/79UL |  |  |  | CDC | 893 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | 1_87UL1 | [17 empty] | 3-39-04 |  | 2-7A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1720_87UL1 | 南科積P3線(1720) #1_87RY U/L | LINE161 | E02/161/1720/85UL2 |  |  |  | CDC | 894 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1720 | 南科積P3線(1720) |  | 1_87UL2 | [17 empty] | 3-39-05 |  | 2-7B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1720_87UL2 | 南科積P3線(1720)#2_87RY U/L | LINE161 | E02/161/1720/79UL |  |  |  | CDC | 895 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | 87A | [17 empty] | 1-01-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1520_87A | 南科道爺二路(1520) 87RY | LINE161 | E02/161/1520/85A |  |  |  | CDC | 896 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1520 | 南科道爺二路(1520) |  | 87UL | [17 empty] | 1-30-10 |  | 1-6C | [5 empty] | ADCS_S | [8 empty] | 南科ES.1520_87UL | 南科道爺二路(1520) 87RY U/L | LINE161 | E02/161/1520/85UL2 |  |  |  | CDC | 897 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1520 | 南科道爺二路(1520) |  | 87CFA | [17 empty] | 1-30-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1520_87CFA | 南科道爺二路(1520)87RY通訊故障 | OTHER | E02/161/1520/87CFA |  |  |  | CDC | 898 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | 87A | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1510_87A | 南科道爺ㄧ路(1510) 87RY | LINE161 | E02/161/1510/85A |  |  |  | CDC | 899 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1510 | 南科道爺ㄧ路(1510) |  | 87UL | [17 empty] | 1-30-06 |  | 1-6A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1510_87UL | 南科道爺ㄧ路(1510) 87RY U/L | LINE161 | E02/161/1510/85UL2 |  |  |  | CDC | 900 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1510 | 南科道爺ㄧ路(1510) |  | 87CFA | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1510_87CFA | 南科道爺ㄧ路(1510)87RY通訊故障 | OTHER | E02/161/1510/87CFA |  |  |  | CDC | 901 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161_12BUS | #1,2BUS 87RY |  | 87CTFA | [17 empty] | 1-37-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161_12BUS_CTFA | 161KV#1,2BUS 87RY CT迴路故障 | OTHER | E02/161/ComPoint/12B_CTFA |  |  |  | CDC | 902 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161_12BUS | #1,2BUS |  | RYFA | [17 empty] | 1-37-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161_12BUS_RYFA | 161KV#1,2BUS 87RY數位電驛故障 | OTHER | E02/161/ComPoint/12B_RYFA |  |  |  | CDC | 903 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161_34BUS | #3,4BUS 87RY |  | 87CTFA | [17 empty] | 1-37-14 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161_34BUS_CTFA | 161KV#3,4BUS 87RY CT迴路故障 | OTHER | E02/161/ComPoint/34B_CTFA |  |  |  | CDC | 904 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 161_34BUS | #3,4BUS |  | RYFA | [17 empty] | 1-37-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161_34BUS_RYFA | 161KV#3,4BUS 87RY數位電驛故障 | OTHER | E02/161/ComPoint/34B_RYFA |  |  |  | CDC | 905 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | PHA | [17 empty] | 1-03-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1580_PHA | 南科道爺四路(1580) 相間RY | LINE161 | E02/161/1580/PHA |  |  |  | CDC | 906 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | GDA | [17 empty] | 1-03-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1580_GDA | 南科道爺四路(1580) 接地RY | LINE161 | E02/161/1580/GDA |  |  |  | CDC | 907 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | 87A | [17 empty] | 1-03-05 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1580_87A | 南科道爺四路(1580) 87RY | LINE161 | E02/161/1580/85A |  |  |  | CDC | 908 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | 87UL | [17 empty] | 1-31-10 |  | 1-72 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1580_87UL | 南科道爺四路(1580) 87RY U/L | LINE161 | E02/161/1580/85UL2 |  |  |  | CDC | 909 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | CB | [17 empty] | 1-03-04 |  | 1-08 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1580_CB | 1580(南科道爺四路) CB | LINE161 | E02/161/1580/CB |  |  |  | CDC | 910 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | 79UL | [17 empty] | 1-31-11 |  | 1-73 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1580_79UL | 南科道爺四路(1580) 79RY U/L | LINE161 | E02/161/1580/79UL |  |  |  | CDC | 911 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | DS1 | 1581 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-42 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1581_DS | 1581(南科道爺四路) DS | LINE161 | E02/161/1580/DS1 |  |  |  | CDC | 912 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | DS2 | 1582 | [16 empty] | 1-3B-06 | 1-3B-07 | 1-43 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1582_DS | 1582(南科道爺四路) DS | LINE161 | E02/161/1580/DS2 |  |  |  | CDC | 913 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | DS3 | 1583 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-44 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1583_DS | 1583(南科道爺四路) DS | LINE161 | E02/161/1580/DS3 |  |  |  | CDC | 914 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1580 | 南科道爺四路(1580) |  | E3 | 1583E | [16 empty] | 1-3B-10 | 1-3B-11 | 1-45 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1583E_ES | 1583E(南科道爺四路) ES | LINE161 | E02/161/1580/E3 |  |  |  | CDC | 915 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 0 |  | 1570 | 南科道爺三路(1570) |  | RYFA | [17 empty] | 1-31-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1570_RYFA | 南科道爺三路(1570)數位電驛故障 | OTHER | E02/161/1570/RYFA |  |  |  | CDC | 916 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1580 | 南科道爺四路(1580) |  | 87CFA | [17 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1580_87CFA | 南科道爺四路(1580)87RY通訊故障 | OTHER | E02/161/1580/87CFA |  |  |  | CDC | 917 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1580 | 南科道爺四路(1580) |  | RYFA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1580_RYFA | 南科道爺四路(1580)數位電驛故障 | OTHER | E02/161/1580/RYFA |  |  |  | CDC | 918 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 斷路器失靈RY | 斷路器失靈RY |  | BFS | [17 empty] | 1-37-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_BFS | 161KV 斷路器失靈RY U/L | OTHER | E02/161/ComPoint/BFS |  |  |  | CDC | 919 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E02 | 南科ES | 161 | 161kV | BVS | #34BUS |  | RY | [17 empty] | 3-3A-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.BVS_RY | 161KV #34BUS GRZ100 RY U/L | OTHER | E02/0/StaDev/GRZ100 |  |  |  | CDC | 920 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E02 | 南科ES | 0 |  | 1640 | 南科豐華白線(1640) |  | 87A1 | [17 empty] | 1-06-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1640_87A1 | 南科豐華白線(1640) 87A1 | OTHER | E02/161/1640/87A1 |  |  |  | CDC | 921 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1640 | 南科豐華白線(1640) |  | 87A2 | [17 empty] | 3-05-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1640_87A2 | 南科豐華白線(1640) 87A2 | OTHER | E02/161/1640/87A2 |  |  |  | CDC | 922 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1640 | 南科豐華白線(1640) |  | 87CFA | [17 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1640_87CFA | 南科豐華白線(1640)電驛通訊故障 | OTHER | E02/161/1640/87CFA |  |  |  | CDC | 923 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1640 | 南科豐華白線(1640) |  | 1_87UL1 | [17 empty] | 1-32-14 |  | 1-7E | [5 empty] | ADCS_S | [8 empty] | 南科ES.1640_87UL1 | 南科豐華白線(1640) 87RY1 U/L | OTHER | E02/161/1640/1_87UL1 |  |  |  | CDC | 924 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1640 | 南科豐華白線(1640) |  | 1_87UL2 | [17 empty] | 3-3A-05 |  | 2-64 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1640_87UL2 | 南科豐華白線(1640) 87RY2 U/L | OTHER | E02/161/1640/1_87UL2 |  |  |  | CDC | 925 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1640 | 南科豐華白線(1640) |  | RYFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1640_RYFA | 南科豐華白線(1640)數位電驛故障 | OTHER | E02/161/1640/RYFA |  |  |  | CDC | 926 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1650 | 三竹ㄧ路(1650) |  | 87A1 | [17 empty] | 3-00-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1650_87A1 | 南科三竹ㄧ路(1650) 87A1 | OTHER | E02/161/1650/87A1 |  |  |  | CDC | 927 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1650 | 三竹ㄧ路(1650) |  | 87A2 | [17 empty] | 3-05-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1650_87A2 | 南科三竹ㄧ路(1650) 87A2 | OTHER | E02/161/1650/87A2 |  |  |  | CDC | 928 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1650 | 三竹ㄧ路(1650) |  | 87CFA | [17 empty] | 3-38-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1650_87CFA | 南科三竹ㄧ路(1650)電驛通訊故障 | OTHER | E02/161/1650/87CFA |  |  |  | CDC | 929 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1650 | 三竹ㄧ路(1650) |  | 1_87UL1 | [17 empty] | 3-38-04 |  | 2-72 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1650_87UL1 | 南科三竹ㄧ路(1650) 87RY1 U/L | OTHER | E02/161/1650/1_87UL1 |  |  |  | CDC | 930 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1650 | 三竹ㄧ路(1650) |  | 1_87UL2 | [17 empty] | 3-3A-06 |  | 2-65 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1650_87UL2 | 南科三竹ㄧ路(1650) 87RY2 U/L | OTHER | E02/161/1650/1_87UL2 |  |  |  | CDC | 931 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1650 | 三竹ㄧ路(1650) |  | RYFA | [17 empty] | 3-38-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1650_RYFA | 南科三竹ㄧ路(1650)數位電驛故障 | OTHER | E02/161/1650/RYFA |  |  |  | CDC | 932 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1660 | 三竹二路(1660) |  | 87A1 | [17 empty] | 3-00-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1660_87A1 | 南科三竹二路(1660) 87A1 | OTHER | E02/161/1660/87A1 |  |  |  | CDC | 933 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1660 | 三竹二路(1660) |  | 87A2 | [17 empty] | 3-05-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1660_87A2 | 南科三竹二路(1660) 87A2 | OTHER | E02/161/1660/87A2 |  |  |  | CDC | 934 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1660 | 三竹二路(1660) |  | 87CFA | [17 empty] | 3-38-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1660_87CFA | 南科三竹二路(1660)電驛通訊故障 | OTHER | E02/161/1660/87CFA |  |  |  | CDC | 935 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1660 | 三竹二路(1660) |  | 1_87UL1 | [17 empty] | 3-38-00 |  | 2-70 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1660_87UL1 | 南科三竹二路(1660) 87RY1 U/L | OTHER | E02/161/1660/1_87UL1 |  |  |  | CDC | 936 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1660 | 三竹二路(1660) |  | 1_87UL2 | [17 empty] | 3-3A-07 |  | 2-66 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1660_87UL2 | 南科三竹二路(1660) 87RY2 U/L | OTHER | E02/161/1660/1_87UL2 |  |  |  | CDC | 937 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1660 | 三竹二路(1660) |  | RYFA | [17 empty] | 3-38-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1660_RYFA | 南科三竹二路(1660)數位電驛故障 | OTHER | E02/161/1660/RYFA |  |  |  | CDC | 938 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  |  |  |  | GEN1 | [17 empty] | 2-3E-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.GEN1 | 緊急發電機運轉(洞道機房用) | OTHER | E02/0/StaDev/9A5Other |  |  |  | CDC | 939 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E02 | 南科ES | 0 |  |  |  |  | GEN2 | [17 empty] | 2-3E-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.GEN2 | 緊急發電機運轉(所內用電用) | OTHER | E02/0/StaDev/10A5Other |  |  |  | CDC | 940 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E02 | 南科ES | 161 | 161kV | _BF | _BF |  | RYFA | [17 empty] | 3-3A-08 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161KV_BF_RYFA | 161KV斷路器失靈電驛故障 | OTHER | E02/161/ComPoint/RYFA |  |  |  | CDC | 941 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | PHA | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1530_PHA | 南科三福一線(1530) 相間RY | LINE161 | E02/161/1530/PHA |  |  |  | CDC | 942 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 161KV_S | [8 empty] | 南科ES.1530_GDA | 南科三福一線(1530) 接地RY | LINE161 | E02/161/1530/GDA |  |  |  | CDC | 943 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | CB | [17 empty] | 1-00-04 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 南科ES.1530_CB | 1530(南科三福一線) CB | LINE161 | E02/161/1530/CB |  |  |  | CDC | 944 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | 79UL | [17 empty] | 1-30-03 |  | 2-69 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1530_79UL | 南科三福一線(1530) 79RY U/L | LINE161 | E02/161/1530/79UL |  |  |  | CDC | 945 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | DS1 | 1531 | [16 empty] | 1-38-00 | 1-38-01 | 1-28 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1531_DS | 1531(南科三福一線) DS | LINE161 | E02/161/1530/DS1 |  |  |  | CDC | 946 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | DS2 | 1532 | [16 empty] | 1-38-02 | 1-38-03 | 1-29 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1532_DS | 1532(南科三福一線) DS | LINE161 | E02/161/1530/DS2 |  |  |  | CDC | 947 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | DS3 | 1533 | [16 empty] | 1-38-04 | 1-38-05 | 1-2A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1533_DS | 1533(南科三福一線) DS | LINE161 | E02/161/1530/DS3 |  |  |  | CDC | 948 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E02 | 南科ES | 161 | 161kV | 1530 | 南科三福一線(1530) |  | E3 | 1533E | [16 empty] | 1-38-06 | 1-38-07 | 1-2B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1533E_ES | 1533E(南科三福一線) ES | LINE161 | E02/161/1530/E3 |  |  |  | CDC | 949 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | 87A1 | [17 empty] | 1-00-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1530_87A1 | 南科三福一線(1530) 87A1 | OTHER | E02/161/1530/87A1 |  |  |  | CDC | 950 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | 87A2 | [17 empty] | 3-05-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1530_87A2 | 南科三福一線(1530) 87A2 | OTHER | E02/161/1530/87A2 |  |  |  | CDC | 951 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | 87CFA | [17 empty] | 1-30-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1530_87CFA | 南科三福一線1530 87RY通訊故障 | OTHER | E02/161/1530/87CFA |  |  |  | CDC | 952 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | 1_87UL1 | [17 empty] | 1-30-02 |  | 2-67 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1530_87UL1 | 南科三福一線(1530) 87RY1 U/L | OTHER | E02/161/1530/1_87UL1 |  |  |  | CDC | 953 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | 1_87UL2 | [17 empty] | 3-3A-09 |  | 2-68 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1530_87UL2 | 南科三福一線(1530) 87RY2 U/L | OTHER | E02/161/1530/1_87UL2 |  |  |  | CDC | 954 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | DTTA | [17 empty] | 3-3A-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1530_DTTA | 南科三福一線(1530) 遠方遙跳 | OTHER | E02/161/1530/DTTA |  |  |  | CDC | 955 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1530 | 南科三福一線(1530) |  | RYFA | [17 empty] | 1-30-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1530_RYFA | 南科三福一線1530 數位電驛故障 | OTHER | E02/161/1530/RYFA |  |  |  | CDC | 956 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | 87A1 | [17 empty] | 1-02-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1540_87A1 | 南科積E六線(1540) 87A1 | OTHER | E02/161/1540/87A1 |  |  |  | CDC | 957 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | 87A2 | [17 empty] | 3-06-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1540_87A2 | 南科積E六線(1540) 87A2 | OTHER | E02/161/1540/87A2 |  |  |  | CDC | 958 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | 1_87UL1 | [17 empty] | 1-30-14 |  | 2-6A | [5 empty] | ADCS_S | [8 empty] | 南科ES.1540_87UL1 | 南科積E六線(1540) 87RY1 U/L | OTHER | E02/161/1540/1_87UL1 |  |  |  | CDC | 959 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | 1_87UL2 | [17 empty] | 3-3A-10 |  | 2-6B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1540_87UL2 | 南科積E六線(1540) 87RY2 U/L | OTHER | E02/161/1540/1_87UL2 |  |  |  | CDC | 960 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1540 | 南科積E六線(1540) |  | DTTA | [17 empty] | 3-3A-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1540_DTTA | 南科積E六線(1540) 遠方遙跳 | OTHER | E02/161/1540/DTTA |  |  |  | CDC | 961 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1670 | 積六線(1670) |  | RYFA | [17 empty] | 3-38-11 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1670_RYFA | 積六線(1670) 數位電驛故障 | OTHER | E02/161/1670/RYFA |  |  |  | CDC | 962 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1680 | 康寧線(1680) |  | RYFA | [17 empty] | 3-38-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1680_RYFA | 康寧線(1680) 數位電驛故障 | OTHER | E02/161/1680/RYFA |  |  |  | CDC | 963 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1550 | 三福科線(1550) |  | RYFA | [17 empty] | 1-31-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1550_RYFA | 三福科線(1550) 數位電驛故障 | OTHER | E02/161/1550/RYFA |  |  |  | CDC | 964 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1670 | 積六線(1670) |  | 87CFA | [17 empty] | 3-38-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1670_87CFA | 積六線(1670) 87RY通訊故障 | OTHER | E02/161/1670/87CFA |  |  |  | CDC | 965 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1680 | 康寧線(1680) |  | 87CFA | [17 empty] | 3-38-14 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1680_87CFA | 康寧線(1680) 87RY通訊故障 | OTHER | E02/161/1680/87CFA |  |  |  | CDC | 966 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 3-3A-13 | [7 empty] | ADCS_S | [8 empty] | 南科ES.OLTCA | OLTC 15分鐘連動3次 | OTHER | E02/0/StaDev/OLTC_A |  |  |  | CDC | 967 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 22 | 22kV | 11_ | 11/ IED |  | RYFA | [17 empty] | 3-37-10 | [7 empty] | ADCS_S | [8 empty] | 南科ES.11/23KV_RYFA | 11/23KV IED 故障 | OTHER | E02/22/ComPoint/RYFA |  |  |  | CDC | 968 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 310 | #1DTR(310) |  | 81A | [17 empty] | 3-06-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.310_81A | #1DTR 310CB 81RY | OTHER | E02/22/310/81A |  |  |  | CDC | 969 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 310_81RY | #1DTR |  | U/L | [17 empty] | 3-37-04 |  | 3-54 | [5 empty] | ADCS_S | [8 empty] | 南科ES.310_81RY_U/L | #1DTR 310CB 81RY U/L | OTHER | E02/22/310/81UL |  |  |  | CDC | 970 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 320 | #1DTR(320) |  | 81A | [17 empty] | 3-06-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.320_81A | #1DTR 320CB 81RY | OTHER | E02/11/320/81A |  |  |  | CDC | 971 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 320_81RY | #1DTR |  | U/L | [17 empty] | 3-37-05 |  | 3-55 | [5 empty] | ADCS_S | [8 empty] | 南科ES.320_81RY_U/L | #1DTR 320CB 81RY U/L | OTHER | E02/11/320/81UL |  |  |  | CDC | 972 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 330 | #2DTR(330) |  | 81A | [17 empty] | 3-06-06 | [7 empty] | ADCS_S | [8 empty] | 南科ES.330_81A | #2DTR 330CB 81RY | OTHER | E02/22/330/81A |  |  |  | CDC | 973 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 330_81RY | #2DTR |  | U/L | [17 empty] | 3-37-06 |  | 3-56 | [5 empty] | ADCS_S | [8 empty] | 南科ES.330_81RY_U/L | #2DTR 330CB 81RY U/L | OTHER | E02/22/330/81UL |  |  |  | CDC | 974 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 340 | #2DTR(340) |  | 81A | [17 empty] | 3-06-07 | [7 empty] | ADCS_S | [8 empty] | 南科ES.340_81A | #2DTR 340CB 81RY | OTHER | E02/22/340/81A |  |  |  | CDC | 975 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 340_81RY | #2DTR |  | U/L | [17 empty] | 3-37-07 |  | 3-57 | [5 empty] | ADCS_S | [8 empty] | 南科ES.340_81RY_U/L | #2DTR 340CB 81RY U/L | OTHER | E02/22/340/81UL |  |  |  | CDC | 976 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 350 | #3DTR(350) |  | 81A | [17 empty] | 3-07-00 | [7 empty] | ADCS_S | [8 empty] | 南科ES.350_81A | #3DTR 350CB 81RY | OTHER | E02/22/350/81A |  |  |  | CDC | 977 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 350_81RY | #3DTR |  | U/L | [17 empty] | 3-37-08 |  | 3-58 | [5 empty] | ADCS_S | [8 empty] | 南科ES.350_81RY_U/L | #3DTR 350CB 81RY U/L | OTHER | E02/22/350/81UL |  |  |  | CDC | 978 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 360 | #3DTR(360) |  | 81A | [17 empty] | 3-07-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.360_81A | #3DTR 360CB 81RY | OTHER | E02/22/360/81A |  |  |  | CDC | 979 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 360_81RY | #3DTR |  | U/L | [17 empty] | 3-37-09 |  | 3-59 | [5 empty] | ADCS_S | [8 empty] | 南科ES.360_81RY_U/L | #3DTR 360CB 81RY U/L | OTHER | E02/22/360/81UL |  |  |  | CDC | 980 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1613DTR | #3DTR |  | DTR_86A | [17 empty] | 1-0F-03 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#3DTR_86A | 161KV #3DTR 86RY | OTHER |  |  |  |  | CDC | 981 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1613DTR | #3DTR |  | 187UL | [17 empty] | 1-34-08 |  | 3-3D | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#3DTR_187UL | 161KV #3DTR 187RY U/L | OTHER | E02//3DTR/87UL |  |  |  | CDC | 982 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1613DTR | #3DTR |  | 287UL | [17 empty] | 2-3B-13 |  | 3-3E | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#3DTR_287UL | 161KV #3DTR 287RY U/L | OTHER |  |  |  |  | CDC | 983 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1613DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-3B-14 |  | 3-3F | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#3DTR_51ZUL | 161KV #3DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 984 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1613DTR | #3DTR |  | RYFA | [17 empty] | 2-3B-15 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#3DTR_RYFA | 161KV #3DTR RYFA | OTHER |  |  |  |  | CDC | 985 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1612DTR | #2DTR |  | DTR_86A | [17 empty] | 1-0F-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#2DTR_86A | 161KV #2DTR 86RY | OTHER |  |  |  |  | CDC | 986 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1612DTR | #2DTR |  | 187UL | [17 empty] | 1-33-14 |  | 3-28 | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#2DTR_187UL | 161KV #2DTR 187RY U/L | OTHER | E02//2DTR/87UL |  |  |  | CDC | 987 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1612DTR | #2DTR |  | 287UL | [17 empty] | 2-3B-10 |  | 3-29 | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#2DTR_287UL | 161KV #2DTR 287RY U/L | OTHER |  |  |  |  | CDC | 988 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1612DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-3B-11 |  | 3-2A | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#2DTR_51ZUL | 161KV #2DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 989 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1612DTR | #2DTR |  | RYFA | [17 empty] | 2-3B-12 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#2DTR_RYFA | 161KV #2DTR RYFA | OTHER |  |  |  |  | CDC | 990 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1611DTR | #1DTR |  | DTR_86A | [17 empty] | 1-0F-01 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#1DTR_86A | 161KV #1DTR 86RY | OTHER |  |  |  |  | CDC | 991 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1611DTR | #1DTR |  | 187UL | [17 empty] | 1-33-02 |  | 2-6D | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#1DTR_187UL | 161KV #1DTR 187RY U/L | OTHER | E02//1DTR/87UL |  |  |  | CDC | 992 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1611DTR | #1DTR |  | 287UL | [17 empty] | 2-3B-07 |  | 2-6E | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#1DTR_287UL | 161KV #1DTR 287RY U/L | OTHER |  |  |  |  | CDC | 993 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1611DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-3B-08 |  | 2-6F | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#1DTR_51ZUL | 161KV #1DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 994 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1611DTR | #1DTR |  | RYFA | [17 empty] | 2-3B-09 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#1DTR_RYFA | 161KV #1DTR RYFA | OTHER |  |  |  |  | CDC | 995 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1614DTR | #4DTR |  | DTR_86A | [17 empty] | 1-0F-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#4DTR_86A | 161KV #4DTR 86RY | OTHER |  |  |  |  | CDC | 996 | GENERICDIPoint | ES002_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E02 | 南科ES | 161 | 161kV | 1614DTR | #4DTR |  | 187UL | [17 empty] | 1-35-02 |  | 3-5A | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#4DTR_187UL | 161KV #4DTR 187RY U/L | OTHER | E02//4DTR/87UL |  |  |  | CDC | 997 | GENERICDIPoint | ES002_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1614DTR | #4DTR |  | 287UL | [17 empty] | 2-3C-00 |  | 3-5B | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#4DTR_287UL | 161KV #4DTR 287RY U/L | OTHER |  |  |  |  | CDC | 998 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1614DTR | #4DTR |  | 51Z_UL | [17 empty] | 2-3C-01 |  | 3-5C | [5 empty] | ADCS_S | [8 empty] | 南科ES.161#4DTR_51ZUL | 161KV #4DTR 51ZRY U/L | OTHER |  |  |  |  | CDC | 999 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 161 | 161kV | 1614DTR | #4DTR |  | RYFA | [17 empty] | 2-3C-02 | [7 empty] | ADCS_S | [8 empty] | 南科ES.161#4DTR_RYFA | 161KV #4DTR RYFA | OTHER |  |  |  |  | CDC | 1000 | GENERICDIPoint | ES002_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1670 | 積六線(1670) |  | 87A1 | [17 empty] | 3-01-04 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1670_87A1 | 南科積六線(1670) 87A1 | OTHER | E02/161/1670/21A |  |  |  | CDC | 1001 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1670 | 積六線(1670) |  | 87A2 | [17 empty] | 3-01-05 | [7 empty] | ADCS_S | [8 empty] | 南科ES.1670_87A2 | 南科積六線(1670) 87A2 | OTHER | E02/161/1670/1A5Other |  |  |  | CDC | 1002 | GENERICDIPoint | ES002_L3 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E02 | 南科ES | 0 |  | 1670 | 積六線(1670) |  | 1_87UL1 | [17 empty] | 3-38-08 |  | 2-74 | [5 empty] | ADCS_S | [8 empty] | 南科ES.1670_87UL1 | 南科積六線(1670) 87RY1 U/L | OTHER | E02/161/1670/85UL |  |  |  | CDC | 1003 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E02 | 南科ES | 0 |  | 1670 | 積六線(1670) |  | 1_87UL2 | [17 empty] | 3-3A-00 |  | 3-2B | [5 empty] | ADCS_S | [8 empty] | 南科ES.1670_87UL2 | 南科積六線(1670) 87RY2 U/L | OTHER |  |  |  |  | CDC | 1004 | GENERICDIPoint | ES002_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo