## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E03 | 龍崎ES | 345 | 345kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0258 |  |  | 3-82 |  |  | 345KV | KV | 一號 BUS PT | kV_-450_450(-2000_2000) | aaa | B2/E03_C | [8 empty] | 龍崎ES.345KV#1BUS_KV | 345KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0259 |  |  | 3-83 |  |  | 345KV | KV | 二號 BUS PT | kV_-450_450(-2000_2000) | aab | B2/E03_C | [8 empty] | 龍崎ES.345KV#2BUS_KV | 345KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E03 | 龍崎ES | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 一號 BUS PD | kV_-210_210(-2000_2000) | aaa | B2/E03_A1 | [8 empty] | 龍崎ES.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 二號 BUS PD | kV_-210_210(-2000_2000) | aab | B2/E03_A1 | [8 empty] | 龍崎ES.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E03 | 龍崎ES | 345 | 345kV | 1BUS | #1BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 3-06-02 |  |  | 345KV | #1BUS | 187B1A |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#1B_87A1 | 345KV #1BUS 第一組 87RY | BUS |  |  |  |  | CDC | 6 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 1BUS | #1BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 3-06-03 |  |  | 345KV | #1BUS | 187B2A |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#1B_87A2 | 345KV #1BUS 第二組 87RY | BUS |  |  |  |  | CDC | 7 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 2BUS | #2BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 3-06-04 |  |  | 345KV | #2BUS | 287B1A |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#2B_87A1 | 345KV #2BUS 第一組 87RY | BUS |  |  |  |  | CDC | 8 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 2BUS | #2BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 3-06-05 |  |  | 345KV | #2BUS | 287B2A |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#2B_87A2 | 345KV #2BUS 第二組 87RY | BUS |  |  |  |  | CDC | 9 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaez | B2/E03_A1 | [8 empty] | 龍崎ES.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | 161kV#1Bus | VUA | 161KV #1BUS VUA1 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 161KV | #1BUS | 87B1A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161#1BUS_87A | 161KV #1BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaez | B2/E03_A1 | [8 empty] | 龍崎ES.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 13 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | 161kV#2Bus | VUA | 161KV #2BUS VUA2 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 14 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 161KV | #2BUS | 87B2A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161#2BUS_87A | 161KV #2BUS 87RY | BUS |  |  |  |  | CDC | 15 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 3510 | MW | 南科龍崎一路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3510_MW | 南科一路 MW | LINE345 |  |  |  |  | CDC | 16 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 3510 | MVAR | 南科龍崎一路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3510_MVAR | 南科一路 MVAR | LINE345 |  |  |  |  | CDC | 17 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 3510 | KV | 南科龍崎一路 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3510LPD_KV | 南科一路(3510) LPD KV | LINE345 |  |  |  |  | CDC | 18 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | 3530 | MVAR | 龍崎(北)~龍崎(南)臨時線 3530 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3530_MW | 北南臨時線(3530) MW | LINE345 |  |  |  |  | CDC | 19 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | 3530 | MW | 龍崎(北)~龍崎(南)臨時線 3530 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3530_MVAR | 北南臨時線(3530) MVAR | LINE345 |  |  |  |  | CDC | 20 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | 3530 | KV | 龍崎(北)~龍崎(南)臨時線 3530 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3530LPD_KV | 北南臨時線(3530) LPD KV | LINE345 |  |  |  |  | CDC | 21 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | 3540 | MW | 龍崎瀰力二路 3540 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3540_MW | 瀰力二路 MW | LINE345 |  |  |  |  | CDC | 22 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | 3540 | MVAR | 龍崎瀰力二路 3540 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3540_MVAR | 瀰力二路 MVAR | LINE345 |  |  |  |  | CDC | 23 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | 3540 | KV | 龍崎瀰力二路 3540 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3540LPD_KV | 瀰力二路(3540) LPD KV | LINE345 |  |  |  |  | CDC | 24 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | 3560 | MVAR | 天輪龍崎海線 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E03_C |  |  | 2000 | [5 empty] | 龍崎ES.3560_MW | 天輪海線 MW | LINE345 |  |  |  |  | CDC | 25 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | 3560 | MW | 天輪龍崎海線 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E03_C |  |  | 2000 | [5 empty] | 龍崎ES.3560_MVAR | 天輪海線 MVAR | LINE345 |  |  |  |  | CDC | 26 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | 3560 | KV | 天輪龍崎海線 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3560LPD_KV | 天輪海線(3560) LPD KV | LINE345 |  |  |  |  | CDC | 27 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | 3610 | MW | 南科龍崎二路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3610_MW | 南科二路 MW | LINE345 |  |  |  |  | CDC | 28 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | 3610 | MVAR | 南科龍崎二路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3610_MVAR | 南科二路 MVAR | LINE345 |  |  |  |  | CDC | 29 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | 3610 | KV | 南科龍崎二路 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3610LPD_KV | 南科二路(3610) LPD KV | LINE345 |  |  |  |  | CDC | 30 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | 3630 | MVAR | 興達龍崎一路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3630_MW | 興達一路 MW | LINE345 |  |  |  |  | CDC | 31 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | 3630 | MW | 興達龍崎一路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3630_MVAR | 興達一路 MVAR | LINE345 |  |  |  |  | CDC | 32 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | 3630 | KV | 興達龍崎一路 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3630LPD_KV | 興達一路(3630) LPD KV | LINE345 |  |  |  |  | CDC | 33 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | 3640 | MW | 路北龍崎紅線 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3640_MW | 路北紅線 MW | LINE345 |  |  |  |  | CDC | 34 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | 3640 | MVAR | 路北龍崎紅線 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E03_C |  |  | 4000 | [5 empty] | 龍崎ES.3640_MVAR | 路北紅線 MVAR | LINE345 |  |  |  |  | CDC | 35 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | 3640 | KV | 路北龍崎紅線 LPD | kV_-450_450(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.3640LPD_KV | 路北紅線(3640) LPD KV | LINE345 |  |  |  |  | CDC | 36 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 3-07-01 |  |  | 3510 | #1RY | 南科龍崎一路 1SSA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_SSA11 | 南科一路(3510) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 37 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 3-07-02 |  |  | 3510 | #1RY | 南科龍崎一路 1SSA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_SSA12 | 南科一路(3510) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 38 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 3-07-04 |  |  | 3530 | 187A1 #1RY | 龍崎(北)~龍崎(南)臨時線 3530 #1SSA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_87A1 | 北南臨時線(3530) #1_187RY | LINE345 |  |  |  |  | CDC | 39 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 3-07-05 |  |  | 3530 | 187A2 #1RY | 龍崎(北)~龍崎(南)臨時線 3530 #1SSA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_87A2 | 北南臨時線(3530) #1_287RY | LINE345 |  |  |  |  | CDC | 40 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0319 |  |  | 3-07-07 |  |  | 3540 | 187A1 | 龍崎瀰力二路 3540 #1_1 87RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87A1 | 瀰力二路(3540) #1_187RY | LINE345 |  |  |  |  | CDC | 41 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 3-08-00 |  |  | 3540 | 187A2 | 龍崎瀰力二路 3540 #1_2 87RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87A2 | 瀰力二路(3540) #1_287RY | LINE345 |  |  |  |  | CDC | 42 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0322 |  |  | 3-08-02 |  |  | 3560 | #1 RY | 天輪龍崎海線 3560 1SSA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_SSA11 | 天輪海線(3560) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 43 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 3-08-03 |  |  | 3560 | #1RY | 天輪龍崎海線 3560 1SSA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_SSA12 | 天輪海線(3560) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 44 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 3-08-05 |  |  | 3610 | #1 RY | 南科龍崎二路1SSA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_SSA11 | 南科二路(3610) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 45 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 3-08-06 |  |  | 3610 | #1RY | 南科龍崎二路1SSA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_SSA12 | 南科二路(3610) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 46 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 3-09-00 |  |  | 3630 | #1 RY | 興達龍崎一路 1SSA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_SSA11 | 興達一路(3630) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 47 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 3-09-01 |  |  | 3630 | #1RY | 興達龍崎一路 1SSA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_SSA12 | 興達一路(3630) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 48 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 3-09-03 |  |  | 3640 | #1 RY | 路北龍崎紅線1SSA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_SSA11 | 路北紅線(3640) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 49 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 3-09-04 |  |  | 3640 | #1RY | 路北龍崎紅線1SSA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_SSA12 | 路北紅線(3640) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 50 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 3-04-04 |  |  | 3910 | PHA | 備用線(3910) 相間RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3910_PHA | 備用線(3910) 相間RY | LINE345 |  |  |  |  | CDC | 51 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 3-04-05 |  |  | 3910 | GDA | 備用線(3910) 接地RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3910_GDA | 備用線(3910) 接地RY | LINE345 |  |  |  |  | CDC | 52 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 3-07-03 |  |  | 3510 | #2 RY | 南科龍崎一路 2SSA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_SSA2 | 南科一路(3510) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 53 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 3-35-15 |  |  | 3510 | #1RY | 南科龍崎一路 RYA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_RYFA1 | 南科一路(3510) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 54 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0865 |  |  | 3-36-01 |  |  | 3510 | #2RY | 南科龍崎一路 RYA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_RYFA2 | 南科一路(3510) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 55 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0861 |  | 0375 | 3-35-13 |  | 3-77 | 3510 | 79S | 南科龍崎一路 3510 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_79UL | 南科一路(3510) 79RY U/L | LINE345 |  |  |  |  | CDC | 56 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 3-07-06 |  |  | 3530 | 287A1 #2RY | 龍崎(北)~龍崎(南)臨時線 3530 #2SSA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_87A3 | 北南臨時線(3530) #2_187RY | LINE345 |  |  |  |  | CDC | 57 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0868 |  |  | 3-36-04 |  |  | 3530 | RYFA1 #1RY | 龍崎(北)~龍崎(南)臨時線 3530 1RYFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_RYFA1 | 北南臨時線(3530) #1_RY故障 | LINE345 |  |  |  |  | CDC | 58 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0870 |  |  | 3-36-06 |  |  | 3530 | RYFA2 #2RY | 龍崎(北)~龍崎(南)臨時線 3530 2RYFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_RYFA2 | 北南臨時線(3530) #2_RY故障 | LINE345 |  |  |  |  | CDC | 59 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0866 |  | 0376 | 3-36-02 |  | 3-78 | 3530 | 79UL | 龍崎(北)~龍崎(南)臨時線 3530 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_79UL | 北南臨時線(3530) 79RY U/L | LINE345 |  |  |  |  | CDC | 60 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 3-08-01 |  |  | 3540 | 287A1 | 龍崎瀰力二路 3540 #2_1 87RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87A3 | 瀰力二路(3540) #2_187RY | LINE345 |  |  |  |  | CDC | 61 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0873 |  |  | 3-36-09 |  |  | 3540 | RYFA1 | 龍崎瀰力二路 3540 #1 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_RYFA1 | 瀰力二路(3540) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 62 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0875 |  |  | 3-36-11 |  |  | 3540 | RYFA2 | 龍崎瀰力二路 3540 #2 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_RYFA2 | 瀰力二路(3540) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 63 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0871 |  | 0377 | 3-36-07 |  | 3-79 | 3540 | 79UL | 龍崎瀰力二路 3540 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_79UL | 瀰力二路(3540) 79RY U/L | LINE345 |  |  |  |  | CDC | 64 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 3-08-04 |  |  | 3560 | #2 RY | 天輪龍崎海線 3560 2SSA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_SSA2 | 天輪海線(3560) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 65 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0878 |  |  | 3-36-14 |  |  | 3560 | #1RY | 天輪龍崎海線 3560 RYA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_RYFA1 | 天輪海線(3560) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 66 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 3-37-00 |  |  | 3560 | #2RY | 天輪龍崎海線 3560 RYA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_RYFA2 | 天輪海線(3560) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 67 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0876 |  | 0378 | 3-36-12 |  | 3-7A | 3560 | 79S | 天輪龍崎海線 3560 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_79UL | 天輪海線(3560) 79RY U/L | LINE345 |  |  |  |  | CDC | 68 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 3-08-07 |  |  | 3610 | #2 RY | 南科龍崎二路2SSA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_SSA2 | 南科二路(3610) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 69 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 3-37-03 |  |  | 3610 | #1RY | 南科龍崎二路 1RYFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_RYFA1 | 南科二路(3610) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 70 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 3-37-05 |  |  | 3610 | #2RY | 南科龍崎二路 2RYFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_RYFA2 | 南科二路(3610) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 71 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0881 |  | 0379 | 3-37-01 |  | 3-7B | 3610 | 79S | 南科龍崎二路3610 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_79UL | 南科二路(3610) 79RY U/L | LINE345 |  |  |  |  | CDC | 72 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 3-09-02 |  |  | 3630 | #2 RY | 興達龍崎一路 2SSA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_SSA2 | 興達一路(3630) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 73 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0888 |  |  | 3-37-08 |  |  | 3630 | #1RY | 興達龍崎一路 RYA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_RYFA1 | 興達一路(3630) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 74 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 3-37-10 |  |  | 3630 | #2RY | 興達龍崎一路 RYA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_RYFA2 | 興達一路(3630) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 75 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0886 |  | 0380 | 3-37-06 |  | 3-7C | 3630 | 79S | 興達龍崎一路 3630 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_79UL | 興達一路(3630) 79RY U/L | LINE345 |  |  |  |  | CDC | 76 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 3-09-05 |  |  | 3640 | #2 RY | 路北龍崎紅線2SSA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_SSA2 | 路北紅線(3640) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 77 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0893 |  |  | 3-37-13 |  |  | 3640 | #1RY | 路北龍崎紅線 1RYFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_RYFA1 | 路北紅線(3640) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 78 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0895 |  |  | 3-37-15 |  |  | 3640 | #2RY | 路北龍崎紅線 2RYFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_RYFA2 | 路北紅線(3640) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 79 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0891 |  | 0381 | 3-37-11 |  | 3-7D | 3640 | 79S | 路北龍崎紅線3640 79RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_79UL | 路北紅線(3640) 79RY U/L | LINE345 |  |  |  |  | CDC | 80 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | ABS1 | 3511 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 0961 | 0288 | 3-3C-00 | 3-3C-01 | 3-20 | 3511 | DS | 南科龍崎一路 3511 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3511_ABS | 3511(南科一路) ABS | LINE345 |  |  |  |  | CDC | 81 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | ABS2 | 3512 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 0963 | 0289 | 3-3C-02 | 3-3C-03 | 3-21 | 3512 | DS | 南科龍崎一路 3512 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3512_ABS | 3512(南科一路) ABS | LINE345 |  |  |  |  | CDC | 82 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | ABS1 | 3531 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0970 | 0971 | 0293 | 3-3C-10 | 3-3C-11 | 3-25 | 3531 | DS | 龍崎(北)~龍崎(南)臨時線 3531 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3531_ABS | 3531(北南臨時線) ABS | LINE345 |  |  |  |  | CDC | 83 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | ABS2 | 3532 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0974 | 0975 | 0295 | 3-3C-14 | 3-3C-15 | 3-27 | 3532 | DS | 龍崎(北)~龍崎(南)臨時線 3532 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3532_ABS | 3532(北南臨時線) ABS | LINE345 |  |  |  |  | CDC | 84 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | ABS1 | 3541 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 0977 | 0296 | 3-3D-00 | 3-3D-01 | 3-28 | 3541 | DS | 龍崎瀰力二路 3541 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3541_ABS | 3541(瀰力二路) ABS | LINE345 |  |  |  |  | CDC | 85 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | ABS2 | 3542 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 0979 | 0297 | 3-3D-02 | 3-3D-03 | 3-29 | 3542 | DS | 龍崎瀰力二路 3542 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3542_ABS | 3542(瀰力二路) ABS | LINE345 |  |  |  |  | CDC | 86 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | DS1 | 3561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 0987 | 0301 | 3-3D-10 | 3-3D-11 | 3-2D | 3561 | DS | 天輪龍崎海線 3561 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3561_DS | 3561(天輪海線) DS | LINE345 |  |  |  |  | CDC | 87 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | DS2 | 3562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0990 | 0991 | 0303 | 3-3D-14 | 3-3D-15 | 3-2F | 3562 | DS | 天輪龍崎海線 3562 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3562_DS | 3562(天輪海線) DS | LINE345 |  |  |  |  | CDC | 88 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | ABS1 | 3611 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1002 | 1003 | 0309 | 3-3E-10 | 3-3E-11 | 3-35 | 3611 | DS | 南科龍崎二路3611 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3611_ABS | 3611(南科二路) ABS | LINE345 |  |  |  |  | CDC | 89 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | ABS2 | 3612 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 | 0310 | 3-3E-12 | 3-3E-13 | 3-36 | 3612 | DS | 南科龍崎二路3612 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3612_ABS | 3612(南科二路) ABS | LINE345 |  |  |  |  | CDC | 90 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | ABS1 | 3631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1012 | 1013 | 0314 | 3-3F-04 | 3-3F-05 | 3-3A | 3631 | DS | 興達龍崎一路3631 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3631_ABS | 3631(興達一路) ABS | LINE345 |  |  |  |  | CDC | 91 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | ABS2 | 3632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1016 | 1017 | 0316 | 3-3F-08 | 3-3F-09 | 3-3C | 3632 | DS | 興達龍崎一路3632 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3632_ABS | 3632(興達一路) ABS | LINE345 |  |  |  |  | CDC | 92 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | ABS1 | 3641 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1024 | 1025 | 0317 | 4-30-00 | 4-30-01 | 3-3D | 3641 | DS | 路北龍崎紅線3641 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3641_ABS | 3641(路北紅線) ABS | LINE345 |  |  |  |  | CDC | 93 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | ABS2 | 3642 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1026 | 1027 | 0318 | 4-30-02 | 4-30-03 | 3-3E | 3642 | DS | 路北龍崎紅線3642 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3642_ABS | 3642(路北紅線) ABS | LINE345 |  |  |  |  | CDC | 94 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | DS1 | 3591 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0998 | 0999 | 0307 | 3-3E-06 | 3-3E-07 | 3-33 | 3591 | DS | 3591 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3591_DS | 3591(#5ATR) DS | ATR |  |  |  |  | CDC | 95 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | DS2 | 3592 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 | 0308 | 3-3E-08 | 3-3E-09 | 3-34 | 3592 | DS | 3592 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3592_DS | 3592(#5ATR) DS | ATR |  |  |  |  | CDC | 96 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | ABS1 | 3691 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1044 | 1045 | 0326 | 4-31-04 | 4-31-05 | 3-46 | 3691 | DS | 3691 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3691_ABS | 3691(#2ATR) ABS | ATR |  |  |  |  | CDC | 97 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | ABS2 | 3692 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1046 | 1047 | 0327 | 4-31-06 | 4-31-07 | 3-47 | 3692 | DS | 3692 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3692_ABS | 3692(#2ATR) ABS | ATR |  |  |  |  | CDC | 98 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | DS1 | 3911 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1048 | 1049 | 0328 | 4-31-08 | 4-31-09 | 3-48 | 3911 | DS | 3911 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3911_DS | 3911(#7ATR) DS | ATR |  |  |  |  | CDC | 99 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | DS2 | 3912 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1050 | 1051 | 0329 | 4-31-10 | 4-31-11 | 3-49 | 3912 | DS | 3912 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3912_DS | 3912(#7ATR) DS | ATR |  |  |  |  | CDC | 100 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | L/E01E021/T2 |  |  | 0256 |  | 0257 | 3-00-00 |  | 3-01 | 3510 | CB | 南科龍崎一路 3510 CB AS |  | aaba | B2/E03_C | [8 empty] | 龍崎ES.3510_CB | 3510(南科一路) CB | LINE345 |  |  |  |  | CDC | 101 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | E2 | 3512E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0964 | 0965 | 0290 | 3-3C-04 | 3-3C-05 | 3-22 | 3512E | DS | 南科龍崎一路 3512E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3512E_ES | 3512E(南科一路) ES | LINE345 |  |  |  |  | CDC | 102 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3510LE | 3510LE (非取樣點) | LINE345 | [5 empty] | 103 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3510BE | 3510BE (非取樣點) | LINE345 | [5 empty] | 104 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | L/E02E02/T1 | B/2Bus |  |  | 0258 |  | 0259 | 3-00-02 |  | 3-03 | 3530 | CB | 龍崎(北)~龍崎(南)臨時線 3530 CB |  | aabc | B2/E03_C | [8 empty] | 龍崎ES.3530_CB | 3530(北南臨時線) CB | LINE345 |  |  |  |  | CDC | 105 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | E1 | 3531E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0972 | 0973 | 0294 | 3-3C-12 | 3-3C-13 | 3-26 | 3531E | DS | 龍崎(北)~龍崎(南)臨時線 3531E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3531E_ES | 3531E(北南臨時線) ES | LINE345 |  |  |  |  | CDC | 106 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3530LE | 3530LE (非取樣點) | LINE345 | [5 empty] | 107 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3530BE | 3530BE (非取樣點) | LINE345 | [5 empty] | 108 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | L/E02E082/T1 |  |  | 0259 |  | 0260 | 3-00-03 |  | 3-04 | 3540 | CB | 龍崎瀰力二路 3540 CB |  | aada | B2/E03_C | [8 empty] | 龍崎ES.3540_CB | 3540(瀰力二路) CB | LINE345 |  |  |  |  | CDC | 109 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | E2 | 3542E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0980 | 0981 | 0298 | 3-3D-04 | 3-3D-05 | 3-2A | 3542E | DS | 龍崎瀰力二路 3542E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3542E_ES | 3542E(瀰力二路) ES | LINE345 |  |  |  |  | CDC | 110 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3540LE | 3540LE (非取樣點) | LINE345 | [5 empty] | 111 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3540BE | 3540BE (非取樣點) | LINE345 | [5 empty] | 112 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaE | L/T12E02O/T2 | B/2Bus |  |  | 0261 |  | 0262 | 3-00-05 |  | 3-06 | 3560 | CB | 天輪龍崎海線 3560 CB AS |  | aadc | B2/E03_C | [8 empty] | 龍崎ES.3560_CB | 3560(天輪海線) CB | LINE345 |  |  |  |  | CDC | 113 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | E1 | 3561E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0988 | 0989 | 0302 | 3-3D-12 | 3-3D-13 | 3-2E | 3561E | DS | 天輪龍崎海線 3561E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3561E_ES | 3561E(天輪海線) ES | LINE345 |  |  |  |  | CDC | 114 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3560LE | 3560LE (非取樣點) | LINE345 | [5 empty] | 115 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3560BE | 3560BE (非取樣點) | LINE345 | [5 empty] | 116 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | L/E01E022/T2 |  |  | 0270 |  | 0267 | 3-01-06 |  | 3-0B | 3610 | CB | 南科龍崎二路 3610 CB AS |  | aaca | B2/E03_C | [8 empty] | 龍崎ES.3610_CB | 3610(南科二路) CB | LINE345 |  |  |  |  | CDC | 117 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | E2 | 3612E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1006 | 1007 | 0311 | 3-3E-14 | 3-3E-15 | 3-37 | 3612E | DS | 南科龍崎二路3612E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3612E_ES | 3612E(南科二路) ES | LINE345 |  |  |  |  | CDC | 118 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3610LE | 3610LE (非取樣點) | LINE345 | [5 empty] | 119 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3610BE | 3610BE (非取樣點) | LINE345 | [5 empty] | 120 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | L/T13E021/T2 | B/2Bus |  |  | 0272 |  | 0269 | 3-02-00 |  | 3-0D | 3630 | CB | 興達龍崎一路 3630 CB AS |  | aacc | B2/E03_C | [8 empty] | 龍崎ES.3630_CB | 3630(興達一路) CB | LINE345 |  |  |  |  | CDC | 121 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | E1 | 3631E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1014 | 1015 | 0315 | 3-3F-06 | 3-3F-07 | 3-3B | 3631E | DS | 興達龍崎一路3631E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3631E_ES | 3631E(興達一路) ES | LINE345 |  |  |  |  | CDC | 122 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3630LE | 3630LE (非取樣點) | LINE345 | [5 empty] | 123 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3630BE | 3630BE (非取樣點) | LINE345 | [5 empty] | 124 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | L/E06E02R/T2 |  |  | 0273 |  | 0270 | 3-02-01 |  | 3-0E | 3640 | CB | 路北龍崎紅線 3640 CB AS |  | aaea | B2/E03_C | [8 empty] | 龍崎ES.3640_CB | 3640(路北紅線) CB | LINE345 |  |  |  |  | CDC | 125 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | E2 | 3642E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1028 | 1029 | 0319 | 4-30-04 | 4-30-05 | 3-3F | 3642E | DS | 路北龍崎紅線3642E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3642E_ES | 3642E(路北紅線) ES | LINE345 |  |  |  |  | CDC | 126 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3640LE | 3640LE (非取樣點) | LINE345 | [5 empty] | 127 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3640BE | 3640BE (非取樣點) | LINE345 | [5 empty] | 128 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | T/5ATR345 | B/2Bus |  |  | 0263 |  | 0264 | 3-00-07 |  | 3-08 | 3590 | CB | 3590 CB AS |  | aafc | B2/E03_C | [8 empty] | 龍崎ES.3590_CB | 3590(#5ATR) CB | LINE345 |  |  |  |  | CDC | 129 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3590TE | 3590TE (非取樣點) | LINE345 | [5 empty] | 130 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3590BE | 3590BE (非取樣點) | LINE345 | [5 empty] | 131 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaA | T/2ATR345 | B/2Bus |  |  | 0283 |  | 0276 | 3-03-03 |  | 3-14 | 3690 | CB | 3690 CB AS |  | aagc | B2/E03_C | [8 empty] | 龍崎ES.3690_CB | 3690(#2ATR) CB | LINE345 |  |  |  |  | CDC | 132 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | E1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3690LE | 3690LE (非取樣點) | LINE345 | [5 empty] | 133 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | E2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3690BE | 3690BE (非取樣點) | LINE345 | [5 empty] | 134 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaE | B/1Bus | T/7ATR345 |  |  | 0290 |  | 0280 | 3-04-02 |  | 3-18 | 3910 | CB | 3910 CB AS |  | aaaa | B2/E03_C | [8 empty] | 龍崎ES.3910_CB | 3910(#7ATR) CB | LINE345 |  |  |  |  | CDC | 135 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | E2 | 3912E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1052 | 1053 | 0330 | 4-31-12 | 4-31-13 | 3-4A | 3912E | DS | 3912E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3912E_ES | 3912E(#7ATR) ES | ATR |  |  |  |  | CDC | 136 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3910TE | 3910TE (非取樣點) | LINE345 | [5 empty] | 137 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3910BE | 3910BE (非取樣點) | LINE345 | [5 empty] | 138 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3520 | TIE(3520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3510 | A/3530 |  |  | 0257 |  | 0258 | 3-00-01 |  | 3-02 | 3520 | CB | 3520 CB AS |  | aabb | B2/E03_C | [8 empty] | 龍崎ES.3520_CB | 3520 CB | LINE345 |  |  |  |  | CDC | 139 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3520 | TIE(3520) |  | E1 | 3521E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3521E | 3521E (非取樣點) | LINE345 | [5 empty] | 140 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3520 | TIE(3520) |  | E2 | 3522E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3522E | 3522E (非取樣點) | LINE345 | [5 empty] | 141 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3550 | TIE(3550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3540 | A/3560 |  |  | 0260 |  | 0261 | 3-00-04 |  | 3-05 | 3550 | CB | 3550 CB AS |  | aadb | B2/E03_C | [8 empty] | 龍崎ES.3550_CB | 3550 CB | LINE345 |  |  |  |  | CDC | 142 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3550 | TIE(3550) |  | E1 | 3551E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3551E | 3551E (非取樣點) | LINE345 | [5 empty] | 143 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3550 | TIE(3550) |  | E2 | 3552E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3552E | 3552E (非取樣點) | LINE345 | [5 empty] | 144 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3620 | TIE(3620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3610 | A/3630 |  |  | 0271 |  | 0268 | 3-01-07 |  | 3-0C | 3620 | CB | 3620 CB AS |  | aacb | B2/E03_C | [8 empty] | 龍崎ES.3620_CB | 3620 CB | LINE345 |  |  |  |  | CDC | 145 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3620 | TIE(3620) |  | E1 | 3621E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3621E | 3621E (非取樣點) | LINE345 | [5 empty] | 146 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3620 | TIE(3620) |  | E2 | 3622E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3622E | 3622E (非取樣點) | LINE345 | [5 empty] | 147 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3650 | TIE(3650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3640 | A/3660 |  |  | 0274 |  | 0271 | 3-02-02 |  | 3-0F | 3650 | CB | 3650 CB AS |  | aaeb | B2/E03_C | [8 empty] | 龍崎ES.3650_CB | 3650 CB | LINE345 |  |  |  |  | CDC | 148 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3650 | TIE(3650) |  | E1 | 3651E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3651E | 3651E (非取樣點) | LINE345 | [5 empty] | 149 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3650 | TIE(3650) |  | E2 | 3652E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3652E | 3652E (非取樣點) | LINE345 | [5 empty] | 150 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3920 | TIE(3920) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3910 | A/3930 |  |  | 0297 |  | 0283 | 3-05-01 |  | 3-1B | 3920 | CB | 3920 CB AS |  | aaab | B2/E03_C | [8 empty] | 龍崎ES.3920_CB | 3920 CB | LINE345 |  |  |  |  | CDC | 151 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3920 | TIE(3920) |  | E2 | 3922E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3922E | 3922E (非取樣點) | LINE345 | [5 empty] | 152 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3520 | TIE(3520) |  | ABS1 | 3521 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0966 | 0967 | 0291 | 3-3C-06 | 3-3C-07 | 3-23 | 3521 | DS | 3521 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3521_ABS | 3521 ABS | LINE345 |  |  |  |  | CDC | 153 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3520 | TIE(3520) |  | ABS2 | 3522 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0968 | 0969 | 0292 | 3-3C-08 | 3-3C-09 | 3-24 | 3522 | DS | 3522 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3522_ABS | 3522 ABS | LINE345 |  |  |  |  | CDC | 154 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3550 | TIE(3550) |  | ABS1 | 3551 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 0983 | 0299 | 3-3D-06 | 3-3D-07 | 3-2B | 3551 | DS | 3551 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3551_ABS | 3551 ABS | LINE345 |  |  |  |  | CDC | 155 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3550 | TIE(3550) |  | ABS2 | 3552 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 0985 | 0300 | 3-3D-08 | 3-3D-09 | 3-2C | 3552 | DS | 3552 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3552_ABS | 3552 ABS | LINE345 |  |  |  |  | CDC | 156 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3620 | TIE(3620) |  | ABS1 | 3621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1008 | 1009 | 0312 | 3-3F-00 | 3-3F-01 | 3-38 | 3621 | DS | 3621 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3621_ABS | 3621 ABS | LINE345 |  |  |  |  | CDC | 157 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3620 | TIE(3620) |  | ABS2 | 3622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1010 | 1011 | 0313 | 3-3F-02 | 3-3F-03 | 3-39 | 3622 | DS | 3622 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3622_ABS | 3622 ABS | LINE345 |  |  |  |  | CDC | 158 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3650 | TIE(3650) |  | ABS1 | 3651 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1030 | 1031 | 0320 | 4-30-06 | 4-30-07 | 3-40 | 3651 | DS | 3651 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3651_ABS | 3651 ABS | LINE345 |  |  |  |  | CDC | 159 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3650 | TIE(3650) |  | ABS2 | 3652 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1032 | 1033 | 0321 | 4-30-08 | 4-30-09 | 3-41 | 3652 | DS | 3652 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3652_ABS | 3652 ABS | LINE345 |  |  |  |  | CDC | 160 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3920 | TIE(3920) |  | DS1 | 3921 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1054 | 1055 | 0331 | 4-31-14 | 4-31-15 | 3-4B | 3921 | DS | 3921 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3921_DS | 3921 DS | LINE345 |  |  |  |  | CDC | 161 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3920 | TIE(3920) |  | DS2 | 3922 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1056 | 1057 | 0332 | 4-32-00 | 4-32-01 | 3-4C | 3922 | DS | 3922 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3922_DS | 3922 DS | LINE345 |  |  |  |  | CDC | 162 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1510 | MW | 龍崎山上一路 瓦 | MW_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1510_MW | 龍崎山上一路 MW | LINE161 |  |  |  |  | CDC | 163 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1510 | MVAR | 龍崎山上一路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1510_MVAR | 龍崎山上一路 MVAR | LINE161 |  |  |  |  | CDC | 164 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1510 | KV | 龍崎山上一路 LPD | kV_-210_210(-2000_2000) |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510LPD_KV | 龍崎山上一路(1510) LPD KV | LINE161 |  |  |  |  | CDC | 165 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1520 | MW | 龍崎山上二路 瓦 | MW_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1520_MW | 龍崎山上二路 MW | LINE161 |  |  |  |  | CDC | 166 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1520 | MVAR | 龍崎山上二路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1520_MVAR | 龍崎山上二路 MVAR | LINE161 |  |  |  |  | CDC | 167 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1520 | KV | 龍崎山上二路 LPD | kV_-210_210(-2000_2000) |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520LPD_KV | 龍崎山上二路(1520) LPD KV | LINE161 |  |  |  |  | CDC | 168 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1530 | MW | 龍崎山上二甲三路 瓦 | MW_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1530_MW | 山上二甲三路 MW | LINE161 |  |  |  |  | CDC | 169 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1530 | MVAR | 龍崎山上二甲三路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1530_MVAR | 山上二甲三路 MVAR | LINE161 |  |  |  |  | CDC | 170 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1530 | KV | 龍崎山上二甲三路 LPD | kV_-210_210(-2000_2000) |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530LPD_KV | 山上二甲三路(1530) LPD KV | LINE161 |  |  |  |  | CDC | 171 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1540 | MW | 龍崎山上二甲四路 瓦 | MW_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1540_MW | 山上二甲四路 MW | LINE161 |  |  |  |  | CDC | 172 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1540 | MVAR | 龍崎山上二甲四路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1540_MVAR | 山上二甲四路 MVAR | LINE161 |  |  |  |  | CDC | 173 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1540 | KV | 龍崎山上二甲四路 LPD | kV_-210_210(-2000_2000) |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540LPD_KV | 山上二甲四路(1540) LPD KV | LINE161 |  |  |  |  | CDC | 174 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1550,1560 | MW | 龍崎台南山線 瓦 | MW_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1550_MW | 龍崎台南山線 MW | LINE161 |  |  |  |  | CDC | 175 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | " | MVAR | 龍崎台南山線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1550_MVAR | 龍崎台南山線 MVAR | LINE161 |  |  |  |  | CDC | 176 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | " | KV | 龍崎台南山線 LPD | kV_-210_210(-2000_2000) |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550LPD_KV | 龍崎台南山線(1550) LPD KV | LINE161 |  |  |  |  | CDC | 177 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 1570,1580 | MW | 龍崎台南海線 瓦 | MW_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1570_MW | 龍崎台南海線 MW | LINE161 |  |  |  |  | CDC | 178 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | " | MVAR | 龍崎台南海線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1570_MVAR | 龍崎台南海線 MVAR | LINE161 |  |  |  |  | CDC | 179 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | " | KV | 龍崎台南海線 LPD | kV_-210_210(-2000_2000) |  | B2/E03_A1 | [8 empty] | 龍崎ES.1570LPD_KV | 龍崎台南海線(1570) LPD KV | LINE161 |  |  |  |  | CDC | 180 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1510 | PHA | 龍崎山上一路 1510 PHA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_PHA | 龍崎山上一路(1510) 相間RY | LINE161 |  |  |  |  | CDC | 181 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1510 | GDA | 龍崎山上一路 1510 GDA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_GDA | 龍崎山上一路(1510) 接地RY | LINE161 |  |  |  |  | CDC | 182 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1510 | 87A | 龍崎山上一路 1510 87A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_87A | 龍崎山上一路(1510) 87RY | LINE161 |  |  |  |  | CDC | 183 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 1520 | PHA | 龍崎山上二路 1520 PHA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_PHA | 龍崎山上二路(1520) 相間RY | LINE161 |  |  |  |  | CDC | 184 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1520 | GDA | 龍崎山上二路 1520 GDA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_GDA | 龍崎山上二路(1520) 接地RY | LINE161 |  |  |  |  | CDC | 185 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1520 | 87A | 龍崎山上二路 1520 87A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_87A | 龍崎山上二路(1520) 87RY | LINE161 |  |  |  |  | CDC | 186 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1530 | PHA | 龍崎山上二甲三路 1530 PHA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_PHA | 山上二甲三路(1530) 相間RY | LINE161 |  |  |  |  | CDC | 187 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 1530 | GDA | 龍崎山上二甲三路 1530 GDA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_GDA | 山上二甲三路(1530) 接地RY | LINE161 |  |  |  |  | CDC | 188 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | 1530 | 87A | 龍崎山上二甲三路 1530 87A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_87A | 山上二甲三路(1530) 85RY | LINE161 |  |  |  |  | CDC | 189 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 1540 | PHA | 龍崎山上二甲四路 1540 PHA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_PHA | 山上二甲四路(1540) 相間RY | LINE161 |  |  |  |  | CDC | 190 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1540 | GDA | 龍崎山上二甲四路 1540 GDA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_GDA | 山上二甲四路(1540) 接地RY | LINE161 |  |  |  |  | CDC | 191 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 1540 | 87A | 龍崎山上二甲四路 1540 87A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_87A | 龍崎山上四路(1540) 87RY | LINE161 |  |  |  |  | CDC | 192 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 1550,1560 | PHA | 龍崎台南山線1550,1560 PHA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_PHA | 龍崎台南山線(1550) 相間RY | LINE161 |  |  |  |  | CDC | 193 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 1550,1560 | GDA | 龍崎台南山線1550,1560 GDA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_GDA | 龍崎台南山線(1550) 接地RY | LINE161 |  |  |  |  | CDC | 194 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 1550,1560 | 87A | 龍崎台南山線1550,1560 87A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_87A | 龍崎台南山線(1550) 87RY | LINE161 |  |  |  |  | CDC | 195 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 1570,1580 | PHA | 龍崎台南海線1570,1580 PHA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_PHA | 龍崎台南海線(1580) 相間RY | LINE161 |  |  |  |  | CDC | 196 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 1570,1580 | GDA | 龍崎台南海線1570,1580 GDA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_GDA | 龍崎台南海線(1580) 接地RY | LINE161 |  |  |  |  | CDC | 197 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 1570,1580 | 87A | 龍崎台南海線1570,1580 87A |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_87A | 龍崎台南海線(1580) 87RY | LINE161 |  |  |  |  | CDC | 198 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0523 |  | 0049 | 1-30-11 |  | 1-31 | 1510 | 87S | 龍崎山上一路 1510 87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_87UL | 龍崎山上一路(1510) 87RY U/L | LINE161 |  |  |  |  | CDC | 199 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0527 |  | 0051 | 1-30-15 |  | 1-33 | 1520 | 87S | 龍崎山上二路 1520 87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_87UL | 龍崎山上二路(1520) 87RY U/L | LINE161 |  |  |  |  | CDC | 200 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  | 0053 | 1-31-03 |  | 1-35 | 1530 | 87S | 龍崎山上二甲三路1530 87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_87UL | 山上二甲三路(1530) 87RY U/L | LINE161 |  |  |  |  | CDC | 201 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  | 0055 | 1-31-07 |  | 1-37 | 1540 | 87S | 龍崎山上二甲四路 1540 87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_87UL | 山上二甲四路(1540) 87RY U/L | LINE161 |  |  |  |  | CDC | 202 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0057 | 1-31-11 |  | 1-39 | 1550,1560 | 87S | 龍崎台南山線87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_87UL | 龍崎台南山線(1550) 87RY U/L | LINE161 |  |  |  |  | CDC | 203 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0543 |  | 0059 | 1-31-15 |  | 1-3B | 1570,1580 | 87S | 龍崎台南海線87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_87UL | 龍崎台南海線(1580) 87RY U/L | LINE161 |  |  |  |  | CDC | 204 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E02P061/T1 |  | 0006 |  | 0001 | 1-00-06 |  | 1-01 | 1510 | CB | 龍崎山上一路 1510 CB AS |  | aacb | B2/E03_A1 | [8 empty] | 龍崎ES.1510_CB | 1510(龍崎山上一路) CB | LINE161 |  |  |  |  | CDC | 205 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0522 |  | 0048 | 1-30-10 |  | 1-30 | 1510 | 79S | 龍崎山上一路 1510 79RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_79UL | 龍崎山上一路(1510) 79RY U/L | LINE161 |  |  |  |  | CDC | 206 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E02P062/T1 |  | 0010 |  | 0002 | 1-01-02 |  | 1-02 | 1520 | CB | 龍崎山上二路 1520 CB AS |  | aadb | B2/E03_A1 | [8 empty] | 龍崎ES.1520_CB | 1520(龍崎山上二路) CB | LINE161 |  |  |  |  | CDC | 207 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0050 | 1-30-14 |  | 1-32 | 1520 | 79S | 龍崎山上二路 1520 79RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_79UL | 龍崎山上二路(1520) 79RY U/L | LINE161 |  |  |  |  | CDC | 208 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E02TN113/T2 |  | 0014 |  | 0003 | 1-01-06 |  | 1-03 | 1530 | CB | 龍崎山上二甲三路 1530 CB AS |  | aafb | B2/E03_A1 | [8 empty] | 龍崎ES.1530_CB | 1530(山上二甲三路) CB | LINE161 |  |  |  |  | CDC | 209 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0052 | 1-31-02 |  | 1-34 | 1530 | 79S | 龍崎山上二甲三路1530 79RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_79UL | 山上二甲三路(1530) 79RY U/L | LINE161 |  |  |  |  | CDC | 210 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | L/E02TN124/T2 |  | 0018 |  | 0004 | 1-02-02 |  | 1-04 | 1540 | CB | 龍崎山上二甲四路 1540 CB AS |  | aagb | B2/E03_A1 | [8 empty] | 龍崎ES.1540_CB | 1540(山上二甲四路) CB | LINE161 |  |  |  |  | CDC | 211 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0054 | 1-31-06 |  | 1-36 | 1540 | 79S | 龍崎山上二甲四路 1540 79RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_79UL | 山上二甲四路(1540) 79RY U/L | LINE161 |  |  |  |  | CDC | 212 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | L/E02P07M/T1 |  |  | 0022 |  | 0006 | 1-02-06 |  | 1-06 | 1550 | CB | 龍崎台南山線1550 CB AS |  | aalb | B2/E03_A1 | [8 empty] | 龍崎ES.1550_CB | 1550(龍崎台南山線) CB | LINE161 |  |  |  |  | CDC | 213 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0056 | 1-31-10 |  | 1-38 | 1550 | 79S | 龍崎台南山線1550 79RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_79UL | 龍崎台南山線(1550) 79RY U/L | LINE161 |  |  |  |  | CDC | 214 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎～台南山線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | L/E02P07M/T1 | B/2Bus |  |  | 0041 |  | 0009 | 1-05-01 |  | 1-09 | 1560 | CB | 1560 CB AS |  | aamb | B2/E03_A1 | [8 empty] | 龍崎ES.1560_CB | 1560(龍崎台南山線) CB | LINE161 |  |  |  |  | CDC | 215 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | L/E02P07O/T1 |  |  | 0042 |  | 0010 | 1-05-02 |  | 1-0A | 1570 | CB | 1570 CB AS |  | aanb | B2/E03_A1 | [8 empty] | 龍崎ES.1570_CB | 1570(龍崎台南海線) CB | LINE161 |  |  |  |  | CDC | 216 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | L/E02P07O/T1 | B/2Bus |  |  | 0026 |  | 0007 | 1-03-02 |  | 1-07 | 1580 | CB | 龍崎台南海線1580 CB AS |  | aaob | B2/E03_A1 | [8 empty] | 龍崎ES.1580_CB | 1580(龍崎台南海線) CB | LINE161 |  |  |  |  | CDC | 217 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0542 |  | 0058 | 1-31-14 |  | 1-3A | 1580 | 79S | 龍崎台南海線1580 79RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_79UL | 龍崎台南海線(1580) 79RY U/L | LINE161 |  |  |  |  | CDC | 218 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | ABS1 | 1511 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0632 | 0633 | 0016 | 1-37-08 | 1-37-09 | 1-10 | 1511 | DS | 龍崎山上一路1511 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1511_ABS | 1511(龍崎山上一路) ABS | LINE161 |  |  |  |  | CDC | 219 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | ABS2 | 1512 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0634 | 0635 | 0017 | 1-37-10 | 1-37-11 | 1-11 | 1512 | DS | 龍崎山上一路1512 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1512_ABS | 1512(龍崎山上一路) ABS | LINE161 |  |  |  |  | CDC | 220 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | ABS1 | 1521 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 0641 | 0020 | 1-38-00 | 1-38-01 | 1-14 | 1521 | DS | 龍崎山上二路1521 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1521_ABS | 1521(龍崎山上二路) ABS | LINE161 |  |  |  |  | CDC | 221 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | ABS2 | 1522 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 0643 | 0021 | 1-38-02 | 1-38-03 | 1-15 | 1522 | DS | 龍崎山上二路1522 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1522_ABS | 1522(龍崎山上二路) ABS | LINE161 |  |  |  |  | CDC | 222 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | ABS1 | 1531 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 0649 | 0024 | 1-38-08 | 1-38-09 | 1-18 | 1531 | DS | 龍崎山上二甲三路1531 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1531_ABS | 1531(山上二甲三路) ABS | LINE161 |  |  |  |  | CDC | 223 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | ABS2 | 1532 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 0651 | 0025 | 1-38-10 | 1-38-11 | 1-19 | 1532 | DS | 龍崎山上二甲三路1532 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1532_ABS | 1532(山上二甲三路) ABS | LINE161 |  |  |  |  | CDC | 224 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | ABS1 | 1541 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 0657 | 0028 | 1-39-00 | 1-39-01 | 1-1C | 1541 | DS | 龍崎山上二甲四路1541 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1541_ABS | 1541(山上二甲四路) ABS | LINE161 |  |  |  |  | CDC | 225 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | ABS2 | 1542 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0658 | 0659 | 0029 | 1-39-02 | 1-39-03 | 1-1D | 1542 | DS | 龍崎山上二甲四路1542 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1542_ABS | 1542(山上二甲四路) ABS | LINE161 |  |  |  |  | CDC | 226 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | ABS1 | 1551 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 0669 | 0034 | 1-39-12 | 1-39-13 | 1-22 | 1551 | DS | 龍崎台南山線1551 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1551_ABS | 1551(龍崎台南山線) ABS | LINE161 |  |  |  |  | CDC | 227 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | ABS2 | 1552 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0670 | 0671 | 0035 | 1-39-14 | 1-39-15 | 1-23 | 1552 | DS | 龍崎台南山線1552 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1552_ABS | 1552(龍崎台南山線) ABS | LINE161 |  |  |  |  | CDC | 228 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎～台南山線(1560) |  | DS1 | 1561 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 0697 | 0044 | 1-3B-08 | 1-3B-09 | 1-2C | 1561 | DS | 龍崎台南山線1561 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1561_ABS | 1561(龍崎台南山線) ABS | LINE161 |  |  |  |  | CDC | 229 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎～台南山線(1560) |  | DS2 | 1562 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0698 | 0699 | 0045 | 1-3B-10 | 1-3B-11 | 1-2D | 1562 | DS | 龍崎台南山線1562 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1562_ABS | 1562(龍崎台南山線) ABS | LINE161 |  |  |  |  | CDC | 230 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | DS1 | 1571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0702 | 0703 | 0046 | 1-3B-14 | 1-3B-15 | 1-2E | 1571 | DS | 龍崎台南海線1571 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1571_DS | 1571(龍崎台南海線) DS | LINE161 |  |  |  |  | CDC | 231 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | DS2 | 1572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 0705 | 0047 | 1-3C-00 | 1-3C-01 | 1-2F | 1572 | DS | 龍崎台南海線1572 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1572_DS | 1572(龍崎台南海線) DS | LINE161 |  |  |  |  | CDC | 232 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | DS1 | 1581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 0677 | 0038 | 1-3A-04 | 1-3A-05 | 1-26 | 1581 | DS | 龍崎台南海線1581 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1581_DS | 1581(龍崎台南海線) DS | LINE161 |  |  |  |  | CDC | 233 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | DS2 | 1582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 0679 | 0039 | 1-3A-06 | 1-3A-07 | 1-27 | 1582 | DS | 龍崎台南海線1582 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1582_DS | 1582(龍崎台南海線) DS | LINE161 |  |  |  |  | CDC | 234 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | ABS3 | 1513 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | 0637 | 0018 | 1-37-12 | 1-37-13 | 1-12 | 1513 | DS | 龍崎山上一路1513 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1513_ABS | 1513(龍崎山上一路) ABS | LINE161 |  |  |  |  | CDC | 235 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | E3 | 1513E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0638 | 0639 | 0019 | 1-37-14 | 1-37-15 | 1-13 | 1513E | DS | 龍崎山上一路1513E DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1513E_ES | 1513E(龍崎山上一路) ES | LINE161 |  |  |  |  | CDC | 236 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 238 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | ABS3 | 1523 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 0645 | 0022 | 1-38-04 | 1-38-05 | 1-16 | 1523 | DS | 龍崎山上二路1523 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1523_ABS | 1523(龍崎山上二路) ABS | LINE161 |  |  |  |  | CDC | 239 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | E3 | 1523E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0646 | 0647 | 0023 | 1-38-06 | 1-38-07 | 1-17 | 1523E | DS | 龍崎山上二路1523E DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1523E_ES | 1523E(龍崎山上二路) ES | LINE161 |  |  |  |  | CDC | 240 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 241 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 242 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | ABS3 | 1533 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 0653 | 0026 | 1-38-12 | 1-38-13 | 1-1A | 1533 | DS | 龍崎山上二甲三路1533 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1533_ABS | 1533(山上二甲三路) ABS | LINE161 |  |  |  |  | CDC | 243 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | E3 | 1533E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0654 | 0655 | 0027 | 1-38-14 | 1-38-15 | 1-1B | 1533E | DS | 龍崎山上二甲三路1533E DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1533E_ES | 1533E(山上二甲三路) ES | LINE161 |  |  |  |  | CDC | 244 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 245 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 246 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | ABS3 | 1543 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0660 | 0661 | 0030 | 1-39-04 | 1-39-05 | 1-1E | 1543 | DS | 龍崎山上二甲四路1543 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1543_ABS | 1543(山上二甲四路) ABS | LINE161 |  |  |  |  | CDC | 247 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | E3 | 1543E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0662 | 0663 | 0031 | 1-39-06 | 1-39-07 | 1-1F | 1543E | DS | 龍崎山上二甲四路1543E DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1543E_ES | 1543E(山上二甲四路) ES | LINE161 |  |  |  |  | CDC | 248 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 249 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 250 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | E2 | 1552E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0700 | 0701 | 0037 | 1-3B-12 | 1-3B-13 | 1-25 | 1552E | ES | 龍崎台南山線1552E DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1552E_ES | 1552E(龍崎台南山線) ES | LINE161 |  |  |  |  | CDC | 251 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 252 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 253 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎～台南山線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 254 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎～台南山線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 255 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | E2 | 1572E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0694 | 0695 | 0041 | 1-3B-06 | 1-3B-07 | 1-29 | 1572E | ES | 龍崎台南海線1572E DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1572E_ES | 1572E(龍崎台南海線) ES | LINE161 |  |  |  |  | CDC | 256 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 257 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 258 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 259 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 260 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1700 | A | 1700 R相電流 | A_-2000_2000(-2000_2000) |  | B2/E03_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1700TIE_AMP | 1700TIE AMP | TIE |  |  |  |  | CDC | 261 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1Bus | B/3Bus |  |  | 0032 |  | 0008 | 1-04-00 |  | 1-08 | 1700 | CB | 1700 CB AS |  | no rule | B2/E03_A1 | [8 empty] | 龍崎ES.1700_CB | 1700(TIE) CB | TIE |  |  |  |  | CDC | 262 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 0685 | 0042 | 1-3A-12 | 1-3A-13 | 1-2A | 1701 | DS | 1701 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1701_DS | 1701(TIE) DS | TIE |  |  |  |  | CDC | 263 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | DS2 | 1703 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0686 | 0687 | 0043 | 1-3A-14 | 1-3A-15 | 1-2B | 1703 | DS | 1703 DS AS |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1703_DS | 1703(TIE) DS | TIE |  |  |  |  | CDC | 264 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | E1 | 1701E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1701E | 1701E (非取樣點) | TIE | [5 empty] | 265 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | E2 | 1703E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1703E | 1703E (非取樣點) | TIE | [5 empty] | 266 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | #1 ATR | MW | #1ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#1ATR_MW | #1ATR二次側 MW | ATR |  |  |  |  | CDC | 267 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1 ATR | MVAR | #1ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#1ATR_MVAR | #1ATR二次側 MVAR | ATR |  |  |  |  | CDC | 268 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2 ATR | MW | #2ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#2ATR_MW | #2ATR二次側 MW | ATR |  |  |  |  | CDC | 269 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #2 ATR | MVAR | #2ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#2ATR_MVAR | #2ATR二次側 MVAR | ATR |  |  |  |  | CDC | 270 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #5 ATR | MW | #5ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#5ATR_MW | #5ATR二次側 MW | ATR |  |  |  |  | CDC | 271 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #5 ATR | MVAR | #5ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#5ATR_MVAR | #5ATR二次側 MVAR | ATR |  |  |  |  | CDC | 272 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #7 ATR | MW | #7ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#7ATR_MW | #7ATR二次側 MW | ATR |  |  |  |  | CDC | 273 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #7 ATR | MVAR | #7ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E03_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#7ATR_MVAR | #7ATR二次側 MVAR | ATR |  |  |  |  | CDC | 274 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0283 |  | 0358 | 3-9B |  | 3-66 | #1 ATR | TAP | #1ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_TAP | #1ATR OLTC TAP | ATR |  |  |  |  | CDC | 275 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | #1 ATR(R) | ℃ | #1ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_OIL_R | #1ATR R相油溫 | ATR |  |  |  |  | CDC | 276 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | #1 ATR(R) | ℃ | #1ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_COIL_R | #1ATR R相線溫 | ATR |  |  |  |  | CDC | 277 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0287 |  |  | 3-9F |  |  | #1 ATR(S) | ℃ | #1ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_OIL_S | #1ATR S相油溫 | ATR |  |  |  |  | CDC | 278 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | #1 ATR(S) | ℃ | #1ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_COIL_S | #1ATR S相線溫 | ATR |  |  |  |  | CDC | 279 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0289 |  |  | 3-A1 |  |  | #1 ATR(T) | ℃ | #1ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_OIL_T | #1ATR T相油溫 | ATR |  |  |  |  | CDC | 280 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0288 |  |  | 3-A0 |  |  | #1 ATR(T) | ℃ | #1ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_COIL_T | #1ATR T相線溫 | ATR |  |  |  |  | CDC | 281 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0292 |  | 0362 | 3-A4 |  | 3-6A | #2 ATR | TAP | #2ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_TAP | #2ATR OLTC TAP | ATR |  |  |  |  | CDC | 282 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0294 |  |  | 3-A6 |  |  | #2 ATR(R) | ℃ | #2ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_OIL_R | #2ATR R相油溫 | ATR |  |  |  |  | CDC | 283 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0293 |  |  | 3-A5 |  |  | #2 ATR(R) | ℃ | #2ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_COIL_R | #2ATR R相線溫 | ATR |  |  |  |  | CDC | 284 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0296 |  |  | 3-A8 |  |  | #2 ATR(S) | ℃ | #2ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_OIL_S | #2ATR S相油溫 | ATR |  |  |  |  | CDC | 285 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0295 |  |  | 3-A7 |  |  | #2 ATR(S) | ℃ | #2ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_COIL_S | #2ATR S相線溫 | ATR |  |  |  |  | CDC | 286 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0298 |  |  | 3-AA |  |  | #2 ATR(T) | ℃ | #2ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_OIL_T | #2ATR T相油溫 | ATR |  |  |  |  | CDC | 287 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0297 |  |  | 3-A9 |  |  | #2 ATR(T) | ℃ | #2ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_COIL_T | #2ATR T相線溫 | ATR |  |  |  |  | CDC | 288 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0301 |  | 0366 | 3-AD |  | 3-6E | #5 ATR | TAP | #5ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_TAP | #5ATR OLTC TAP | ATR |  |  |  |  | CDC | 289 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0303 |  |  | 3-AF |  |  | #5 ATR(R) | ℃ | #5ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_OIL_R | #5ATR R相油溫 | ATR |  |  |  |  | CDC | 290 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0302 |  |  | 3-AE |  |  | #5 ATR(R) | ℃ | #5ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_COIL_R | #5ATR R相線溫 | ATR |  |  |  |  | CDC | 291 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0305 |  |  | 3-B1 |  |  | #5 ATR(S) | ℃ | #5ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_OIL_S | #5ATR S相油溫 | ATR |  |  |  |  | CDC | 292 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0304 |  |  | 3-B0 |  |  | #5 ATR(S) | ℃ | #5ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_COIL_S | #5ATR S相線溫 | ATR |  |  |  |  | CDC | 293 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0307 |  |  | 3-B3 |  |  | #5 ATR(T) | ℃ | #5ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_OIL_T | #5ATR T相油溫 | ATR |  |  |  |  | CDC | 294 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0306 |  |  | 3-B2 |  |  | #5 ATR(T) | ℃ | #5ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_COIL_T | #5ATR T相線溫 | ATR |  |  |  |  | CDC | 295 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0310 |  | 0370 | 3-B6 |  | 3-72 | #7 ATR | TAP | #7ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_TAP | #7ATR OLTC TAP | ATR |  |  |  |  | CDC | 296 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0312 |  |  | 3-B8 |  |  | #7 ATR(R) | ℃ | #7ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_OIL_R | #7ATR R相油溫 | ATR |  |  |  |  | CDC | 297 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0311 |  |  | 3-B7 |  |  | #7 ATR(R) | ℃ | #7ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_COIL_R | #7ATR R相線溫 | ATR |  |  |  |  | CDC | 298 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0314 |  |  | 3-BA |  |  | #7 ATR(S) | ℃ | #7ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_OIL_S | #7ATR S相油溫 | ATR |  |  |  |  | CDC | 299 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0313 |  |  | 3-B9 |  |  | #7 ATR(S) | ℃ | #7ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_COIL_S | #7ATR S相線溫 | ATR |  |  |  |  | CDC | 300 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0316 |  |  | 3-BC |  |  | #7 ATR(T) | ℃ | #7ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_OIL_T | #7ATR T相油溫 | ATR |  |  |  |  | CDC | 301 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0315 |  |  | 3-BB |  |  | #7 ATR(T) | ℃ | #7ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_COIL_T | #7ATR T相線溫 | ATR |  |  |  |  | CDC | 302 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaA | T/1ATR345 | B/2Bus |  |  | 0275 |  | 0272 | 3-02-03 |  | 3-10 | 3660 | CB | 3660 CB AS |  | aaec | B2/E03_C | [8 empty] | 龍崎ES.3660_CB | 3660(#1ATR) CB | ATR |  |  |  |  | CDC | 303 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | E1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3660TE | 3660TE (非取樣點) | ATR | [5 empty] | 304 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | E2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3660BE | 3660BE (非取樣點) | ATR | [5 empty] | 305 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | T/1ATR161 |  |  | 0276 |  | 0273 | 3-02-04 |  | 3-11 | 1810 | CB | 1810 CB AS |  | aaja | B3/E03_C | [8 empty] | 龍崎ES.1810_CB | 1810(#1ATR) CB | ATR |  |  |  |  | CDC | 306 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaB | B/1Bus | T/2ATR345 |  |  | 0282 |  | 0275 | 3-03-02 |  | 3-13 | 3670 | CB | 3670 CB AS |  | aaga | B2/E03_C | [8 empty] | 龍崎ES.3670_CB | 3670(#2ATR) CB | ATR |  |  |  |  | CDC | 307 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3670TE | 3670TE (非取樣點) | ATR | [5 empty] | 308 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3670BE | 3670BE (非取樣點) | ATR | [5 empty] | 309 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | T/2ATR161 | B/2Bus |  |  | 0284 |  | 0277 | 3-03-04 |  | 3-15 | 1840 | CB | 1840 CB AS |  | aaqa | B3/E03_C | [8 empty] | 龍崎ES.1840_CB | 1840(#2ATR) CB | ATR |  |  |  |  | CDC | 310 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | T/5ATR345 |  |  | 0262 |  | 0263 | 3-00-06 |  | 3-07 | 3570 | CB | 3570 CB AS |  | aafa | B2/E03_C | [8 empty] | 龍崎ES.3570_CB | 3570(#5ATR) CB | ATR |  |  |  |  | CDC | 311 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3570TE | 3570TE (非取樣點) | ATR | [5 empty] | 312 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3570BE | 3570BE (非取樣點) | ATR | [5 empty] | 313 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | T/5ATR161 |  |  | 0264 |  | 0265 | 3-01-00 |  | 3-09 | 1910 | CB | 1910 CB AS |  | aaha | B3/E03_C | [8 empty] | 龍崎ES.1910_CB | 1910(#5ATR) CB | ATR |  |  |  |  | CDC | 314 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaE | T/7ATR345 | B/2Bus |  |  | 0298 |  | 0284 | 3-05-02 |  | 3-1C | 3930 | CB | 3930 CB AS |  | aaac | B2/E03_C | [8 empty] | 龍崎ES.3930_CB | 3930(#7ATR) CB | ATR |  |  |  |  | CDC | 315 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3930TE | 3930TE (非取樣點) | ATR | [5 empty] | 316 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3930BE | 3930BE (非取樣點) | ATR | [5 empty] | 317 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaF | B/1Bus | T/7ATR161 |  |  | 0299 |  | 0285 | 3-05-03 |  | 3-1D | 1750 | CB | 1750 CB AS |  | aaaa | B3/E03_C | [8 empty] | 龍崎ES.1750_CB | 1750(#7ATR) CB | ATR |  |  |  |  | CDC | 318 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaE | T/7ATR161 | B/2Bus |  |  | 0300 |  | 0286 | 3-05-04 |  | 3-1E | 1760 | CB | 1760 CB AS |  | aaba | B3/E03_C | [8 empty] | 龍崎ES.1760_CB | 1760(#7ATR) CB | ATR |  |  |  |  | CDC | 319 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1920 | #6ATR(1920) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | T/5ATR161 | B/2Bus |  |  | 0336 |  | 0392 | 3-0A-00 |  | 4-08 | 1920 | CB | 1920 CB AS |  | aaia | B3/E03_C | [8 empty] | 龍崎ES.1920_CB | 1920(#5ATR) CB | ATR |  |  |  |  | CDC | 320 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | T/1ATR161 | B/2Bus |  |  | 0337 |  | 0393 | 3-0A-01 |  | 4-09 | 1820 | CB | 1820 CB AS |  | aaka | B3/E03_C | [8 empty] | 龍崎ES.1820_CB | 1820(#1ATR) CB | ATR |  |  |  |  | CDC | 321 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/1Bus | T/2ATR161 |  |  | 0338 |  | 0394 | 3-0A-02 |  | 4-0A | 1830 | CB | 1830 CB AS |  | aapb | B3/E03_C | [8 empty] | 龍崎ES.1830_CB | 1830(#2ATR) CB | ATR |  |  |  |  | CDC | 322 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0277 |  |  | 3-02-05 |  |  | #1 ATR | 87T1A | #1 ATR 87T1A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_87A1 | #1ATR 第一組 87RY | ATR |  |  |  |  | CDC | 323 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 3-02-06 |  |  | #1 ATR | 87T2A | #1 ATR 87T2A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_87A2 | #1ATR 第二組 87RY | ATR |  |  |  |  | CDC | 324 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0279 |  |  | 3-02-07 |  |  | #1 ATR | 96PA | #1 ATR 機械保護動作(96PA) |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_96PA | #1ATR 機械保護動作 | ATR |  |  |  |  | CDC | 325 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0280 |  |  | 3-03-00 |  |  | #1 ATR | 51ZA | #1 ATR 51ZA |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_51ZA | #1ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 326 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0281 |  |  | 3-03-01 |  |  | #1 ATR | 59A | #1 ATR 59A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_59A | #1ATR 59RY | ATR |  |  |  |  | CDC | 327 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 3-03-05 |  |  | #2 ATR | 87T1A | #2 ATR 87T1A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_87A1 | #2ATR 第一組 87RY | ATR |  |  |  |  | CDC | 328 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0286 |  |  | 3-03-06 |  |  | #2 ATR | 87T2A | #2 ATR 87T2A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_87A2 | #2ATR 第二組 87RY | ATR |  |  |  |  | CDC | 329 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 3-03-07 |  |  | #2 ATR | 96PA | #2 ATR 機械保護動作(96PA) |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_96PA | #2ATR 機械保護動作 | ATR |  |  |  |  | CDC | 330 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 3-04-00 |  |  | #2 ATR | 51ZA | #2 ATR 51ZA |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_51ZA | #2ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 331 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0289 |  |  | 3-04-01 |  |  | #2 ATR | 59A | #2 ATR 59A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_59A | #2ATR 59RY | ATR |  |  |  |  | CDC | 332 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 |  |  | 3-01-01 |  |  | #5 ATR | 87T1A | #5 ATR 87T1A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_87A1 | #5ATR 第一組 87RY | ATR |  |  |  |  | CDC | 333 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 3-01-02 |  |  | #5 ATR | 87T2A | #5 ATR 87T2A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_87A2 | #5ATR 第二組 87RY | ATR |  |  |  |  | CDC | 334 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 3-01-03 |  |  | #5 ATR | 96PA | #5 ATR 機械保護動作(96PA) |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_96PA | #5ATR 機械保護動作 | ATR |  |  |  |  | CDC | 335 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 3-01-04 |  |  | #5 ATR | 51ZA | #5 ATR 51ZA |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_51ZA | #5ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 336 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0269 |  |  | 3-01-05 |  |  | #5 ATR | 59A | #5 ATR 59A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_59A | #5ATR 59RY | ATR |  |  |  |  | CDC | 337 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 3-05-05 |  |  | #7 ATR | 87T1A | #7 ATR 87T1A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_87A1 | #7ATR 第一組 87RY | ATR |  |  |  |  | CDC | 338 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 3-05-06 |  |  | #7 ATR | 87T2A | #7 ATR 87T2A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_87A2 | #7ATR 第二組 87RY | ATR |  |  |  |  | CDC | 339 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 3-05-07 |  |  | #7 ATR | 96PA | #7 ATR 機械保護動作(96PA) |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_96PA | #7ATR 機械保護動作 | ATR |  |  |  |  | CDC | 340 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0304 |  |  | 3-06-00 |  |  | #7 ATR | 51ZA | #7 ATR 51ZA |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_51ZA | #7ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 341 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0305 |  |  | 3-06-01 |  |  | #7 ATR | 59A | #7 ATR 59A |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_59A | #7ATR 59RY | ATR |  |  |  |  | CDC | 342 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0787 |  |  | 3-31-03 |  |  | #1 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_96D | #1ATR 96D RY | ATR |  |  |  |  | CDC | 343 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0788 |  |  | 3-31-04 |  |  | #1 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_96P | #1ATR 96P RY | ATR |  |  |  |  | CDC | 344 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0789 |  |  | 3-31-05 |  |  | #1 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_63Q | #1ATR 63Q RY | ATR |  |  |  |  | CDC | 345 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0785 |  |  | 3-31-01 |  |  | #1 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_96B1 | #1ATR 96B1 RY | ATR |  |  |  |  | CDC | 346 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0786 |  |  | 3-31-02 |  |  | #1 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_96B2 | #1ATR 96B2 RY | ATR |  |  |  |  | CDC | 347 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0803 |  |  | 3-32-03 |  |  | #2 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_96D | #2ATR 96D RY | ATR |  |  |  |  | CDC | 348 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0804 |  |  | 3-32-04 |  |  | #2 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_96P | #2ATR 96P RY | ATR |  |  |  |  | CDC | 349 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0805 |  |  | 3-32-05 |  |  | #2 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_63Q | #2ATR 63Q RY | ATR |  |  |  |  | CDC | 350 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0801 |  |  | 3-32-01 |  |  | #2 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_96B1 | #2ATR 96B1 RY | ATR |  |  |  |  | CDC | 351 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0802 |  |  | 3-32-02 |  |  | #2 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_96B2 | #2ATR 96B2 RY | ATR |  |  |  |  | CDC | 352 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0776 |  |  | 3-30-08 |  |  | #5 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_96D | #5ATR 96D RY | ATR |  |  |  |  | CDC | 353 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0777 |  |  | 3-30-09 |  |  | #5 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_96P | #5ATR 96P RY | ATR |  |  |  |  | CDC | 354 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0778 |  |  | 3-30-10 |  |  | #5 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_63Q | #5ATR 63Q RY | ATR |  |  |  |  | CDC | 355 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 3-30-06 |  |  | #5 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_96B1 | #5ATR 96B1 RY | ATR |  |  |  |  | CDC | 356 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0775 |  |  | 3-30-07 |  |  | #5 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_96B2 | #5ATR 96B2 RY | ATR |  |  |  |  | CDC | 357 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0819 |  |  | 3-33-03 |  |  | #7 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_96D | #7ATR 96D RY | ATR |  |  |  |  | CDC | 358 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0820 |  |  | 3-33-04 |  |  | #7 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_96P | #7ATR 96P RY | ATR |  |  |  |  | CDC | 359 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0821 |  |  | 3-33-05 |  |  | #7 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_63Q | #7ATR 63Q RY | ATR |  |  |  |  | CDC | 360 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 3-33-01 |  |  | #7 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_96B1 | #7ATR 96B1 RY | ATR |  |  |  |  | CDC | 361 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0818 |  |  | 3-33-02 |  |  | #7 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_96B2 | #7ATR 96B2 RY | ATR |  |  |  |  | CDC | 362 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0791 |  |  | 3-31-07 |  |  | #1 ATR | TRA | #1 ATR 重故障 |  | a | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_TRA | #1ATR 重故障 | ATR |  |  |  |  | CDC | 363 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0790 |  |  | 3-31-06 |  |  | #1 ATR | TRF | #1 ATR 輕故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_TRF | #1ATR 輕故障 | ATR |  |  |  |  | CDC | 364 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0783 |  |  | 3-30-15 |  |  | #1 ATR | S/L | #1 ATR 遙測/本地 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_S/L | #1ATR OLTC S/L | ATR |  |  |  |  | CDC | 365 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0784 |  | 0355 | 3-31-00 |  | 3-63 | #1 ATR | A/M | #1 ATR 自動/手動 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_A/M | #1ATR OLTC A/M | ATR |  |  |  |  | CDC | 366 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1108 | 1109 | 0356 | 4-35-04 | 4-35-05 | 3-64 | #1 ATR | MY-S | #1 ATR MY-S |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_M/F/I | #1ATR M/F/I | ATR |  |  |  |  | CDC | 367 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0807 |  |  | 3-32-07 |  |  | #2 ATR | TRA | #2 ATR 重故障 |  | a | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_TRA | #2ATR 重故障 | ATR |  |  |  |  | CDC | 368 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0806 |  |  | 3-32-06 |  |  | #2 ATR | TRF | #2 ATR 輕故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_TRF | #2ATR 輕故障 | ATR |  |  |  |  | CDC | 369 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0799 |  |  | 3-31-15 |  |  | #2 ATR | S/L | #2 ATR 遙測/本地 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_S/L | #2ATR OLTC S/L | ATR |  |  |  |  | CDC | 370 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0359 | 3-32-00 |  | 3-67 | #2 ATR | A/M | #2 ATR 自動/手動 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_A/M | #2ATR OLTC A/M | ATR |  |  |  |  | CDC | 371 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1110 | 1111 | 0360 | 4-35-06 | 4-35-07 | 3-68 | #2 ATR | MY-S | #2 ATR MY-S |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_M/F/I | #2ATR M/F/I | ATR |  |  |  |  | CDC | 372 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0780 |  |  | 3-30-12 |  |  | #5 ATR | TRA | #5 ATR 重故障 |  | a | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_TRA | #5ATR 重故障 | ATR |  |  |  |  | CDC | 373 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0779 |  |  | 3-30-11 |  |  | #5 ATR | TRF | #5 ATR 輕故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_TRF | #5ATR 輕故障 | ATR |  |  |  |  | CDC | 374 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 3-30-04 |  |  | #5 ATR | S/L | #5 ATR 遙測/本地 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_S/L | #5ATR OLTC S/L | ATR |  |  |  |  | CDC | 375 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0363 | 3-30-05 |  | 3-6B | #5 ATR | A/M | #5 ATR 自動/手動 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_A/M | #5ATR OLTC A/M | ATR |  |  |  |  | CDC | 376 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1106 | 1107 | 0364 | 4-35-02 | 4-35-03 | 3-6C | #5 ATR | MY-S | #5 ATR MY-S |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_M/F/I | #5ATR M/F/I | ATR |  |  |  |  | CDC | 377 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0823 |  |  | 3-33-07 |  |  | #7 ATR | TRA | #7 ATR 重故障 |  | a | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_TRA | #7ATR 重故障 | ATR |  |  |  |  | CDC | 378 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0822 |  |  | 3-33-06 |  |  | #7 ATR | TRF | #7 ATR 輕故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_TRF | #7ATR 輕故障 | ATR |  |  |  |  | CDC | 379 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0815 |  |  | 3-32-15 |  |  | #7 ATR | S/L | #7 ATR 遙測/本地 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_S/L | #7ATR OLTC S/L | ATR |  |  |  |  | CDC | 380 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0816 |  | 0367 | 3-33-00 |  | 3-6F | #7 ATR | A/M | #7 ATR 自動/手動 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_A/M | #7ATR OLTC A/M | ATR |  |  |  |  | CDC | 381 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1114 | 1115 | 0368 | 4-35-10 | 4-35-11 | 3-70 | #7 ATR | MY-S | #7 ATR MY-S |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_M/F/I | #7ATR M/F/I | ATR |  |  |  |  | CDC | 382 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | ABS1 | 3661 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1034 | 1035 | 0322 | 4-30-10 | 4-30-11 | 3-42 | 3661 | DS | 3661 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3661_ABS | 3661(#1ATR) ABS | ATR |  |  |  |  | CDC | 383 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | ABS2 | 3662 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1036 | 1037 | 0323 | 4-30-12 | 4-30-13 | 3-43 | 3662 | DS | 3662 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3662_ABS | 3662(#1ATR) ABS | ATR |  |  |  |  | CDC | 384 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | ABS1 | 3671 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1038 | 1039 | 0324 | 4-30-14 | 4-30-15 | 3-44 | 3671 | DS | 3671 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3671_ABS | 3671(#2ATR) ABS | ATR |  |  |  |  | CDC | 385 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | ABS2 | 3672 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1040 | 1041 | 0325 | 4-31-00 | 4-31-01 | 3-45 | 3672 | DS | 3672 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3672_ABS | 3672(#2ATR) ABS | ATR |  |  |  |  | CDC | 386 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | DS1 | 3571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 0993 | 0304 | 3-3E-00 | 3-3E-01 | 3-30 | 3571 | DS | 3571 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3571_DS | 3571(#5ATR) DS | ATR |  |  |  |  | CDC | 387 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | DS2 | 3572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 0995 | 0305 | 3-3E-02 | 3-3E-03 | 3-31 | 3572 | DS | 3572 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3572_DS | 3572(#5ATR) DS | ATR |  |  |  |  | CDC | 388 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | DS1 | 3931 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1058 | 1059 | 0333 | 4-32-02 | 4-32-03 | 3-4D | 3931 | DS | 3931 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3931_DS | 3931(#7ATR) DS | ATR |  |  |  |  | CDC | 389 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | DS2 | 3932 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1062 | 1063 | 0335 | 4-32-06 | 4-32-07 | 3-4F | 3932 | DS | 3932 DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3932_DS | 3932(#7ATR) DS | ATR |  |  |  |  | CDC | 390 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS1 | 1811 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1068 | 1069 | 0339 | 4-32-12 | 4-32-13 | 3-53 | 1811 | DS | 1811 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1811_DS | 1811(#1ATR) DS | ATR |  |  |  |  | CDC | 391 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS2 | 1812 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1070 | 1071 | 0340 | 4-32-14 | 4-32-15 | 3-54 | 1812 | DS | 1812 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1812_DS | 1812(#1ATR) DS | ATR |  |  |  |  | CDC | 392 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | DS1 | 1841 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1076 | 1077 | 0343 | 4-33-04 | 4-33-05 | 3-57 | 1841 | DS | 1841 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1841_DS | 1841(#2ATR) DS | ATR |  |  |  |  | CDC | 393 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | DS2 | 1842 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1078 | 1079 | 0344 | 4-33-06 | 4-33-07 | 3-58 | 1842 | DS | 1842 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1842_DS | 1842(#2ATR) DS | ATR |  |  |  |  | CDC | 394 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | DS1 | 1911 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1064 | 1065 | 0336 | 4-32-08 | 4-32-09 | 3-50 | 1911 | DS | 1911 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1911_DS | 1911(#5ATR) DS | ATR |  |  |  |  | CDC | 395 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | DS2 | 1912 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1066 | 1067 | 0337 | 4-32-10 | 4-32-11 | 3-51 | 1912 | DS | 1912 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1912_DS | 1912(#5ATR) DS | ATR |  |  |  |  | CDC | 396 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | DS1 | 1751 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1092 | 1093 | 0350 | 4-34-04 | 4-34-05 | 3-5E | 1751 | DS | 1751 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1751_DS | 1751(#7ATR) DS | ATR |  |  |  |  | CDC | 397 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | DS2 | 1752 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1094 | 1095 | 0351 | 4-34-06 | 4-34-07 | 3-5F | 1752 | DS | 1752 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1752_DS | 1752(#7ATR) DS | ATR |  |  |  |  | CDC | 398 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | DS1 | 1761 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1098 | 1099 | 0352 | 4-34-10 | 4-34-11 | 3-60 | 1761 | DS | 1761 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1761_DS | 1761(#7ATR) DS | ATR |  |  |  |  | CDC | 399 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | DS2 | 1762 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1100 | 1101 | 0353 | 4-34-12 | 4-34-13 | 3-61 | 1762 | DS | 1762 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1762_DS | 1762(#7ATR) DS | ATR |  |  |  |  | CDC | 400 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1920 | #6ATR(1920) |  | DS1 | 1921 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1140 | 1141 | 0400 | 4-37-04 | 4-37-05 | 4-10 | 1921 | DS | 1921 AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1921_DS | 1921(#5ATR) DS | ATR |  |  |  |  | CDC | 401 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1920 | #6ATR(1920) |  | DS2 | 1922 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1144 | 1145 | 0401 | 4-37-08 | 4-37-09 | 4-11 | 1922 | DS | 1922 AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1922_DS | 1922(#5ATR) DS | ATR |  |  |  |  | CDC | 402 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | DS1 | 1821 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1130 | 1131 | 0402 | 4-36-10 | 4-36-11 | 4-12 | 1821 | DS | 1821 AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1821_DS | 1821(#1ATR) DS | ATR |  |  |  |  | CDC | 403 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | DS2 | 1822 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1134 | 1135 | 0403 | 4-36-14 | 4-36-15 | 4-13 | 1822 | DS | 1822 AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1822_DS | 1822(#1ATR) DS | ATR |  |  |  |  | CDC | 404 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | DS1 | 1831 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1136 | 1137 | 0404 | 4-37-00 | 4-37-01 | 4-14 | 1831 | DS | 1831 AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1831_DS | 1831(#2ATR) DS | ATR |  |  |  |  | CDC | 405 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | DS2 | 1832 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1138 | 1139 | 0405 | 4-37-02 | 4-37-03 | 4-15 | 1832 | DS | 1832 AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1832_DS | 1832(#2ATR) DS | ATR |  |  |  |  | CDC | 406 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | T/1SSTR | T/2ATR33 |  |  | 0424 |  | 0279 | 3-15-00 |  | 3-17 | 390 | CB | 390 CB AS |  | acbb | B3/E03_A1 | [8 empty] | 龍崎ES.390_CB | 390(#1SSTR) CB | OTHER |  |  |  |  | CDC | 407 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0425 |  |  | 3-15-01 |  |  | 390 | CB | 390 CB PHA |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 408 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 590 | #3SSTR(590) |  | CB |  | (B3) | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/3SSTR | T/5ATR33 |  |  | 0416 |  | 0266 | 3-14-00 |  | 3-0A | 590 | CB | 590 CB AS |  | adbb | B3/E03_A1 | [8 empty] | 龍崎ES.590_CB | 590(#3SSTR) CB | OTHER |  |  |  |  | CDC | 409 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 33 | 33kV | 590 | #3SSTR(590) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0417 |  |  | 3-14-01 |  |  | 590 | CB | 590 CB PHA |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.#3SSTR_51A | #3SSTR 51RY | OTHER |  |  |  |  | CDC | 410 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/1ATR33 | R/1SHR |  |  | 0418 |  | 0274 | 3-14-02 |  | 3-12 | 510 | CB | 510 CB AS |  | abab | B3/E03_C | [8 empty] | 龍崎ES.510_CB | 510 CB | OTHER |  |  |  |  | CDC | 411 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0420 |  |  | 3-14-04 |  |  | 510 | 87A | #1ATR THI 510 87RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.510_87A | 510 87RY | OTHER |  |  |  |  | CDC | 412 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0419 |  |  | 3-14-03 |  |  | 510 | 51A | #1ATR THI 510 51RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.510_PHA | 510 相間RY | OTHER |  |  |  |  | CDC | 413 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/2ATR33 | R/2SHR |  |  | 0421 |  | 0278 | 3-14-05 |  | 3-16 | 520 | CB | 520 CB AS |  | acab | B3/E03_C | [8 empty] | 龍崎ES.520_CB | 520 CB | OTHER |  |  |  |  | CDC | 414 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0423 |  |  | 3-14-07 |  |  | 520 | 87A | #2ATR THI 520 87RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.520_87A | 520 87RY | OTHER |  |  |  |  | CDC | 415 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0422 |  |  | 3-14-06 |  |  | 520 | 51A | #2ATR THI 520 51RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.520_PHA | 520 相間RY | OTHER |  |  |  |  | CDC | 416 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/7ATR33 | R/7SHR |  |  | 0429 |  | 0287 | 3-15-05 |  | 3-1F | 570 | CB | 570 CB AS |  | aaab | B3/E03_C | [8 empty] | 龍崎ES.570_CB | 570 CB | OTHER |  |  |  |  | CDC | 417 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0431 |  |  | 3-15-07 |  |  | 570 | 87A | #7ATR THI 570 87RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.570_87A | 570 87RY | OTHER |  |  |  |  | CDC | 418 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0430 |  |  | 3-15-06 |  |  | 570 | 51A | #7ATR THI 570 51RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.570_PHA | 570 相間RY | OTHER |  |  |  |  | CDC | 419 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/5ATR33 | R/5SHR |  |  | 0426 |  | 0382 | 3-15-02 |  | 3-7E | 550 | CB | 550 CB AS |  | adab | B3/E03_C | [8 empty] | 龍崎ES.550_CB | 550 CB | OTHER |  |  |  |  | CDC | 420 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0428 |  |  | 3-15-04 |  |  | 550 | 87A | #5ATR THI 550 87RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.550_87A | 550 87RY | OTHER |  |  |  |  | CDC | 421 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0427 |  |  | 3-15-03 |  |  | 550 | 51A | #5ATR THI 550 51RY |  |  | B3/E03_C | [8 empty] | 龍崎ES.550_PHA | 550 相間RY | OTHER |  |  |  |  | CDC | 422 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | DS1 | 511 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1072 | 1073 | 0341 | 4-33-00 | 4-33-01 | 3-55 | 511 | DS | 511 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.511_ABS | 511 ABS | OTHER |  |  |  |  | CDC | 423 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | ABS1 | 521 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1080 | 1081 | 0345 | 4-33-08 | 4-33-09 | 3-59 | 521 | DS | 521 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.521_ABS | 521 ABS | OTHER |  |  |  |  | CDC | 424 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | ABS1 | 571 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1104 | 1105 | 0354 | 4-35-00 | 4-35-01 | 3-62 | 571 | DS | 571 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.571_ABS | 571 ABS | OTHER |  |  |  |  | CDC | 425 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | ABS1 | 551 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1088 | 1089 | 0383 | 4-34-00 | 4-34-01 | 3-7F | 551 | DS | 551 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.551_ABS | 551 ABS | OTHER |  |  |  |  | CDC | 426 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 427 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 428 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 429 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 430 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 431 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 432 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 433 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 434 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0320 |  |  | 3-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER |  |  |  |  | CDC | 435 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0321 |  |  | 3-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER |  |  |  |  | CDC | 436 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL6 |  | Element | [12 empty] | 0384 |  |  | 4-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCL6 | AI 10%參考點 ADCL6 | OTHER |  |  |  |  | CDC | 437 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH6 |  | Element | [12 empty] | 0385 |  |  | 4-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.AI_ADCH6 | AI 90%參考點 ADCH6 | OTHER |  |  |  |  | CDC | 438 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 1_DCV_P | #1直流P電源 | Element | MvMoment | #1 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0336 |  |  | 3-D0 |  |  | DCV | DCV | #1BATT P-G | kV_-150_150(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.#1直流P電源 | #1直流P電源電壓 | OTHER |  |  |  |  | CDC | 439 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 1_DCV_N | #1直流N電源 | Element | MvMoment | #1 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0337 |  |  | 3-D1 |  |  | DCV | DCV | #1BATT N-G | kV_-150_150(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.#1直流N電源 | #1直流N電源電壓 | OTHER |  |  |  |  | CDC | 440 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 2_DCV_P | #2直流P電源 | Element | MvMoment | #2 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | DCV |  | #2BATT P-G | kV_-150_150(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.#2直流P電源 | #2直流P電源電壓 | OTHER |  |  |  |  | CDC | 441 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 2_DCV_N | #2直流N電源 | Element | MvMoment | #2 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | DCV |  | #2BATTN-G | kV_-150_150(-2000_2000) |  | B3/E03_A1 | [8 empty] | 龍崎ES.#2直流N電源 | #2直流N電源電壓 | OTHER |  |  |  |  | CDC | 442 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0309 |  |  | 3-B5 |  |  | 5QT+- | ℃ | NO.5 A.TR二次側S.R.油溫 | OIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#5ATR_SR_OIL | #5ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 443 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0308 |  |  | 3-B4 |  |  | 5WX+- | ℃ | NO.5 A.TR二次側S.R.線溫 | COIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#5ATR_SR_COIL | #5ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 444 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0291 |  |  | 3-A3 |  |  | 1QT+- | ℃ | NO.1 A.TR二次側S.R.油溫 | OIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#1ATR_SR_OIL | #1ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 445 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0290 |  |  | 3-A2 |  |  | 1WX+- | ℃ | NO.1 A.TR二次側S.R.線溫 | COIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#1ATR_SR_COIL | #1ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 446 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0300 |  |  | 3-AC |  |  | 2QT+- | ℃ | NO.2 A.TR二次側S.R.油溫 | OIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#2ATR_SR_OIL | #2ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 447 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0299 |  |  | 3-AB |  |  | 2WX+- | ℃ | NO.2 A.TR二次側S.R.線溫 | COIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#2ATR_SR_COIL | #2ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 448 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0318 |  |  | 3-BE |  |  | 7QT+- | ℃ | NO.7 A.TR二次側S.R.油溫 | OIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#7ATR_SR_OIL | #7ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 449 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0317 |  |  | 3-BD |  |  | 7WX+- | ℃ | NO.7 A.TR二次側S.R.線溫 | COIL_-120_120(-2000_2000) |  | B1/E03_C | [8 empty] | 龍崎ES.#7ATR_SR_COIL | #7ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 450 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0896 |  | 0384 | 3-38-00 |  | 4-00 | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.所內電源ACB1 | 所內電源開關ACB1 | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0898 |  | 0386 | 3-38-02 |  | 4-02 | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.所內電源ACB2 | 所內電源開關ACB2 | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E03 | 龍崎ES | 0 |  | RTU | RTU |  | Test_CB1 | TEST_CB(N_1) | B2,Element | Status | TEST CB1 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0256 | 3-30-00 |  | 3-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 龍崎ES.TEST_CB(N_1) | 345KV(N)TEST CB | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | RTU1 | RTU1 |  | RTU_R_L | RTU_S/L(N_1) | Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 3-30-01 |  |  | RTU |  | LOCAL/REMOTE |  |  | B1/E03_C | [8 empty] | 龍崎ES.RTU_S/L(N_1) | 345KV(N)RTU S/L | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E03 | 龍崎ES | 0 |  | RTU | RTU |  | Test_CB2 | TEST_CB(N_2) | B2,Element | Status | TEST CB2 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 龍崎ES.TEST_CB(N_2) | 161KV(N)TEST CB | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | RTU2 | RTU2 |  | RTU_R_L | RTU_S/L(N_2) | Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU |  | LOCAL/REMOTE |  |  | B1/E03_C | [8 empty] | 龍崎ES.RTU_S/L(N_2) | 161KV(N)RTU S/L | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | BFS |  | Element | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0849 |  |  | 3-35-01 |  |  | 345KV | BF-S | 345KV BFS |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_BFS | 345KV(N)斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | BFA |  | Element | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 3-06-06 |  |  | 345KV | BFA | 345KV BFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_BFA | 345KV(N)斷路器失靈(BF)警報 | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RCA |  | Element | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0312 |  |  | 3-07-00 |  |  | 345KV | RCA | 345KV RCA |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_RCA | 345KV(N)LINE 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | OSCA |  | Element | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 3-06-07 |  |  | 345KV | OSCA | 345KV示波器啟動警報OSCA |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_OSCA | 345KV(N)示波器起動 | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | OSCF |  | Element | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0913 |  |  | 3-39-01 |  |  | OSCF | A/N | 345KV示波器缺紙或故障警報OSCF |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_OSCF | 345KV(N)示波器故障,電源跳脫 | OTHER |  |  |  |  | CDC | 461 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | BFS |  | Element | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 161KV | BF-S | 161KV BFS |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.161KV_N_BFS | 161KV(N)斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | BFA |  | Element | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 161KV | BFA | 161KV BFA |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.161KV_N_BFA | 161KV(N)斷路器失靈(BF)RY | OTHER |  |  |  |  | CDC | 463 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 79UL | N_RCA | Element | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 161KV | RCA | 161KV RCA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_N_RCA | 161KV(N)LINE 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | OSCA |  | Element | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 161KV | OSCA | 161KV OSCA(備用) |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_N_OSCA | 161KV(N)示波器起動 | OTHER |  |  |  |  | CDC | 465 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | OSCF |  | Element | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF(備用) |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_N_OSCF | 161KV(N)示波器故障,電源跳脫 | OTHER |  |  |  |  | CDC | 466 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 25TA |  | Element | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0432 |  |  | 3-16-00 |  |  | 25RY | 25TA | 自動同步校核裝置超時警報 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_25TA | 345KV(N)同步電驛25TA | OTHER |  |  |  |  | CDC | 467 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 25PFA |  | Element | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0433 |  |  | 3-16-01 |  |  | 25RY | 25PFA | 自動同步校核裝置電源故障警報 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_25PFA | 345KV(N)同步電驛25PFA | OTHER |  |  |  |  | CDC | 468 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 25TA |  | Element | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | 25RY | 25TA | 自動同步校核裝置超時警報 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_N_25TA | 161KV(N)同步電驛25TA | OTHER |  |  |  |  | CDC | 469 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 25PFA |  | Element | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 25RY | 25PFA | 自動同步校核裝置電源故障警報 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_N_25PFA | 161KV(N)同步電驛25PFA | OTHER |  |  |  |  | CDC | 470 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | CBA |  | Element | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0850 |  |  | 3-35-02 |  |  | 345KV | CBA | 345KV CB 重故障 |  |  | ELEM/E03_C | [8 empty] | 龍崎ES.345KV_N_CBA | 345KV(N)重故障 | OTHER |  |  |  |  | CDC | 471 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | CBF |  | Element | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0851 |  |  | 3-35-03 |  |  | 345KV | CBF | 345KV CB 輕故障 |  |  | ELEM/E03_C | [8 empty] | 龍崎ES.345KV_N_CBF | 345KV(N)斷路器輕故障 | OTHER |  |  |  |  | CDC | 472 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | CBA |  | Element | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 161KV | CBA | 161KV CB 重故障 |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.161KV_N_CBA | 161KV(N)斷路器重故障 | OTHER |  |  |  |  | CDC | 473 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | CBF |  | Element | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | 161KV | CBF | 161KV CB 輕故障 |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.161KV_N_CBF | 161KV(N)斷路器輕故障 | OTHER |  |  |  |  | CDC | 474 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | COMT |  | Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 3-35-04 |  |  | 345KV | COMT | 345KV COMT |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_COMT | 345KV(N)空壓機警報 | OTHER |  |  |  |  | CDC | 475 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | COMT |  | Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | 161KV | COMT | 161KV COMT |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_N_COMT | 161KV(N)空壓機警報 | OTHER |  |  |  |  | CDC | 476 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | E2 | 3572E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0996 | 0997 | 0306 | 3-3E-04 | 3-3E-05 | 3-32 | 3572E | DS | 3572E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3572E_ES | 3572E(#5ATR) ES | OTHER |  |  |  |  | CDC | 477 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | E1 | 3931E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1060 | 1061 | 0334 | 4-32-04 | 4-32-05 | 3-4E | 3931E | DS | 3931E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3931E_ES | 3931E(#7ATR) ES | OTHER |  |  |  |  | CDC | 478 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | E1 | 1761E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0692 | 0693 |  | 1-3B-04 | 1-3B-05 |  | 1761E | DS | 1761E DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1761E_ES | 1761E(#7ATR) ES | OTHER |  |  |  |  | CDC | 479 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | E2 | 3562E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1120 | 1121 |  | 4-36-00 | 4-36-01 |  | 3562E | DS | 3562E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3562E_ES | 3562E ES | OTHER |  |  |  |  | CDC | 480 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | E1 | 3911E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1122 | 1123 |  | 4-36-02 | 4-36-03 |  | 3911E | DS | 3911E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3911E_ES | 3911E ES | OTHER |  |  |  |  | CDC | 481 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3920 | TIE(3920) |  | E1 | 3921E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1124 | 1125 |  | 4-36-04 | 4-36-05 |  | 3932E | DS | 3921E DS AS |  |  | B2/E03_C | [8 empty] | 龍崎ES.3921E_ES | 3921E ES | OTHER |  |  |  |  | CDC | 482 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | DS1 | 391 | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1082 | 1083 | 0346 | 4-33-10 | 4-33-11 | 3-5A | 391 | DS | 391 DS AS |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.391_ABS | 391ABS | OTHER |  |  |  |  | CDC | 483 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 33 | 33kV | 590 | #3SSTR(590) |  | DS1 | 591 | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1126 | 1127 | 0338 | 4-36-06 | 4-36-07 | 3-52 | 591 | DS | 591 DS AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.591_ABS | 591ABS | OTHER |  |  |  |  | CDC | 484 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | E2 | 1812E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1132 | 1133 |  | 4-36-12 | 4-36-13 |  | 1812E | ES | 1812E AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1812E_ES | 1812E(#1ATR) ES | OTHER |  |  |  |  | CDC | 485 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close |  | 2 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | E2 | 1912E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1142 | 1143 |  | 4-37-06 | 4-37-07 |  | 1912E | ES | 1912E AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1912E_ES | 1912E(#5ATR) ES | OTHER |  |  |  |  | CDC | 486 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | E2 | 1832E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1128 | 1129 |  | 4-36-08 | 4-36-09 |  | 1832E | ES | 1832E AS |  |  | B3/E03_C | [8 empty] | 龍崎ES.1832E_ES | 1832E(#2ATR) ES | OTHER |  |  |  |  | CDC | 487 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 3-31-08 |  |  | NO.1 SH.R | 96B1 | NO.1 SH.R 96B1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_SR96B1 | #1ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 488 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0793 |  |  | 3-31-09 |  |  | NO.1 SH.R | 96B1 | NO.1 SH.R 96B2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_SR96B2 | #1ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 489 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0794 |  |  | 3-31-10 |  |  | NO.1 SH.R | 96D | NO.1 SH.R 96D |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_SR96D | #1ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 490 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0795 |  |  | 3-31-11 |  |  | NO.1 SH.R | 96P | NO.1 SH.R 96P |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_SR96P | #1ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 491 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 3-32-08 |  |  | NO.2 SH.R | 96B1 | NO.2 SH.R 96B1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_SR96B1 | #2ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 492 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0809 |  |  | 3-32-09 |  |  | NO.2 SH.R | 96B2 | NO.2 SH.R 96B2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_SR96B2 | #2ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 493 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0810 |  |  | 3-32-10 |  |  | NO.2 SH.R | 96D | NO.2 SH.R 96D |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_SR96D | #2ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 494 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0811 |  |  | 3-32-11 |  |  | NO.2 SH.R | 96P | NO.2 SH.R 96P |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_SR96P | #2ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 495 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 3-33-08 |  |  | NO.7 SH.R | 96B1 | NO.7 SH.R 96B1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_SR96B1 | #7ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 496 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0825 |  |  | 3-33-09 |  |  | NO.7 SH.R | 96B2 | NO.7 SH.R 96B2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_SR96B2 | #7ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 497 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0826 |  |  | 3-33-10 |  |  | NO.7 SH.R | 96D | NO.7 SH.R 96D |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_SR96D | #7ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 498 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0827 |  |  | 3-33-11 |  |  | NO.7 SH.R | 96P | NO.7 SH.R 96P |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_SR96P | #7ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 499 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 3-34-08 |  |  | NO.5 SH.R | 96B1 | NO.5 SH.R 96B1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_SR96B1 | #5ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 500 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0841 |  |  | 3-34-09 |  |  | NO.5 SH.R | 96B2 | NO.5 SH.R 96B2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_SR96B2 | #5ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 501 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0842 |  |  | 3-34-10 |  |  | NO.5 SH.R | 96D | NO.5 SH.R 96D |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_SR96D | #5ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 502 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0843 |  |  | 3-34-11 |  |  | NO.5 SH.R | 96P | NO.5 SH.R 96P |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_SR96P | #5ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 503 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 3-0A-06 |  |  | 3540 | PHA1 | 龍崎瀰力二路 3540 #1 相間RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_PHA1 | 瀰力二路(3540) #1相間RY | OTHER |  |  |  |  | CDC | 504 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | GDA1 |  | B2,B3,Element | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 3-0A-07 |  |  | 3540 | GDA1 | 龍崎瀰力二路 3540 #1 接地RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_GDA1 | 瀰力二路(3540) #1接地RY | OTHER |  |  |  |  | CDC | 505 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 3-0B-00 |  |  | 3540 | PHA2 | 龍崎瀰力二路 3540 #2 相間RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_PHA2 | 瀰力二路(3540) #2相間RY | OTHER |  |  |  |  | CDC | 506 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | GDA2 |  | B2,B3,Element | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 3-0B-01 |  |  | 3540 | GDA2 | 龍崎瀰力二路 3540 #2 接地RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_GDA2 | 瀰力二路(3540) #2接地RY | OTHER |  |  |  |  | CDC | 507 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 2_87A2 |  | B2,B3,Element | Status | 第2套第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0346 |  |  | 3-0B-02 |  |  | 3540 | 287A2 | 龍崎瀰力二路 3540 #2_2 87RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87A4 | 瀰力二路(3540) #2_287RY | OTHER |  |  |  |  | CDC | 508 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | DTTA1 |  | B2,B3,Element | Status | 第1具遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 3-0B-07 |  |  | 3540 | 1DTTA1 | 龍崎瀰力二路 3540 #1_1 遠方遙跳 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_DTTA1 | 瀰力二路(3540)#1_1遠方遙跳 | OTHER |  |  |  |  | CDC | 509 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | DTTA2 |  | B2,B3,Element | Status | 第2具遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 3-0C-00 |  |  | 3540 | 1DTTA2 | 龍崎瀰力二路 3540 #1_2 遠方遙跳 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_DTTA2 | 瀰力二路(3540)#1_2遠方遙跳 | OTHER |  |  |  |  | CDC | 510 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 1A5Other | 3540_DTTA3 | B2,B3,Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0353 |  |  | 3-0C-01 |  |  | 3540 | 2DTTA1 | 龍崎瀰力二路 3540 #2_1 遠方遙跳 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_DTTA3 | 瀰力二路(3540)#2_1遠方遙跳 | OTHER |  |  |  |  | CDC | 511 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 2A5Other | 3540_DTTA4 | B2,B3,Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0354 |  |  | 3-0C-02 |  |  | 3540 | 2DTTA2 | 龍崎瀰力二路 3540 #2_2 遠方遙跳 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_DTTA4 | 瀰力二路(3540)#2_2遠方遙跳 | OTHER |  |  |  |  | CDC | 512 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 1_87UL1 |  | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0833 |  | 0347 | 3-34-01 |  | 3-5B | 3540 | 187UL1 | 龍崎瀰力二路 3540 #1_1 87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87UL1 | 瀰力二路(3540)#1_187RY U/L | OTHER |  |  |  |  | CDC | 513 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 1_87UL2 |  | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0834 |  | 0348 | 3-34-02 |  | 3-5C | 3540 | 187UL2 | 龍崎瀰力二路 3540 #1_2 87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87UL2 | 瀰力二路(3540)#1_287RY U/L | OTHER |  |  |  |  | CDC | 514 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 2_87UL1 |  | B2,B3,Element | Status | 第2套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0835 |  | 0349 | 3-34-03 |  | 3-5D | 3540 | 287UL1 | 龍崎瀰力二路 3540 #2_1 87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87UL3 | 瀰力二路(3540)#2_187RY U/L | OTHER |  |  |  |  | CDC | 515 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 2_87UL2 |  | B2,B3,Element | Status | 第2套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0836 |  | 0342 | 3-34-04 |  | 3-56 | 3540 | 287UL2 | 龍崎瀰力二路 3540 #2_2 87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87UL4 | 瀰力二路(3540)#2_287RY U/L | OTHER |  |  |  |  | CDC | 516 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | 87CFA1 |  | B2,B3,Element | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0867 |  |  | 3-36-03 |  |  | 3530 | 87CFA1 #1RY | 龍崎(北)~龍崎(南)臨時線 3530 187CFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_87CFA1 | 北南臨時線(3530) #187RY_CFA | OTHER |  |  |  |  | CDC | 517 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | 87CFA2 |  | B2,B3,Element | Status | 第2具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0869 |  |  | 3-36-05 |  |  | 3530 | 87CFA2 #2RY | 龍崎(北)~龍崎(南)臨時線 3530 285CFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3530_87CFA2 | 北南臨時線(3530) #285RY_CFA | OTHER |  |  |  |  | CDC | 518 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 87CFA1 |  | B2,B3,Element | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0872 |  |  | 3-36-08 |  |  | 3540 | 87CFA1 | 龍崎瀰力二路 3540 #1 87RY 通訊故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87CFA1 | 瀰力二路(3540) #187RY通訊故障 | OTHER |  |  |  |  | CDC | 519 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | 87CFA2 |  | B2,B3,Element | Status | 第2具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0874 |  |  | 3-36-10 |  |  | 3540 | 87CFA2 | 龍崎瀰力二路 3540 #2 87RY 通訊故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3540_87CFA2 | 瀰力二路(3540) #287RY通訊故障 | OTHER |  |  |  |  | CDC | 520 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 3-35-14 |  |  | 3510 | #1RY | 南科龍崎一路 RAOA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_87CFA | 南科一路(3510) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 521 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0864 |  |  | 3-36-00 |  |  | 3510 | #2RY | 南科龍崎一路 RAOA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3510_85CFA | 南科一路(3510) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 522 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0877 |  |  | 3-36-13 |  |  | 3560 | #1RY | 天輪龍崎海線 3560 RAOA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_87CFA | 天輪海線(3560) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 523 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0879 |  |  | 3-36-15 |  |  | 3560 | #2RY | 天輪龍崎海線 3560 RAOA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3560_85CFA | 天輪海線(3560) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 524 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 3-37-02 |  |  | 3610 | #1RY | 南科龍崎二路 187CFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_87CFA | 南科二路(3610) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 525 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 3-37-04 |  |  | 3610 | #2RY | 南科龍崎二路 285CFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3610_85CFA | 南科二路(3610) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 526 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0887 |  |  | 3-37-07 |  |  | 3630 | #1RY | 興達龍崎一路 RAOA1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_87CFA | 興達一路(3630) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 527 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 3-37-09 |  |  | 3630 | #2RY | 興達龍崎一路 RAOA2 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3630_85CFA | 興達一路(3630) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 528 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0892 |  |  | 3-37-12 |  |  | 3640 | #1RY | 路北龍崎紅線 187CFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_87CFA | 路北紅線(3640) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 529 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0894 |  |  | 3-37-14 |  |  | 3640 | #2RY | 路北龍崎紅線 285CFA |  |  | B2/E03_C | [8 empty] | 龍崎ES.3640_85CFA | 路北紅線(3640) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 530 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | ABS_89A | N_89A | Element | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 3-39-00 |  |  | ABS AL |  | ABS 警報 |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.345KV_N_89A | 345KV(N)ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 531 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | ABS_89A | N_89A | Element | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | ABS AL |  | ABS NFB跳脫警報 |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.161KV_N_89A | 161KV(N)ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 532 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | OilLeak | N_洩油池 | Element | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0914 |  |  | 3-39-02 |  |  | 洩油池警報 |  | 液位過高1 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_N_洩油池 | 345KV(N)洩油池水位警報 | OTHER |  |  |  |  | CDC | 533 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0915 |  |  | 3-39-03 |  |  | DCA |  | NFB跳脫警報 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_DCA | 345KV直流電源故障警報 | OTHER |  |  |  |  | CDC | 534 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1750TE | 1750TE(#7ATR)(非取樣點) | OTHER | [5 empty] | 535 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1750BE | 1750BE(#7ATR)(非取樣點) | OTHER | [5 empty] | 536 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1760TE | 1760TE(#7ATR)(非取樣點) | OTHER | [5 empty] | 537 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1760BE | 1760BE(#7ATR)(非取樣點) | OTHER | [5 empty] | 538 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | E2 | 3932E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_C | [8 empty] | 龍崎ES.3932E | 3932E(非取樣點) | OTHER | [5 empty] | 539 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | 1510 | 87L CFA | 龍崎山上一路 1510 87L CFA(87L通訊故障) |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_87CFA | 龍崎山上一路(1510)87RY通訊故障 | OTHER |  |  |  |  | CDC | 540 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 1510 | 87LA | 龍崎山上一路 1510 87LA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_RYFA | 龍崎山上一路(1510)數位電驛故障 | OTHER |  |  |  |  | CDC | 541 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | 50SA |  | B2,B3,Element | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0550 |  | 0061 | 1-32-06 |  | 1-3D | 1510 | 測試/正常 | 1510 50RY 測試/正常 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1510_50SA | 山上一路(1510) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 542 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | 1520 | 87L CFA | 龍崎山上二路 1520 87L CFA(87L通訊故障) |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_87CFA | 龍崎山上二路(1520)87RY通訊故障 | OTHER |  |  |  |  | CDC | 543 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | 1520 | 87LA | 龍崎山上二路 1520 87LA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_RYFA | 龍崎山上二路(1520)數位電驛故障 | OTHER |  |  |  |  | CDC | 544 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | 50SA |  | B2,B3,Element | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0551 |  | 0060 | 1-32-07 |  | 1-3C | 1520 | 測試/正常 | 1520 50RY 測試/正常 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1520_50SA | 山上二路(1520) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 545 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | 1530 | 87L CFA | 龍崎山上二甲三路1530 87 CFA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_87CFA | 山上二甲三路(1530)87RY通訊故障 | OTHER |  |  |  |  | CDC | 546 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | 1530 | 87LA | 龍崎山上二甲三路1530 RYFA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1530_RYFA | 山上二甲三路(1530)數位電驛故障 | OTHER |  |  |  |  | CDC | 547 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | 1540 | 87L CFA | 龍崎山上二甲四路 1540 87 CFA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_87CFA | 山上二甲四路(1540)87RY通訊故障 | OTHER |  |  |  |  | CDC | 548 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | 1540 | 87LA | 龍崎山上二甲四路 1540 RYFA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1540_RYFA | 山上二甲四路(1540)數位電驛故障 | OTHER |  |  |  |  | CDC | 549 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | 1550,1560 | 87L CFA | 龍崎台南山線CFA(87L通訊故障) |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_87CFA | 龍崎台南山線(1550)87RY通訊故障 | OTHER |  |  |  |  | CDC | 550 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | 1550,1560 | 87LA | 龍崎台南山線87LA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1550_RYFA | 龍崎台南山線(1550)數位電驛故障 | OTHER |  |  |  |  | CDC | 551 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0544 |  |  | 1-32-00 |  |  | 1570,1580 | 87L CFA | 龍崎台南海線87L CFA(87L通訊故障) |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_87CFA | 龍崎台南海線(1580)87RY通訊故障 | OTHER |  |  |  |  | CDC | 552 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎～台南海線(1580) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0545 |  |  | 1-32-01 |  |  | 1570,1580 | 87LA | 龍崎台南海線87LA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.1580_RYFA | 龍崎台南海線(1580)數位電驛故障 | OTHER |  |  |  |  | CDC | 553 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  | Element | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0556 |  |  | 1-32-12 |  |  | 161kV#1.2Bus | RYFA | 161kV#1.2Bus RYFA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161_NBUS_RYFA | 161KV#1,2BUS 87RY數位電驛故障 | OTHER |  |  |  |  | CDC | 554 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 87CTFA | NBUS_CTFA | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0557 |  |  | 1-32-13 |  |  | 161kV#1.2Bus | CTFA | 161kV#1.2Bus CTFA |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161_NBUS_CTFA | 161KV#1,2BUS 87RYCT迴路故障 | OTHER |  |  |  |  | CDC | 555 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1810BE | 1810BE(#1ATR)(非取樣點) | OTHER | [5 empty] | 556 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1810TE | 1810TE(#1ATR)(非取樣點) | OTHER | [5 empty] | 557 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1820BE | 1820BE(#1ATR)(非取樣點) | OTHER | [5 empty] | 558 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1820TE | 1820TE(#1ATR)(非取樣點) | OTHER | [5 empty] | 559 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1830BE | 1830BE(#2ATR)(非取樣點) | OTHER | [5 empty] | 560 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1830TE | 1830TE(#2ATR)(非取樣點) | OTHER | [5 empty] | 561 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1840BE | 1840BE(#2ATR)(非取樣點) | OTHER | [5 empty] | 562 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1840TE | 1840TE(#2ATR)(非取樣點) | OTHER | [5 empty] | 563 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1910BE | 1910BE(#5ATR)(非取樣點) | OTHER | [5 empty] | 564 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1910TE | 1910TE(#5ATR)(非取樣點) | OTHER | [5 empty] | 565 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1920 | #5ATR(1920) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1920BE | 1920BE(#5ATR)(非取樣點) | OTHER | [5 empty] | 566 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1920 | #5ATR(1920) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1920TE | 1920TE(#5ATR)(非取樣點) | OTHER | [5 empty] | 567 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | E1 | 1751E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1751E | 1751E(#7ATR)(非取樣點) | OTHER | [5 empty] | 568 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | E2 | 1762E(非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E03_C | [8 empty] | 龍崎ES.1762E | 1762E(#7ATR)(非取樣點) | OTHER | [5 empty] | 569 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | ACBT1 | ACB_TIE1 | Element | Status | 所內電源ACB TIE1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0897 |  | 0385 | 3-38-01 |  | 4-01 | ACB TIE1 | ON/OFF | 所內電源ACB TIE1 |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.ACB_TIE1 | 所內電源ACB TIE1 | OTHER |  |  |  |  | CDC | 570 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | CHG1 | 充電機故障_N | Element | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | 充電機 | CHG1 | #1.2.3充電機警報 |  |  | B3/E03_A1 | [8 empty] | 龍崎ES.充電機故障_N | #1,#2,#3直流充電機故障 | OTHER |  |  |  |  | CDC | 571 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | DCE |  | Element | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | DCE | DCE1 | DC接第警報 |  |  | ELEM/E03_A1 | [8 empty] | 龍崎ES.直流電源DCE_N | #1,#2直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 572 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | SHRA | 2SRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0940 |  |  | 3-3A-12 |  |  | #5 A.TR S.R | 5SH.R TRA | NO.5 A.TR二次側S.R |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#5ATR_2SRTRA | #5ATR 161KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 573 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | SHRF | 2SRTRF | B2,Element | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0941 |  |  | 3-3A-13 |  |  | " | 5SH.R TRF | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#5ATR_2SRTRF | #5ATR 161KV 電抗器 輕故障 | OTHER |  |  |  |  | CDC | 574 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0942 |  |  | 3-3A-14 |  |  | " | 5SH.R 96B1 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#5ATR_2SR96B1 | #5ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 575 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0943 |  |  | 3-3A-15 |  |  | " | 5SH.R 96B2 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#5ATR_2SR96B2 | #5ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 576 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0944 |  |  | 3-3B-00 |  |  | " | 5SH.R 96D | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#5ATR_2SR96D | #5ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 577 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0945 |  |  | 3-3B-01 |  |  | " | 5SH.R 96P | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#5ATR_2SR96P | #5ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 578 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | 10A5Other | PF (請TPC確認) | DEL | [23 empty] | B1/E03_C | [16 empty] | 579 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | SHRA | 2SRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0928 |  |  | 3-3A-00 |  |  | #1 A.TR S.R | 1SH.R TRA | NO.1 A.TR二次側S.R |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#1ATR_2SRTRA | #1ATR 161KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 580 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | SHRF | 2SRTRF | B2,Element | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0929 |  |  | 3-3A-01 |  |  | " | 1SH.R TRF | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#1ATR_2SRTRF | #1ATR 161KV 電抗器 輕故障 | OTHER |  |  |  |  | CDC | 581 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0930 |  |  | 3-3A-02 |  |  | " | 1SH.R 96B1 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#1ATR_2SR96B1 | #1ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 582 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0931 |  |  | 3-3A-03 |  |  | " | 1SH.R 96B2 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#1ATR_2SR96B2 | #1ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 583 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0932 |  |  | 3-3A-04 |  |  | " | 1SH.R 96D | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#1ATR_2SR96D | #1ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 584 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0933 |  |  | 3-3A-05 |  |  | " | 1SH.R 96P | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#1ATR_2SR96P | #1ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 585 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | SHRA | 2SRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0934 |  |  | 3-3A-06 |  |  | #2 A.TR S.R | 2SH.R TRA | NO.2 A.TR二次側S.R |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#2ATR_2SRTRA | #2ATR 161KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 586 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | SHRF | 2SRTRF | B2,Element | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0935 |  |  | 3-3A-07 |  |  | " | 2SH.R TRF | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#2ATR_2SRTRF | #2ATR 161KV 電抗器 輕故障 | OTHER |  |  |  |  | CDC | 587 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0936 |  |  | 3-3A-08 |  |  | " | 2SH.R 96B1 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#2ATR_2SR96B1 | #2ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 588 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0937 |  |  | 3-3A-09 |  |  | " | 2SH.R 96B2 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#2ATR_2SR96B2 | #2ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 589 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0938 |  |  | 3-3A-10 |  |  | " | 2SH.R 96D | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#2ATR_2SR96D | #2ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 590 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0939 |  |  | 3-3A-11 |  |  | " | 2SH.R 96P | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#2ATR_2SR96P | #2ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 591 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | SHRA | 2SRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0946 |  |  | 3-3B-02 |  |  | #7 A.TR S.R | 7SH.R TRA | NO.7 A.TR二次側S.R |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#7ATR_2SRTRA | #7ATR 161KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 592 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | SHRF | 2SRTRF | B2,Element | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0947 |  |  | 3-3B-03 |  |  | " | 7SH.R TRF | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#7ATR_2SRTRF | #7ATR 161KV 電抗器 輕故障 | OTHER |  |  |  |  | CDC | 593 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0948 |  |  | 3-3B-04 |  |  | " | 7SH.R 96B1 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#7ATR_2SR96B1 | #7ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 594 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0949 |  |  | 3-3B-05 |  |  | " | 7SH.R 96B2 | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#7ATR_2SR96B2 | #7ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 595 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0950 |  |  | 3-3B-06 |  |  | " | 7SH.R 96D | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#7ATR_2SR96D | #7ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 596 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0951 |  |  | 3-3B-07 |  |  | " | 7SH.R 96P | " |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.#7ATR_2SR96P | #7ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 597 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0062 | 1-30-02 |  | 1-3E | 161KV | 87B1S | 161KV #1BUS 87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 598 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0063 | 1-30-03 |  | 1-3F | 161KV | 87B2S | 161KV #2BUS 87RY U/L |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 599 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 3-35-11 |  |  | 345kV #1,2Bus | RYFA1 | 345kV #1,2Bus RYFA第一套 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KVBUS_RYFA1 | 345KV #1,2BUS 第一套數位RY故障 | OTHER |  |  |  |  | CDC | 600 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 87CTFA1 | CTFA1 | Element | Status | 第1具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 3-35-12 |  |  | 345kV #1,2Bus | CTFA1 | 345kV #1,2Bus CTFA第一套 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KVBUS_CTFA1 | 345KV #1,2BUS 第一套CT回路故障 | OTHER |  |  |  |  | CDC | 601 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 1BUS | #1BUS |  | 1_87UL1 | 345#1B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0845 |  | 0387 | 3-34-13 |  | 4-03 | 345KV | #1BUS | 187B1S |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#1B_87UL1 | 345KV #1BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 602 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 2BUS | #2BUS |  | 1_87UL1 | 345#2B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0847 |  | 0388 | 3-34-15 |  | 4-04 | 345KV | #2BUS | 287B1S |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#2B_87UL1 | 345KV #2BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 603 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0899 |  |  | 3-38-03 |  |  | 345kV #1,2Bus | RYFA2 | 345kV #1,2Bus RYFA第二套 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KVBUS_RYFA2 | 345KV #1,2BUS 第二套數位RY故障 | OTHER |  |  |  |  | CDC | 604 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 87CTFA2 | CTFA2 | Element | Status | 第2具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0900 |  |  | 3-38-04 |  |  | 345kV #1,2Bus | CTFA2 | 345kV #1,2Bus CTFA第二套 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KVBUS_CTFA2 | 345KV #1,2BUS 第二套CT回路故障 | OTHER |  |  |  |  | CDC | 605 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 1BUS | #1BUS |  | 1_87UL2 | 345#1B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0846 |  | 0389 | 3-34-14 |  | 4-05 | 345KV | #1BUS | 187B2S |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#1B_87UL2 | 345KV #1BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 606 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 2BUS | #2BUS |  | 1_87UL2 | 345#2B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0848 |  | 0390 | 3-35-00 |  | 4-06 | 345KV | #2BUS | 287B2S |  |  | B2/E03_C | [8 empty] | 龍崎ES.345#2B_87UL2 | 345KV #2BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 607 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | RYFA | 斷路器失靈電驛故障 | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0558 |  |  | 1-32-14 |  |  | 161KV | BF_RYFA | 161KV斷路器失靈電驛故障 |  |  | B2/E03_A1 | [8 empty] | 龍崎ES.161KV_NBFRYFA | 161KV(N)斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 608 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RYFA | 斷路器失靈電驛故障 | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 3-35-05 |  |  | 345KV | BF_RYFA | 345KV斷路器失靈電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.345KV_NBFRYFA | 345KV(N)斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 609 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 1_87UL1 |  | B2,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0414 | 3-32-13 |  | 4-1E | #7 ATR | ON/OFF | #7ATR 第一套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_87UL1 | #7ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 610 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 1_87UL2 |  | B2,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0415 | 3-32-14 |  | 4-1F | #7 ATR | ON/OFF | #7ATR 第二套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_87UL2 | #7ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 611 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | 51Z_UL |  | B2,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0925 |  | 0416 | 3-39-13 |  | 4-20 | #7ATR | 51Z U/L | #7ATR 51Z RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_51ZUL | #7ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 612 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0927 |  | 0417 | 3-39-15 |  | 4-21 | #7ATR | 87U/L | #7ATR 電抗器(570) 87RY U/L |  |  | B3/E03_C | [8 empty] | 龍崎ES.#7ATR_570_87UL | #7ATR 電抗器(570) 87RY U/L | OTHER |  |  |  |  | CDC | 613 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0926 |  |  | 3-39-14 |  |  | #7ATR | RYFA | #7ATR 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_RYFA | #7ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 614 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | ATR_86A |  | B2,Element | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0924 |  |  | 3-39-12 |  |  | #7ATR | 86A | #7ATR 86(51Z/87/96) RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.#7ATR_86A | #7ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 615 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 1_87UL1 |  | B2,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0797 |  | 0406 | 3-31-13 |  | 4-16 | #2 ATR | ON/OFF | #2ATR 第一套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_87UL1 | #2ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 616 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 1_87UL2 |  | B2,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0407 | 3-31-14 |  | 4-17 | #2 ATR | ON/OFF | #2ATR 第二套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_87UL2 | #2ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 617 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | 51Z_UL |  | B2,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0917 |  | 0408 | 3-39-05 |  | 4-18 | #2ATR | 51Z U/L | #2ATR 51Z RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_51ZUL | #2ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 618 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0919 |  | 0409 | 3-39-07 |  | 4-19 | #2ATR | 87U/L | #2ATR 電抗器(520) 87RY U/L |  |  | B3/E03_C | [8 empty] | 龍崎ES.#2ATR_520_87UL | #2ATR 電抗器(520) 87RY U/L | OTHER |  |  |  |  | CDC | 619 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0918 |  |  | 3-39-06 |  |  | #2ATR | RYFA | #2ATR 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_RYFA | #2ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 620 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | ATR_86A |  | B2,Element | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0916 |  |  | 3-39-04 |  |  | #2ATR | 86A | #2ATR 86(51Z/87/96) RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.#2ATR_86A | #2ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 621 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 1_87UL1 |  | B2,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0410 | 3-30-02 |  | 4-1A | #5 ATR | ON/OFF | #5ATR 第一套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_87UL1 | #5ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 622 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 1_87UL2 |  | B2,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0411 | 3-30-03 |  | 4-1B | #5 ATR | ON/OFF | #5ATR 第二套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_87UL2 | #5ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 623 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | 51Z_UL |  | B2,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0921 |  | 0412 | 3-39-09 |  | 4-1C | #5ATR | 51Z U/L | #5ATR 51Z RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_51ZUL | #5ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 624 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0923 |  | 0413 | 3-39-11 |  | 4-1D | #5ATR | 87U/L | #5ATR 電抗器(550) 87RY U/L |  |  | B3/E03_C | [8 empty] | 龍崎ES.#5ATR_550_87UL | #5ATR 電抗器(550) 87RY U/L | OTHER |  |  |  |  | CDC | 625 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 3-39-10 |  |  | #5ATR | RYFA | #5ATR 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_RYFA | #5ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 626 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | ATR_86A |  | B2,Element | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0920 |  |  | 3-39-08 |  |  | #5ATR | 86A | #5ATR 86(51Z/87/96) RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.#5ATR_86A | #5ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 627 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 1_87UL1 |  | B2,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0395 | 3-30-13 |  | 4-0B | #1 ATR | ON/OFF | #1ATR 第一套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_87UL1 | #1ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 628 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 1_87UL2 |  | B2,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0396 | 3-30-14 |  | 4-0C | #1 ATR | ON/OFF | #1ATR 第二套87RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_87UL2 | #1ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 629 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | 51Z_UL |  | B2,Element | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0906 |  | 0397 | 3-38-10 |  | 4-0D | #1ATR | 51Z U/L | #1ATR 51Z RY U/L |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_51ZUL | #1ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 630 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0908 |  | 0398 | 3-38-12 |  | 4-0E | #1ATR | 87U/L | #1ATR 電抗器(510) 87RY U/L |  |  | B3/E03_C | [8 empty] | 龍崎ES.#1ATR_510_87UL | #1ATR 電抗器(510) 87RY U/L | OTHER |  |  |  |  | CDC | 631 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0907 |  |  | 3-38-11 |  |  | #1ATR | RYFA | #1ATR 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_RYFA | #1ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 632 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | ATR_86A |  | B2,Element | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0905 |  |  | 3-38-09 |  |  | #1ATR | 86A | #1ATR 86(51Z/87/96) RY |  |  | B2/E03_C | [8 empty] | 龍崎ES.#1ATR_86A | #1ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 633 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RTU_MCT | N_MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0355 |  |  | 3-0C-03 |  |  | 345_N_RTU | MCT_ SOE | 345 N RTU MASTER RY SOE |  |  | B2/E03_C | [15 empty] | CDC | 634 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E03 | 龍崎ES | 161 | 161kV | ComPoint |  |  | RTU_MCT | N_MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 161_N_RTU | MCT_ SOE | 161 N RTU MASTER RY SOE |  |  | B2/E03_A1 | [15 empty] | CDC | 635 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E03 | 龍崎ES | 345 | 345kV | 3910 | 備用線(3910) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 3-34-05 |  |  | 3910 | RYFA | 備用線(3910) 數位電驛故障 |  |  | B2/E03_C | [8 empty] | 龍崎ES.3910_RYFA | 備用線(3910)數位電驛故障 | OTHER |  |  |  |  | CDC | 636 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | ComPoint |  |  | CBA |  | Element | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 3-35-08 |  |  | 33kV | CBA | 33kV CB重故障 |  |  | ELEM/E03_C | [8 empty] | 龍崎ES.33KV_N_CBA | 33KV(N) CB重故障 | OTHER |  |  |  |  | CDC | 637 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | ComPoint |  |  | CBF |  | Element | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0857 |  |  | 3-35-09 |  |  | 33kV | CBF | 33kV CB輕故障 |  |  | ELEM/E03_C | [8 empty] | 龍崎ES.33KV_N_CBF | 33KV(N) CB輕故障 | OTHER |  |  |  |  | CDC | 638 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | ComPoint |  |  | COMT |  | Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 3-35-10 |  |  | 33kV | COMT | 33kV COMT |  |  | B2/E03_C | [8 empty] | 龍崎ES.33KV_N_COMT | 33KV(N) 空壓機運轉超時警報 | OTHER |  |  |  |  | CDC | 639 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | TE0 | 391TE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 390 | #1SSTR(390) |  | LE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 510 | #1SHR(510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 520 | #2SHR(520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 570 | #7SHR(570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 550 | #5SHR(550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 590 | #3SSTR(590) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 33 | 33kV | 590 | #3SSTR(590) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/E03_C | [12 empty] | 龍崎ES.161KV_12BUS_KV | 161KV #1,#2 BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: E03/161/1BUS/V; OPRD2: E03/161/2BUS/V
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | Vbs8 | [9 empty] | B1/E03_C | [15 empty] | BEST_SOURCE_35KV_1 |  | v_best_345_12 | OPRD1: E03/345/1BUS/V; OPRD2: E03/345/2BUS/V
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/E03_C | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: E03/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: E03/0/CalcPoint/Vbs8; OPRD9: NULL
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/E03_C | [15 empty] | TOT_1MTR_CAL |  | p_sum_17 | OPRD1: E03/161/1510/MW; OPRD2: E03/161/1520/MW; OPRD3: E03/161/1530/MW; OPRD4: E03/161/1540/MW; OPRD5: E03/161/1550/MW; OPRD6: E03/161/1570/MW; OPRD7: E03/345/3510/MW; OPRD8: E03/345/3530/MW; OPRD9: E03/345/3540/MW; OPRD10: E03/345/3560/MW; OPRD11: E03/345/3570/MW; OPRD12: E03/345/3610/MW; OPRD13: E03/345/3630/MW; OPRD14: E03/345/3640/MW; OPRD15: E03/345/3660/MW; OPRD16: E03/345/3690/MW; OPRD17: E03/345/3930/MW
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/E03_C | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: E03/0/CalcPoint/OPRN2_MW
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/E03_C | [17 empty] | none
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/E03_C | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: E03/0/CalcPoint/OPRN1; OPRD2: E03/0/CalcPoint/OPRN2; OPRD3: E03/0/CalcPoint/PRFL_UL
E03 | 龍崎ES |  |  | 1ATR | 1ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.#1ATR_AMP | #1ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E03/345/3660/MW; OPRD2: E03/345/3660/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES |  |  | 2ATR | 2ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.#2ATR_AMP | #2ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E03/345/3690/MW; OPRD2: E03/345/3690/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES |  |  | 5ATR | 5ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.#5ATR_AMP | #5ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E03/345/3570/MW; OPRD2: E03/345/3570/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES |  |  | 7ATR | 7ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.#7ATR_AMP | #7ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E03/345/3930/MW; OPRD2: E03/345/3930/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎～山上一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_A1 | [12 empty] | 龍崎ES.1510_AMP | 龍崎山上一路 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: E03/161/1510/MW; OPRD2: E03/161/1510/MVAR; OPRD3: E03/0/CalcPoint/Vbs4
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎～山上二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_A1 | [12 empty] | 龍崎ES.1520_AMP | 龍崎山上二路 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: E03/161/1520/MW; OPRD2: E03/161/1520/MVAR; OPRD3: E03/0/CalcPoint/Vbs4
E03 | 龍崎ES | 161 | 161kV | 1530 | 龍崎～山上、二甲三路(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_A1 | [12 empty] | 龍崎ES.1530_AMP | 山上二甲三路 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E03/161/1530/MW; OPRD2: E03/161/1530/MVAR; OPRD3: E03/0/CalcPoint/Vbs4
E03 | 龍崎ES | 161 | 161kV | 1540 | 龍崎～山上、二甲四路(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_A1 | [12 empty] | 龍崎ES.1540_AMP | 山上二甲四路 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E03/161/1540/MW; OPRD2: E03/161/1540/MVAR; OPRD3: E03/0/CalcPoint/Vbs4
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_A1 | [12 empty] | 龍崎ES.1550_AMP | 龍崎台南山線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: E03/161/1550/MW; OPRD2: E03/161/1550/MVAR; OPRD3: E03/0/CalcPoint/Vbs4
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_A1 | [12 empty] | 龍崎ES.1570_AMP | 龍崎台南海線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: E03/161/1570/MW; OPRD2: E03/161/1570/MVAR; OPRD3: E03/0/CalcPoint/Vbs4
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科～龍崎一路(3510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3510_AMP | 南科一路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E03/345/3510/MW; OPRD2: E03/345/3510/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 345 | 345kV | 3530 | 龍崎(北)～龍崎(南)臨時線(3530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3530_AMP | 北南臨時線(3530) AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E03/345/3530/MW; OPRD2: E03/345/3530/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 345 | 345kV | 3540 | 龍崎～瀰力二路(3540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3540_AMP | 瀰力二路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E03/345/3540/MW; OPRD2: E03/345/3540/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪～龍崎海線(3560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3560_AMP | 天輪海線 AMP | LINE345 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E03/345/3560/MW; OPRD2: E03/345/3560/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科～龍崎二路(3610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3610_AMP | 南科二路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E03/345/3610/MW; OPRD2: E03/345/3610/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達～龍崎一路(3630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3630_AMP | 興達一路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E03/345/3630/MW; OPRD2: E03/345/3630/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北～龍崎紅線(3640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E03_C | [12 empty] | 龍崎ES.3640_AMP | 路北紅線 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E03/345/3640/MW; OPRD2: E03/345/3640/MVAR; OPRD3: E03/0/CalcPoint/Vbs8
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E03_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 龍崎ES.#1ATR_MVA | #1ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E03/345/3660/MW; OPRD2: E03/345/3660/MVAR
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E03_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 龍崎ES.#2ATR_MVA | #2ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E03/345/3690/MW; OPRD2: E03/345/3690/MVAR
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E03_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 龍崎ES.#5ATR_MVA | #5ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E03/345/3570/MW; OPRD2: E03/345/3570/MVAR
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E03_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 龍崎ES.#7ATR_MVA | #7ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E03/345/3930/MW; OPRD2: E03/345/3930/MVAR
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | LOAD | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#1ATR_LOAD | #1ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E03//1ATR/MVA; OPRD2: 500
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | LOAD | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#2ATR_LOAD | #2ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E03//2ATR/MVA; OPRD2: 500
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | LOAD | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#5ATR_LOAD | #5ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E03//5ATR/MVA; OPRD2: 500
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | LOAD | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#7ATR_LOAD | #7ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E03//7ATR/MVA; OPRD2: 500
E03 | 龍崎ES |  |  | 1ATR | #1ATR |  | PF | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#1ATR_PF | #1ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E03/345/3660/MW; OPRD2: E03/345/3660/MVAR
E03 | 龍崎ES |  |  | 2ATR | #2ATR |  | PF | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#2ATR_PF | #2ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E03/345/3690/MW; OPRD2: E03/345/3690/MVAR
E03 | 龍崎ES |  |  | 5ATR | #5ATR |  | PF | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#5ATR_PF | #5ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E03/345/3570/MW; OPRD2: E03/345/3570/MVAR
E03 | 龍崎ES |  |  | 7ATR | #7ATR |  | PF | [9 empty] | B2/E03_C | [12 empty] | 龍崎ES.#7ATR_PF | #7ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E03/345/3930/MW; OPRD2: E03/345/3930/MVAR
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/E03_C | [15 empty] | STATION_FAULT_1 |  | com_alarm_42 | E03//1ATR/96D | E03//1ATR/TRA | E03//1ATR/63Q | E03//1ATR/96B2 | E03//1ATR/96B1 | E03//1ATR/96PA | E03//1ATR/51ZA | E03//2ATR/96B2 | E03//2ATR/TRA | E03//2ATR/96D | E03//2ATR/96PA | E03//2ATR/51ZA | E03//2ATR/63Q | E03//2ATR/96B1 | E03//5ATR/96B2 | E03//5ATR/TRA | E03//5ATR/63Q | E03//5ATR/96B1 | E03//5ATR/96D | E03//5ATR/51ZA | E03//5ATR/96PA | E03//7ATR/96B1 | E03//7ATR/96B2 | E03//7ATR/TRA | E03//7ATR/96PA | E03//7ATR/51ZA | E03//7ATR/63Q | E03//7ATR/96D | E03/161/1BUS/87A | E03/161/2BUS/87A | E03/33/1ATR/96D | E03/33/1ATR/96B2 | E03/33/1ATR/96B1 | E03/33/2ATR/96D | E03/33/2ATR/96B2 | E03/33/2ATR/96B1 | E03/33/5ATR/96B1 | E03/33/5ATR/96B2 | E03/33/5ATR/96D | E03/33/7ATR/96B1 | E03/33/7ATR/96B2 | E03/33/7ATR/96D
E03 | 龍崎ES | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/E03_C | [15 empty] | STATION_FAULT_1 |  | com_alarm_4 | OPRD1: E03//1ATR/TRF; OPRD2: E03//2ATR/TRF; OPRD3: E03//5ATR/TRF; OPRD4: E03//7ATR/TRF
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 1_DCV_P | #1直流P電源 |  | MvMoment | #1 直流P電源電壓 |  | Y |  | AI |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/1_DCV_P
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 1_DCV_N | #1直流N電源 |  | MvMoment | #1 直流N電源電壓 |  | Y |  | AI |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/1_DCV_N
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 2_DCV_P | #2直流P電源 |  | MvMoment | #2 直流P電源電壓 |  | Y |  | AI |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/2_DCV_P
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 2_DCV_N | #2直流N電源 |  | MvMoment | #2 直流N電源電壓 |  | Y |  | AI |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/2_DCV_N
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/ACB1
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/ACB2
E03 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | BFS | N_BFS |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/161/ComPoint/BFS
E03 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | BFA | N_BFA |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/161/ComPoint/BFA
E03 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | CBA | N_CBA |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/161/ComPoint/CBA
E03 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | CBF | N_CBF |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/161/ComPoint/CBF
E03 | 龍崎ES | 345 | 345kV | ComPoint_C |  |  | ABS_89A | N_89A |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/345/ComPoint/ABS_89A
E03 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | ABS_89A | N_89A |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/161/ComPoint/ABS_89A
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | ACBT1 | ACB_TIE1 |  | Status | 所內電源ACB TIE1 | Close/Open | Y | 3 | DI-SP |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/ACBT1
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | CHG1 | 充電機故障_N |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/CHG1
E03 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | DCE | 直流電源DCE_N |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E03_C | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/DCE
E03 | 龍崎ES | 0 |  | StaDev_D1 | 所內設施 |  | DCE | 直流電源DCE_N |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E03_D1 | [17 empty] | lamp2CC | OPRD1: E03/0/StaDev/DCE

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E03 | 龍崎ES | 161 | 161kV | _12BUS | #1,#2 |  | V | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_12BUS_KV | 161KV #1,#2 BUS BEST SOURCE | BUS | E03/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
E03 | 龍崎ES | 345 | 345kV | _12BUS | #1,#2 |  | V | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_12BUS_KV | 345KV #1,#2 BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_345KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_AMP | 南科一路 AMP | LINE345 | E03/345/3510/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3530_AMP | 北南臨時線(3530) AMP | LINE345 | E03/345/3530/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3540_AMP | 瀰力二路 AMP | LINE345 | E03/345/3540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3560_AMP | 天輪海線 AMP | LINE345 | E03/345/3560/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_AMP | 南科二路 AMP | LINE345 | E03/345/3610/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_AMP | 興達一路 AMP | LINE345 | E03/345/3630/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_AMP | 路北紅線 AMP | LINE345 | E03/345/3640/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_AMP | 龍崎山上一路 AMP | LINE161 | E03/161/1510/I |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_AMP | 龍崎山上二路 AMP | LINE161 | E03/161/1520/I |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1530_AMP | 山上二甲三路 AMP | LINE161 | E03/161/1530/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1540_AMP | 山上二甲四路 AMP | LINE161 | E03/161/1540/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1570_AMP | 龍崎台南海線 AMP | LINE161 | E03/161/1570/I |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_MVA | #1ATR二次側 MVA | ATR | E03//1ATR/MVA |  | MVA_CAL |  |  | 16 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_LOAD | #1ATR 負載率 | ATR | E03//1ATR/Loading |  | TR_LOAD_500 |  |  | 17 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_PF | #1ATR 功率因素 | ATR | E03//1ATR/PF |  | RPDC_PF_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_AMP | #1ATR 二次側 AMP | ATR | E03//1ATR/I |  | AMP_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_MVA | #2ATR二次側 MVA | ATR | E03//2ATR/MVA |  | MVA_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_LOAD | #2ATR 負載率 | ATR | E03//2ATR/Loading |  | TR_LOAD_500 |  |  | 21 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_PF | #2ATR 功率因素 | ATR | E03//2ATR/PF |  | RPDC_PF_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_AMP | #2ATR 二次側 AMP | ATR | E03//2ATR/I |  | AMP_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_MVA | #5ATR二次側 MVA | ATR | E03//5ATR/MVA |  | MVA_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_LOAD | #5ATR 負載率 | ATR | E03//5ATR/Loading |  | TR_LOAD_500 |  |  | 25 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_PF | #5ATR 功率因素 | ATR | E03//5ATR/PF |  | RPDC_PF_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_AMP | #5ATR 二次側 AMP | ATR | E03//5ATR/I |  | AMP_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_MVA | #7ATR二次側 MVA | ATR | E03//7ATR/MVA |  | MVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_LOAD | #7ATR 負載率 | ATR | E03//7ATR/Loading |  | TR_LOAD_500 |  |  | 29 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_PF | #7ATR 功率因素 | ATR | E03//7ATR/PF |  | RPDC_PF_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_AMP | #7ATR 二次側 AMP | ATR | E03//7ATR/I |  | AMP_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | _34BUS | #3,#4 |  | V | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_34BUS_KV | 161KV #3,#4 BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_161KV_2 |  |  | 32 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
E03 | 龍崎ES | 345 | 345kV | _34BUS | #3,#4 |  | V | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_34BUS_KV | 345KV #3,#4 BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_345KV_2 |  |  | 33 | CalcAIPoint | [21 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000
E03 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_AMP | 天輪山線 AMP | LINE345 |  |  | AMP_CAL |  |  | 34 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E03 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_AMP | 嘉民紅線 AMP | LINE345 |  |  | AMP_CAL |  |  | 35 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_AMP | 北南臨時線(3770) AMP | LINE345 |  |  | AMP_CAL |  |  | 36 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_AMP | 仁武山線 AMP | LINE345 |  |  | AMP_CAL |  |  | 37 | CalcAIPoint | [21 empty] | C30R2020 | 1818.000000 | 1818.000000 | 2020.000000 | 3000.000000 | 1.560000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_AMP | 興達三路 AMP | LINE345 |  |  | AMP_CAL |  |  | 38 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_AMP | 路北白線 AMP | LINE345 |  |  | AMP_CAL |  |  | 39 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | I | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_AMP | 仁武海線 AMP | LINE345 |  |  | AMP_CAL |  |  | 40 | CalcAIPoint | [21 empty] | C30R2020 | 1818.000000 | 1818.000000 | 2020.000000 | 3000.000000 | 1.560000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1640_AMP | 岡山嘉峰線 AMP | LINE161 |  |  | AMP_CAL |  |  | 41 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1710_AMP | 龍崎路園線 AMP | LINE161 |  |  | AMP_CAL |  |  | 42 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1720_AMP | 龍崎岡山二路 AMP | LINE161 |  |  | AMP_CAL |  |  | 43 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1730_AMP | 龍崎岡山三路 AMP | LINE161 |  |  | AMP_CAL |  |  | 44 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 3ATR | #3ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_MVA | #3ATR二次側 MVA | ATR |  |  | MVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_LOAD | #3ATR 負載率 | ATR |  |  | TR_LOAD_500 |  |  | 46 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_PF | #3ATR 功率因素 | ATR |  |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_AMP | #3ATR 二次側 AMP | ATR |  |  | AMP_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 4ATR | #4ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_MVA | #4ATR二次側 MVA | ATR |  |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_LOAD | #4ATR 負載率 | ATR |  |  | TR_LOAD_500 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_PF | #4ATR 功率因素 | ATR |  |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_AMP | #4ATR 二次側 AMP | ATR |  |  | AMP_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 6ATR | #6ATR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_MVA | #6ATR二次側 MVA | ATR |  |  | MVA_CAL |  |  | 53 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_LOAD | #6ATR 負載率 | ATR |  |  | TR_LOAD_500 |  |  | 54 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E03 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | PF | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_PF | #6ATR 功率因素 | ATR |  |  | RPDC_PF_CAL |  |  | 55 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E03 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_AMP | #6ATR 二次側 AMP | ATR |  |  | AMP_CAL |  |  | 56 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E03 | 龍崎ES | 0 |  | TRTOT | 龍崎主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 龍崎ES.TRTOT_MW | 龍崎主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_7 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 0 |  | STOTAL | 龍崎南轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 龍崎ES.STOTAL_MW | 龍崎南轄區瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 0 |  | STOTAL | 龍崎南轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 龍崎ES.STOTAL_MVAR | 龍崎南轄區瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 0 |  | NTOTAL | 龍崎北轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 龍崎ES.NTOTAL_MW | 龍崎北轄區瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 0 |  | NTOTAL | 龍崎北轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 龍崎ES.NTOTAL_MVAR | 龍崎北轄區瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_4 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 0 |  | NIPPTOTAL | 龍崎北轄區IPP瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 龍崎ES.NIPPTOTAL_MW | 龍崎北轄區IPP瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 0 |  | NIPPTOTAL | 龍崎北轄區IPP瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 龍崎ES.NIPPTOTAL_MVAR | 龍崎北轄區IPP瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E03 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1630_AMP | 龍崎聯錏線 AMP | LINE161 |  |  | AMP_CAL |  |  | 64 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.1550_AMP | 龍崎台南山線 AMP | LINE161 | E03/161/1550/I |  | AMP_CAL |  |  | 65 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E03 | 龍崎ES | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 龍崎ES.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_ES_8 |  |  | 66 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510_AMP | 南科一路 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_AMP_A | 南科一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 67 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530_AMP | 北南臨時線(3530) | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3530_AMP_A | 北南臨時線(3530) AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 68 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540_AMP | 瀰力二路 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3540_AMP_A | 瀰力二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 69 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560_AMP | 天輪海線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3560_AMP_A | 天輪海線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 70 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610_AMP | 南科二路 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_AMP_A | 南科二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 71 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630_AMP | 興達一路 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_AMP_A | 興達一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 72 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640_AMP | 路北紅線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_AMP_A | 路北紅線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 73 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510_AMP | 龍崎山上一路 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_AMP_A | 龍崎山上一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 74 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520_AMP | 龍崎山上二路 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_AMP_A | 龍崎山上二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530_AMP | 山上二甲三路 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1530_AMP_A | 山上二甲三路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540_AMP | 山上二甲四路 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1540_AMP_A | 山上二甲四路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1570_AMP | 龍崎台南海線 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1570_AMP_A | 龍崎台南海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR_MVA | #1ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_MVA_A | #1ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_PERM | #1ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR_MVA | #2ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_MVA_A | #2ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_PERM | #2ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 82 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR_MVA | #5ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_MVA_A | #5ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_PERM | #5ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR_MVA | #7ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_MVA_A | #7ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_PERM | #7ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3740_AMP | 天輪山線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_AMP_A | 天輪山線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3760_AMP | 嘉民紅線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_AMP_A | 嘉民紅線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3770_AMP | 北南臨時線(3770) | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_AMP_A | 北南臨時線(3770) AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3790_AMP | 仁武山線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_AMP_A | 仁武山線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3860_AMP | 興達三路 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_AMP_A | 興達三路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3870_AMP | 路北白線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_AMP_A | 路北白線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3890_AMP | 仁武海線 | [27 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_AMP_A | 仁武海線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1640_AMP | 岡山嘉峰線 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1640_AMP_A | 岡山嘉峰線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1710_AMP | 龍崎路園線 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1710_AMP_A | 龍崎路園線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1720_AMP | 龍崎岡山二路 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1720_AMP_A | 龍崎岡山二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1730_AMP | 龍崎岡山三路 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1730_AMP_A | 龍崎岡山三路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 3ATR_MVA | #3ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_MVA_A | #3ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_PERM | #3ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 4ATR_MVA | #4ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_MVA_A | #4ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_PERM | #4ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 6ATR_MVA | #6ATR | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_MVA_A | #6ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | PERM | [25 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_PERM | #6ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1630_AMP | 龍崎聯錏線 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1630_AMP_A | 龍崎聯錏線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550_AMP | 龍崎台南山線 | [27 empty] | ADCS_S | [8 empty] | 龍崎ES.1550_AMP_A | 龍崎台南山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E03 | 龍崎ES | 345 | 345kV | 1BUS | #1BUS |  | V | [17 empty] | 3-82 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.345KV#1BUS_KV | 345KV #1BUS KV | BUS | E03/345/1BUS/V |  |  |  | CDC | 106 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | MW | [17 empty] | 3-84 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3510_MW | 南科一路 MW | LINE345 | E03/345/3510/MW |  |  |  | CDC | 107 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | MVAR | [17 empty] | 3-85 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3510_MVAR | 南科一路 MVAR | LINE345 | E03/345/3510/MVAR |  |  |  | CDC | 108 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | MW | [17 empty] | 3-87 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3530_MW | 北南臨時線(3530) MW | LINE345 | E03/345/3530/MW |  |  |  | CDC | 109 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | MVAR | [17 empty] | 3-88 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3530_MVAR | 北南臨時線(3530) MVAR | LINE345 | E03/345/3530/MVAR |  |  |  | CDC | 110 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | MW | [17 empty] | 3-8A | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3540_MW | 瀰力二路 MW | LINE345 | E03/345/3540/MW |  |  |  | CDC | 111 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | MVAR | [17 empty] | 3-8B | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3540_MVAR | 瀰力二路 MVAR | LINE345 | E03/345/3540/MVAR |  |  |  | CDC | 112 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | MW | [17 empty] | 3-8D | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3560_MW | 天輪海線 MW | LINE345 | E03/345/3560/MW |  |  |  | CDC | 113 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | MVAR | [17 empty] | 3-8E | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3560_MVAR | 天輪海線 MVAR | LINE345 | E03/345/3560/MVAR |  |  |  | CDC | 114 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | MW | [17 empty] | 3-90 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3610_MW | 南科二路 MW | LINE345 | E03/345/3610/MW |  |  |  | CDC | 115 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | MVAR | [17 empty] | 3-91 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3610_MVAR | 南科二路 MVAR | LINE345 | E03/345/3610/MVAR |  |  |  | CDC | 116 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | MW | [17 empty] | 3-93 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3630_MW | 興達一路 MW | LINE345 | E03/345/3630/MW |  |  |  | CDC | 117 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | MVAR | [17 empty] | 3-94 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3630_MVAR | 興達一路 MVAR | LINE345 | E03/345/3630/MVAR |  |  |  | CDC | 118 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | MW | [17 empty] | 3-96 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3640_MW | 路北紅線 MW | LINE345 | E03/345/3640/MW |  |  |  | CDC | 119 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | MVAR | [17 empty] | 3-97 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3640_MVAR | 路北紅線 MVAR | LINE345 | E03/345/3640/MVAR |  |  |  | CDC | 120 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | E03/0/RTU/ADCH1 |  |  |  | CDC | 121 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | E03/0/RTU/ADCH2 |  |  |  | CDC | 122 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | E03/0/RTU/ADCH3 |  |  |  | CDC | 123 | GENERICAIPoint | ES003_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | E03/0/RTU/ADCH4 |  |  |  | CDC | 124 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | E03/0/RTU/ADCH5 |  |  |  | CDC | 125 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCH6 | [17 empty] | 4-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCH6 | AI 90%參考點 ADCH6 | OTHER | E03/0/RTU/ADCH6 |  |  |  | CDC | 126 | GENERICAIPoint | ES003_L4 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | E03/0/RTU/ADCL1 |  |  |  | CDC | 127 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | E03/0/RTU/ADCL2 |  |  |  | CDC | 128 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | E03/0/RTU/ADCL3 |  |  |  | CDC | 129 | GENERICAIPoint | ES003_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | E03/0/RTU/ADCL4 |  |  |  | CDC | 130 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | E03/0/RTU/ADCL5 |  |  |  | CDC | 131 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 0 |  | AI | AI |  | ADCL6 | [17 empty] | 4-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.AI_ADCL6 | AI 10%參考點 ADCL6 | OTHER | E03/0/RTU/ADCL6 |  |  |  | CDC | 132 | GENERICAIPoint | ES003_L4 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.161KV#1BUS_KV | 161KV #1BUS KV | BUS | E03/161/1BUS/V |  |  |  | CDC | 133 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.161KV#2BUS_KV | 161KV #2BUS KV | BUS | E03/161/2BUS/V |  |  |  | CDC | 134 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E03 | 龍崎ES | 345 | 345kV | 2BUS | #2BUS |  | V | [17 empty] | 3-83 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.345KV#2BUS_KV | 345KV #2BUS KV | BUS | E03/345/2BUS/V |  |  |  | CDC | 135 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3510LPD | 南科一路(3510) |  | V | [17 empty] | 3-86 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3510LPD_KV | 南科一路(3510) LPD KV | LINE345 | E03/345/3510/V |  |  |  | CDC | 136 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3530LPD | 北南臨時線(3530) |  | V | [17 empty] | 3-89 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3530LPD_KV | 北南臨時線(3530) LPD KV | LINE345 | E03/345/3530/V |  |  |  | CDC | 137 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3540LPD | 瀰力二路(3540) |  | V | [17 empty] | 3-8C | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3540LPD_KV | 瀰力二路(3540) LPD KV | LINE345 | E03/345/3540/V |  |  |  | CDC | 138 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3560LPD | 天輪海線(3560) |  | V | [17 empty] | 3-8F | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3560LPD_KV | 天輪海線(3560) LPD KV | LINE345 | E03/345/3560/V |  |  |  | CDC | 139 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3610LPD | 南科二路(3610) |  | V | [17 empty] | 3-92 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3610LPD_KV | 南科二路(3610) LPD KV | LINE345 | E03/345/3610/V |  |  |  | CDC | 140 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3630LPD | 興達一路(3630) |  | V | [17 empty] | 3-95 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3630LPD_KV | 興達一路(3630) LPD KV | LINE345 | E03/345/3630/V |  |  |  | CDC | 141 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 345 | 345kV | 3640LPD | 路北紅線(3640) |  | V | [17 empty] | 3-98 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3640LPD_KV | 路北紅線(3640) LPD KV | LINE345 | E03/345/3640/V |  |  |  | CDC | 142 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1510_MW | 龍崎山上一路 MW | LINE161 | E03/161/1510/MW |  |  |  | CDC | 143 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1510_MVAR | 龍崎山上一路 MVAR | LINE161 | E03/161/1510/MVAR |  |  |  | CDC | 144 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1510LPD | 龍崎山上一路(1510) |  | V | [17 empty] | 1-88 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1510LPD_KV | 龍崎山上一路(1510) LPD KV | LINE161 | E03/161/1510/V |  |  |  | CDC | 145 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | MW | [17 empty] | 1-89 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1520_MW | 龍崎山上二路 MW | LINE161 | E03/161/1520/MW |  |  |  | CDC | 146 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | MVAR | [17 empty] | 1-8A | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1520_MVAR | 龍崎山上二路 MVAR | LINE161 | E03/161/1520/MVAR |  |  |  | CDC | 147 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1520LPD | 龍崎山上二路(1520) |  | V | [17 empty] | 1-8B | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1520LPD_KV | 龍崎山上二路(1520) LPD KV | LINE161 | E03/161/1520/V |  |  |  | CDC | 148 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1530_MW | 山上二甲三路 MW | LINE161 | E03/161/1530/MW |  |  |  | CDC | 149 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1530_MVAR | 山上二甲三路 MVAR | LINE161 | E03/161/1530/MVAR |  |  |  | CDC | 150 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1530LPD | 山上二甲三路(1530) |  | V | [17 empty] | 1-8E | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1530LPD_KV | 山上二甲三路(1530) LPD KV | LINE161 | E03/161/1530/V |  |  |  | CDC | 151 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | MW | [17 empty] | 1-8F | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1540_MW | 山上二甲四路 MW | LINE161 | E03/161/1540/MW |  |  |  | CDC | 152 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | MVAR | [17 empty] | 1-90 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1540_MVAR | 山上二甲四路 MVAR | LINE161 | E03/161/1540/MVAR |  |  |  | CDC | 153 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1540LPD | 山上二甲四路(1540) |  | V | [17 empty] | 1-91 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1540LPD_KV | 山上二甲四路(1540) LPD KV | LINE161 | E03/161/1540/V |  |  |  | CDC | 154 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1570_MW | 龍崎台南海線 MW | LINE161 | E03/161/1570/MW |  |  |  | CDC | 155 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1570_MVAR | 龍崎台南海線 MVAR | LINE161 | E03/161/1570/MVAR |  |  |  | CDC | 156 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1570LPD | 龍崎台南海線(1570) |  | V | [17 empty] | 1-97 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1570LPD_KV | 龍崎台南海線(1570) LPD KV | LINE161 | E03/161/1570/V |  |  |  | CDC | 157 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR二次側 |  | MW | [17 empty] | 1-98 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#1ATR_MW | #1ATR二次側 MW | ATR | E03/345/3660/MW |  |  |  | CDC | 158 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR二次側 |  | MVAR | [17 empty] | 1-99 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#1ATR_MVAR | #1ATR二次側 MVAR | ATR | E03/345/3660/MVAR |  |  |  | CDC | 159 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | TapPosMv | [17 empty] | 3-9B |  | 3-66 |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_TAP | #1ATR OLTC TAP | ATR | E03//1ATR/TapPosMv |  |  |  | CDC | 160 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES | 0 |  | 1ATR_OIL | #1ATR |  | R | [17 empty] | 3-9D | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_OIL_R | #1ATR R相油溫 | ATR | E03//1ATR/Oil_R |  |  |  | CDC | 161 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 1ATR_COIL | #1ATR |  | R | [17 empty] | 3-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_COIL_R | #1ATR R相線溫 | ATR | E03//1ATR/Coil_R |  |  |  | CDC | 162 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 1ATR_OIL | #1ATR |  | S | [17 empty] | 3-9F | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_OIL_S | #1ATR S相油溫 | ATR | E03//1ATR/Oil_S |  |  |  | CDC | 163 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 1ATR_COIL | #1ATR |  | S | [17 empty] | 3-9E | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_COIL_S | #1ATR S相線溫 | ATR | E03//1ATR/Coil_S |  |  |  | CDC | 164 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 1ATR_OIL | #1ATR |  | T | [17 empty] | 3-A1 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_OIL_T | #1ATR T相油溫 | ATR | E03//1ATR/Oil_T |  |  |  | CDC | 165 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 1ATR_COIL | #1ATR |  | T | [17 empty] | 3-A0 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#1ATR_COIL_T | #1ATR T相線溫 | ATR | E03//1ATR/Coil_T |  |  |  | CDC | 166 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR二次側 |  | MW | [17 empty] | 1-9A | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#2ATR_MW | #2ATR二次側 MW | ATR | E03/345/3690/MW |  |  |  | CDC | 167 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR二次側 |  | MVAR | [17 empty] | 1-9B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#2ATR_MVAR | #2ATR二次側 MVAR | ATR | E03/345/3690/MVAR |  |  |  | CDC | 168 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | TapPosMv | [17 empty] | 3-A4 |  | 3-6A |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_TAP | #2ATR OLTC TAP | ATR | E03//2ATR/TapPosMv |  |  |  | CDC | 169 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES | 0 |  | 2ATR_OIL | #2ATR |  | R | [17 empty] | 3-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_OIL_R | #2ATR R相油溫 | ATR | E03//2ATR/Oil_R |  |  |  | CDC | 170 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_COIL | #2ATR |  | R | [17 empty] | 3-A5 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_COIL_R | #2ATR R相線溫 | ATR | E03//2ATR/Coil_R |  |  |  | CDC | 171 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_OIL | #2ATR |  | S | [17 empty] | 3-A8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_OIL_S | #2ATR S相油溫 | ATR | E03//2ATR/Oil_S |  |  |  | CDC | 172 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_COIL | #2ATR |  | S | [17 empty] | 3-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_COIL_S | #2ATR S相線溫 | ATR | E03//2ATR/Coil_S |  |  |  | CDC | 173 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_OIL | #2ATR |  | T | [17 empty] | 3-AA | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_OIL_T | #2ATR T相油溫 | ATR | E03//2ATR/Oil_T |  |  |  | CDC | 174 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_COIL | #2ATR |  | T | [17 empty] | 3-A9 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#2ATR_COIL_T | #2ATR T相線溫 | ATR | E03//2ATR/Coil_T |  |  |  | CDC | 175 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR二次側 |  | MW | [17 empty] | 1-9C | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#5ATR_MW | #5ATR二次側 MW | ATR | E03/345/3570/MW |  |  |  | CDC | 176 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR二次側 |  | MVAR | [17 empty] | 1-9D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#5ATR_MVAR | #5ATR二次側 MVAR | ATR | E03/345/3570/MVAR |  |  |  | CDC | 177 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | TapPosMv | [17 empty] | 3-AD |  | 3-6E |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_TAP | #5ATR OLTC TAP | ATR | E03//5ATR/TapPosMv |  |  |  | CDC | 178 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES | 0 |  | 5ATR_OIL | #5ATR |  | R | [17 empty] | 3-AF | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_OIL_R | #5ATR R相油溫 | ATR | E03//5ATR/Oil_R |  |  |  | CDC | 179 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_COIL | #5ATR |  | R | [17 empty] | 3-AE | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_COIL_R | #5ATR R相線溫 | ATR | E03//5ATR/Coil_R |  |  |  | CDC | 180 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_OIL | #5ATR |  | S | [17 empty] | 3-B1 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_OIL_S | #5ATR S相油溫 | ATR | E03//5ATR/Oil_S |  |  |  | CDC | 181 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_COIL | #5ATR |  | S | [17 empty] | 3-B0 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_COIL_S | #5ATR S相線溫 | ATR | E03//5ATR/Coil_S |  |  |  | CDC | 182 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_OIL | #5ATR |  | T | [17 empty] | 3-B3 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_OIL_T | #5ATR T相油溫 | ATR | E03//5ATR/Oil_T |  |  |  | CDC | 183 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_COIL | #5ATR |  | T | [17 empty] | 3-B2 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#5ATR_COIL_T | #5ATR T相線溫 | ATR | E03//5ATR/Coil_T |  |  |  | CDC | 184 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR二次側 |  | MW | [17 empty] | 1-9E | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#7ATR_MW | #7ATR二次側 MW | ATR | E03/345/3930/MW |  |  |  | CDC | 185 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR二次側 |  | MVAR | [17 empty] | 1-9F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#7ATR_MVAR | #7ATR二次側 MVAR | ATR | E03/345/3930/MVAR |  |  |  | CDC | 186 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | TapPosMv | [17 empty] | 3-B6 |  | 3-72 |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_TAP | #7ATR OLTC TAP | ATR | E03//7ATR/TapPosMv |  |  |  | CDC | 187 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E03 | 龍崎ES | 0 |  | 7ATR_OIL | #7ATR |  | R | [17 empty] | 3-B8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_OIL_R | #7ATR R相油溫 | ATR | E03//7ATR/Oil_R |  |  |  | CDC | 188 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_COIL | #7ATR |  | R | [17 empty] | 3-B7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_COIL_R | #7ATR R相線溫 | ATR | E03//7ATR/Coil_R |  |  |  | CDC | 189 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_OIL | #7ATR |  | S | [17 empty] | 3-BA | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_OIL_S | #7ATR S相油溫 | ATR | E03//7ATR/Oil_S |  |  |  | CDC | 190 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_COIL | #7ATR |  | S | [17 empty] | 3-B9 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_COIL_S | #7ATR S相線溫 | ATR | E03//7ATR/Coil_S |  |  |  | CDC | 191 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_OIL | #7ATR |  | T | [17 empty] | 3-BC | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_OIL_T | #7ATR T相油溫 | ATR | E03//7ATR/Oil_T |  |  |  | CDC | 192 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_COIL | #7ATR |  | T | [17 empty] | 3-BB | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#7ATR_COIL_T | #7ATR T相線溫 | ATR | E03//7ATR/Coil_T |  |  |  | CDC | 193 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  |  |  |  | #1直流N電源 | [17 empty] | 3-D1 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#1直流N電源 | #1直流N電源電壓 | OTHER | E03/0/StaDev/1_DCV_N |  |  |  | CDC | 194 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  |  |  |  | #1直流P電源 | [17 empty] | 3-D0 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#1直流P電源 | #1直流P電源電壓 | OTHER | E03/0/StaDev/1_DCV_P |  |  |  | CDC | 195 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  |  |  |  | #2直流N電源 | [17 empty] | 1-B1 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#2直流N電源 | #2直流N電源電壓 | OTHER | E03/0/StaDev/2_DCV_N |  |  |  | CDC | 196 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  |  |  |  | #2直流P電源 | [17 empty] | 1-B0 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#2直流P電源 | #2直流P電源電壓 | OTHER | E03/0/StaDev/2_DCV_P |  |  |  | CDC | 197 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E03 | 龍崎ES | 0 |  | 1700TIE | 1700TIE |  | I | [17 empty] | 1-85 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1700TIE_AMP | 1700TIE AMP | TIE | E03/161/1700/I |  |  |  | CDC | 198 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1550_MW | 龍崎台南山線 MW | LINE161 | E03/161/1550/MW |  |  |  | CDC | 199 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1550_MVAR | 龍崎台南山線 MVAR | LINE161 | E03/161/1550/MVAR |  |  |  | CDC | 200 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E03 | 龍崎ES | 161 | 161kV | 1550LPD | 龍崎台南山線(1550) |  | V | [17 empty] | 1-94 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1550LPD_KV | 龍崎台南山線(1550) LPD KV | LINE161 | E03/161/1550/V |  |  |  | CDC | 201 | GENERICAIPoint | ES003_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E03 | 龍崎ES | 0 |  | 1ATR_SR | #1ATR |  | CoilTemp | [17 empty] | 3-A2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#1ATR_SR_COIL | #1ATR 二次側 SR 線溫 | OTHER | E03/0/1SR/CoilTemp |  |  |  | CDC | 202 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 1ATR_SR | #1ATR |  | OilTemp | [17 empty] | 3-A3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#1ATR_SR_OIL | #1ATR 二次側 SR 油溫 | OTHER | E03/0/1SR/OilTemp |  |  |  | CDC | 203 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_SR | #2ATR |  | CoilTemp | [17 empty] | 3-AB | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#2ATR_SR_COIL | #2ATR 二次側 SR 線溫 | OTHER | E03/0/2SR/CoilTemp |  |  |  | CDC | 204 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 2ATR_SR | #2ATR |  | OilTemp | [17 empty] | 3-AC | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#2ATR_SR_OIL | #2ATR 二次側 SR 油溫 | OTHER | E03/0/2SR/OilTemp |  |  |  | CDC | 205 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_SR | #5ATR |  | CoilTemp | [17 empty] | 3-B4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#5ATR_SR_COIL | #5ATR 二次側 SR 線溫 | OTHER | E03/0/5SR/CoilTemp |  |  |  | CDC | 206 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 5ATR_SR | #5ATR |  | OilTemp | [17 empty] | 3-B5 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#5ATR_SR_OIL | #5ATR 二次側 SR 油溫 | OTHER | E03/0/5SR/OilTemp |  |  |  | CDC | 207 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_SR | #7ATR |  | CoilTemp | [17 empty] | 3-BD | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#7ATR_SR_COIL | #7ATR 二次側 SR 線溫 | OTHER | E03/0/7SR/CoilTemp |  |  |  | CDC | 208 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 0 |  | 7ATR_SR | #7ATR |  | OilTemp | [17 empty] | 3-BE | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#7ATR_SR_OIL | #7ATR 二次側 SR 油溫 | OTHER | E03/0/7SR/OilTemp |  |  |  | CDC | 209 | GENERICAIPoint | ES003_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | CB | [17 empty] | 3-00-05 |  | 3-06 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3560_CB | 3560(天輪海線) CB | LINE345 | E03/345/3560/CB |  |  |  | CDC | 210 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | CB | [17 empty] | 3-02-00 |  | 3-0D | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3630_CB | 3630(興達一路) CB | LINE345 | E03/345/3630/CB |  |  |  | CDC | 211 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | CB | [17 empty] | 3-02-01 |  | 3-0E | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3640_CB | 3640(路北紅線) CB | LINE345 | E03/345/3640/CB |  |  |  | CDC | 212 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | CB | [17 empty] | 3-00-02 |  | 3-03 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3530_CB | 3530(北南臨時線) CB | LINE345 | E03/345/3530/CB |  |  |  | CDC | 213 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | CB | [17 empty] | 3-00-03 |  | 3-04 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_CB | 3540(瀰力二路) CB | LINE345 | E03/345/3540/CB |  |  |  | CDC | 214 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | CB | [17 empty] | 3-00-00 |  | 3-01 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3510_CB | 3510(南科一路) CB | LINE345 | E03/345/3510/CB |  |  |  | CDC | 215 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | CB | [17 empty] | 3-01-06 |  | 3-0B | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3610_CB | 3610(南科二路) CB | LINE345 | E03/345/3610/CB |  |  |  | CDC | 216 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | CB | [17 empty] | 1-05-02 |  | 1-0A | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1570_CB | 1570(龍崎台南海線) CB | LINE161 | E03/161/1570/CB |  |  |  | CDC | 217 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | CB | [17 empty] | 1-03-02 |  | 1-07 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1580_CB | 1580(龍崎台南海線) CB | LINE161 | E03/161/1580/CB |  |  |  | CDC | 218 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | CB | [17 empty] | 1-00-06 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1510_CB | 1510(龍崎山上一路) CB | LINE161 | E03/161/1510/CB |  |  |  | CDC | 219 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | CB | [17 empty] | 1-01-02 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1520_CB | 1520(龍崎山上二路) CB | LINE161 | E03/161/1520/CB |  |  |  | CDC | 220 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | CB | [17 empty] | 1-01-06 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1530_CB | 1530(山上二甲三路) CB | LINE161 | E03/161/1530/CB |  |  |  | CDC | 221 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | CB | [17 empty] | 1-02-02 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1540_CB | 1540(山上二甲四路) CB | LINE161 | E03/161/1540/CB |  |  |  | CDC | 222 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3520 | 3520 |  | CB | [17 empty] | 3-00-01 |  | 3-02 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3520_CB | 3520 CB | LINE345 | E03/345/3520/CB |  |  |  | CDC | 223 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3550 | 3550 |  | CB | [17 empty] | 3-00-04 |  | 3-05 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3550_CB | 3550 CB | LINE345 | E03/345/3550/CB |  |  |  | CDC | 224 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | CB | [17 empty] | 3-00-06 |  | 3-07 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3570_CB | 3570(#5ATR) CB | ATR | E03/345/3570/CB |  |  |  | CDC | 225 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | CB | [17 empty] | 3-00-07 |  | 3-08 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3590_CB | 3590(#5ATR) CB | LINE345 | E03/345/3590/CB |  |  |  | CDC | 226 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3620 | 3620 |  | CB | [17 empty] | 3-01-07 |  | 3-0C | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3620_CB | 3620 CB | LINE345 | E03/345/3620/CB |  |  |  | CDC | 227 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3650 | 3650 |  | CB | [17 empty] | 3-02-02 |  | 3-0F | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3650_CB | 3650 CB | LINE345 | E03/345/3650/CB |  |  |  | CDC | 228 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | CB | [17 empty] | 3-02-03 |  | 3-10 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3660_CB | 3660(#1ATR) CB | ATR | E03/345/3660/CB |  |  |  | CDC | 229 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | CB | [17 empty] | 3-03-02 |  | 3-13 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3670_CB | 3670(#2ATR) CB | ATR | E03/345/3670/CB |  |  |  | CDC | 230 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | CB | [17 empty] | 3-03-03 |  | 3-14 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3690_CB | 3690(#2ATR) CB | LINE345 | E03/345/3690/CB |  |  |  | CDC | 231 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | CB | [17 empty] | 3-04-02 |  | 3-18 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3910_CB | 3910(#7ATR) CB | LINE345 | E03/345/3910/CB |  |  |  | CDC | 232 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3920 | 3920 |  | CB | [17 empty] | 3-05-01 |  | 3-1B | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3920_CB | 3920 CB | LINE345 | E03/345/3920/CB |  |  |  | CDC | 233 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | CB | [17 empty] | 3-05-02 |  | 3-1C | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3930_CB | 3930(#7ATR) CB | ATR | E03/345/3930/CB |  |  |  | CDC | 234 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | SSA11 | [17 empty] | 3-07-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3510_SSA11 | 南科一路(3510) #1差流(87L)RY | LINE345 | E03/345/3510/1SSA1 |  |  |  | CDC | 235 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | SSA12 | [17 empty] | 3-07-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3510_SSA12 | 南科一路(3510) #1測距(21)RY | LINE345 | E03/345/3510/1SSA2 |  |  |  | CDC | 236 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | SSA2 | [17 empty] | 3-07-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3510_SSA2 | 南科一路(3510) #2測距(21)RY | LINE345 | E03/345/3510/2SSA |  |  |  | CDC | 237 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | RYFA1 | [17 empty] | 3-35-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_RYFA1 | 南科一路(3510) 第一套RY故障 | LINE345 | E03/345/3510/RYFA1 |  |  |  | CDC | 238 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | RYFA2 | [17 empty] | 3-36-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_RYFA2 | 南科一路(3510) 第二套RY故障 | LINE345 | E03/345/3510/RYFA2 |  |  |  | CDC | 239 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | 79UL | [17 empty] | 3-35-13 |  | 3-77 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_79UL | 南科一路(3510) 79RY U/L | LINE345 | E03/345/3510/79UL |  |  |  | CDC | 240 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | ABS1 | 3511 | [16 empty] | 3-3C-00 | 3-3C-01 | 3-20 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3511_ABS | 3511(南科一路) ABS | LINE345 | E03/345/3510/ABS1 |  |  |  | CDC | 241 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | ABS2 | 3512 | [16 empty] | 3-3C-02 | 3-3C-03 | 3-21 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3512_ABS | 3512(南科一路) ABS | LINE345 | E03/345/3510/ABS2 |  |  |  | CDC | 242 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | E2 | 3512E | [16 empty] | 3-3C-04 | 3-3C-05 | 3-22 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3512E_ES | 3512E(南科一路) ES | LINE345 | E03/345/3510/E2 |  |  |  | CDC | 243 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | RYFA1 | [17 empty] | 3-36-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3530_RYFA1 | 北南臨時線(3530) #1_RY故障 | LINE345 | E03/345/3530/RYFA1 |  |  |  | CDC | 244 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | RYFA2 | [17 empty] | 3-36-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3530_RYFA2 | 北南臨時線(3530) #2_RY故障 | LINE345 | E03/345/3530/RYFA2 |  |  |  | CDC | 245 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | 79UL | [17 empty] | 3-36-02 |  | 3-78 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3530_79UL | 北南臨時線(3530) 79RY U/L | LINE345 | E03/345/3530/79UL |  |  |  | CDC | 246 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | ABS1 | 3531 | [16 empty] | 3-3C-10 | 3-3C-11 | 3-25 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3531_ABS | 3531(北南臨時線) ABS | LINE345 | E03/345/3530/ABS1 |  |  |  | CDC | 247 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | ABS2 | 3532 | [16 empty] | 3-3C-14 | 3-3C-15 | 3-27 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3532_ABS | 3532(北南臨時線) ABS | LINE345 | E03/345/3530/ABS2 |  |  |  | CDC | 248 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | E1 | 3531E | [16 empty] | 3-3C-12 | 3-3C-13 | 3-26 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3531E_ES | 3531E(北南臨時線) ES | LINE345 | E03/345/3530/E1 |  |  |  | CDC | 249 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | RYFA1 | [17 empty] | 3-36-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3540_RYFA1 | 瀰力二路(3540) 第一套RY故障 | LINE345 | E03/345/3540/RYFA1 |  |  |  | CDC | 250 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | RYFA2 | [17 empty] | 3-36-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3540_RYFA2 | 瀰力二路(3540) 第二套RY故障 | LINE345 | E03/345/3540/RYFA2 |  |  |  | CDC | 251 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | 79UL | [17 empty] | 3-36-07 |  | 3-79 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3540_79UL | 瀰力二路(3540) 79RY U/L | LINE345 | E03/345/3540/79UL |  |  |  | CDC | 252 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | ABS1 | 3541 | [16 empty] | 3-3D-00 | 3-3D-01 | 3-28 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3541_ABS | 3541(瀰力二路) ABS | LINE345 | E03/345/3540/ABS1 |  |  |  | CDC | 253 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | ABS2 | 3542 | [16 empty] | 3-3D-02 | 3-3D-03 | 3-29 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3542_ABS | 3542(瀰力二路) ABS | LINE345 | E03/345/3540/ABS2 |  |  |  | CDC | 254 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | E2 | 3542E | [16 empty] | 3-3D-04 | 3-3D-05 | 3-2A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3542E_ES | 3542E(瀰力二路) ES | LINE345 | E03/345/3540/E2 |  |  |  | CDC | 255 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | SSA11 | [17 empty] | 3-08-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3560_SSA11 | 天輪海線(3560) #1差流(87L)RY | LINE345 | E03/345/3560/1SSA1 |  |  |  | CDC | 256 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | SSA12 | [17 empty] | 3-08-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3560_SSA12 | 天輪海線(3560) #1測距(21)RY | LINE345 | E03/345/3560/1SSA2 |  |  |  | CDC | 257 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | SSA2 | [17 empty] | 3-08-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3560_SSA2 | 天輪海線(3560) #2測距(21)RY | LINE345 | E03/345/3560/2SSA |  |  |  | CDC | 258 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | RYFA1 | [17 empty] | 3-36-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3560_RYFA1 | 天輪海線(3560) 第一套RY故障 | LINE345 | E03/345/3560/RYFA1 |  |  |  | CDC | 259 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | RYFA2 | [17 empty] | 3-37-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3560_RYFA2 | 天輪海線(3560) 第二套RY故障 | LINE345 | E03/345/3560/RYFA2 |  |  |  | CDC | 260 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | 79UL | [17 empty] | 3-36-12 |  | 3-7A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3560_79UL | 天輪海線(3560) 79RY U/L | LINE345 | E03/345/3560/79UL |  |  |  | CDC | 261 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | DS1 | 3561 | [16 empty] | 3-3D-10 | 3-3D-11 | 3-2D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3561_DS | 3561(天輪海線) DS | LINE345 | E03/345/3560/DS1 |  |  |  | CDC | 262 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | DS2 | 3562 | [16 empty] | 3-3D-14 | 3-3D-15 | 3-2F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3562_DS | 3562(天輪海線) DS | LINE345 | E03/345/3560/DS2 |  |  |  | CDC | 263 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | E1 | 3561E | [16 empty] | 3-3D-12 | 3-3D-13 | 3-2E | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3561E_ES | 3561E(天輪海線) ES | LINE345 | E03/345/3560/E1 |  |  |  | CDC | 264 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | DS1 | 3591 | [16 empty] | 3-3E-06 | 3-3E-07 | 3-33 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3591_DS | 3591(#5ATR) DS | ATR | E03/345/3590/DS1 |  |  |  | CDC | 265 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | DS2 | 3592 | [16 empty] | 3-3E-08 | 3-3E-09 | 3-34 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3592_DS | 3592(#5ATR) DS | ATR | E03/345/3590/DS2 |  |  |  | CDC | 266 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | SSA11 | [17 empty] | 3-08-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3610_SSA11 | 南科二路(3610) #1差流(87L)RY | LINE345 | E03/345/3610/1SSA1 |  |  |  | CDC | 267 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | SSA12 | [17 empty] | 3-08-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3610_SSA12 | 南科二路(3610) #1測距(21)RY | LINE345 | E03/345/3610/1SSA2 |  |  |  | CDC | 268 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | SSA2 | [17 empty] | 3-08-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3610_SSA2 | 南科二路(3610) #2測距(21)RY | LINE345 | E03/345/3610/2SSA |  |  |  | CDC | 269 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | RYFA1 | [17 empty] | 3-37-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_RYFA1 | 南科二路(3610) 第一套RY故障 | LINE345 | E03/345/3610/RYFA1 |  |  |  | CDC | 270 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | RYFA2 | [17 empty] | 3-37-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_RYFA2 | 南科二路(3610) 第二套RY故障 | LINE345 | E03/345/3610/RYFA2 |  |  |  | CDC | 271 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | 79UL | [17 empty] | 3-37-01 |  | 3-7B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_79UL | 南科二路(3610) 79RY U/L | LINE345 | E03/345/3610/79UL |  |  |  | CDC | 272 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | ABS1 | 3611 | [16 empty] | 3-3E-10 | 3-3E-11 | 3-35 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3611_ABS | 3611(南科二路) ABS | LINE345 | E03/345/3610/ABS1 |  |  |  | CDC | 273 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | ABS2 | 3612 | [16 empty] | 3-3E-12 | 3-3E-13 | 3-36 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3612_ABS | 3612(南科二路) ABS | LINE345 | E03/345/3610/ABS2 |  |  |  | CDC | 274 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | E2 | 3612E | [16 empty] | 3-3E-14 | 3-3E-15 | 3-37 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3612E_ES | 3612E(南科二路) ES | LINE345 | E03/345/3610/E2 |  |  |  | CDC | 275 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | SSA11 | [17 empty] | 3-09-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3630_SSA11 | 興達一路(3630) #1差流(87L)RY | LINE345 | E03/345/3630/1SSA1 |  |  |  | CDC | 276 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | SSA12 | [17 empty] | 3-09-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3630_SSA12 | 興達一路(3630) #1測距(21)RY | LINE345 | E03/345/3630/1SSA2 |  |  |  | CDC | 277 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | SSA2 | [17 empty] | 3-09-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3630_SSA2 | 興達一路(3630) #2測距(21)RY | LINE345 | E03/345/3630/2SSA |  |  |  | CDC | 278 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | RYFA1 | [17 empty] | 3-37-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_RYFA1 | 興達一路(3630) 第一套RY故障 | LINE345 | E03/345/3630/RYFA1 |  |  |  | CDC | 279 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | RYFA2 | [17 empty] | 3-37-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_RYFA2 | 興達一路(3630) 第二套RY故障 | LINE345 | E03/345/3630/RYFA2 |  |  |  | CDC | 280 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | 79UL | [17 empty] | 3-37-06 |  | 3-7C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_79UL | 興達一路(3630) 79RY U/L | LINE345 | E03/345/3630/79UL |  |  |  | CDC | 281 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | ABS1 | 3631 | [16 empty] | 3-3F-04 | 3-3F-05 | 3-3A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3631_ABS | 3631(興達一路) ABS | LINE345 | E03/345/3630/ABS1 |  |  |  | CDC | 282 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | ABS2 | 3632 | [16 empty] | 3-3F-08 | 3-3F-09 | 3-3C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3632_ABS | 3632(興達一路) ABS | LINE345 | E03/345/3630/ABS2 |  |  |  | CDC | 283 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | E1 | 3631E | [16 empty] | 3-3F-06 | 3-3F-07 | 3-3B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3631E_ES | 3631E(興達一路) ES | LINE345 | E03/345/3630/E1 |  |  |  | CDC | 284 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | SSA11 | [17 empty] | 3-09-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3640_SSA11 | 路北紅線(3640) #1差流(87L)RY | LINE345 | E03/345/3640/1SSA1 |  |  |  | CDC | 285 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | SSA12 | [17 empty] | 3-09-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3640_SSA12 | 路北紅線(3640) #1測距(21)RY | LINE345 | E03/345/3640/1SSA2 |  |  |  | CDC | 286 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | SSA2 | [17 empty] | 3-09-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3640_SSA2 | 路北紅線(3640) #2測距(21)RY | LINE345 | E03/345/3640/2SSA |  |  |  | CDC | 287 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | RYFA1 | [17 empty] | 3-37-13 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_RYFA1 | 路北紅線(3640) 第一套RY故障 | LINE345 | E03/345/3640/RYFA1 |  |  |  | CDC | 288 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | RYFA2 | [17 empty] | 3-37-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_RYFA2 | 路北紅線(3640) 第二套RY故障 | LINE345 | E03/345/3640/RYFA2 |  |  |  | CDC | 289 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | 79UL | [17 empty] | 3-37-11 |  | 3-7D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_79UL | 路北紅線(3640) 79RY U/L | LINE345 | E03/345/3640/79UL |  |  |  | CDC | 290 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | ABS1 | 3641 | [16 empty] | 4-30-00 | 4-30-01 | 3-3D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3641_ABS | 3641(路北紅線) ABS | LINE345 | E03/345/3640/ABS1 |  |  |  | CDC | 291 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | ABS2 | 3642 | [16 empty] | 4-30-02 | 4-30-03 | 3-3E | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3642_ABS | 3642(路北紅線) ABS | LINE345 | E03/345/3640/ABS2 |  |  |  | CDC | 292 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | E2 | 3642E | [16 empty] | 4-30-04 | 4-30-05 | 3-3F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3642E_ES | 3642E(路北紅線) ES | LINE345 | E03/345/3640/E2 |  |  |  | CDC | 293 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | ABS1 | 3691 | [16 empty] | 4-31-04 | 4-31-05 | 3-46 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3691_ABS | 3691(#2ATR) ABS | ATR | E03/345/3690/ABS1 |  |  |  | CDC | 294 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | ABS2 | 3692 | [16 empty] | 4-31-06 | 4-31-07 | 3-47 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3692_ABS | 3692(#2ATR) ABS | ATR | E03/345/3690/ABS2 |  |  |  | CDC | 295 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | DS1 | 3911 | [16 empty] | 4-31-08 | 4-31-09 | 3-48 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3911_DS | 3911(#7ATR) DS | ATR | E03/345/3910/DS1 |  |  |  | CDC | 296 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | DS2 | 3912 | [16 empty] | 4-31-10 | 4-31-11 | 3-49 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3912_DS | 3912(#7ATR) DS | ATR | E03/345/3910/DS2 |  |  |  | CDC | 297 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | E2 | 3912E | [16 empty] | 4-31-12 | 4-31-13 | 3-4A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3912E_ES | 3912E(#7ATR) ES | ATR | E03/345/3910/E2 |  |  |  | CDC | 298 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3920 | 3920 |  | DS1 | 3921 | [16 empty] | 4-31-14 | 4-31-15 | 3-4B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3921_DS | 3921 DS | LINE345 | E03/345/3920/DS1 |  |  |  | CDC | 299 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3920 | 3920 |  | DS2 | 3922 | [16 empty] | 4-32-00 | 4-32-01 | 3-4C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3922_DS | 3922 DS | LINE345 | E03/345/3920/DS2 |  |  |  | CDC | 300 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1510_PHA | 龍崎山上一路(1510) 相間RY | LINE161 | E03/161/1510/PHA |  |  |  | CDC | 301 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1510_GDA | 龍崎山上一路(1510) 接地RY | LINE161 | E03/161/1510/GDA |  |  |  | CDC | 302 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | 87A | [17 empty] | 1-00-07 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1510_87A | 龍崎山上一路(1510) 87RY | LINE161 | E03/161/1510/85A |  |  |  | CDC | 303 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | 87UL | [17 empty] | 1-30-11 |  | 1-31 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_87UL | 龍崎山上一路(1510) 87RY U/L | LINE161 | E03/161/1510/85UL |  |  |  | CDC | 304 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | 79UL | [17 empty] | 1-30-10 |  | 1-30 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_79UL | 龍崎山上一路(1510) 79RY U/L | LINE161 | E03/161/1510/79UL |  |  |  | CDC | 305 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | ABS1 | 1511 | [16 empty] | 1-37-08 | 1-37-09 | 1-10 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1511_ABS | 1511(龍崎山上一路) ABS | LINE161 | E03/161/1510/ABS1 |  |  |  | CDC | 306 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | ABS2 | 1512 | [16 empty] | 1-37-10 | 1-37-11 | 1-11 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1512_ABS | 1512(龍崎山上一路) ABS | LINE161 | E03/161/1510/ABS2 |  |  |  | CDC | 307 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | ABS3 | 1513 | [16 empty] | 1-37-12 | 1-37-13 | 1-12 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1513_ABS | 1513(龍崎山上一路) ABS | LINE161 | E03/161/1510/ABS3 |  |  |  | CDC | 308 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | E3 | 1513E | [16 empty] | 1-37-14 | 1-37-15 | 1-13 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1513E_ES | 1513E(龍崎山上一路) ES | LINE161 | E03/161/1510/E3 |  |  |  | CDC | 309 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | PHA | [17 empty] | 1-01-04 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1520_PHA | 龍崎山上二路(1520) 相間RY | LINE161 | E03/161/1520/PHA |  |  |  | CDC | 310 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | GDA | [17 empty] | 1-01-05 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1520_GDA | 龍崎山上二路(1520) 接地RY | LINE161 | E03/161/1520/GDA |  |  |  | CDC | 311 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1520_87A | 龍崎山上二路(1520) 87RY | LINE161 | E03/161/1520/85A |  |  |  | CDC | 312 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | 87UL | [17 empty] | 1-30-15 |  | 1-33 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_87UL | 龍崎山上二路(1520) 87RY U/L | LINE161 | E03/161/1520/85UL |  |  |  | CDC | 313 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | 79UL | [17 empty] | 1-30-14 |  | 1-32 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_79UL | 龍崎山上二路(1520) 79RY U/L | LINE161 | E03/161/1520/79UL |  |  |  | CDC | 314 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | ABS1 | 1521 | [16 empty] | 1-38-00 | 1-38-01 | 1-14 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1521_ABS | 1521(龍崎山上二路) ABS | LINE161 | E03/161/1520/ABS1 |  |  |  | CDC | 315 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | ABS2 | 1522 | [16 empty] | 1-38-02 | 1-38-03 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1522_ABS | 1522(龍崎山上二路) ABS | LINE161 | E03/161/1520/ABS2 |  |  |  | CDC | 316 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | ABS3 | 1523 | [16 empty] | 1-38-04 | 1-38-05 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1523_ABS | 1523(龍崎山上二路) ABS | LINE161 | E03/161/1520/ABS3 |  |  |  | CDC | 317 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | E3 | 1523E | [16 empty] | 1-38-06 | 1-38-07 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1523E_ES | 1523E(龍崎山上二路) ES | LINE161 | E03/161/1520/E3 |  |  |  | CDC | 318 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | PHA | [17 empty] | 1-02-00 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1530_PHA | 山上二甲三路(1530) 相間RY | LINE161 | E03/161/1530/PHA |  |  |  | CDC | 319 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | GDA | [17 empty] | 1-02-01 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1530_GDA | 山上二甲三路(1530) 接地RY | LINE161 | E03/161/1530/GDA |  |  |  | CDC | 320 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | 87A | [17 empty] | 1-01-07 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1530_87A | 山上二甲三路(1530) 85RY | LINE161 | E03/161/1530/85A |  |  |  | CDC | 321 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | 87UL | [17 empty] | 1-31-03 |  | 1-35 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1530_87UL | 山上二甲三路(1530) 87RY U/L | LINE161 | E03/161/1530/85UL |  |  |  | CDC | 322 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | 79UL | [17 empty] | 1-31-02 |  | 1-34 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1530_79UL | 山上二甲三路(1530) 79RY U/L | LINE161 | E03/161/1530/79UL |  |  |  | CDC | 323 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | ABS1 | 1531 | [16 empty] | 1-38-08 | 1-38-09 | 1-18 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1531_ABS | 1531(山上二甲三路) ABS | LINE161 | E03/161/1530/ABS1 |  |  |  | CDC | 324 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | ABS2 | 1532 | [16 empty] | 1-38-10 | 1-38-11 | 1-19 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1532_ABS | 1532(山上二甲三路) ABS | LINE161 | E03/161/1530/ABS2 |  |  |  | CDC | 325 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | ABS3 | 1533 | [16 empty] | 1-38-12 | 1-38-13 | 1-1A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1533_ABS | 1533(山上二甲三路) ABS | LINE161 | E03/161/1530/ABS3 |  |  |  | CDC | 326 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | E3 | 1533E | [16 empty] | 1-38-14 | 1-38-15 | 1-1B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1533E_ES | 1533E(山上二甲三路) ES | LINE161 | E03/161/1530/E3 |  |  |  | CDC | 327 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | PHA | [17 empty] | 1-02-04 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1540_PHA | 山上二甲四路(1540) 相間RY | LINE161 | E03/161/1540/PHA |  |  |  | CDC | 328 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | GDA | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1540_GDA | 山上二甲四路(1540) 接地RY | LINE161 | E03/161/1540/GDA |  |  |  | CDC | 329 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | 87A | [17 empty] | 1-02-03 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1540_87A | 龍崎山上四路(1540) 87RY | LINE161 | E03/161/1540/85A |  |  |  | CDC | 330 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | 87UL | [17 empty] | 1-31-07 |  | 1-37 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1540_87UL | 山上二甲四路(1540) 87RY U/L | LINE161 | E03/161/1540/85UL |  |  |  | CDC | 331 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | 79UL | [17 empty] | 1-31-06 |  | 1-36 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1540_79UL | 山上二甲四路(1540) 79RY U/L | LINE161 | E03/161/1540/79UL |  |  |  | CDC | 332 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | ABS1 | 1541 | [16 empty] | 1-39-00 | 1-39-01 | 1-1C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1541_ABS | 1541(山上二甲四路) ABS | LINE161 | E03/161/1540/ABS1 |  |  |  | CDC | 333 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | ABS2 | 1542 | [16 empty] | 1-39-02 | 1-39-03 | 1-1D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1542_ABS | 1542(山上二甲四路) ABS | LINE161 | E03/161/1540/ABS2 |  |  |  | CDC | 334 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | ABS3 | 1543 | [16 empty] | 1-39-04 | 1-39-05 | 1-1E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1543_ABS | 1543(山上二甲四路) ABS | LINE161 | E03/161/1540/ABS3 |  |  |  | CDC | 335 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | E3 | 1543E | [16 empty] | 1-39-06 | 1-39-07 | 1-1F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1543E_ES | 1543E(山上二甲四路) ES | LINE161 | E03/161/1540/E3 |  |  |  | CDC | 336 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1580_PHA | 龍崎台南海線(1580) 相間RY | LINE161 | E03/161/1580/PHA |  |  |  | CDC | 337 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1580_GDA | 龍崎台南海線(1580) 接地RY | LINE161 | E03/161/1580/GDA |  |  |  | CDC | 338 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | 87A | [17 empty] | 1-03-03 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1580_87A | 龍崎台南海線(1580) 87RY | LINE161 | E03/161/1580/85A |  |  |  | CDC | 339 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | 87UL | [17 empty] | 1-31-15 |  | 1-3B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1580_87UL | 龍崎台南海線(1580) 87RY U/L | LINE161 | E03/161/1580/85UL2 |  |  |  | CDC | 340 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | 79UL | [17 empty] | 1-31-14 |  | 1-3A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1580_79UL | 龍崎台南海線(1580) 79RY U/L | LINE161 | E03/161/1580/79UL |  |  |  | CDC | 341 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | CB | [17 empty] | 1-04-00 |  | 1-08 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1700_CB | 1700(TIE) CB | TIE | E03/161/1700/CB |  |  |  | CDC | 342 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-2A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1701_DS | 1701(TIE) DS | TIE | E03/161/1700/DS1 |  |  |  | CDC | 343 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | DS3 | 1703 | [16 empty] | 1-3A-14 | 1-3A-15 | 1-2B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1703_DS | 1703(TIE) DS | TIE | E03/161/1700/DS2 |  |  |  | CDC | 344 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 87A1 | [17 empty] | 3-02-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#1ATR_87A1 | #1ATR 第一組 87RY | ATR | E03//1ATR/87A1 |  |  |  | CDC | 345 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 87A2 | [17 empty] | 3-02-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#1ATR_87A2 | #1ATR 第二組 87RY | ATR | E03//1ATR/87A2 |  |  |  | CDC | 346 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 96PA | [17 empty] | 3-02-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#1ATR_96PA | #1ATR 機械保護動作 | ATR | E03//1ATR/96PA |  |  |  | CDC | 347 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 51ZA | [17 empty] | 3-03-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#1ATR_51ZA | #1ATR 51Z(21+50,59-2,51Z) | ATR | E03//1ATR/51ZA |  |  |  | CDC | 348 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 59A | [17 empty] | 3-03-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#1ATR_59A | #1ATR 59RY | ATR | E03//1ATR/59A |  |  |  | CDC | 349 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 1_87UL1 | [17 empty] | 3-30-13 |  | 4-0B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_87UL1 | #1ATR 第一套 87RY U/L | OTHER | E03//1ATR/1_87UL1 |  |  |  | CDC | 350 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 1_87UL2 | [17 empty] | 3-30-14 |  | 4-0C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_87UL2 | #1ATR 第二套 87RY U/L | OTHER | E03//1ATR/1_87UL2 |  |  |  | CDC | 351 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 96D | [17 empty] | 3-31-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_96D | #1ATR 96D RY | ATR | E03//1ATR/96D |  |  |  | CDC | 352 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 96P | [17 empty] | 3-31-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_96P | #1ATR 96P RY | ATR | E03//1ATR/96P |  |  |  | CDC | 353 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 63Q | [17 empty] | 3-31-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_63Q | #1ATR 63Q RY | ATR | E03//1ATR/63Q |  |  |  | CDC | 354 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 96B1 | [17 empty] | 3-31-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_96B1 | #1ATR 96B1 RY | ATR | E03//1ATR/96B1 |  |  |  | CDC | 355 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 96B2 | [17 empty] | 3-31-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_96B2 | #1ATR 96B2 RY | ATR | E03//1ATR/96B2 |  |  |  | CDC | 356 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | TRA | [17 empty] | 3-31-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_TRA | #1ATR 重故障 | ATR | E03//1ATR/TRA |  |  |  | CDC | 357 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | TRF | [17 empty] | 3-31-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_TRF | #1ATR 輕故障 | ATR | E03//1ATR/TRF |  |  |  | CDC | 358 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | SupLocal | [17 empty] | 3-30-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_S/L | #1ATR OLTC S/L | ATR | E03//1ATR/SupLocal |  |  |  | CDC | 359 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | A_M | [17 empty] | 3-31-00 |  | 3-63 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_A/M | #1ATR OLTC A/M | ATR | E03/345/3660/Tap Chan |  |  |  | CDC | 360 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | M/F/I | [17 empty] | 4-35-04 | 4-35-05 | 3-64 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_M/F/I | #1ATR M/F/I | ATR | E03//1ATR/M_F_I |  |  |  | CDC | 361 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | ABS1 | 3661 | [16 empty] | 4-30-10 | 4-30-11 | 3-42 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3661_ABS | 3661(#1ATR) ABS | ATR | E03/345/3660/ABS1 |  |  |  | CDC | 362 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | ABS2 | 3662 | [16 empty] | 4-30-12 | 4-30-13 | 3-43 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3662_ABS | 3662(#1ATR) ABS | ATR | E03/345/3660/ABS2 |  |  |  | CDC | 363 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 87A1 | [17 empty] | 3-03-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#2ATR_87A1 | #2ATR 第一組 87RY | ATR | E03//2ATR/87A1 |  |  |  | CDC | 364 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 87A2 | [17 empty] | 3-03-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#2ATR_87A2 | #2ATR 第二組 87RY | ATR | E03//2ATR/87A2 |  |  |  | CDC | 365 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 96PA | [17 empty] | 3-03-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#2ATR_96PA | #2ATR 機械保護動作 | ATR | E03//2ATR/96PA |  |  |  | CDC | 366 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 51ZA | [17 empty] | 3-04-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#2ATR_51ZA | #2ATR 51Z(21+50,59-2,51Z) | ATR | E03//2ATR/51ZA |  |  |  | CDC | 367 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 59A | [17 empty] | 3-04-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#2ATR_59A | #2ATR 59RY | ATR | E03//2ATR/59A |  |  |  | CDC | 368 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 1_87UL1 | [17 empty] | 3-31-13 |  | 4-16 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_87UL1 | #2ATR 第一套 87RY U/L | OTHER | E03//2ATR/1_87UL1 |  |  |  | CDC | 369 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 1_87UL2 | [17 empty] | 3-31-14 |  | 4-17 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_87UL2 | #2ATR 第二套 87RY U/L | OTHER | E03//2ATR/1_87UL2 |  |  |  | CDC | 370 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 96D | [17 empty] | 3-32-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_96D | #2ATR 96D RY | ATR | E03//2ATR/96D |  |  |  | CDC | 371 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 96P | [17 empty] | 3-32-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_96P | #2ATR 96P RY | ATR | E03//2ATR/96P |  |  |  | CDC | 372 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 63Q | [17 empty] | 3-32-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_63Q | #2ATR 63Q RY | ATR | E03//2ATR/63Q |  |  |  | CDC | 373 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 96B1 | [17 empty] | 3-32-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_96B1 | #2ATR 96B1 RY | ATR | E03//2ATR/96B1 |  |  |  | CDC | 374 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 96B2 | [17 empty] | 3-32-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_96B2 | #2ATR 96B2 RY | ATR | E03//2ATR/96B2 |  |  |  | CDC | 375 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | TRA | [17 empty] | 3-32-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_TRA | #2ATR 重故障 | ATR | E03//2ATR/TRA |  |  |  | CDC | 376 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | TRF | [17 empty] | 3-32-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_TRF | #2ATR 輕故障 | ATR | E03//2ATR/TRF |  |  |  | CDC | 377 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | SupLocal | [17 empty] | 3-31-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_S/L | #2ATR OLTC S/L | ATR | E03//2ATR/SupLocal |  |  |  | CDC | 378 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | A_M | [17 empty] | 3-32-00 |  | 3-67 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_A/M | #2ATR OLTC A/M | ATR | E03/345/3690/Tap Chan |  |  |  | CDC | 379 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | M/F/I | [17 empty] | 4-35-06 | 4-35-07 | 3-68 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_M/F/I | #2ATR M/F/I | ATR | E03//2ATR/M_F_I |  |  |  | CDC | 380 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | ABS1 | 3671 | [16 empty] | 4-30-14 | 4-30-15 | 3-44 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3671_ABS | 3671(#2ATR) ABS | ATR | E03/345/3670/ABS1 |  |  |  | CDC | 381 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | ABS2 | 3672 | [16 empty] | 4-31-00 | 4-31-01 | 3-45 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3672_ABS | 3672(#2ATR) ABS | ATR | E03/345/3670/ABS2 |  |  |  | CDC | 382 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 87A1 | [17 empty] | 3-01-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#5ATR_87A1 | #5ATR 第一組 87RY | ATR | E03//5ATR/87A1 |  |  |  | CDC | 383 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 87A2 | [17 empty] | 3-01-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#5ATR_87A2 | #5ATR 第二組 87RY | ATR | E03//5ATR/87A2 |  |  |  | CDC | 384 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 96PA | [17 empty] | 3-01-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#5ATR_96PA | #5ATR 機械保護動作 | ATR | E03//5ATR/96PA |  |  |  | CDC | 385 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 51ZA | [17 empty] | 3-01-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#5ATR_51ZA | #5ATR 51Z(21+50,59-2,51Z) | ATR | E03//5ATR/51ZA |  |  |  | CDC | 386 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 59A | [17 empty] | 3-01-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#5ATR_59A | #5ATR 59RY | ATR | E03//5ATR/59A |  |  |  | CDC | 387 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 1_87UL1 | [17 empty] | 3-30-02 |  | 4-1A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_87UL1 | #5ATR 第一套 87RY U/L | OTHER | E03//5ATR/1_87UL1 |  |  |  | CDC | 388 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 1_87UL2 | [17 empty] | 3-30-03 |  | 4-1B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_87UL2 | #5ATR 第二套 87RY U/L | OTHER | E03//5ATR/1_87UL2 |  |  |  | CDC | 389 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 96D | [17 empty] | 3-30-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_96D | #5ATR 96D RY | ATR | E03//5ATR/96D |  |  |  | CDC | 390 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 96P | [17 empty] | 3-30-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_96P | #5ATR 96P RY | ATR | E03//5ATR/96P |  |  |  | CDC | 391 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 63Q | [17 empty] | 3-30-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_63Q | #5ATR 63Q RY | ATR | E03//5ATR/63Q |  |  |  | CDC | 392 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 96B1 | [17 empty] | 3-30-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_96B1 | #5ATR 96B1 RY | ATR | E03//5ATR/96B1 |  |  |  | CDC | 393 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 96B2 | [17 empty] | 3-30-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_96B2 | #5ATR 96B2 RY | ATR | E03//5ATR/96B2 |  |  |  | CDC | 394 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | TRA | [17 empty] | 3-30-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_TRA | #5ATR 重故障 | ATR | E03//5ATR/TRA |  |  |  | CDC | 395 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | TRF | [17 empty] | 3-30-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_TRF | #5ATR 輕故障 | ATR | E03//5ATR/TRF |  |  |  | CDC | 396 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | SupLocal | [17 empty] | 3-30-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_S/L | #5ATR OLTC S/L | ATR | E03//5ATR/SupLocal |  |  |  | CDC | 397 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | A_M | [17 empty] | 3-30-05 |  | 3-6B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_A/M | #5ATR OLTC A/M | ATR | E03/345/3590/Tap Chan |  |  |  | CDC | 398 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | M/F/I | [17 empty] | 4-35-02 | 4-35-03 | 3-6C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_M/F/I | #5ATR M/F/I | ATR | E03//5ATR/M_F_I |  |  |  | CDC | 399 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | DS1 | 3571 | [16 empty] | 3-3E-00 | 3-3E-01 | 3-30 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3571_DS | 3571(#5ATR) DS | ATR | E03/345/3570/DS1 |  |  |  | CDC | 400 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | DS2 | 3572 | [16 empty] | 3-3E-02 | 3-3E-03 | 3-31 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3572_DS | 3572(#5ATR) DS | ATR | E03/345/3570/DS2 |  |  |  | CDC | 401 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | CB | [17 empty] | 3-05-03 |  | 3-1D | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1750_CB | 1750(#7ATR) CB | ATR | E03/161/1750/CB |  |  |  | CDC | 402 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 87A1 | [17 empty] | 3-05-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#7ATR_87A1 | #7ATR 第一組 87RY | ATR | E03//7ATR/87A1 |  |  |  | CDC | 403 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 87A2 | [17 empty] | 3-05-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#7ATR_87A2 | #7ATR 第二組 87RY | ATR | E03//7ATR/87A2 |  |  |  | CDC | 404 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 96PA | [17 empty] | 3-05-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#7ATR_96PA | #7ATR 機械保護動作 | ATR | E03//7ATR/96PA |  |  |  | CDC | 405 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 51ZA | [17 empty] | 3-06-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#7ATR_51ZA | #7ATR 51Z(21+50,59-2,51Z) | ATR | E03//7ATR/51ZA |  |  |  | CDC | 406 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 59A | [17 empty] | 3-06-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#7ATR_59A | #7ATR 59RY | ATR | E03//7ATR/59A |  |  |  | CDC | 407 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 1_87UL1 | [17 empty] | 3-32-13 |  | 4-1E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_87UL1 | #7ATR 第一套 87RY U/L | OTHER | E03//7ATR/1_87UL1 |  |  |  | CDC | 408 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 1_87UL2 | [17 empty] | 3-32-14 |  | 4-1F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_87UL2 | #7ATR 第二套 87RY U/L | OTHER | E03//7ATR/1_87UL2 |  |  |  | CDC | 409 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 96D | [17 empty] | 3-33-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_96D | #7ATR 96D RY | ATR | E03//7ATR/96D |  |  |  | CDC | 410 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 96P | [17 empty] | 3-33-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_96P | #7ATR 96P RY | ATR | E03//7ATR/96P |  |  |  | CDC | 411 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 63Q | [17 empty] | 3-33-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_63Q | #7ATR 63Q RY | ATR | E03//7ATR/63Q |  |  |  | CDC | 412 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 96B1 | [17 empty] | 3-33-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_96B1 | #7ATR 96B1 RY | ATR | E03//7ATR/96B1 |  |  |  | CDC | 413 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 96B2 | [17 empty] | 3-33-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_96B2 | #7ATR 96B2 RY | ATR | E03//7ATR/96B2 |  |  |  | CDC | 414 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | TRA | [17 empty] | 3-33-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_TRA | #7ATR 重故障 | ATR | E03//7ATR/TRA |  |  |  | CDC | 415 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | TRF | [17 empty] | 3-33-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_TRF | #7ATR 輕故障 | ATR | E03//7ATR/TRF |  |  |  | CDC | 416 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | SupLocal | [17 empty] | 3-32-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_S/L | #7ATR OLTC S/L | ATR | E03//7ATR/SupLocal |  |  |  | CDC | 417 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | A_M | [17 empty] | 3-33-00 |  | 3-6F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_A/M | #7ATR OLTC A/M | ATR | E03/345/3930/Tap Chan |  |  |  | CDC | 418 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | M/F/I | [17 empty] | 4-35-10 | 4-35-11 | 3-70 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_M/F/I | #7ATR M/F/I | ATR | E03//7ATR/M_F_I |  |  |  | CDC | 419 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | DS1 | 3931 | [16 empty] | 4-32-02 | 4-32-03 | 3-4D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3931_DS | 3931(#7ATR) DS | ATR | E03/345/3930/DS1 |  |  |  | CDC | 420 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | DS2 | 3932 | [16 empty] | 4-32-06 | 4-32-07 | 3-4F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3932_DS | 3932(#7ATR) DS | ATR | E03/345/3930/DS2 |  |  |  | CDC | 421 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | DS1 | 1751 | [16 empty] | 4-34-04 | 4-34-05 | 3-5E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1751_DS | 1751(#7ATR) DS | ATR | E03/161/1750/DS1 |  |  |  | CDC | 422 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1750 | #7ATR(1750) |  | DS2 | 1752 | [16 empty] | 4-34-06 | 4-34-07 | 3-5F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1752_DS | 1752(#7ATR) DS | ATR | E03/161/1750/DS2 |  |  |  | CDC | 423 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | CB | [17 empty] | 3-05-04 |  | 3-1E | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1760_CB | 1760(#7ATR) CB | ATR | E03/161/1760/CB |  |  |  | CDC | 424 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | DS1 | 1761 | [16 empty] | 4-34-10 | 4-34-11 | 3-60 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1761_DS | 1761(#7ATR) DS | ATR | E03/161/1760/DS1 |  |  |  | CDC | 425 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | DS2 | 1762 | [16 empty] | 4-34-12 | 4-34-13 | 3-61 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1762_DS | 1762(#7ATR) DS | ATR | E03/161/1760/DS2 |  |  |  | CDC | 426 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 390 | #1SSTR(390) |  | CB | [17 empty] | 3-15-00 |  | 3-17 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.390_CB | 390(#1SSTR) CB | OTHER | E03/22/390/CB |  |  |  | CDC | 427 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 3-15-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1SSTR_51A | #1SSTR 51RY | OTHER | E03/22/390/PHA |  |  |  | CDC | 428 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3SSTR | #3SSTR |  | 51A | [17 empty] | 3-14-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#3SSTR_51A | #3SSTR 51RY | OTHER | E03/22/3SSTR/PHA |  |  |  | CDC | 429 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | E03/161/1BUS/BUS_VUA |  |  |  | CDC | 430 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-04-02 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.161#1BUS_87A | 161KV #1BUS 87RY | BUS | E03/161/1BUS/87A |  |  |  | CDC | 431 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-30-02 |  | 1-3E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | E03/161/1BUS/87UL |  |  |  | CDC | 432 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | E03/161/2BUS/BUS_VUA |  |  |  | CDC | 433 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-04-03 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.161#2BUS_87A | 161KV #2BUS 87RY | BUS | E03/161/2BUS/87A |  |  |  | CDC | 434 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-30-03 |  | 1-3F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | E03/161/2BUS/87UL |  |  |  | CDC | 435 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3451B | #1BUS |  | 87A1 | [17 empty] | 3-06-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#1B_87A1 | 345KV #1BUS 第一組 87RY | BUS | E03/345/1BUS/87A1 |  |  |  | CDC | 436 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3451B | #1BUS |  | 87A2 | [17 empty] | 3-06-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#1B_87A2 | 345KV #1BUS 第二組 87RY | BUS | E03/345/1BUS/87A2 |  |  |  | CDC | 437 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3451B | #1BUS |  | 1_87UL1 | [17 empty] | 3-34-13 |  | 4-03 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#1B_87UL1 | 345KV #1BUS 第一組 87RY U/L | OTHER | E03/345/1BUS/1_87UL1 |  |  |  | CDC | 438 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3451B | #1BUS |  | 1_87UL2 | [17 empty] | 3-34-14 |  | 4-05 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#1B_87UL2 | 345KV #1BUS 第二組 87RY U/L | OTHER | E03/345/1BUS/1_87UL2 |  |  |  | CDC | 439 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3452B | #2BUS |  | 87A1 | [17 empty] | 3-06-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#2B_87A1 | 345KV #2BUS 第一組 87RY | BUS | E03/345/2BUS/87A1 |  |  |  | CDC | 440 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3452B | #2BUS |  | 87A2 | [17 empty] | 3-06-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#2B_87A2 | 345KV #2BUS 第二組 87RY | BUS | E03/345/2BUS/87A2 |  |  |  | CDC | 441 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3452B | #2BUS |  | 1_87UL1 | [17 empty] | 3-34-15 |  | 4-04 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#2B_87UL1 | 345KV #2BUS 第一組 87RY U/L | OTHER | E03/345/2BUS/1_87UL1 |  |  |  | CDC | 442 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 345 | 345kV | 3452B | #2BUS |  | 1_87UL2 | [17 empty] | 3-35-00 |  | 4-06 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#2B_87UL2 | 345KV #2BUS 第二組 87RY U/L | OTHER | E03/345/2BUS/1_87UL2 |  |  |  | CDC | 443 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 510 | 510 |  | CB | [17 empty] | 3-14-02 |  | 3-12 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.510_CB | 510 CB | OTHER | E03/33/510/CB |  |  |  | CDC | 444 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 510 | 510 |  | 87A | [17 empty] | 3-14-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.510_87A | 510 87RY | OTHER | E03/33/510/87A |  |  |  | CDC | 445 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 510 | 510 |  | PHA | [17 empty] | 3-14-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.510_PHA | 510 相間RY | OTHER | E03/33/510/PHA |  |  |  | CDC | 446 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 510 | 510 |  | ABS1 | 511 | [16 empty] | 4-33-00 | 4-33-01 | 3-55 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.511_ABS | 511 ABS | OTHER | E03/33/510/ABS1 |  |  |  | CDC | 447 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 520 | 520 |  | CB | [17 empty] | 3-14-05 |  | 3-16 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.520_CB | 520 CB | OTHER | E03/33/520/CB |  |  |  | CDC | 448 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 520 | 520 |  | 87A | [17 empty] | 3-14-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.520_87A | 520 87RY | OTHER | E03/33/520/87A |  |  |  | CDC | 449 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 520 | 520 |  | PHA | [17 empty] | 3-14-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.520_PHA | 520 相間RY | OTHER | E03/33/520/PHA |  |  |  | CDC | 450 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 520 | 520 |  | ABS1 | 521 | [16 empty] | 4-33-08 | 4-33-09 | 3-59 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.521_ABS | 521 ABS | OTHER | E03/33/520/ABS1 |  |  |  | CDC | 451 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 570 | 570 |  | CB | [17 empty] | 3-15-05 |  | 3-1F | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.570_CB | 570 CB | OTHER | E03/33/570/CB |  |  |  | CDC | 452 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 570 | 570 |  | 87A | [17 empty] | 3-15-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.570_87A | 570 87RY | OTHER | E03/33/570/87A |  |  |  | CDC | 453 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 570 | 570 |  | PHA | [17 empty] | 3-15-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.570_PHA | 570 相間RY | OTHER | E03/33/570/PHA |  |  |  | CDC | 454 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 570 | 570 |  | ABS1 | 571 | [16 empty] | 4-35-00 | 4-35-01 | 3-62 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.571_ABS | 571 ABS | OTHER | E03/33/570/ABS1 |  |  |  | CDC | 455 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  |  |  |  | ACB1 | [17 empty] | 3-38-00 |  | 4-00 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.所內電源ACB1 | 所內電源開關ACB1 | OTHER | E03/0/StaDev/ACB1 |  |  |  | CDC | 456 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E03 | 龍崎ES | 0 |  |  |  |  | ACB2 | [17 empty] | 3-38-02 |  | 4-02 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.所內電源ACB2 | 所內電源開關ACB2 | OTHER | E03/0/StaDev/ACB2 |  |  |  | CDC | 457 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | SR96B1 | [17 empty] | 3-31-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_SR96B1 | #1ATR 33KV 電抗器96B1 RY | OTHER | E03/33/1ATR/96B1 |  |  |  | CDC | 458 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | SR96B2 | [17 empty] | 3-31-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_SR96B2 | #1ATR 33KV 電抗器96B2 RY | OTHER | E03/33/1ATR/96B2 |  |  |  | CDC | 459 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | SR96D | [17 empty] | 3-31-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_SR96D | #1ATR 33KV 電抗器96D RY | OTHER | E03/33/1ATR/96D |  |  |  | CDC | 460 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | SR96P | [17 empty] | 3-31-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#1ATR_SR96P | #1ATR 33KV 電抗器96P RY | OTHER | E03/33/1ATR/96P |  |  |  | CDC | 461 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | SR96B1 | [17 empty] | 3-32-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_SR96B1 | #2ATR 33KV 電抗器96B1 RY | OTHER | E03/33/2ATR/96B1 |  |  |  | CDC | 462 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | SR96B2 | [17 empty] | 3-32-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_SR96B2 | #2ATR 33KV 電抗器96B2 RY | OTHER | E03/33/2ATR/96B2 |  |  |  | CDC | 463 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | SR96D | [17 empty] | 3-32-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_SR96D | #2ATR 33KV 電抗器96D RY | OTHER | E03/33/2ATR/96D |  |  |  | CDC | 464 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | SR96P | [17 empty] | 3-32-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#2ATR_SR96P | #2ATR 33KV 電抗器96P RY | OTHER | E03/33/2ATR/96P |  |  |  | CDC | 465 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | SR96B1 | [17 empty] | 3-33-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_SR96B1 | #7ATR 33KV 電抗器96B1 RY | OTHER | E03/33/7ATR/96B1 |  |  |  | CDC | 466 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | SR96B2 | [17 empty] | 3-33-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_SR96B2 | #7ATR 33KV 電抗器96B2 RY | OTHER | E03/33/7ATR/96B2 |  |  |  | CDC | 467 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | SR96D | [17 empty] | 3-33-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_SR96D | #7ATR 33KV 電抗器96D RY | OTHER | E03/33/7ATR/96D |  |  |  | CDC | 468 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | SR96P | [17 empty] | 3-33-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#7ATR_SR96P | #7ATR 33KV 電抗器96P RY | OTHER | E03/33/7ATR/96P |  |  |  | CDC | 469 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1510 | 龍崎山上一路(1510) |  | 87CFA | [17 empty] | 1-30-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_87CFA | 龍崎山上一路(1510)87RY通訊故障 | OTHER | E03/161/1510/87CFA |  |  |  | CDC | 470 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1510 | 龍崎山上一路(1510) |  | RYFA | [17 empty] | 1-30-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_RYFA | 龍崎山上一路(1510)數位電驛故障 | OTHER | E03/161/1510/RYFA |  |  |  | CDC | 471 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1520 | 龍崎山上二路(1520) |  | 87CFA | [17 empty] | 1-31-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_87CFA | 龍崎山上二路(1520)87RY通訊故障 | OTHER | E03/161/1520/87CFA |  |  |  | CDC | 472 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1520 | 龍崎山上二路(1520) |  | RYFA | [17 empty] | 1-31-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_RYFA | 龍崎山上二路(1520)數位電驛故障 | OTHER | E03/161/1520/RYFA |  |  |  | CDC | 473 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1530 | 山上二甲三路(1530) |  | 87CFA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1530_87CFA | 山上二甲三路(1530)87RY通訊故障 | OTHER | E03/161/1530/87CFA |  |  |  | CDC | 474 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1530 | 山上二甲三路(1530) |  | RYFA | [17 empty] | 1-31-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1530_RYFA | 山上二甲三路(1530)數位電驛故障 | OTHER | E03/161/1530/RYFA |  |  |  | CDC | 475 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1540 | 山上二甲四路(1540) |  | 87CFA | [17 empty] | 1-31-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1540_87CFA | 山上二甲四路(1540)87RY通訊故障 | OTHER | E03/161/1540/87CFA |  |  |  | CDC | 476 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1540 | 山上二甲四路(1540) |  | RYFA | [17 empty] | 1-31-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1540_RYFA | 山上二甲四路(1540)數位電驛故障 | OTHER | E03/161/1540/RYFA |  |  |  | CDC | 477 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1580 | 龍崎台南海線(1580) |  | 87CFA | [17 empty] | 1-32-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1580_87CFA | 龍崎台南海線(1580)87RY通訊故障 | OTHER | E03/161/1580/87CFA |  |  |  | CDC | 478 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1580 | 龍崎台南海線(1580) |  | RYFA | [17 empty] | 1-32-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1580_RYFA | 龍崎台南海線(1580)數位電驛故障 | OTHER | E03/161/1580/RYFA |  |  |  | CDC | 479 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | 25PFA | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_25PFA | 161KV(N)同步電驛25PFA | OTHER | E03/161/ComPoint/25PFA |  |  |  | CDC | 480 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | 25TA | [17 empty] | 1-14-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_25TA | 161KV(N)同步電驛25TA | OTHER | E03/161/ComPoint/25TA |  |  |  | CDC | 481 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | N |  | ABS_89A | [17 empty] | 1-32-10 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_89A | 161KV(N)ABS NFB 跳脫警報 | OTHER | E03/161/ComPoint/ABS_89A |  |  |  | CDC | 482 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | BFA | [17 empty] | 1-04-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_BFA | 161KV(N)斷路器失靈(BF)RY | OTHER | E03/161/ComPoint/BFA |  |  |  | CDC | 483 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | N |  | BFS | [17 empty] | 1-30-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_BFS | 161KV(N)斷路器失靈RY U/L | OTHER | E03/161/ComPoint/BFS |  |  |  | CDC | 484 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | CBA | [17 empty] | 1-30-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_CBA | 161KV(N)斷路器重故障 | OTHER | E03/161/ComPoint/CBA |  |  |  | CDC | 485 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | CBF | [17 empty] | 1-30-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_CBF | 161KV(N)斷路器輕故障 | OTHER | E03/161/ComPoint/CBF |  |  |  | CDC | 486 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | COMT | [17 empty] | 1-30-07 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_COMT | 161KV(N)空壓機警報 | OTHER | E03/161/ComPoint/COMT |  |  |  | CDC | 487 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | OSCA | [17 empty] | 1-04-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_OSCA | 161KV(N)示波器起動 | OTHER | E03/161/ComPoint/OSCA |  |  |  | CDC | 488 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | _N | N |  | RCA | [17 empty] | 1-04-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_RCA | 161KV(N)LINE 79RY(復閉)動作 | OTHER | E03/161/ComPoint/79UL |  |  |  | CDC | 489 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1760 | #7ATR(1760) |  | E1 | 1761E | [16 empty] | 1-3B-04 | 1-3B-05 | [6 empty] | ADCS_S | [8 empty] | 龍崎ES.1761E_ES | 1761E(#7ATR) ES | OTHER | E03/161/1760/E1 |  |  |  | CDC | 490 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | 25PFA | [17 empty] | 3-16-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_25PFA | 345KV(N)同步電驛25PFA | OTHER | E03/345/ComPoint/25PFA |  |  |  | CDC | 491 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | 25TA | [17 empty] | 3-16-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_25TA | 345KV(N)同步電驛25TA | OTHER | E03/345/ComPoint/25TA |  |  |  | CDC | 492 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | N |  | ABS_89A | [17 empty] | 3-39-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_89A | 345KV(N)ABS NFB 跳脫警報 | OTHER | E03/345/ComPoint/ABS_89A |  |  |  | CDC | 493 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | BFA | [17 empty] | 3-06-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_BFA | 345KV(N)斷路器失靈(BF)警報 | OTHER | E03/345/ComPoint/BFA |  |  |  | CDC | 494 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | N |  | BFS | [17 empty] | 3-35-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_BFS | 345KV(N)斷路器失靈RY U/L | OTHER | E03/345/ComPoint/BFS |  |  |  | CDC | 495 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | CBA | [17 empty] | 3-35-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_CBA | 345KV(N)重故障 | OTHER | E03/345/ComPoint/CBA |  |  |  | CDC | 496 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | CBF | [17 empty] | 3-35-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_CBF | 345KV(N)斷路器輕故障 | OTHER | E03/345/ComPoint/CBF |  |  |  | CDC | 497 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | COMT | [17 empty] | 3-35-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_COMT | 345KV(N)空壓機警報 | OTHER | E03/345/ComPoint/COMT |  |  |  | CDC | 498 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | OSCA | [17 empty] | 3-06-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_OSCA | 345KV(N)示波器起動 | OTHER | E03/345/ComPoint/OSCA |  |  |  | CDC | 499 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | N |  | RCA | [17 empty] | 3-07-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_RCA | 345KV(N)LINE 79RY(復閉)動作 | OTHER | E03/345/ComPoint/RCA |  |  |  | CDC | 500 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | 洩油池 | [17 empty] | 3-39-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_洩油池 | 345KV(N)洩油池水位警報 | OTHER | E03/345/ComPoint/OilLeak |  |  |  | CDC | 501 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3510 | 南科一路(3510) |  | 85CFA | [17 empty] | 3-36-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_85CFA | 南科一路(3510) 85RY通訊故障 | OTHER | E03/345/3510/85CFA |  |  |  | CDC | 502 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3510 | 南科一路(3510) |  | 87CFA | [17 empty] | 3-35-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3510_87CFA | 南科一路(3510) 87RY通訊故障 | OTHER | E03/345/3510/87CFA |  |  |  | CDC | 503 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3560 | 天輪海線(3560) |  | 85CFA | [17 empty] | 3-36-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3560_85CFA | 天輪海線(3560) 85RY通訊故障 | OTHER | E03/345/3560/85CFA |  |  |  | CDC | 504 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3560 | 天輪海線(3560) |  | 87CFA | [17 empty] | 3-36-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3560_87CFA | 天輪海線(3560) 87RY通訊故障 | OTHER | E03/345/3560/87CFA |  |  |  | CDC | 505 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | E2 | 3562E | [16 empty] | 4-36-00 | 4-36-01 | [6 empty] | CDCS_S | [8 empty] | 龍崎ES.3562E_ES | 3562E ES | OTHER | E03/345/3560/E2 |  |  |  | CDC | 506 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | E2 | 3572E | [16 empty] | 3-3E-04 | 3-3E-05 | 3-32 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3572E_ES | 3572E(#5ATR) ES | OTHER | E03/345/3570/E2 |  |  |  | CDC | 507 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 0 |  | 3610 | 南科二路(3610) |  | 85CFA | [17 empty] | 3-37-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_85CFA | 南科二路(3610) 85RY通訊故障 | OTHER | E03/345/3610/85CFA |  |  |  | CDC | 508 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3610 | 南科二路(3610) |  | 87CFA | [17 empty] | 3-37-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3610_87CFA | 南科二路(3610) 87RY通訊故障 | OTHER | E03/345/3610/87CFA |  |  |  | CDC | 509 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3630 | 興達一路(3630) |  | 85CFA | [17 empty] | 3-37-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_85CFA | 興達一路(3630) 85RY通訊故障 | OTHER | E03/345/3630/85CFA |  |  |  | CDC | 510 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3630 | 興達一路(3630) |  | 87CFA | [17 empty] | 3-37-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3630_87CFA | 興達一路(3630) 87RY通訊故障 | OTHER | E03/345/3630/87CFA |  |  |  | CDC | 511 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3640 | 路北紅線(3640) |  | 85CFA | [17 empty] | 3-37-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_85CFA | 路北紅線(3640) 85RY通訊故障 | OTHER | E03/345/3640/85CFA |  |  |  | CDC | 512 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3640 | 路北紅線(3640) |  | 87CFA | [17 empty] | 3-37-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3640_87CFA | 路北紅線(3640) 87RY通訊故障 | OTHER | E03/345/3640/87CFA |  |  |  | CDC | 513 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | E1 | 3911E | [16 empty] | 4-36-02 | 4-36-03 | [6 empty] | CDCS_S | [8 empty] | 龍崎ES.3911E_ES | 3911E ES | OTHER | E03/345/3910/E1 |  |  |  | CDC | 514 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 0 |  | 390 | #1SSTR(390) |  | ABS1 | 391 | [16 empty] | 4-33-10 | 4-33-11 | 3-5A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.391_ABS | 391ABS | OTHER | E03/22/390/ABS1 |  |  |  | CDC | 515 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3920 | 3920 |  | E1 | 3921E | [16 empty] | 4-36-04 | 4-36-05 | [6 empty] | CDCS_S | [8 empty] | 龍崎ES.3921E_ES | 3921E ES | OTHER | E03/345/3920/E1 |  |  |  | CDC | 516 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | E1 | 3931E | [16 empty] | 4-32-04 | 4-32-05 | 3-4E | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3931E_ES | 3931E(#7ATR) ES | OTHER | E03/345/3930/E1 |  |  |  | CDC | 517 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 0 |  | RTU_S_L(N | N |  | 1) | [17 empty] | 3-30-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.RTU_S/L(N_1) | 345KV(N)RTU S/L | OTHER | E03/0/RTU1/RTU_R_L |  |  |  | CDC | 518 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E03 | 龍崎ES | 0 |  | RTU_S_L(N | N |  | 2) | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.RTU_S/L(N_2) | 161KV(N)RTU S/L | OTHER | E03/0/RTU2/RTU_R_L |  |  |  | CDC | 519 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E03 | 龍崎ES | 0 |  | TEST_CB(N | N(TEST_CB(N) |  | 1) | [17 empty] | 3-30-00 |  | 3-00 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.TEST_CB(N_1) | 345KV(N)TEST CB | OTHER | E03/0/RTU/Test_CB1 |  |  |  | CDC | 520 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | TEST_CB(N | N(TEST_CB(N) |  | 2) | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.TEST_CB(N_2) | 161KV(N)TEST CB | OTHER | E03/0/RTU/Test_CB2 |  |  |  | CDC | 521 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | 充電機故障 | 充電機故障 |  | N | [17 empty] | 1-32-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.充電機故障_N | #1,#2,#3直流充電機故障 | OTHER | E03/0/StaDev/CHG1 |  |  |  | CDC | 522 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 直流電源DCE | 直流電源DCE |  | N | [17 empty] | 1-32-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.直流電源DCE_N | #1,#2直流電源接地故障警報 | OTHER | E03/0/StaDev/DCE |  |  |  | CDC | 523 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3520 | 3520 |  | ABS1 | 3521 | [16 empty] | 3-3C-06 | 3-3C-07 | 3-23 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3521_ABS | 3521 ABS | LINE345 | E03/345/3520/ABS1 |  |  |  | CDC | 524 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3520 | 3520 |  | ABS2 | 3522 | [16 empty] | 3-3C-08 | 3-3C-09 | 3-24 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3522_ABS | 3522 ABS | LINE345 | E03/345/3520/ABS2 |  |  |  | CDC | 525 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3550 | 3550 |  | ABS1 | 3551 | [16 empty] | 3-3D-06 | 3-3D-07 | 3-2B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3551_ABS | 3551 ABS | LINE345 | E03/345/3550/ABS1 |  |  |  | CDC | 526 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3550 | 3550 |  | ABS2 | 3552 | [16 empty] | 3-3D-08 | 3-3D-09 | 3-2C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3552_ABS | 3552 ABS | LINE345 | E03/345/3550/ABS2 |  |  |  | CDC | 527 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3620 | 3620 |  | ABS1 | 3621 | [16 empty] | 3-3F-00 | 3-3F-01 | 3-38 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3621_ABS | 3621 ABS | LINE345 | E03/345/3620/ABS1 |  |  |  | CDC | 528 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3620 | 3620 |  | ABS2 | 3622 | [16 empty] | 3-3F-02 | 3-3F-03 | 3-39 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3622_ABS | 3622 ABS | LINE345 | E03/345/3620/ABS2 |  |  |  | CDC | 529 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3650 | 3650 |  | ABS1 | 3651 | [16 empty] | 4-30-06 | 4-30-07 | 3-40 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3651_ABS | 3651 ABS | LINE345 | E03/345/3650/ABS1 |  |  |  | CDC | 530 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 345 | 345kV | 3650 | 3650 |  | ABS2 | 3652 | [16 empty] | 4-30-08 | 4-30-09 | 3-41 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3652_ABS | 3652 ABS | LINE345 | E03/345/3650/ABS2 |  |  |  | CDC | 531 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | _N | _N |  | OSCF | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_N_OSCF | 161KV(N)示波器故障,電源跳脫 | OTHER | E03/161/ComPoint/OSCF |  |  |  | CDC | 532 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | _N | _N |  | OSCF | [17 empty] | 3-39-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_N_OSCF | 345KV(N)示波器故障,電源跳脫 | OTHER | E03/345/ComPoint/OSCF |  |  |  | CDC | 533 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | PHA | [17 empty] | 1-03-00 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1550_PHA | 龍崎台南山線(1550) 相間RY | LINE161 | E03/161/1550/PHA |  |  |  | CDC | 534 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | GDA | [17 empty] | 1-03-01 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1550_GDA | 龍崎台南山線(1550) 接地RY | LINE161 | E03/161/1550/GDA |  |  |  | CDC | 535 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 87A | [17 empty] | 1-02-07 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1550_87A | 龍崎台南山線(1550) 87RY | LINE161 | E03/161/1550/85A |  |  |  | CDC | 536 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 87UL | [17 empty] | 1-31-11 |  | 1-39 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1550_87UL | 龍崎台南山線(1550) 87RY U/L | LINE161 | E03/161/1550/85UL2 |  |  |  | CDC | 537 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | CB | [17 empty] | 1-02-06 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1550_CB | 1550(龍崎台南山線) CB | LINE161 | E03/161/1550/CB |  |  |  | CDC | 538 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | 79UL | [17 empty] | 1-31-10 |  | 1-38 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1550_79UL | 龍崎台南山線(1550) 79RY U/L | LINE161 | E03/161/1550/79UL |  |  |  | CDC | 539 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | ABS1 | 1551 | [16 empty] | 1-39-12 | 1-39-13 | 1-22 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1551_ABS | 1551(龍崎台南山線) ABS | LINE161 | E03/161/1550/ABS1 |  |  |  | CDC | 540 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | ABS2 | 1552 | [16 empty] | 1-39-14 | 1-39-15 | 1-23 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1552_ABS | 1552(龍崎台南山線) ABS | LINE161 | E03/161/1550/ABS2 |  |  |  | CDC | 541 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | E2 | 1552E | [16 empty] | 1-3B-12 | 1-3B-13 | 1-25 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1552E_ES | 1552E(龍崎台南山線) ES | LINE161 | E03/161/1550/E2 |  |  |  | CDC | 542 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎台南山線(1560) |  | CB | [17 empty] | 1-05-01 |  | 1-09 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1560_CB | 1560(龍崎台南山線) CB | LINE161 | E03/161/1560/CB |  |  |  | CDC | 543 | GENERICDIPoint | ES003_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎台南山線(1560) |  | ABS1 | 1561 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-2C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1561_ABS | 1561(龍崎台南山線) ABS | LINE161 | E03/161/1560/ABS1 |  |  |  | CDC | 544 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎台南山線(1560) |  | ABS2 | 1562 | [16 empty] | 1-3B-10 | 1-3B-11 | 1-2D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1562_ABS | 1562(龍崎台南山線) ABS | LINE161 | E03/161/1560/ABS2 |  |  |  | CDC | 545 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 1550 | 龍崎台南山線(1550) |  | 87CFA | [17 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1550_87CFA | 龍崎台南山線(1550)87RY通訊故障 | OTHER | E03/161/1550/87CFA |  |  |  | CDC | 546 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1550 | 龍崎台南山線(1550) |  | RYFA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1550_RYFA | 龍崎台南山線(1550)數位電驛故障 | OTHER | E03/161/1550/RYFA |  |  |  | CDC | 547 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | CB | [17 empty] | 3-01-00 |  | 3-09 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1910_CB | 1910(#5ATR) CB | ATR | E03/161/1910/CB |  |  |  | CDC | 548 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | DS1 | 1911 | [16 empty] | 4-32-08 | 4-32-09 | 3-50 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1911_DS | 1911(#5ATR) DS | ATR | E03/161/1910/DS1 |  |  |  | CDC | 549 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | DS2 | 1912 | [16 empty] | 4-32-10 | 4-32-11 | 3-51 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1912_DS | 1912(#5ATR) DS | ATR | E03/161/1910/DS2 |  |  |  | CDC | 550 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1920 | #5ATR(1920) |  | CB | [17 empty] | 3-0A-00 |  | 4-08 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1920_CB | 1920(#5ATR) CB | ATR | E03/161/1920/CB |  |  |  | CDC | 551 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1920 | #5ATR(1920) |  | DS1 | 1921 | [16 empty] | 4-37-04 | 4-37-05 | 4-10 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1921_DS | 1921(#5ATR) DS | ATR | E03/161/1920/DS1 |  |  |  | CDC | 552 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1920 | #5ATR(1920) |  | DS2 | 1922 | [16 empty] | 4-37-08 | 4-37-09 | 4-11 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1922_DS | 1922(#5ATR) DS | ATR | E03/161/1920/DS2 |  |  |  | CDC | 553 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 590 | #3SSTR(590) |  | CB | [17 empty] | 3-14-00 |  | 3-0A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.590_CB | 590(#3SSTR) CB | OTHER | E03/22/3SSTR/CB |  |  |  | CDC | 554 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 550 | 550 |  | CB | [17 empty] | 3-15-02 |  | 3-7E | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.550_CB | 550 CB | OTHER | E03/33/550/CB |  |  |  | CDC | 555 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 550 | 550 |  | 87A | [17 empty] | 3-15-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.550_87A | 550 87RY | OTHER | E03/33/550/87A |  |  |  | CDC | 556 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 550 | 550 |  | PHA | [17 empty] | 3-15-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.550_PHA | 550 相間RY | OTHER | E03/33/550/PHA |  |  |  | CDC | 557 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 550 | 550 |  | ABS1 | 551 | [16 empty] | 4-34-00 | 4-34-01 | 3-7F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.551_ABS | 551 ABS | OTHER | E03/33/550/ABS1 |  |  |  | CDC | 558 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 2SR96B1 | [17 empty] | 3-3A-14 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_2SR96B1 | #5ATR 161KV 電抗器96B1 RY | OTHER | E03/161/5SR/96B1 |  |  |  | CDC | 559 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 2SR96B2 | [17 empty] | 3-3A-15 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_2SR96B2 | #5ATR 161KV 電抗器96B2 RY | OTHER | E03/161/5SR/96B2 |  |  |  | CDC | 560 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 2SR96D | [17 empty] | 3-3B-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_2SR96D | #5ATR 161KV 電抗器96D RY | OTHER | E03/161/5SR/96D |  |  |  | CDC | 561 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 2SR96P | [17 empty] | 3-3B-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_2SR96P | #5ATR 161KV 電抗器96P RY | OTHER | E03/161/5SR/96P |  |  |  | CDC | 562 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 2SRTRA | [17 empty] | 3-3A-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_2SRTRA | #5ATR 161KV 電抗器 重故障 | OTHER | E03/161/5SR/SHRA |  |  |  | CDC | 563 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 2SRTRF | [17 empty] | 3-3A-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_2SRTRF | #5ATR 161KV 電抗器 輕故障 | OTHER | E03/161/5SR/SHRF |  |  |  | CDC | 564 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | SR96B1 | [17 empty] | 3-34-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_SR96B1 | #5ATR 33KV 電抗器96B1 RY | OTHER | E03/33/5ATR/96B1 |  |  |  | CDC | 565 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | SR96B2 | [17 empty] | 3-34-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_SR96B2 | #5ATR 33KV 電抗器96B2 RY | OTHER | E03/33/5ATR/96B2 |  |  |  | CDC | 566 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | SR96D | [17 empty] | 3-34-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_SR96D | #5ATR 33KV 電抗器96D RY | OTHER | E03/33/5ATR/96D |  |  |  | CDC | 567 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | SR96P | [17 empty] | 3-34-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#5ATR_SR96P | #5ATR 33KV 電抗器96P RY | OTHER | E03/33/5ATR/96P |  |  |  | CDC | 568 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1910 | #5ATR(1910) |  | E2 | 1912E | [16 empty] | 4-37-06 | 4-37-07 | [6 empty] | ADCS_S | [8 empty] | 龍崎ES.1912E_ES | 1912E(#5ATR) ES | OTHER | E03/161/1910/E2 |  |  |  | CDC | 569 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 0 |  | 590 | #3SSTR(590) |  | ABS1 | 591 | [16 empty] | 4-36-06 | 4-36-07 | 3-52 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.591_ABS | 591ABS | OTHER | E03/33/590/ABS1 |  |  |  | CDC | 570 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | CB | [17 empty] | 3-02-04 |  | 3-11 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1810_CB | 1810(#1ATR) CB | ATR | E03/161/1810/CB |  |  |  | CDC | 571 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS1 | 1811 | [16 empty] | 4-32-12 | 4-32-13 | 3-53 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1811_DS | 1811(#1ATR) DS | ATR | E03/161/1810/DS1 |  |  |  | CDC | 572 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | DS2 | 1812 | [16 empty] | 4-32-14 | 4-32-15 | 3-54 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1812_DS | 1812(#1ATR) DS | ATR | E03/161/1810/DS2 |  |  |  | CDC | 573 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | CB | [17 empty] | 3-0A-01 |  | 4-09 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1820_CB | 1820(#1ATR) CB | ATR | E03/161/1820/CB |  |  |  | CDC | 574 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | DS1 | 1821 | [16 empty] | 4-36-10 | 4-36-11 | 4-12 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1821_DS | 1821(#1ATR) DS | ATR | E03/161/1820/DS1 |  |  |  | CDC | 575 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1820 | #1ATR(1820) |  | DS2 | 1822 | [16 empty] | 4-36-14 | 4-36-15 | 4-13 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1822_DS | 1822(#1ATR) DS | ATR | E03/161/1820/DS2 |  |  |  | CDC | 576 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 2SR96B1 | [17 empty] | 3-3A-02 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_2SR96B1 | #1ATR 161KV 電抗器96B1 RY | OTHER | E03/161/1SR/96B1 |  |  |  | CDC | 577 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 2SR96B2 | [17 empty] | 3-3A-03 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_2SR96B2 | #1ATR 161KV 電抗器96B2 RY | OTHER | E03/161/1SR/96B2 |  |  |  | CDC | 578 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 2SR96D | [17 empty] | 3-3A-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_2SR96D | #1ATR 161KV 電抗器96D RY | OTHER | E03/161/1SR/96D |  |  |  | CDC | 579 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 2SR96P | [17 empty] | 3-3A-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_2SR96P | #1ATR 161KV 電抗器96P RY | OTHER | E03/161/1SR/96P |  |  |  | CDC | 580 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 2SRTRA | [17 empty] | 3-3A-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_2SRTRA | #1ATR 161KV 電抗器 重故障 | OTHER | E03/161/1SR/SHRA |  |  |  | CDC | 581 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 2SRTRF | [17 empty] | 3-3A-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_2SRTRF | #1ATR 161KV 電抗器 輕故障 | OTHER | E03/161/1SR/SHRF |  |  |  | CDC | 582 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | DS1 | 1571 | [16 empty] | 1-3B-14 | 1-3B-15 | 1-2E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1571_DS | 1571(龍崎台南海線) DS | LINE161 | E03/161/1570/DS1 |  |  |  | CDC | 583 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | E2 | 1572E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-29 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1572E_ES | 1572E(龍崎台南海線) ES | LINE161 | E03/161/1570/E2 |  |  |  | CDC | 584 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | DS1 | 1581 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-26 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1581_DS | 1581(龍崎台南海線) DS | LINE161 | E03/161/1580/DS1 |  |  |  | CDC | 585 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | DS2 | 1582 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-27 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1582_DS | 1582(龍崎台南海線) DS | LINE161 | E03/161/1580/DS2 |  |  |  | CDC | 586 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | DS2 | 1572 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-2F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1572_DS | 1572(龍崎台南海線) DS | LINE161 | E03/161/1570/DS2 |  |  |  | CDC | 587 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1810 | #1ATR(1810) |  | E2 | 1812E | [16 empty] | 4-36-12 | 4-36-13 | [6 empty] | ADCS_S | [8 empty] | 龍崎ES.1812E_ES | 1812E(#1ATR) ES | OTHER | E03/161/1810/E2 |  |  |  | CDC | 588 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 161_NBUS | #1,2BUS |  | 87CTFA | [17 empty] | 1-32-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161_NBUS_CTFA | 161KV#1,2BUS 87RYCT迴路故障 | OTHER | E03/161/ComPoint/87CTFA |  |  |  | CDC | 589 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 161_NBUS | #1,2BUS |  | RYFA | [17 empty] | 1-32-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161_NBUS_RYFA | 161KV#1,2BUS 87RY數位電驛故障 | OTHER | E03/161/ComPoint/BUS_RYFA |  |  |  | CDC | 590 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | CB | [17 empty] | 3-03-04 |  | 3-15 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1840_CB | 1840(#2ATR) CB | ATR | E03/161/1840/CB |  |  |  | CDC | 591 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | DS1 | 1841 | [16 empty] | 4-33-04 | 4-33-05 | 3-57 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1841_DS | 1841(#2ATR) DS | ATR | E03/161/1840/DS1 |  |  |  | CDC | 592 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1840 | #2ATR(1840) |  | DS2 | 1842 | [16 empty] | 4-33-06 | 4-33-07 | 3-58 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1842_DS | 1842(#2ATR) DS | ATR | E03/161/1840/DS2 |  |  |  | CDC | 593 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | CB | [17 empty] | 3-0A-02 |  | 4-0A | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1830_CB | 1830(#2ATR) CB | ATR | E03/161/1830/CB |  |  |  | CDC | 594 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | DS1 | 1831 | [16 empty] | 4-37-00 | 4-37-01 | 4-14 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1831_DS | 1831(#2ATR) DS | ATR | E03/161/1830/DS1 |  |  |  | CDC | 595 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | DS2 | 1832 | [16 empty] | 4-37-02 | 4-37-03 | 4-15 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1832_DS | 1832(#2ATR) DS | ATR | E03/161/1830/DS2 |  |  |  | CDC | 596 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E03 | 龍崎ES | 161 | 161kV | 1830 | #2ATR(1830) |  | E2 | 1832E | [16 empty] | 4-36-08 | 4-36-09 | [6 empty] | ADCS_S | [8 empty] | 龍崎ES.1832E_ES | 1832E(#2ATR) ES | OTHER | E03/161/1830/E2 |  |  |  | CDC | 597 | GENERICDIPoint | ES003_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 2SR96B1 | [17 empty] | 3-3A-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_2SR96B1 | #2ATR 161KV 電抗器96B1 RY | OTHER | E03/161/2SR/96B1 |  |  |  | CDC | 598 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 2SR96B2 | [17 empty] | 3-3A-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_2SR96B2 | #2ATR 161KV 電抗器96B2 RY | OTHER | E03/161/2SR/96B2 |  |  |  | CDC | 599 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 2SR96D | [17 empty] | 3-3A-10 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_2SR96D | #2ATR 161KV 電抗器96D RY | OTHER | E03/161/2SR/96D |  |  |  | CDC | 600 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 2SR96P | [17 empty] | 3-3A-11 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_2SR96P | #2ATR 161KV 電抗器96P RY | OTHER | E03/161/2SR/96P |  |  |  | CDC | 601 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 2SRTRA | [17 empty] | 3-3A-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_2SRTRA | #2ATR 161KV 電抗器 重故障 | OTHER | E03/161/2SR/SHRA |  |  |  | CDC | 602 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 2SRTRF | [17 empty] | 3-3A-07 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_2SRTRF | #2ATR 161KV 電抗器 輕故障 | OTHER | E03/161/2SR/SHRF |  |  |  | CDC | 603 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 2SR96B1 | [17 empty] | 3-3B-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_2SR96B1 | #7ATR 161KV 電抗器96B1 RY | OTHER | E03/161/7SR/96B1 |  |  |  | CDC | 604 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 2SR96B2 | [17 empty] | 3-3B-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_2SR96B2 | #7ATR 161KV 電抗器96B2 RY | OTHER | E03/161/7SR/96B2 |  |  |  | CDC | 605 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 2SR96D | [17 empty] | 3-3B-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_2SR96D | #7ATR 161KV 電抗器96D RY | OTHER | E03/161/7SR/96D |  |  |  | CDC | 606 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 2SR96P | [17 empty] | 3-3B-07 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_2SR96P | #7ATR 161KV 電抗器96P RY | OTHER | E03/161/7SR/96P |  |  |  | CDC | 607 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 2SRTRA | [17 empty] | 3-3B-02 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_2SRTRA | #7ATR 161KV 電抗器 重故障 | OTHER | E03/161/7SR/SHRA |  |  |  | CDC | 608 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 2SRTRF | [17 empty] | 3-3B-03 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_2SRTRF | #7ATR 161KV 電抗器 輕故障 | OTHER | E03/161/7SR/SHRF |  |  |  | CDC | 609 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | ACB | 所內電源ACB |  | TIE1 | [17 empty] | 3-38-01 |  | 4-01 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.ACB_TIE1 | 所內電源ACB TIE1 | OTHER | E03/0/StaDev/ACBT1 |  |  |  | CDC | 610 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E03 | 龍崎ES | 0 |  | 1510 | 龍崎山上一路(1510) |  | 50SA | [17 empty] | 1-32-06 |  | 1-3D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1510_50SA | 山上一路(1510) 50RY 測試/正常 | OTHER | E03/161/1510/50SA |  |  |  | CDC | 611 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1520 | 龍崎山上二路(1520) |  | 50SA | [17 empty] | 1-32-07 |  | 1-3C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1520_50SA | 山上二路(1520) 50RY 測試/正常 | OTHER | E03/161/1520/50SA |  |  |  | CDC | 612 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | BUS | #1,2BUS |  | CTFA1 | [17 empty] | 3-35-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_CTFA1 | 345KV #1,2BUS 第一套CT回路故障 | OTHER | E03/345/ComPoint/87CTFA1 |  |  |  | CDC | 613 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | BUS | #1,2BUS |  | RYFA1 | [17 empty] | 3-35-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_RYFA1 | 345KV #1,2BUS 第一套數位RY故障 | OTHER | E03/345/ComPoint/RYFA1 |  |  |  | CDC | 614 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | BUS | #1,2BUS |  | CTFA2 | [17 empty] | 3-38-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_CTFA2 | 345KV #1,2BUS 第二套CT回路故障 | OTHER | E03/345/ComPoint/87CTFA2 |  |  |  | CDC | 615 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | BUS | #1,2BUS |  | RYFA2 | [17 empty] | 3-38-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_RYFA2 | 345KV #1,2BUS 第二套數位RY故障 | OTHER | E03/345/ComPoint/RYFA2 |  |  |  | CDC | 616 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV |  |  |  | DCA | [17 empty] | 3-39-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_DCA | 345KV直流電源故障警報 | OTHER | E03/345/ComPoint/DCA |  |  |  | CDC | 617 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | 87A1 | [17 empty] | 3-07-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3530_87A1 | 北南臨時線(3530) #1_187RY | LINE345 | E03/345/3530/1SSA1 |  |  |  | CDC | 618 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | 87A2 | [17 empty] | 3-07-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3530_87A2 | 北南臨時線(3530) #1_287RY | LINE345 | E03/345/3530/1SSA2 |  |  |  | CDC | 619 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | 2_87A1 | [17 empty] | 3-07-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3530_87A3 | 北南臨時線(3530) #2_187RY | LINE345 | E03/345/3530/2SSA |  |  |  | CDC | 620 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | 87A1 | [17 empty] | 3-07-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_87A1 | 瀰力二路(3540) #1_187RY | LINE345 | E03/345/3540/1SSA1 |  |  |  | CDC | 621 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | 87A2 | [17 empty] | 3-08-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_87A2 | 瀰力二路(3540) #1_287RY | LINE345 | E03/345/3540/1SSA2 |  |  |  | CDC | 622 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | 2_87A1 | [17 empty] | 3-08-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_87A3 | 瀰力二路(3540) #2_187RY | LINE345 | E03/345/3540/2SSA |  |  |  | CDC | 623 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3530 | 北南臨時線(3530) |  | 87CFA1 | [17 empty] | 3-36-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3530_87CFA1 | 北南臨時線(3530) #187RY_CFA | OTHER | E03/345/3530/87CFA1 |  |  |  | CDC | 624 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3530 | 北南臨時線(3530) |  | 87CFA2 | [17 empty] | 3-36-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3530_87CFA2 | 北南臨時線(3530) #285RY_CFA | OTHER | E03/345/3530/87CFA2 |  |  |  | CDC | 625 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 2_87A2 | [17 empty] | 3-0B-02 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_87A4 | 瀰力二路(3540) #2_287RY | OTHER | E03/345/3540/2_87A2 |  |  |  | CDC | 626 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 87CFA1 | [17 empty] | 3-36-08 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_87CFA1 | 瀰力二路(3540) #187RY通訊故障 | OTHER | E03/345/3540/87CFA1 |  |  |  | CDC | 627 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 87CFA2 | [17 empty] | 3-36-10 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_87CFA2 | 瀰力二路(3540) #287RY通訊故障 | OTHER | E03/345/3540/87CFA2 |  |  |  | CDC | 628 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 1_87UL1 | [17 empty] | 3-34-01 |  | 3-5B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_87UL1 | 瀰力二路(3540)#1_187RY U/L | OTHER | E03/345/3540/1_87UL1 |  |  |  | CDC | 629 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 1_87UL2 | [17 empty] | 3-34-02 |  | 3-5C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_87UL2 | 瀰力二路(3540)#1_287RY U/L | OTHER | E03/345/3540/1_87UL2 |  |  |  | CDC | 630 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 2_87UL1 | [17 empty] | 3-34-03 |  | 3-5D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_87UL3 | 瀰力二路(3540)#2_187RY U/L | OTHER | E03/345/3540/2_87UL1 |  |  |  | CDC | 631 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | 2_87UL2 | [17 empty] | 3-34-04 |  | 3-56 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_87UL4 | 瀰力二路(3540)#2_287RY U/L | OTHER | E03/345/3540/2_87UL2 |  |  |  | CDC | 632 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | DTTA1 | [17 empty] | 3-0B-07 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_DTTA1 | 瀰力二路(3540)#1_1遠方遙跳 | OTHER | E03/345/3540/DTTA1 |  |  |  | CDC | 633 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | DTTA2 | [17 empty] | 3-0C-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_DTTA2 | 瀰力二路(3540)#1_2遠方遙跳 | OTHER | E03/345/3540/DTTA2 |  |  |  | CDC | 634 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | DTTA3 | [17 empty] | 3-0C-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_DTTA3 | 瀰力二路(3540)#2_1遠方遙跳 | OTHER | E03/345/3540/1A5Other |  |  |  | CDC | 635 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | DTTA4 | [17 empty] | 3-0C-02 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3540_DTTA4 | 瀰力二路(3540)#2_2遠方遙跳 | OTHER | E03/345/3540/2A5Other |  |  |  | CDC | 636 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | GDA1 | [17 empty] | 3-0A-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_GDA1 | 瀰力二路(3540) #1接地RY | OTHER | E03/345/3540/GDA1 |  |  |  | CDC | 637 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | GDA2 | [17 empty] | 3-0B-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_GDA2 | 瀰力二路(3540) #2接地RY | OTHER | E03/345/3540/GDA2 |  |  |  | CDC | 638 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | PHA1 | [17 empty] | 3-0A-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_PHA1 | 瀰力二路(3540) #1相間RY | OTHER | E03/345/3540/PHA1 |  |  |  | CDC | 639 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3540 | 瀰力二路(3540) |  | PHA2 | [17 empty] | 3-0B-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3540_PHA2 | 瀰力二路(3540) #2相間RY | OTHER | E03/345/3540/PHA2 |  |  |  | CDC | 640 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 161 | 161kV |  |  |  | NBFRYFA | [17 empty] | 1-32-14 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_NBFRYFA | 161KV(N)斷路器失靈電驛故障 | OTHER | E03/161/ComPoint/RYFA |  |  |  | CDC | 641 | GENERICDIPoint | ES003_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV |  |  |  | NBFRYFA | [17 empty] | 3-35-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_NBFRYFA | 345KV(N)斷路器失靈電驛故障 | OTHER | E03/345/ComPoint/RYFA |  |  |  | CDC | 642 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | 51Z_UL | [17 empty] | 3-39-13 |  | 4-20 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_51ZUL | #7ATR 51ZRY U/L | OTHER | E03//7ATR/51Z_UL |  |  |  | CDC | 643 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 7ATR_570 | #7ATR |  | 87UL | [17 empty] | 3-39-15 |  | 4-21 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_570_87UL | #7ATR 電抗器(570) 87RY U/L | OTHER | E03/33/570/87UL |  |  |  | CDC | 644 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | ATR_86A | [17 empty] | 3-39-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_86A | #7ATR 86(51Z/87/96)RY | OTHER | E03//7ATR/ATR_86A |  |  |  | CDC | 645 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 7ATR | #7ATR |  | RYFA | [17 empty] | 3-39-14 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#7ATR_RYFA | #7ATR 數位電驛故障 | OTHER | E03//7ATR/RYFA |  |  |  | CDC | 646 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | 51Z_UL | [17 empty] | 3-39-05 |  | 4-18 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_51ZUL | #2ATR 51ZRY U/L | OTHER | E03//2ATR/51Z_UL |  |  |  | CDC | 647 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 2ATR_520 | #2ATR |  | 87UL | [17 empty] | 3-39-07 |  | 4-19 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_520_87UL | #2ATR 電抗器(520) 87RY U/L | OTHER | E03/33/520/87UL |  |  |  | CDC | 648 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | ATR_86A | [17 empty] | 3-39-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_86A | #2ATR 86(51Z/87/96)RY | OTHER | E03//2ATR/ATR_86A |  |  |  | CDC | 649 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 2ATR | #2ATR |  | RYFA | [17 empty] | 3-39-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2ATR_RYFA | #2ATR 數位電驛故障 | OTHER | E03//2ATR/RYFA |  |  |  | CDC | 650 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | 51Z_UL | [17 empty] | 3-39-09 |  | 4-1C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_51ZUL | #5ATR 51ZRY U/L | OTHER | E03//5ATR/51Z_UL |  |  |  | CDC | 651 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 5ATR_550 | #5ATR |  | 87UL | [17 empty] | 3-39-11 |  | 4-1D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_550_87UL | #5ATR 電抗器(550) 87RY U/L | OTHER | E03/33/550/87UL |  |  |  | CDC | 652 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | ATR_86A | [17 empty] | 3-39-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_86A | #5ATR 86(51Z/87/96)RY | OTHER | E03//5ATR/ATR_86A |  |  |  | CDC | 653 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 5ATR | #5ATR |  | RYFA | [17 empty] | 3-39-10 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#5ATR_RYFA | #5ATR 數位電驛故障 | OTHER | E03//5ATR/RYFA |  |  |  | CDC | 654 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR_510 | #1ATR |  | 87UL | [17 empty] | 3-38-12 |  | 4-0E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_510_87UL | #1ATR 電抗器(510) 87RY U/L | OTHER | E03/33/510/87UL |  |  |  | CDC | 655 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | 51Z_UL | [17 empty] | 3-38-10 |  | 4-0D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_51ZUL | #1ATR 51ZRY U/L | OTHER | E03//1ATR/51Z_UL |  |  |  | CDC | 656 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | ATR_86A | [17 empty] | 3-38-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_86A | #1ATR 86(51Z/87/96)RY | OTHER | E03//1ATR/ATR_86A |  |  |  | CDC | 657 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 1ATR | #1ATR |  | RYFA | [17 empty] | 3-38-11 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#1ATR_RYFA | #1ATR 數位電驛故障 | OTHER | E03//1ATR/RYFA |  |  |  | CDC | 658 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | PHA | [17 empty] | 3-04-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3910_PHA | 備用線(3910) 相間RY | LINE345 | E03/345/3910/PHA |  |  |  | CDC | 659 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | GDA | [17 empty] | 3-04-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3910_GDA | 備用線(3910) 接地RY | LINE345 | E03/345/3910/GDA |  |  |  | CDC | 660 | GENERICDIPoint | ES003_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 3910 | #7ATR(3910) |  | RYFA | [17 empty] | 3-34-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.3910_RYFA | 備用線(3910)數位電驛故障 | OTHER | E03/345/3910/RYFA |  |  |  | CDC | 661 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | _N | N |  | CBA | [17 empty] | 3-35-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.33KV_N_CBA | 33KV(N) CB重故障 | OTHER | E03/33/ComPoint/CBA |  |  |  | CDC | 662 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | _N | N |  | CBF | [17 empty] | 3-35-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.33KV_N_CBF | 33KV(N) CB輕故障 | OTHER | E03/33/ComPoint/CBF |  |  |  | CDC | 663 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E03 | 龍崎ES | 33 | 33kV | _N | N |  | COMT | [17 empty] | 3-35-10 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.33KV_N_COMT | 33KV(N) 空壓機運轉超時警報 | OTHER | E03/33/ComPoint/COMT |  |  |  | CDC | 664 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | 有感地震警報 | 有感地震警報 |  | EQA | [17 empty] | 3-31-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.EQA | 有感地震警報 EQA | OTHER |  |  |  |  | CDC | 665 | GENERICDIPoint | ES003_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E03 | 龍崎ES | 0 |  | NA | NA |  | 01 | [25 empty] | CDCS | [8 empty] | 龍崎ES.NA_01 | 龍崎ES裝置容量 | [6 empty] | 666 | NotelAIPoint | [21 empty] | MW | 10000.000000 | 10000.000000 | 10000.000000 | 10000.000000 | 0.100000 | -10000.000000 | -10000.000000 | -10000.000000 | -10000.000000
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | LE0 | 3510LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3510LE | 3510LE (非取樣點) | LINE345 | E03/345/3510/LE0 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3510 | 南科一路(3510) |  | BE0 | 3510BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3510BE | 3510BE (非取樣點) | LINE345 | E03/345/3510/BE0 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | LE0 | 3530LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3530LE | 3530LE (非取樣點) | LINE345 | E03/345/3530/LE0 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3530 | 北南臨時線(3530) |  | BE0 | 3530BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3530BE | 3530BE (非取樣點) | LINE345 | E03/345/3530/BE0 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | LE0 | 3540LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3540LE | 3540LE (非取樣點) | LINE345 | E03/345/3540/LE0 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3540 | 瀰力二路(3540) |  | BE0 | 3540BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3540BE | 3540BE (非取樣點) | LINE345 | E03/345/3540/BE0 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | LE0 | 3560LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3560LE | 3560LE (非取樣點) | LINE345 | E03/345/3560/LE0 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3560 | 天輪海線(3560) |  | BE0 | 3560BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3560BE | 3560BE (非取樣點) | LINE345 | E03/345/3560/BE0 |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | TE0 | 3590TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3590TE | 3590TE (非取樣點) | LINE345 | E03/345/3590/TE0 |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3590 | #5ATR(3590) |  | BE0 | 3590BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3590BE | 3590BE (非取樣點) | LINE345 | E03/345/3590/BE0 |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | LE0 | 3610LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3610LE | 3610LE (非取樣點) | LINE345 | E03/345/3610/LE0 |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3610 | 南科二路(3610) |  | BE0 | 3610BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3610BE | 3610BE (非取樣點) | LINE345 | E03/345/3610/BE0 |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | LE0 | 3630LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3630LE | 3630LE (非取樣點) | LINE345 | E03/345/3630/LE0 |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3630 | 興達一路(3630) |  | BE0 | 3630BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3630BE | 3630BE (非取樣點) | LINE345 | E03/345/3630/BE0 |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | LE0 | 3640LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3640LE | 3640LE (非取樣點) | LINE345 | E03/345/3640/LE0 |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3640 | 路北紅線(3640) |  | BE0 | 3640BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3640BE | 3640BE (非取樣點) | LINE345 | E03/345/3640/BE0 |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | LE0 | 3690LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3690LE | 3690LE (非取樣點) | LINE345 | E03/345/3690/E1 |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3690 | #2ATR(3690) |  | BE0 | 3690BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3690BE | 3690BE (非取樣點) | LINE345 | E03/345/3690/E2 |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | TE0 | 3910TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3910TE | 3910TE (非取樣點) | LINE345 | E03/345/3910/TE0 |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3910 | #7ATR(3910) |  | BE0 | 3910BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3910BE | 3910BE (非取樣點) | LINE345 | E03/345/3910/BE0 |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3520 | 3520 |  | E1 | 3521E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3521E | 3521E (非取樣點) | LINE345 | E03/345/3520/E1 |  |  |  |  | 687 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3520 | 3520 |  | E2 | 3522E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3522E | 3522E (非取樣點) | LINE345 | E03/345/3520/E2 |  |  |  |  | 688 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3550 | 3550 |  | E1 | 3551E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3551E | 3551E (非取樣點) | LINE345 | E03/345/3550/E1 |  |  |  |  | 689 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3550 | 3550 |  | E2 | 3552E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3552E | 3552E (非取樣點) | LINE345 | E03/345/3550/E2 |  |  |  |  | 690 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3620 | 3620 |  | E1 | 3621E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3621E | 3621E (非取樣點) | LINE345 | E03/345/3620/E1 |  |  |  |  | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3620 | 3620 |  | E2 | 3622E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3622E | 3622E (非取樣點) | LINE345 | E03/345/3620/E2 |  |  |  |  | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3650 | 3650 |  | E1 | 3651E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3651E | 3651E (非取樣點) | LINE345 | E03/345/3650/E1 |  |  |  |  | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3650 | 3650 |  | E2 | 3652E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3652E | 3652E (非取樣點) | LINE345 | E03/345/3650/E2 |  |  |  |  | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3920 | 3920 |  | E2 | 3922E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3922E | 3922E (非取樣點) | LINE345 | E03/345/3920/E2 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | E03/161/1510/LE0 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1510 | 龍崎山上一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1510BE | 1510BE (非取樣點) | LINE161 | E03/161/1510/BE0 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1520LE | 1520LE (非取樣點) | LINE161 | E03/161/1520/LE0 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1520 | 龍崎山上二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1520BE | 1520BE (非取樣點) | LINE161 | E03/161/1520/BE0 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1530LE | 1530LE (非取樣點) | LINE161 | E03/161/1530/LE0 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1530 | 山上二甲三路(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1530BE | 1530BE (非取樣點) | LINE161 | E03/161/1530/BE0 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1540LE | 1540LE (非取樣點) | LINE161 | E03/161/1540/LE0 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1540 | 山上二甲四路(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1540BE | 1540BE (非取樣點) | LINE161 | E03/161/1540/BE0 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1570LE | 1570LE (非取樣點) | LINE161 | E03/161/1570/LE0 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1570 | 龍崎台南海線(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1570BE | 1570BE (非取樣點) | LINE161 | E03/161/1570/BE0 |  |  |  |  | 705 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1580LE | 1580LE (非取樣點) | LINE161 | E03/161/1580/LE0 |  |  |  |  | 706 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1580 | 龍崎台南海線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1580BE | 1580BE (非取樣點) | LINE161 | E03/161/1580/BE0 |  |  |  |  | 707 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | E1 | 1701E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1701E | 1701E (非取樣點) | TIE | E03/161/1700/E1 |  |  |  |  | 708 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1700 | TIE(1700) |  | E3 | 1703E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1703E | 1703E (非取樣點) | TIE | E03/161/1700/E2 |  |  |  |  | 709 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | TE0 | 3660TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3660TE | 3660TE (非取樣點) | ATR | E03/345/3660/E1 |  |  |  |  | 710 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3660 | #1ATR(3660) |  | BE0 | 3660BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3660BE | 3660BE (非取樣點) | ATR | E03/345/3660/E2 |  |  |  |  | 711 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | TE0 | 3670TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3670TE | 3670TE (非取樣點) | ATR | E03/345/3670/TE0 |  |  |  |  | 712 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3670 | #2ATR(3670) |  | BE0 | 3670BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3670BE | 3670BE (非取樣點) | ATR | E03/345/3670/BE0 |  |  |  |  | 713 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | TE0 | 3570TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3570TE | 3570TE (非取樣點) | ATR | E03/345/3570/TE0 |  |  |  |  | 714 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3570 | #5ATR(3570) |  | BE0 | 3570BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3570BE | 3570BE (非取樣點) | ATR | E03/345/3570/BE0 |  |  |  |  | 715 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | TE0 | 3930TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3930TE | 3930TE (非取樣點) | ATR | E03/345/3930/TE0 |  |  |  |  | 716 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3930 | #7ATR(3930) |  | BE0 | 3930BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3930BE | 3930BE (非取樣點) | ATR | E03/345/3930/BE0 |  |  |  |  | 717 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.161B1E | 161B1E (非取樣點) | BUS | E03/161/161B1E/BE1 |  |  |  |  | 718 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.161B2E | 161B2E (非取樣點) | BUS | E03/161/161B2E/BE2 |  |  |  |  | 719 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 720 | NotelDIPoint | [38 empty] | START/STOP | STOP
E03 | 龍崎ES | 0 |  |  |  |  | 1750BE | 1750BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1750BE | 1750BE(#7ATR)(非取樣點) | OTHER | E03/161/1750/BE0 |  |  |  |  | 721 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1750TE | 1750TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1750TE | 1750TE(#7ATR)(非取樣點) | OTHER | E03/161/1750/TE0 |  |  |  |  | 722 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1760BE | 1760BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1760BE | 1760BE(#7ATR)(非取樣點) | OTHER | E03/161/1760/BE0 |  |  |  |  | 723 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1760TE | 1760TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1760TE | 1760TE(#7ATR)(非取樣點) | OTHER | E03/161/1760/TE0 |  |  |  |  | 724 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 3932E | 3932E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3932E | 3932E(非取樣點) | OTHER | E03/345/3930/E2 |  |  |  |  | 725 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3740 | 3740 |  | LE0 | 3740LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3740LE | 3740LE (非取樣點) | LINE345 | [5 empty] | 726 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3740 | 3740 |  | BE0 | 3740BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3740BE | 3740BE (非取樣點) | LINE345 | [5 empty] | 727 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3760 | 3760 |  | LE0 | 3760LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3760LE | 3760LE (非取樣點) | LINE345 | [5 empty] | 728 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3760 | 3760 |  | BE0 | 3760BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3760BE | 3760BE (非取樣點) | LINE345 | [5 empty] | 729 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3770 | 3770 |  | LE0 | 3770LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3770LE | 3770LE (非取樣點) | LINE345 | [5 empty] | 730 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3770 | 3770 |  | BE0 | 3770BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3770BE | 3770BE (非取樣點) | LINE345 | [5 empty] | 731 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3790 | 3790 |  | LE0 | 3790LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3790LE | 3790LE (非取樣點) | LINE345 | [5 empty] | 732 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3790 | 3790 |  | BE0 | 3790BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3790BE | 3790BE (非取樣點) | LINE345 | [5 empty] | 733 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3830 | 3830 |  | LE0 | 3830LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3830LE | 3830LE (非取樣點) | LINE345 | [5 empty] | 734 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3830 | 3830 |  | BE0 | 3830BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3830BE | 3830BE (非取樣點) | LINE345 | [5 empty] | 735 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3860 | 3860 |  | LE0 | 3860LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3860LE | 3860LE (非取樣點) | LINE345 | [5 empty] | 736 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3860 | 3860 |  | BE0 | 3860BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3860BE | 3860BE (非取樣點) | LINE345 | [5 empty] | 737 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3870 | 3870 |  | LE0 | 3870LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3870LE | 3870LE (非取樣點) | LINE345 | [5 empty] | 738 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3870 | 3870 |  | BE0 | 3870BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3870BE | 3870BE (非取樣點) | LINE345 | [5 empty] | 739 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3890 | 3890 |  | LE0 | 3890LE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3890LE | 3890LE (非取樣點) | LINE345 | [5 empty] | 740 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3890 | 3890 |  | BE0 | 3890BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3890BE | 3890BE (非取樣點) | LINE345 | [5 empty] | 741 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3750 | 3750 |  | E1 | 3751E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3751E | 3751E (非取樣點) | LINE345 | [5 empty] | 742 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3750 | 3750 |  | E2 | 3752E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3752E | 3752E (非取樣點) | LINE345 | [5 empty] | 743 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3780 | 3780 |  | E1 | 3781E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3781E | 3781E (非取樣點) | LINE345 | [5 empty] | 744 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3780 | 3780 |  | E2 | 3782E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3782E | 3782E (非取樣點) | LINE345 | [5 empty] | 745 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3850 | 3850 |  | E1 | 3851E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3851E | 3851E (非取樣點) | LINE345 | [5 empty] | 746 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3850 | 3850 |  | E2 | 3852E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3852E | 3852E (非取樣點) | LINE345 | [5 empty] | 747 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3880 | 3880 |  | E1 | 3881E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3881E | 3881E (非取樣點) | LINE345 | [5 empty] | 748 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3880 | 3880 |  | E2 | 3882E | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3882E | 3882E (非取樣點) | LINE345 | [5 empty] | 749 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1640 | 1640 |  | LE0 | 1640LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1640LE | 1640LE (非取樣點) | LINE161 | [5 empty] | 750 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1640 | 1640 |  | BE0 | 1640BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1640BE | 1640BE (非取樣點) | LINE161 | [5 empty] | 751 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1710 | 1710 |  | LE0 | 1710LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1710LE | 1710LE (非取樣點) | LINE161 | [5 empty] | 752 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1710 | 1710 |  | BE0 | 1710BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1710BE | 1710BE (非取樣點) | LINE161 | [5 empty] | 753 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1720 | 1720 |  | LE0 | 1720LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1720LE | 1720LE (非取樣點) | LINE161 | [5 empty] | 754 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1720 | 1720 |  | BE0 | 1720BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1720BE | 1720BE (非取樣點) | LINE161 | [5 empty] | 755 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1730 | 1730 |  | LE0 | 1730LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1730LE | 1730LE (非取樣點) | LINE161 | [5 empty] | 756 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1730 | 1730 |  | BE0 | 1730BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1730BE | 1730BE (非取樣點) | LINE161 | [5 empty] | 757 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1600 | 1600 |  | E1 | 1601E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1601E | 1601E (非取樣點) | TIE | [5 empty] | 758 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1600 | 1600 |  | E2 | 1602E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1602E | 1602E (非取樣點) | TIE | [5 empty] | 759 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1800 | 1800 |  | E2 | 1802E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1802E | 1802E (非取樣點) | TIE | [5 empty] | 760 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1800 | 1800 |  | E4 | 1804E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1804E | 1804E (非取樣點) | TIE | [5 empty] | 761 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3810 | 3810 |  | TE0 | 3810TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3810TE | 3810TE (非取樣點) | ATR | [5 empty] | 762 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3810 | 3810 |  | BE0 | 3810BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3810BE | 3810BE (非取樣點) | ATR | [5 empty] | 763 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3840 | 3840 |  | TE0 | 3840TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3840TE | 3840TE (非取樣點) | ATR | [5 empty] | 764 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3840 | 3840 |  | BE0 | 3840BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3840BE | 3840BE (非取樣點) | ATR | [5 empty] | 765 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3710 | 3710 |  | TE0 | 3710TE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3710TE | 3710TE (非取樣點) | ATR | [5 empty] | 766 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 345 | 345kV | 3710 | 3710 |  | BE0 | 3710BE | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.3710BE | 3710BE (非取樣點) | ATR | [5 empty] | 767 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | 160 | 160 |  | BE3 | 161B3E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.161B3E | 161B3E (非取樣點) | BUS | [5 empty] | 768 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | 160 | 160 |  | BE4 | 161B4E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.161B4E | 161B4E (非取樣點) | BUS | [5 empty] | 769 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1670BE | 1670BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1670BE | 1670BE(#3ATR)(非取樣點) | OTHER | [5 empty] | 770 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1670TE | 1670TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1670TE | 1670TE(#3ATR)(非取樣點) | OTHER | [5 empty] | 771 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1680BE | 1680BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1680BE | 1680BE(#4ATR)(非取樣點) | OTHER | [5 empty] | 772 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1680TE | 1680TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1680TE | 1680TE(#4ATR)(非取樣點) | OTHER | [5 empty] | 773 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1780BE | 1780BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1780BE | 1780BE(#6ATR)(非取樣點) | OTHER | [5 empty] | 774 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1780TE | 1780TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1780TE | 1780TE(#6ATR)(非取樣點) | OTHER | [5 empty] | 775 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 3730BE | 3730BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.3730BE | 3730BE(#6ATR)(非取樣點) | OTHER | [5 empty] | 776 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 3730TE | 3730TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.3730TE | 3730TE(#6ATR)(非取樣點) | OTHER | [5 empty] | 777 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 778 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | CDCS_S | [8 empty] | 龍崎ES.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 779 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
E03 | 龍崎ES | 0 |  |  |  |  | 1751E | 1751E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1751E | 1751E(#7ATR)(非取樣點) | OTHER | E03/161/1750/E1 |  |  |  |  | 780 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1762E | 1762E | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1762E | 1762E(#7ATR)(非取樣點) | OTHER | E03/161/1760/E2 |  |  |  |  | 781 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1630 | 1630 |  | LE0 | 1630LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1630LE | 1630LE (非取樣點) | LINE161 | [5 empty] | 782 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1630 | 1630 |  | BE0 | 1630BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1630BE | 1630BE (非取樣點) | LINE161 | [5 empty] | 783 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1550LE | 1550LE (非取樣點) | LINE161 | E03/161/1550/LE0 |  |  |  |  | 784 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1550 | 龍崎台南山線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1550BE | 1550BE (非取樣點) | LINE161 | E03/161/1550/BE0 |  |  |  |  | 785 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎台南山線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1560LE | 1560LE (非取樣點) | LINE161 | E03/161/1560/LE0 |  |  |  |  | 786 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 161 | 161kV | 1560 | 龍崎台南山線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1560BE | 1560BE (非取樣點) | LINE161 | E03/161/1560/BE0 |  |  |  |  | 787 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1910BE | 1910BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1910BE | 1910BE(#5ATR)(非取樣點) | OTHER | E03/161/1910/BE0 |  |  |  |  | 788 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1910TE | 1910TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1910TE | 1910TE(#5ATR)(非取樣點) | OTHER | E03/161/1910/TE0 |  |  |  |  | 789 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1920BE | 1920BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1920BE | 1920BE(#5ATR)(非取樣點) | OTHER | E03/161/1920/BE0 |  |  |  |  | 790 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1920TE | 1920TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1920TE | 1920TE(#5ATR)(非取樣點) | OTHER | E03/161/1920/TE0 |  |  |  |  | 791 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1810BE | 1810BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1810BE | 1810BE(#1ATR)(非取樣點) | OTHER | E03/161/1810/BE0 |  |  |  |  | 792 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1810TE | 1810TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1810TE | 1810TE(#1ATR)(非取樣點) | OTHER | E03/161/1810/TE0 |  |  |  |  | 793 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1820BE | 1820BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1820BE | 1820BE(#1ATR)(非取樣點) | OTHER | E03/161/1820/BE0 |  |  |  |  | 794 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1820TE | 1820TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1820TE | 1820TE(#1ATR)(非取樣點) | OTHER | E03/161/1820/TE0 |  |  |  |  | 795 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1830BE | 1830BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1830BE | 1830BE(#2ATR)(非取樣點) | OTHER | E03/161/1830/BE0 |  |  |  |  | 796 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1830TE | 1830TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1830TE | 1830TE(#2ATR)(非取樣點) | OTHER | E03/161/1830/TE0 |  |  |  |  | 797 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1840BE | 1840BE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1840BE | 1840BE(#2ATR)(非取樣點) | OTHER | E03/161/1840/BE0 |  |  |  |  | 798 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E03 | 龍崎ES | 0 |  |  |  |  | 1840TE | 1840TE | [24 empty] | ADCS_S | [8 empty] | 龍崎ES.1840TE | 1840TE(#2ATR)(非取樣點) | OTHER | E03/161/1840/TE0 |  |  |  |  | 799 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo