## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E04 | 龍崎ES | 345 | 345kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0258 |  |  | 3-82 |  |  | 345KV | KV | 三號 BUS PT | kV_-450_450(-2000_2000) | aba | B2/E04_C | [8 empty] | 龍崎ES.345KV#3BUS_KV | 345KV #3BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0259 |  |  | 3-83 |  |  | 345KV | KV | 四號 BUS PT | kV_-450_450(-2000_2000) | abb | B2/E04_C | [8 empty] | 龍崎ES.345KV#4BUS_KV | 345KV #4BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E04 | 龍崎ES | 161 | 161kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 三號 BUS PD | kV_-210_210(-2000_2000) | aba | B2/E04_A1 | [8 empty] | 龍崎ES.161KV#3BUS_KV | 161KV #3BUS KV | BUS |  |  |  |  | CDC | 4 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 四號 BUS PD | kV_-210_210(-2000_2000) | abb | B2/E04_A1 | [8 empty] | 龍崎ES.161KV#4BUS_KV | 161KV #4BUS KV | BUS |  |  |  |  | CDC | 5 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E04 | 龍崎ES | 345 | 345kV | 3BUS | #3BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 3-04-03 |  |  | 345KV | #3BUS | 387B1A |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#3B_87A1 | 345KV #3BUS 第一組 87RY | BUS |  |  |  |  | CDC | 6 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3BUS | #3BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 3-04-04 |  |  | 345KV | #3BUS | 387B2A |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#3B_87A2 | 345KV #3BUS 第二組 87RY | BUS |  |  |  |  | CDC | 7 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 4BUS | #4BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 3-04-05 |  |  | 345KV | #4BUS | 487B1A |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#4B_87A1 | 345KV #4BUS 第一組 87RY | BUS |  |  |  |  | CDC | 8 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 4BUS | #4BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 3-04-06 |  |  | 345KV | #4BUS | 487B2A |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#4B_87A2 | 345KV #4BUS 第二組 87RY | BUS |  |  |  |  | CDC | 9 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 161B3E | #3BUS(161B3E) |  | BE1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/3Bus | [13 empty] | abhz | B2/E04_A1 | [16 empty] | 10 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 3BUS | #3BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0520 |  |  | 1-30-08 |  |  | 161KV | VUA3 | 161kV #3Bus VUA3 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS |  |  |  |  | CDC | 11 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 3BUS | #3BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 161KV | #3BUS | 87B3A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161#3BUS_87A | 161KV #3BUS 87RY | BUS |  |  |  |  | CDC | 12 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 161B4E | #4BUS(161B4E) |  | BE2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/4Bus | [13 empty] | abhz | B2/E04_A1 | [16 empty] | 13 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 4BUS | #4BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0521 |  |  | 1-30-09 |  |  | 161KV | VUA4 | 161kV #4Bus VUA4 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS |  |  |  |  | CDC | 14 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 4BUS | #4BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 161KV | #4BUS | 87B4A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161#4BUS_87A | 161KV #4BUS 87RY | BUS |  |  |  |  | CDC | 15 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 3740 | MW | 天輪龍崎山線 瓦 | MW_-1200_1200(-2000_2000) |  | B2/E04_C |  |  | 2000 | [5 empty] | 龍崎ES.3740_MW | 天輪山線 MW | LINE345 |  |  |  |  | CDC | 16 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 3740 | MVAR | 天輪龍崎山線 乏 | MVAR_-1200_1200(-2000_2000) |  | B2/E04_C |  |  | 2000 | [5 empty] | 龍崎ES.3740_MVAR | 天輪山線 MVAR | LINE345 |  |  |  |  | CDC | 17 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 3740 | KV | 天輪龍崎山線 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3740LPD_KV | 天輪山線(3740) LPD KV | LINE345 |  |  |  |  | CDC | 18 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | 3760 | MW | 嘉民龍崎紅線 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3760_MW | 嘉民紅線 MW | LINE345 |  |  |  |  | CDC | 19 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | 3760 | MVAR | 嘉民龍崎紅線 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3760_MVAR | 嘉民紅線 MVAR | LINE345 |  |  |  |  | CDC | 20 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | 3760 | KV | 嘉民龍崎紅線 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3760LPD_KV | 嘉民紅線(3760) LPD KV | LINE345 |  |  |  |  | CDC | 21 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | 3770 | MW | 龍崎(北)~龍崎(南)臨時線 3770 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3770_MW | 北南臨時線(3770) MW | LINE345 |  |  |  |  | CDC | 22 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | 3770 | MVAR | 龍崎(北)~龍崎(南)臨時線 3770 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3770_MVAR | 北南臨時線(3770) MVAR | LINE345 |  |  |  |  | CDC | 23 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | 3770 | KV | 龍崎(北)~龍崎(南)臨時線 3770 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3770LPD_KV | 北南臨時線(3770) LPD KV | LINE345 |  |  |  |  | CDC | 24 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | 3790 | MW | 龍崎仁武山線 瓦 | MW_-1800_1800(-2000_2000) |  | B2/E04_C |  |  | 3000 | [5 empty] | 龍崎ES.3790_MW | 仁武山線 MW | LINE345 |  |  |  |  | CDC | 25 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | 3790 | MVAR | 龍崎仁武山線 乏 | MVAR_-1800_1800(-2000_2000) |  | B2/E04_C |  |  | 3000 | [5 empty] | 龍崎ES.3790_MVAR | 仁武山線 MVAR | LINE345 |  |  |  |  | CDC | 26 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | 3790 | KV | 龍崎仁武山線 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3790LPD_KV | 仁武山線(3790) LPD KV | LINE345 |  |  |  |  | CDC | 27 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | 3860 | MW | 興達龍崎三路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3860_MW | 興達三路 MW | LINE345 |  |  |  |  | CDC | 28 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | 3860 | MVAR | 興達龍崎三路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3860_MVAR | 興達三路 MVAR | LINE345 |  |  |  |  | CDC | 29 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | 3860 | KV | 興達龍崎三路 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3860LPD_KV | 興達三路(3860) LPD KV | LINE345 |  |  |  |  | CDC | 30 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | 3870 | MW | 路北龍崎白線 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3870_MW | 路北白線 MW | LINE345 |  |  |  |  | CDC | 31 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | 3870 | MVAR | 路北龍崎白線 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E04_C |  |  | 4000 | [5 empty] | 龍崎ES.3870_MVAR | 路北白線 MVAR | LINE345 |  |  |  |  | CDC | 32 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | 3870 | KV | 路北龍崎白線 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3870LPD_KV | 路北白線(3870) LPD KV | LINE345 |  |  |  |  | CDC | 33 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | 3890 | MW | 龍崎仁武海線 瓦 | MW_-1800_1800(-2000_2000) |  | B2/E04_C |  |  | 3000 | [5 empty] | 龍崎ES.3890_MW | 仁武海線 MW | LINE345 |  |  |  |  | CDC | 34 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | 3890 | MVAR | 龍崎仁武海線 乏 | MVAR_-1800_1800(-2000_2000) |  | B2/E04_C |  |  | 3000 | [5 empty] | 龍崎ES.3890_MVAR | 仁武海線 MVAR | LINE345 |  |  |  |  | CDC | 35 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | 3890 | KV | 龍崎仁武海線 LPD | kV_-450_450(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.3890LPD_KV | 仁武海線(3890) LPD KV | LINE345 |  |  |  |  | CDC | 36 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0298 |  |  | 3-05-02 |  |  | 3740 | #1 RY | 天輪龍崎山線 1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_SSA11 | 天輪山線(3740) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 37 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 3-05-03 |  |  | 3740 | #1RY | 天輪龍崎山線 1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_SSA12 | 天輪山線(3740) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 38 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 3-05-05 |  |  | 3760 | #1 RY | 嘉民龍崎紅線 1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_SSA11 | 嘉民紅線(3760) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 39 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 3-05-06 |  |  | 3760 | #1RY | 嘉民龍崎紅線 1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_SSA12 | 嘉民紅線(3760) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 40 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0304 |  |  | 3-06-00 |  |  | 3770 | #1RY | 龍崎(北)~龍崎(南)臨時線 3770 1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_SSA11 | 北南臨時線(3770) #1(87L)RY | LINE345 |  |  |  |  | CDC | 41 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 3-06-01 |  |  | 3770 | #1RY | 龍崎(北)~龍崎(南)臨時線 3770 1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_SSA12 | 北南臨時線(3770) #1(21)RY | LINE345 |  |  |  |  | CDC | 42 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 3-06-03 |  |  | 3790 | #1 RY | 龍崎仁武山線 1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_SSA11 | 仁武山線(3790) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 43 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 3-06-04 |  |  | 3790 | #1RY | 龍崎仁武山線 1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_SSA12 | 仁武山線(3790) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 44 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0310 |  |  | 3-06-06 |  |  | 3860 | #1 RY | 興達龍崎三路 1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_SSA11 | 興達三路(3860) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 45 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 3-06-07 |  |  | 3860 | #1RY | 興達龍崎三路 1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_SSA12 | 興達三路(3860) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 46 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 3-07-01 |  |  | 3870 | #1 RY | 路北龍崎白線1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_SSA11 | 路北白線(3870) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 47 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 3-07-02 |  |  | 3870 | #1RY | 路北龍崎白線1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_SSA12 | 路北白線(3870) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 48 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 3-07-04 |  |  | 3890 | #1 RY | 龍崎仁武海線 1SSA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_SSA11 | 仁武海線(3890) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 49 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 3-07-05 |  |  | 3890 | #1RY | 龍崎仁武海線 1SSA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_SSA12 | 仁武海線(3890) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 50 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 3-05-04 |  |  | 3740 | #2 RY | 天輪龍崎山線 2SSA |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_SSA2 | 天輪山線(3740) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 51 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 3-34-07 |  |  | 3740 | #1RY | 天輪龍崎山線 RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_RYFA1 | 天輪山線(3740) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 52 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0841 |  |  | 3-34-09 |  |  | 3740 | #2RY | 天輪龍崎山線RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_RYFA2 | 天輪山線(3740) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 53 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0837 |  | 0353 | 3-34-05 |  | 3-61 | 3740 | 79S | 天輪龍崎山線 3740 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_79UL | 天輪山線(3740) 79RY U/L | LINE345 |  |  |  |  | CDC | 54 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 3-05-07 |  |  | 3760 | #2 RY | 嘉民龍崎紅線 2SSA3 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_SSA2 | 嘉民紅線(3760) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 55 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0844 |  |  | 3-34-12 |  |  | 3760 | #1RY | 嘉民龍崎紅線 RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_RYFA1 | 嘉民紅線(3760) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 56 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0846 |  |  | 3-34-14 |  |  | 3760 | #2RY | 嘉民龍崎紅線 RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_RYFA2 | 嘉民紅線(3760) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 57 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0842 |  | 0354 | 3-34-10 |  | 3-62 | 3760 | 79S | 嘉民龍崎紅線3760 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_79UL | 嘉民紅線(3760) 79RY U/L | LINE345 |  |  |  |  | CDC | 58 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 3-06-02 |  |  | 3770 | #2RY | 龍崎(北)~龍崎(南)臨時線 3770 2SSA3 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_SSA2 | 北南臨時線(3770) #2(21)RY | LINE345 |  |  |  |  | CDC | 59 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0849 |  |  | 3-35-01 |  |  | 3770 | #1RY | 龍崎(北)~龍崎(南)臨時線 3770 RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_RYFA1 | 北南臨時線(3770) #1RY故障 | LINE345 |  |  |  |  | CDC | 60 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 3-35-03 |  |  | 3770 | #2RY | 龍崎(北)~龍崎(南)臨時線 3770 RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_RYFA2 | 北南臨時線(3770) #2RY故障 | LINE345 |  |  |  |  | CDC | 61 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0847 |  | 0355 | 3-34-15 |  | 3-63 | 3770 | 79S | 龍崎(北)~龍崎(南)臨時線 3770 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_79UL | 北南臨時線(3770) 79RY U/L | LINE345 |  |  |  |  | CDC | 62 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 3-06-05 |  |  | 3790 | #2 RY | 龍崎仁武山線 2SSA3 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_SSA2 | 仁武山線(3790) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 63 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 3-35-06 |  |  | 3790 | #1RY | 龍崎仁武山線 RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_RYFA1 | 仁武山線(3790) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 64 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 3-35-08 |  |  | 3790 | #2RY | 龍崎仁武山線 RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_RYFA2 | 仁武山線(3790) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 65 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0852 |  | 0356 | 3-35-04 |  | 3-64 | 3790 | 79S | 龍崎仁武山線 3790 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_79UL | 仁武山線(3790) 79RY U/L | LINE345 |  |  |  |  | CDC | 66 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 3-07-00 |  |  | 3860 | #2 RY | 興達龍崎三路 2SSA3 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_SSA2 | 興達三路(3860) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 67 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 3-35-11 |  |  | 3860 | #1RY | 興達龍崎三路 RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_RYFA1 | 興達三路(3860) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 68 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 3-35-13 |  |  | 3860 | #2RY | 興達龍崎三路 RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_RYFA2 | 興達三路(3860) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 69 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0857 |  | 0357 | 3-35-09 |  | 3-65 | 3860 | 79S | 興達龍崎三路 3860 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_79UL | 興達三路(3860) 79RY U/L | LINE345 |  |  |  |  | CDC | 70 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 3-07-03 |  |  | 3870 | #2 RY | 路北龍崎白線2SSA |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_SSA2 | 路北白線(3870) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 71 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0864 |  |  | 3-36-00 |  |  | 3870 | #1RY | 路北龍崎白線RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_RYFA1 | 路北白線(3870) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 72 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 3-36-02 |  |  | 3870 | #2RY | 路北龍崎白線RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_RYFA2 | 路北白線(3870) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 73 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0862 |  | 0358 | 3-35-14 |  | 3-66 | 3870 | 79S | 路北龍崎白線3870 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_79UL | 路北白線(3870) 79RY U/L | LINE345 |  |  |  |  | CDC | 74 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 3-07-06 |  |  | 3890 | #2 RY | 龍崎仁武海線 2SSA3 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_SSA2 | 仁武海線(3890) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 75 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0869 |  |  | 3-36-05 |  |  | 3890 | #1RY | 龍崎仁武海線 RYA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_RYFA1 | 仁武海線(3890) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 76 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 3-36-07 |  |  | 3890 | #2RY | 龍崎仁武海線 RYA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_RYFA2 | 仁武海線(3890) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 77 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0359 | 3-36-03 |  | 3-67 | 3890 | 79S | 龍崎仁武海線 3890 79RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_79UL | 仁武海線(3890) 79RY U/L | LINE345 |  |  |  |  | CDC | 78 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | DS1 | 3741 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0974 | 0975 | 0293 | 3-3C-14 | 3-3C-15 | 3-25 | 3741 | DS | 天輪龍崎山線 3741 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3741_DS | 3741(天輪山線) DS | LINE345 |  |  |  |  | CDC | 79 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | DS2 | 3742 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 0977 | 0294 | 3-3D-00 | 3-3D-01 | 3-26 | 3742 | DS | 天輪龍崎山線 3742 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3742_DS | 3742(天輪山線) DS | LINE345 |  |  |  |  | CDC | 80 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | ABS1 | 3761 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 0985 | 0298 | 3-3D-08 | 3-3D-09 | 3-2A | 3761 | DS | 嘉民龍崎紅線 3761 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3761_ABS | 3761(嘉民紅線) ABS | LINE345 |  |  |  |  | CDC | 81 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | ABS2 | 3762 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0988 | 0989 | 0300 | 3-3D-12 | 3-3D-13 | 3-2C | 3762 | DS | 嘉民龍崎紅線 3762 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3762_ABS | 3762(嘉民紅線) ABS | LINE345 |  |  |  |  | CDC | 82 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | ABS1 | 3771 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0990 | 0991 | 0301 | 3-3D-14 | 3-3D-15 | 3-2D | 3771 | DS | 龍崎(北)~龍崎(南)臨時線 3771 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3771_ABS | 3771(北南臨時線) ABS | LINE345 |  |  |  |  | CDC | 83 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | ABS2 | 3772 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 0993 | 0302 | 3-3E-00 | 3-3E-01 | 3-2E | 3772 | DS | 龍崎(北)~龍崎(南)臨時線 3772 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3772_ABS | 3772(北南臨時線) ABS | LINE345 |  |  |  |  | CDC | 84 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | ABS1 | 3791 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 | 0306 | 3-3E-08 | 3-3E-09 | 3-32 | 3791 | DS | 龍崎仁武山線 3791 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3791_ABS | 3791(仁武山線) ABS | LINE345 |  |  |  |  | CDC | 85 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | ABS2 | 3792 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 | 0308 | 3-3E-12 | 3-3E-13 | 3-34 | 3792 | DS | 龍崎仁武山線 3792 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3792_ABS | 3792(仁武山線) ABS | LINE345 |  |  |  |  | CDC | 86 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | ABS1 | 3861 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1034 | 1035 | 0317 | 4-30-10 | 4-30-11 | 3-3D | 3861 | DS | 興達龍崎三路 3861 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3861_ABS | 3861(興達三路) ABS | LINE345 |  |  |  |  | CDC | 87 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | ABS2 | 3862 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1036 | 1037 | 0319 | 4-30-12 | 4-30-13 | 3-3F | 3862 | DS | 興達龍崎三路 3862 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3862_ABS | 3862(興達三路) ABS | LINE345 |  |  |  |  | CDC | 88 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | ABS1 | 3871 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1038 | 1039 | 0320 | 4-30-14 | 4-30-15 | 3-40 | 3871 | DS | 路北龍崎白線3871 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3871_ABS | 3871(路北白線) ABS | LINE345 |  |  |  |  | CDC | 89 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | ABS2 | 3872 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1040 | 1041 | 0321 | 4-31-00 | 4-31-01 | 3-41 | 3872 | DS | 路北龍崎白線3872 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3872_ABS | 3872(路北白線) ABS | LINE345 |  |  |  |  | CDC | 90 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | ABS1 | 3891 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1048 | 1049 | 0325 | 4-31-08 | 4-31-09 | 3-45 | 3891 | DS | 龍崎仁武海線 3891 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3891_ABS | 3891(仁武海線) ABS | LINE345 |  |  |  |  | CDC | 91 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | ABS2 | 3892 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1052 | 1053 | 0327 | 4-31-12 | 4-31-13 | 3-47 | 3892 | DS | 龍崎仁武海線 3892 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3892_ABS | 3892(仁武海線) ABS | LINE345 |  |  |  |  | CDC | 92 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | DS1 | 3731 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0970 | 0971 | 0291 | 3-3C-10 | 3-3C-11 | 3-23 | 3731 | DS | 3731 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3731_DS | 3731(#6ATR) DS | ATR |  |  |  |  | CDC | 93 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | DS2 | 3732 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0972 | 0973 | 0292 | 3-3C-12 | 3-3C-13 | 3-24 | 3732 | DS | 3732 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3732_DS | 3732(#6ATR) DS | ATR |  |  |  |  | CDC | 94 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | ABS1 | 3831 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1016 | 1017 | 0311 | 3-3F-08 | 3-3F-09 | 3-37 | 3831 | DS | 3831 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3831_ABS | 3831(#3ATR) ABS | ATR |  |  |  |  | CDC | 95 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | ABS2 | 3832 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1018 | 1019 | 0312 | 3-3F-10 | 3-3F-11 | 3-38 | 3832 | DS | 3832 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3832_ABS | 3832(#3ATR) ABS | ATR |  |  |  |  | CDC | 96 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaE | B/3Bus | L/T12E02M/T2 |  |  | 0264 |  | 0261 | 3-01-00 |  | 3-05 | 3740 | CB | 天輪龍崎山線 3740 CB AS |  | abba | B2/E04_C | [8 empty] | 龍崎ES.3740_CB | 3740(天輪山線) CB | LINE345 |  |  |  |  | CDC | 97 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | E2 | 3742E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0978 | 0979 | 0295 | 3-3D-02 | 3-3D-03 | 3-27 | 3742E | DS | 天輪龍崎山線 3742E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3742E_ES | 3742E(天輪山線) ES | LINE345 |  |  |  |  | CDC | 98 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 99 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 100 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | L/E03E02R/T2 | B/4Bus |  |  | 0266 |  | 0263 | 3-01-02 |  | 3-07 | 3760 | CB | 嘉民龍崎紅線 3760 CB AS |  | abbc | B2/E04_C | [8 empty] | 龍崎ES.3760_CB | 3760(嘉民紅線) CB | LINE345 |  |  |  |  | CDC | 101 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | E1 | 3761E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0986 | 0987 | 0299 | 3-3D-10 | 3-3D-11 | 3-2B | 3761E | DS | 嘉民龍崎紅線 3761E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3761E_ES | 3761E(嘉民紅線) ES | LINE345 |  |  |  |  | CDC | 102 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 103 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 104 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/3Bus | L/E02E02/T2 |  |  | 0267 |  | 0264 | 3-01-03 |  | 3-08 | 3770 | CB | 龍崎(北)~龍崎(南)臨時線 3770 CB AS |  | abca | B2/E04_C | [8 empty] | 龍崎ES.3770_CB | 3770(北南臨時線) CB | LINE345 |  |  |  |  | CDC | 105 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | E2 | 3772E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0994 | 0995 | 0303 | 3-3E-02 | 3-3E-03 | 3-2F | 3772E | DS | 龍崎(北)~龍崎(南)臨時線 3772E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3772E_ES | 3772E(北南臨時線) ES | LINE345 |  |  |  |  | CDC | 106 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 107 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 108 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | L/E02E07M/T1 | B/4Bus |  |  | 0269 |  | 0266 | 3-01-05 |  | 3-0A | 3790 | CB | 龍崎仁武山線 3790 CB AS |  | abcc | B2/E04_C | [8 empty] | 龍崎ES.3790_CB | 3790(仁武山線) CB | LINE345 |  |  |  |  | CDC | 109 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | E1 | 3791E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1002 | 1003 | 0307 | 3-3E-10 | 3-3E-11 | 3-33 | 3791E | DS | 龍崎仁武山線 3791E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3791E_ES | 3791E(仁武山線) ES | LINE345 |  |  |  |  | CDC | 110 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 111 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 112 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | L/T13E023/T2 | B/4Bus |  |  | 0280 |  | 0274 | 3-03-00 |  | 3-12 | 3860 | CB | 興達龍崎三路 3860 CB AS |  | abec | B2/E04_C | [8 empty] | 龍崎ES.3860_CB | 3860(興達三路) CB | LINE345 |  |  |  |  | CDC | 113 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | E1 | 3861E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1032 | 1033 | 0318 | 4-30-08 | 4-30-09 | 3-3E | 3861E | DS | 興達龍崎三路 3861E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3861E_ES | 3861E(興達三路) ES | LINE345 |  |  |  |  | CDC | 114 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 115 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 116 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/3Bus | L/E06E02W/T2 |  |  | 0288 |  | 0277 | 3-04-00 |  | 3-15 | 3870 | CB | 路北龍崎白線3870 CB AS |  | abfa | B2/E04_C | [8 empty] | 龍崎ES.3870_CB | 3870(路北白線) CB | LINE345 |  |  |  |  | CDC | 117 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | E2 | 3872E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1042 | 1043 | 0322 | 4-31-02 | 4-31-03 | 3-42 | 3872E | DS | 路北龍崎白線3872E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3872E_ES | 3872E(路北白線) ES | LINE345 |  |  |  |  | CDC | 118 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 119 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 120 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDia | L/E02E07O/T1 | B/4Bus |  |  | 0290 |  | 0279 | 3-04-02 |  | 3-17 | 3890 | CB | 3890 CB AS |  | abfc | B2/E04_C | [8 empty] | 龍崎ES.3890_CB | 3890(仁武海線) CB | LINE345 |  |  |  |  | CDC | 121 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | E1 | 3891E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1050 | 1051 | 0326 | 4-31-10 | 4-31-11 | 3-46 | 3891E | DS | 龍崎仁武海線 3891E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3891E_ES | 3891E(仁武海線) ES | LINE345 |  |  |  |  | CDC | 122 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 123 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 124 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | T/6ATR345 | B/4Bus |  |  | 0257 |  | 0258 | 3-00-01 |  | 3-02 | 3730 | CB | 3730 CB AS |  | abac | B2/E04_C | [8 empty] | 龍崎ES.3730_CB | 3730(#6ATR) CB | LINE345 |  |  |  |  | CDC | 125 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaB | T/3ATR345 | B/4Bus |  |  | 0271 |  | 0268 | 3-01-07 |  | 3-0C | 3830 | CB | 3830 CB AS |  | abdc | B2/E04_C | [8 empty] | 龍崎ES.3830_CB | 3830(#3ATR) CB | LINE345 |  |  |  |  | CDC | 126 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 127 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 128 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3750 | TIE(3750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3740 | A/3760 |  |  | 0265 |  | 0262 | 3-01-01 |  | 3-06 | 3750 | CB | 3750 CB AS |  | abbb | B2/E04_C | [8 empty] | 龍崎ES.3750_CB | 3750 CB | LINE345 |  |  |  |  | CDC | 129 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3750 | TIE(3750) |  | E1 | 3751E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 130 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3750 | TIE(3750) |  | E2 | 3752E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 131 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3780 | TIE(3780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3770 | A/3790 |  |  | 0268 |  | 0265 | 3-01-04 |  | 3-09 | 3780 | CB | 3780 CB AS |  | abcb | B2/E04_C | [8 empty] | 龍崎ES.3780_CB | 3780 CB | LINE345 |  |  |  |  | CDC | 132 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3780 | TIE(3780) |  | E1 | 3781E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 133 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3780 | TIE(3780) |  | E2 | 3782E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 134 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3880 | TIE(3880) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3870 | A/3890 |  |  | 0289 |  | 0278 | 3-04-01 |  | 3-16 | 3880 | CB | 3880 CB AS |  | abfb | B2/E04_C | [8 empty] | 龍崎ES.3880_CB | 3880 CB | LINE345 |  |  |  |  | CDC | 135 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3880 | TIE(3880) |  | E1 | 3881E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 136 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3880 | TIE(3880) |  | E2 | 3882E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 137 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3850 | TIE(3850) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3840 | A/3860 |  |  | 0279 |  | 0273 | 3-02-07 |  | 3-11 | 3850 | CB | 3850 CB AS |  | abeb | B2/E04_C | [8 empty] | 龍崎ES.3850_CB | 3850 CB | LINE345 |  |  |  |  | CDC | 138 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3850 | TIE(3850) |  | E1 | 3851E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 139 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3850 | TIE(3850) |  | E2 | 3852E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 140 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3750 | TIE(3750) |  | ABS1 | 3751 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 0981 | 0296 | 3-3D-04 | 3-3D-05 | 3-28 | 3751 | DS | 3751 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3751_ABS | 3751 ABS | LINE345 |  |  |  |  | CDC | 141 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3750 | TIE(3750) |  | ABS2 | 3752 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 0983 | 0297 | 3-3D-06 | 3-3D-07 | 3-29 | 3752 | DS | 3752 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3752_ABS | 3752 ABS | LINE345 |  |  |  |  | CDC | 142 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3780 | TIE(3780) |  | ABS1 | 3781 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0996 | 0997 | 0304 | 3-3E-04 | 3-3E-05 | 3-30 | 3781 | DS | 3781 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3781_ABS | 3781 ABS | LINE345 |  |  |  |  | CDC | 143 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3780 | TIE(3780) |  | ABS2 | 3782 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0998 | 0999 | 0305 | 3-3E-06 | 3-3E-07 | 3-31 | 3782 | DS | 3782 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3782_ABS | 3782 ABS | LINE345 |  |  |  |  | CDC | 144 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3880 | TIE(3880) |  | ABS1 | 3881 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1044 | 1045 | 0323 | 4-31-04 | 4-31-05 | 3-43 | 3881 | DS | 3881 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3881_ABS | 3881 ABS | LINE345 |  |  |  |  | CDC | 145 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3880 | TIE(3880) |  | ABS2 | 3882 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1046 | 1047 | 0324 | 4-31-06 | 4-31-07 | 3-44 | 3882 | DS | 3882 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3882_ABS | 3882 ABS | LINE345 |  |  |  |  | CDC | 146 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3850 | TIE(3850) |  | ABS1 | 3851 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1028 | 1029 | 0315 | 4-30-04 | 4-30-05 | 3-3B | 3851 | DS | 3851 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3851_ABS | 3851 ABS | LINE345 |  |  |  |  | CDC | 147 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3850 | TIE(3850) |  | ABS2 | 3852 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1030 | 1031 | 0316 | 4-30-06 | 4-30-07 | 3-3C | 3852 | DS | 3852 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3852_ABS | 3852 ABS | LINE345 |  |  |  |  | CDC | 148 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1630 | MW | 龍崎聯錏線1630 瓦 | MW_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1630_MW | 龍崎聯錏線 MW | LINE161 |  |  |  |  | CDC | 149 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1630 | MVAR | 龍崎聯錏線1630 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1630_MVAR | 龍崎聯錏線 MVAR | LINE161 |  |  |  |  | CDC | 150 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1640 | MW | 龍崎岡山嘉峰線 MW | MW_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1640_MW | 岡山嘉峰線 MW | LINE161 |  |  |  |  | CDC | 151 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1640 | MVAR | 龍崎岡山嘉峰線 MVAR | MVAR_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1640_MVAR | 岡山嘉峰線 MVAR | LINE161 |  |  |  |  | CDC | 152 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1640 | KV | 龍崎岡山嘉峰線(1640) LPD kV | kV_-210_210(-2000_2000) |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640LPD_KV | 岡山嘉峰線(1640) LPD KV | LINE161 |  |  |  |  | CDC | 153 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1710 | MW | 龍崎路園線 瓦 | MW_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1710_MW | 龍崎路園線 MW | LINE161 |  |  |  |  | CDC | 154 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1710 | MVAR | 龍崎路園線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1710_MVAR | 龍崎路園線 MVAR | LINE161 |  |  |  |  | CDC | 155 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1710 | KV | 龍崎路園線 LPD | kV_-210_210(-2000_2000) |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710LPD_KV | 龍崎路園線(1710) LPD KV | LINE161 |  |  |  |  | CDC | 156 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1720 | MW | 龍崎岡山二路 瓦 | MW_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1720_MW | 龍崎岡山二路 MW | LINE161 |  |  |  |  | CDC | 157 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1720 | MVAR | 龍崎岡山二路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1720_MVAR | 龍崎岡山二路 MVAR | LINE161 |  |  |  |  | CDC | 158 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1720 | KV | 龍崎岡山二路 LPD | kV_-210_210(-2000_2000) |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720LPD_KV | 龍崎岡山二路(1720) LPD KV | LINE161 |  |  |  |  | CDC | 159 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1730 | MW | 龍崎岡山三路 瓦 | MW_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1730_MW | 龍崎岡山三路 MW | LINE161 |  |  |  |  | CDC | 160 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 1730 | MVAR | 龍崎岡山三路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1730_MVAR | 龍崎岡山三路 MVAR | LINE161 |  |  |  |  | CDC | 161 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1730 | KV | 龍崎岡山三路 LPD | kV_-210_210(-2000_2000) |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730LPD_KV | 龍崎岡山三路(1730) LPD KV | LINE161 |  |  |  |  | CDC | 162 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 1630 | PHA | 龍崎聯錏線1630 PHA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1630_PHA | 龍崎聯錏線(1630) 相間RY | LINE161 |  |  |  |  | CDC | 163 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1630 | GDA | 龍崎聯錏線 1630 GDA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1630_GDA | 龍崎聯錏線(1630) 接地RY | LINE161 |  |  |  |  | CDC | 164 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 1640 | PHA | 龍崎岡山嘉峰線1640 PHA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_PHA | 岡山嘉峰線(1640) 相間RY | LINE161 |  |  |  |  | CDC | 165 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 1640 | GDA | 龍崎岡山嘉峰線1640 GDA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_GDA | 岡山嘉峰線(1640) 接地RY | LINE161 |  |  |  |  | CDC | 166 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1640 | 87A | 龍崎岡山嘉峰線1640 87A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_87A | 岡山嘉峰線(1640) 87RY | LINE161 |  |  |  |  | CDC | 167 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 1710 | PHA | 龍崎路園線 1710 PHA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_PHA | 龍崎路園線(1710) 相間RY | LINE161 |  |  |  |  | CDC | 168 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1710 | GDA | 龍崎路園線 1710 GDA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_GDA | 龍崎路園線(1710) 接地RY | LINE161 |  |  |  |  | CDC | 169 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 1710 | 87A | 龍崎路園線 1710 87A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_87A | 龍崎路園線(1710) 87RY | LINE161 |  |  |  |  | CDC | 170 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 1720 | PHA | 龍崎岡山二路1720 PHA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_PHA | 龍崎岡山二路(1720) 相間RY | LINE161 |  |  |  |  | CDC | 171 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | 1720 | GDA | 龍崎岡山二路1720 GDA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_GDA | 龍崎岡山二路(1720) 接地RY | LINE161 |  |  |  |  | CDC | 172 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1720 | 87A | 龍崎岡山二路1720 87A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_87A | 龍崎岡山二路(1720) 87RY | LINE161 |  |  |  |  | CDC | 173 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1730 | PHA | 岡山三路1730 PHA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_PHA | 龍崎岡山三路(1730) 相間RY | LINE161 |  |  |  |  | CDC | 174 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 1730 | GDA | 岡山三路1730 GDA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_GDA | 龍崎岡山三路(1730) 接地RY | LINE161 |  |  |  |  | CDC | 175 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 1730 | 87A | 岡山三路1730 87A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_87A | 龍崎岡山三路(1730) 87RY | LINE161 |  |  |  |  | CDC | 176 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | 85UL2 | 85UL(BA) | Element | Status | 第2具85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0527 |  | 0051 | 1-30-15 |  | 1-33 | 1640 | 87UL | 龍崎岡山嘉峰線(1640) 87RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_87UL | 岡山嘉峰線(1640) 87RY U/L | LINE161 |  |  |  |  | CDC | 177 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0531 |  | 0053 | 1-31-03 |  | 1-35 | 1710 | 87S | 龍崎路園線 1710 87RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_87UL | 龍崎路園線(1710) 87RY U/L | LINE161 |  |  |  |  | CDC | 178 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0535 |  | 0055 | 1-31-07 |  | 1-37 | 1720 | 87S | 龍崎岡山二路1720 87RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_87UL | 龍崎岡山二路(1720) 87RY U/L | LINE161 |  |  |  |  | CDC | 179 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0539 |  | 0057 | 1-31-11 |  | 1-39 | 1730 | 87S | 龍崎岡山三路1730 87RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_87UL | 龍崎岡山三路(1730) 87RY U/L | LINE161 |  |  |  |  | CDC | 180 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E02C77/T1 |  | 0003 |  | 0001 | 1-00-03 |  | 1-01 | 1630 | CB | 龍崎聯錏線 1630 CB AS |  | abab | B2/E04_A1 | [8 empty] | 龍崎ES.1630_CB | 1630(龍崎聯錏線) CB | LINE161 |  |  |  |  | CDC | 181 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E02TN14/T2 |  | 0007 |  | 0002 | 1-00-07 |  | 1-02 | 1640 | CB | 1640 (龍崎岡山嘉峰線) CB |  | abdb | B2/E04_A1 | [8 empty] | 龍崎ES.1640_CB | 1640(岡山嘉峰線) CB | LINE161 |  |  |  |  | CDC | 182 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0526 |  | 0050 | 1-30-14 |  | 1-32 | 1640 | 79UL | 龍崎岡山嘉峰線(1640) 79RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_79UL | 岡山嘉峰線(1640) 79RY U/L | LINE161 |  |  |  |  | CDC | 183 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E02D40/T1 |  | 0011 |  | 0003 | 1-01-03 |  | 1-03 | 1710 | CB | 龍崎路園線 1710 CB AS |  | abeb | B2/E04_A1 | [8 empty] | 龍崎ES.1710_CB | 1710(龍崎路園線) CB | LINE161 |  |  |  |  | CDC | 184 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0530 |  | 0052 | 1-31-02 |  | 1-34 | 1710 | 79S | 龍崎路園線 1710 79RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_79UL | 龍崎路園線(1710) 79RY U/L | LINE161 |  |  |  |  | CDC | 185 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E02P112/T1 |  | 0015 |  | 0005 | 1-01-07 |  | 1-05 | 1720 | CB | 龍崎岡山二路1720 CB AS |  | abib | B2/E04_A1 | [8 empty] | 龍崎ES.1720_CB | 1720(龍崎岡山二路) CB | LINE161 |  |  |  |  | CDC | 186 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0534 |  | 0054 | 1-31-06 |  | 1-36 | 1720 | 79S | 龍崎岡山二路1720 79RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_79UL | 龍崎岡山二路(1720) 79RY U/L | LINE161 |  |  |  |  | CDC | 187 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/3Bus | B/4Bus | L/E02P113/T1 |  | 0019 |  | 0006 | 1-02-03 |  | 1-06 | 1730 | CB | 岡山三路1730 CB AS |  | abjb | B2/E04_A1 | [8 empty] | 龍崎ES.1730_CB | 1730(龍崎岡山三路) CB | LINE161 |  |  |  |  | CDC | 188 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0538 |  | 0056 | 1-31-10 |  | 1-38 | 1730 | 79S | 龍崎岡山三路1730 79RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_79UL | 龍崎岡山三路(1730) 79RY U/L | LINE161 |  |  |  |  | CDC | 189 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | ABS1 | 1631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0620 | 0621 | 0016 | 1-36-12 | 1-36-13 | 1-10 | 1631 | DS | 龍崎聯錏線1631 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1631_ABS | 1631(龍崎聯錏線) ABS | LINE161 |  |  |  |  | CDC | 190 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | ABS2 | 1632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0622 | 0623 | 0017 | 1-36-14 | 1-36-15 | 1-11 | 1632 | DS | 龍崎聯錏線1632 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1632_ABS | 1632(龍崎聯錏線) ABS | LINE161 |  |  |  |  | CDC | 191 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | ABS1 | 1641 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | 0629 | 0020 | 1-37-04 | 1-37-05 | 1-14 | 1641 | DS | 龍崎岡山嘉峰線 1641 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1641_ABS | 1641(岡山嘉峰線) ABS | LINE161 |  |  |  |  | CDC | 192 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | ABS2 | 1642 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0630 | 0631 | 0021 | 1-37-06 | 1-37-07 | 1-15 | 1642 | DS | 龍崎岡山嘉峰線 1642 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1642_ABS | 1642(岡山嘉峰線) ABS | LINE161 |  |  |  |  | CDC | 193 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | ABS1 | 1711 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | 0637 | 0024 | 1-37-12 | 1-37-13 | 1-18 | 1711 | DS | 龍崎路園線 1711 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1711_ABS | 1711(龍崎路園線) ABS | LINE161 |  |  |  |  | CDC | 194 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | ABS2 | 1712 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0638 | 0639 | 0025 | 1-37-14 | 1-37-15 | 1-19 | 1712 | DS | 龍崎路園線 1712 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1712_ABS | 1712(龍崎路園線) ABS | LINE161 |  |  |  |  | CDC | 195 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | ABS1 | 1721 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 0645 | 0030 | 1-38-04 | 1-38-05 | 1-1E | 1721 | DS | 龍崎岡山二路1721 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1721_ABS | 1721(龍崎岡山二路) ABS | LINE161 |  |  |  |  | CDC | 196 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | ABS2 | 1722 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0646 | 0647 | 0031 | 1-38-06 | 1-38-07 | 1-1F | 1722 | DS | 龍崎岡山二路1722 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1722_ABS | 1722(龍崎岡山二路) ABS | LINE161 |  |  |  |  | CDC | 197 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | ABS1 | 1731 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 0653 | 0034 | 1-38-12 | 1-38-13 | 1-22 | 1731 | DS | 龍崎岡山三路1731 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1731_ABS | 1731(龍崎岡山三路) ABS | LINE161 |  |  |  |  | CDC | 198 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | ABS2 | 1732 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0654 | 0655 | 0035 | 1-38-14 | 1-38-15 | 1-23 | 1732 | DS | 龍崎岡山三路1732 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1732_ABS | 1732(龍崎岡山三路) ABS | LINE161 |  |  |  |  | CDC | 199 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | ABS3 | 1633 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0624 | 0625 | 0018 | 1-37-00 | 1-37-01 | 1-12 | 1633 | DS | 龍崎聯錏線1633 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1633_ABS | 1633(龍崎聯錏線) ABS | LINE161 |  |  |  |  | CDC | 200 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | E3 | 1633E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0626 | 0627 | 0019 | 1-37-02 | 1-37-03 | 1-13 | 1633E | DS | 龍崎聯錏線1633E DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1633E_ES | 1633E(龍崎聯錏線) ES | LINE161 |  |  |  |  | CDC | 201 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 203 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | ABS3 | 1643 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0632 | 0633 | 0022 | 1-37-08 | 1-37-09 | 1-16 | 1643 | DS | 龍崎岡山嘉峰線 1643 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1643_ABS | 1643(岡山嘉峰線) ABS | LINE161 |  |  |  |  | CDC | 204 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | E3 | 1643E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0634 | 0635 | 0023 | 1-37-10 | 1-37-11 | 1-17 | 1643E | DS | 龍崎岡山嘉峰線 1643E DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1643E_ES | 1643E(岡山嘉峰線) ES | LINE161 |  |  |  |  | CDC | 205 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 206 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 207 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | ABS3 | 1713 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 0641 | 0026 | 1-38-00 | 1-38-01 | 1-1A | 1713 | DS | 龍崎路園線 1713 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1713_ABS | 1713(龍崎路園線) ABS | LINE161 |  |  |  |  | CDC | 208 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | E3 | 1713E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0642 | 0643 | 0027 | 1-38-02 | 1-38-03 | 1-1B | 1713E | DS | 龍崎路園線 1713E DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1713E_ES | 1713E(龍崎路園線) ES | LINE161 |  |  |  |  | CDC | 209 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 210 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 211 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | ABS3 | 1723 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 0649 | 0032 | 1-38-08 | 1-38-09 | 1-20 | 1723 | DS | 龍崎岡山二路1723 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1723_ABS | 1723(龍崎岡山二路) ABS | LINE161 |  |  |  |  | CDC | 212 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | E3 | 1723E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0650 | 0651 | 0033 | 1-38-10 | 1-38-11 | 1-21 | 1723E | DS | 龍崎岡山二路1723E DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1723E_ES | 1723E(龍崎岡山二路) ES | LINE161 |  |  |  |  | CDC | 213 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 214 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 215 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | ABS3 | 1733 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 0657 | 0036 | 1-39-00 | 1-39-01 | 1-24 | 1733 | DS | 龍崎岡山三路1733 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1733_ABS | 1733(龍崎岡山三路) ABS | LINE161 |  |  |  |  | CDC | 216 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | E3 | 1733E |  | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0658 | 0659 | 0037 | 1-39-02 | 1-39-03 | 1-25 | 1733E | DS | 龍崎岡山三路1733E DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1733E_ES | 1733E(龍崎岡山三路) ES | LINE161 |  |  |  |  | CDC | 217 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 218 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 219 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1600 | A | 1600 R相電流 | A_-2000_2000(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1600TIE_AMP | 1600TIE AMP | TIE |  |  |  |  | CDC | 220 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1800 | A | 1800 R相電流 | A_-2000_2000(-2000_2000) |  | B2/E04_A1 |  |  | 2000 | [5 empty] | 龍崎ES.1800TIE_AMP | 1800TIE AMP | TIE |  |  |  |  | CDC | 221 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/3Bus | B/4Bus |  |  | 0031 |  | 0004 | 1-03-07 |  | 1-04 | 1600 | CB | 1600 CB AS |  | abgz | B2/E04_A1 | [8 empty] | 龍崎ES.1600_CB | 1600(TIE) CB | TIE |  |  |  |  | CDC | 222 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 1600 | 50A | 1600 50A |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1600_50A | 161KV TIE(1600) 50RY | TIE |  |  |  |  | CDC | 223 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/2Bus | B/4Bus |  |  | 0033 |  | 0009 | 1-04-01 |  | 1-09 | 1800 | CB | 1800 CB AS |  | no rule | B2/E04_A1 | [8 empty] | 龍崎ES.1800_CB | 1800(TIE) CB | TIE |  |  |  |  | CDC | 224 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | ABS1 | 1601 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 0677 | 0028 | 1-3A-04 | 1-3A-05 | 1-1C | 1601 | DS | 1601 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1601_ABS | 1601(TIE) ABS | TIE |  |  |  |  | CDC | 225 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | ABS2 | 1602 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 0679 | 0029 | 1-3A-06 | 1-3A-07 | 1-1D | 1602 | DS | 1602 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1602_ABS | 1602(TIE) ABS | TIE |  |  |  |  | CDC | 226 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | E1 | 1601E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 227 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | E2 | 1602E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 228 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | DS1 | 1802 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 0681 | 0046 | 1-3A-08 | 1-3A-09 | 1-2E | 1802 | DS | 1802 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1802_DS | 1802(TIE) DS | TIE |  |  |  |  | CDC | 229 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1804 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0682 | 0683 | 0047 | 1-3A-10 | 1-3A-11 | 1-2F | 1804 | DS | 1804 DS AS |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1804_DS | 1804(TIE) DS | TIE |  |  |  |  | CDC | 230 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | E1 | 1802E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 231 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | E2 | 1804E(非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_A1 | [16 empty] | 232 | DI_TIE(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #3 ATR | MW | #3ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E04_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#3ATR_MW | #3ATR二次側 MW | ATR |  |  |  |  | CDC | 233 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #3 ATR | MVAR | #3ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#3ATR_MVAR | #3ATR二次側 MVAR | ATR |  |  |  |  | CDC | 234 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #4 ATR | MW | #4ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E04_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#4ATR_MW | #4ATR二次側 MW | ATR |  |  |  |  | CDC | 235 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #4 ATR | MVAR | #4ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#4ATR_MVAR | #4ATR二次側 MVAR | ATR |  |  |  |  | CDC | 236 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | #6 ATR | MW | #6ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E04_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#6ATR_MW | #6ATR二次側 MW | ATR |  |  |  |  | CDC | 237 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | #6 ATR | MVAR | #6ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E04_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 龍崎ES.#6ATR_MVAR | #6ATR二次側 MVAR | ATR |  |  |  |  | CDC | 238 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0283 |  | 0345 | 3-9B |  | 3-59 | #3 ATR | TAP | #3ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_TAP | #3ATR OLTC TAP | ATR |  |  |  |  | CDC | 239 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | #3 ATR(R) | ℃ | #3ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_OIL_R | #3ATR R相油溫 | ATR |  |  |  |  | CDC | 240 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | #3 ATR(R) | ℃ | #3ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_COIL_R | #3ATR R相線溫 | ATR |  |  |  |  | CDC | 241 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0287 |  |  | 3-9F |  |  | #3 ATR(S) | ℃ | #3ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_OIL_S | #3ATR S相油溫 | ATR |  |  |  |  | CDC | 242 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | #3 ATR(S) | ℃ | #3ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_COIL_S | #3ATR S相線溫 | ATR |  |  |  |  | CDC | 243 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0289 |  |  | 3-A1 |  |  | #3 ATR(T) | ℃ | #3ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_OIL_T | #3ATR T相油溫 | ATR |  |  |  |  | CDC | 244 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0288 |  |  | 3-A0 |  |  | #3 ATR(T) | ℃ | #3ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_COIL_T | #3ATR T相線溫 | ATR |  |  |  |  | CDC | 245 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0292 |  | 0349 | 3-A4 |  | 3-5D | #4 ATR | TAP | #4ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_TAP | #4ATR OLTC TAP | ATR |  |  |  |  | CDC | 246 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0294 |  |  | 3-A6 |  |  | #4 ATR(R) | ℃ | #4ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_OIL_R | #4ATR R相油溫 | ATR |  |  |  |  | CDC | 247 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0293 |  |  | 3-A5 |  |  | #4 ATR(R) | ℃ | #4ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_COIL_R | #4ATR R相線溫 | ATR |  |  |  |  | CDC | 248 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0296 |  |  | 3-A8 |  |  | #4 ATR(S) | ℃ | #4ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_OIL_S | #4ATR S相油溫 | ATR |  |  |  |  | CDC | 249 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0295 |  |  | 3-A7 |  |  | #4 ATR(S) | ℃ | #4ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_COIL_S | #4ATR S相線溫 | ATR |  |  |  |  | CDC | 250 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0298 |  |  | 3-AA |  |  | #4 ATR(T) | ℃ | #4ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_OIL_T | #4ATR T相油溫 | ATR |  |  |  |  | CDC | 251 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0297 |  |  | 3-A9 |  |  | #4 ATR(T) | ℃ | #4ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_COIL_T | #4ATR T相線溫 | ATR |  |  |  |  | CDC | 252 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0301 |  | 0341 | 3-AD |  | 3-55 | #6 ATR | TAP | #6ATR TAP | TAP_0.5_16.5(0_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_TAP | #6ATR OLTC TAP | ATR |  |  |  |  | CDC | 253 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP16_0 | 15 | 16 | 17 | 17.5 | 0 | 2 | 1 | 0 | -0.5 | 0.1 |  | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0303 |  |  | 3-AF |  |  | #6 ATR(R) | ℃ | #6ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_OIL_R | #6ATR R相油溫 | ATR |  |  |  |  | CDC | 254 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0302 |  |  | 3-AE |  |  | #6 ATR(R) | ℃ | #6ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_COIL_R | #6ATR R相線溫 | ATR |  |  |  |  | CDC | 255 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0305 |  |  | 3-B1 |  |  | #6 ATR(S) | ℃ | #6ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_OIL_S | #6ATR S相油溫 | ATR |  |  |  |  | CDC | 256 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0304 |  |  | 3-B0 |  |  | #6 ATR(S) | ℃ | #6ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_COIL_S | #6ATR S相線溫 | ATR |  |  |  |  | CDC | 257 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0307 |  |  | 3-B3 |  |  | #6 ATR(T) | ℃ | #6ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_OIL_T | #6ATR T相油溫 | ATR |  |  |  |  | CDC | 258 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0306 |  |  | 3-B2 |  |  | #6 ATR(T) | ℃ | #6ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_COIL_T | #6ATR T相線溫 | ATR |  |  |  |  | CDC | 259 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaH | B/3Bus | T/3ATR345 |  |  | 0270 |  | 0267 | 3-01-06 |  | 3-0B | 3810 | CB | 3810 CB AS |  | abda | B2/E04_C | [8 empty] | 龍崎ES.3810_CB | 3810(#3ATR) CB | ATR |  |  |  |  | CDC | 260 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | E1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 261 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | E2 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 262 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/3ATR161 |  | 0272 |  | 0269 | 3-02-00 |  | 3-0D | 1670 | CB | 1670 CB AS |  | abca | B3/E04_C | [8 empty] | 龍崎ES.1670_CB | 1670(#3ATR) CB | ATR |  |  |  |  | CDC | 263 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/3Bus | T/4ATR345 |  |  | 0278 |  | 0272 | 3-02-06 |  | 3-10 | 3840 | CB | 3840 CB AS |  | abea | B2/E04_C | [8 empty] | 龍崎ES.3840_CB | 3840(#4ATR) CB | ATR |  |  |  |  | CDC | 264 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 265 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 266 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/4ATR161 |  | 0281 |  | 0275 | 3-03-01 |  | 3-13 | 1680 | CB | 1680 CB AS |  | abfa | B3/E04_C | [8 empty] | 龍崎ES.1680_CB | 1680(#4ATR) CB | ATR |  |  |  |  | CDC | 267 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDia | B/3Bus | T/6ATR345 |  |  | 0256 |  | 0257 | 3-00-00 |  | 3-01 | 3710 | CB | 3710 CB AS |  | abaa | B2/E04_C | [8 empty] | 龍崎ES.3710_CB | 3710(#6ATR) CB | ATR |  |  |  |  | CDC | 268 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 269 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 270 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/6ATR161 |  | 0258 |  | 0259 | 3-00-02 |  | 3-03 | 1780 | CB | 1780 CB AS |  | abbb | B3/E04_C | [8 empty] | 龍崎ES.1780_CB | 1780(#6ATR) CB | ATR |  |  |  |  | CDC | 271 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 |  |  | 3-02-01 |  |  | #3 ATR | 87T1A | #3 ATR 87T1A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_87A1 | #3ATR 第一組 87RY | ATR |  |  |  |  | CDC | 272 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 |  |  | 3-02-02 |  |  | #3 ATR | 87T2A | #3 ATR 87T2A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_87A2 | #3ATR 第二組 87RY | ATR |  |  |  |  | CDC | 273 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 3-02-03 |  |  | #3 ATR | 96PA | #3 ATR 機械保護動作(96PA) |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_96PA | #3ATR 機械保護動作 | ATR |  |  |  |  | CDC | 274 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0276 |  |  | 3-02-04 |  |  | #3 ATR | 51ZA | #3 ATR 51ZA |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_51ZA | #3ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 275 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0277 |  |  | 3-02-05 |  |  | #3 ATR | 59A | #3 ATR 59A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_59A | #3ATR 59RY | ATR |  |  |  |  | CDC | 276 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 3-03-02 |  |  | #4 ATR | 87T1A | #4 ATR 87T1A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_87A1 | #4ATR 第一組 87RY | ATR |  |  |  |  | CDC | 277 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0283 |  |  | 3-03-03 |  |  | #4 ATR | 87T2A | #4 ATR 87T2A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_87A2 | #4ATR 第二組 87RY | ATR |  |  |  |  | CDC | 278 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 3-03-04 |  |  | #4 ATR | 96PA | #4 ATR 機械保護動作(96PA) |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_96PA | #4ATR 機械保護動作 | ATR |  |  |  |  | CDC | 279 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 3-03-05 |  |  | #4 ATR | 51ZA | #4 ATR 51ZA |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_51ZA | #4ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 280 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0286 |  |  | 3-03-06 |  |  | #4 ATR | 59A | #4 ATR 59A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_59A | #4ATR 59RY | ATR |  |  |  |  | CDC | 281 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 3-00-03 |  |  | #6 ATR | 87T1A | #6 ATR 87T1A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_87A1 | #6ATR 第一組 87RY | ATR |  |  |  |  | CDC | 282 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 3-00-04 |  |  | #6 ATR | 87T2A | #6 ATR 87T2A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_87A2 | #6ATR 第二組 87RY | ATR |  |  |  |  | CDC | 283 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 3-00-05 |  |  | #6 ATR | 96PA | #6 ATR 機械保護動作(96PA) |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_96PA | #6ATR 機械保護動作 | ATR |  |  |  |  | CDC | 284 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 3-00-06 |  |  | #6 ATR | 51ZA | #6 ATR 51ZA |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_51ZA | #6ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 285 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0263 |  |  | 3-00-07 |  |  | #6 ATR | 59A | #6 ATR 59A |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_59A | #6ATR 59RY | ATR |  |  |  |  | CDC | 286 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0787 |  |  | 3-31-03 |  |  | #3 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_96D | #3ATR 96D RY | ATR |  |  |  |  | CDC | 287 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0788 |  |  | 3-31-04 |  |  | #3 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_96P | #3ATR 96P RY | ATR |  |  |  |  | CDC | 288 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0789 |  |  | 3-31-05 |  |  | #3 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_63Q | #3ATR 63Q RY | ATR |  |  |  |  | CDC | 289 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0785 |  |  | 3-31-01 |  |  | #3 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_96B1 | #3ATR 96B1 RY | ATR |  |  |  |  | CDC | 290 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0786 |  |  | 3-31-02 |  |  | #3 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_96B2 | #3ATR 96B2 RY | ATR |  |  |  |  | CDC | 291 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0803 |  |  | 3-32-03 |  |  | #4 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_96D | #4ATR 96D RY | ATR |  |  |  |  | CDC | 292 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0804 |  |  | 3-32-04 |  |  | #4 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_96P | #4ATR 96P RY | ATR |  |  |  |  | CDC | 293 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0805 |  |  | 3-32-05 |  |  | #4 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_63Q | #4ATR 63Q RY | ATR |  |  |  |  | CDC | 294 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0801 |  |  | 3-32-01 |  |  | #4 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_96B1 | #4ATR 96B1 RY | ATR |  |  |  |  | CDC | 295 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0802 |  |  | 3-32-02 |  |  | #4 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_96B2 | #4ATR 96B2 RY | ATR |  |  |  |  | CDC | 296 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0776 |  |  | 3-30-08 |  |  | #6 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_96D | #6ATR 96D RY | ATR |  |  |  |  | CDC | 297 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0777 |  |  | 3-30-09 |  |  | #6 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_96P | #6ATR 96P RY | ATR |  |  |  |  | CDC | 298 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0778 |  |  | 3-30-10 |  |  | #6 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_63Q | #6ATR 63Q RY | ATR |  |  |  |  | CDC | 299 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 3-30-06 |  |  | #6 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_96B1 | #6ATR 96B1 RY | ATR |  |  |  |  | CDC | 300 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0775 |  |  | 3-30-07 |  |  | #6 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_96B2 | #6ATR 96B2 RY | ATR |  |  |  |  | CDC | 301 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0791 |  |  | 3-31-07 |  |  | #3 ATR | TRA | #3 ATR 重故障 |  | a | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_TRA | #3ATR 重故障 | ATR |  |  |  |  | CDC | 302 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0790 |  |  | 3-31-06 |  |  | #3 ATR | TRF | #3 ATR 輕故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_TRF | #3ATR 輕故障 | ATR |  |  |  |  | CDC | 303 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0783 |  |  | 3-30-15 |  |  | #3 ATR | S/L | #3 ATR 遙測/本地 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_S/L | #3ATR OLTC S/L | ATR |  |  |  |  | CDC | 304 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0784 |  | 0342 | 3-31-00 |  | 3-56 | #3 ATR | A/M | #3 ATR 自動/手動 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_A/M | #3ATR OLTC A/M | ATR |  |  |  |  | CDC | 305 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1078 | 1079 | 0343 | 4-33-06 | 4-33-07 | 3-57 | #3 ATR | MY-S | #3 ATR MY-S |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_M/F/I | #3ATR M/F/I | ATR |  |  |  |  | CDC | 306 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0807 |  |  | 3-32-07 |  |  | #4 ATR | TRA | #4 ATR 重故障 |  | a | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_TRA | #4ATR 重故障 | ATR |  |  |  |  | CDC | 307 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0806 |  |  | 3-32-06 |  |  | #4 ATR | TRF | #4 ATR 輕故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_TRF | #4ATR 輕故障 | ATR |  |  |  |  | CDC | 308 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0799 |  |  | 3-31-15 |  |  | #4 ATR | S/L | #4 ATR 遙測/本地 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_S/L | #4ATR OLTC S/L | ATR |  |  |  |  | CDC | 309 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0346 | 3-32-00 |  | 3-5A | #4 ATR | A/M | #4 ATR 自動/手動 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_A/M | #4ATR OLTC A/M | ATR |  |  |  |  | CDC | 310 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1080 | 1081 | 0347 | 4-33-08 | 4-33-09 | 3-5B | #4 ATR | MY-S | #4 ATR MY-S |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_M/F/I | #4ATR M/F/I | ATR |  |  |  |  | CDC | 311 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 0780 |  |  | 3-30-12 |  |  | #6 ATR | TRA | #6 ATR 重故障 |  | a | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_TRA | #6ATR 重故障 | ATR |  |  |  |  | CDC | 312 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0779 |  |  | 3-30-11 |  |  | #6 ATR | TRF | #6 ATR 輕故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_TRF | #6ATR 輕故障 | ATR |  |  |  |  | CDC | 313 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 3-30-04 |  |  | #6 ATR | S/L | #6 ATR 遙測/本地 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_S/L | #6ATR OLTC S/L | ATR |  |  |  |  | CDC | 314 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0338 | 3-30-05 |  | 3-52 | #6 ATR | A/M | #6 ATR 自動/手動 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_A/M | #6ATR OLTC A/M | ATR |  |  |  |  | CDC | 315 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1076 | 1077 | 0339 | 4-33-04 | 4-33-05 | 3-53 | #6 ATR | MY-S | #6 ATR MY-S |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_M/F/I | #6ATR M/F/I | ATR |  |  |  |  | CDC | 316 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | ABS1 | 3811 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1006 | 1007 | 0309 | 3-3E-14 | 3-3E-15 | 3-35 | 3811 | DS | 3811 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3811_ABS | 3811(#3ATR) ABS | ATR |  |  |  |  | CDC | 317 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | ABS2 | 3812 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1008 | 1009 | 0310 | 3-3F-00 | 3-3F-01 | 3-36 | 3812 | DS | 3812 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3812_ABS | 3812(#3ATR) ABS | ATR |  |  |  |  | CDC | 318 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | ABS1 | 3841 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1024 | 1025 | 0313 | 4-30-00 | 4-30-01 | 3-39 | 3841 | DS | 3841 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3841_ABS | 3841(#4ATR) ABS | ATR |  |  |  |  | CDC | 319 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | ABS2 | 3842 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1026 | 1027 | 0314 | 4-30-02 | 4-30-03 | 3-3A | 3842 | DS | 3842 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3842_ABS | 3842(#4ATR) ABS | ATR |  |  |  |  | CDC | 320 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | DS1 | 3711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 0961 | 0288 | 3-3C-00 | 3-3C-01 | 3-20 | 3711 | DS | 3711 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3711_DS | 3711(#6ATR) DS | ATR |  |  |  |  | CDC | 321 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | DS2 | 3712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 0963 | 0289 | 3-3C-02 | 3-3C-03 | 3-21 | 3712 | DS | 3712 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3712_DS | 3712(#6ATR) DS | ATR |  |  |  |  | CDC | 322 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | ABS1 | 1671 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1060 | 1061 | 0330 | 4-32-04 | 4-32-05 | 3-4A | 1671 | DS | 1671 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.1671_ABS | 1671(#3ATR) ABS | ATR |  |  |  |  | CDC | 323 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | ABS2 | 1672 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1062 | 1063 | 0331 | 4-32-06 | 4-32-07 | 3-4B | 1672 | DS | 1672 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.1672_ABS | 1672(#3ATR) ABS | ATR |  |  |  |  | CDC | 324 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | ABS1 | 1681 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1068 | 1069 | 0334 | 4-32-12 | 4-32-13 | 3-4E | 1681 | DS | 1681 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.1681_ABS | 1681(#4ATR) ABS | ATR |  |  |  |  | CDC | 325 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | ABS2 | 1682 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1070 | 1071 | 0335 | 4-32-14 | 4-32-15 | 3-4F | 1682 | DS | 1682 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.1682_ABS | 1682(#4ATR) ABS | ATR |  |  |  |  | CDC | 326 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | ABS1 | 1781 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1056 | 1057 | 0328 | 4-32-00 | 4-32-01 | 3-48 | 1781 | DS | 1781 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.1781_ABS | 1781(#6ATR) ABS | ATR |  |  |  |  | CDC | 327 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | ABS2 | 1782 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1058 | 1059 | 0329 | 4-32-02 | 4-32-03 | 3-49 | 1782 | DS | 1782 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.1782_ABS | 1782(#6ATR) ABS | ATR |  |  |  |  | CDC | 328 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 33 | 33kV | 490 | #2SSTR(490) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | T/2SSTR | T/3ATR33 |  |  | 0421 |  | 0271 | 3-14-05 |  | 3-0F | 490 | CB | 490 CB AS |  | aabb | B3/E04_A1 | [8 empty] | 龍崎ES.490_CB | 490(#2SSTR) CB | OTHER |  |  |  |  | CDC | 329 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 33 | 33kV | 490 | #2SSTR(490) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0422 |  |  | 3-14-06 |  |  | 490 | CB | 490 CB PHA |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 330 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 360 | #4SSTR(360) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1Bb | T/6ATR33 | T/4SSTR |  |  | 0416 |  | 0260 | 3-14-00 |  | 3-04 | 360 | CB | 360 CB AS |  | abab | B3/E04_A1 | [8 empty] | 龍崎ES.360_CB | 360(#4SSTR) CB | OTHER |  |  |  |  | CDC | 331 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 33 | 33kV | 360 | #4SSTR(360) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0417 |  |  | 3-14-01 |  |  | 360 | 51A | #6ATR THI 360 51RY |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.#4SSTR_51A | #4SSTR 51RY | OTHER |  |  |  |  | CDC | 332 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/3ATR33 | R/3SHR |  |  | 0418 |  | 0270 | 3-14-02 |  | 3-0E | 530 | CB | 530 CB AS |  | aaab | B3/E04_C | [8 empty] | 龍崎ES.530_CB | 530 CB | OTHER |  |  |  |  | CDC | 333 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0420 |  |  | 3-14-04 |  |  | 530 | 87A | #3ATR THI 530 87RY |  |  | B3/E04_C | [8 empty] | 龍崎ES.530_87A | 530 87RY | OTHER |  |  |  |  | CDC | 334 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0419 |  |  | 3-14-03 |  |  | 530 | 51A | #3ATR THI 530 51RY |  |  | B3/E04_C | [8 empty] | 龍崎ES.530_PHA | 530 相間RY | OTHER |  |  |  |  | CDC | 335 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | R/4SHR | T/4ATR33 |  |  | 0423 |  | 0276 | 3-14-07 |  | 3-14 | 540 | CB | 540 CB AS |  | acab | B3/E04_C | [8 empty] | 龍崎ES.540_CB | 540 CB | OTHER |  |  |  |  | CDC | 336 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0425 |  |  | 3-15-01 |  |  | 540 | 87A | #4ATR THI 540 87RY |  |  | B3/E04_C | [8 empty] | 龍崎ES.540_87A | 540 87RY | OTHER |  |  |  |  | CDC | 337 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0424 |  |  | 3-15-00 |  |  | 540 | 51A | #4ATR THI 540 51RY |  |  | B3/E04_C | [8 empty] | 龍崎ES.540_PHA | 540 相間RY | OTHER |  |  |  |  | CDC | 338 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | DS1 | 531 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1064 | 1065 | 0332 | 4-32-08 | 4-32-09 | 3-4C | 531 | DS | 531 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.531_ABS | 531 ABS | OTHER |  |  |  |  | CDC | 339 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | ABS1 | 541 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1072 | 1073 | 0336 | 4-33-00 | 4-33-01 | 3-50 | 541 | DS | 541 DS AS |  |  | B3/E04_C | [8 empty] | 龍崎ES.541_ABS | 541 ABS | OTHER |  |  |  |  | CDC | 340 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 341 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 342 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 343 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 344 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 345 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 346 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 347 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 348 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL5 |  |  | MvMoment | No5 AI參考點 10% |  | Y |  | AI | [6 empty] | 0320 |  |  | 3-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER |  |  |  |  | CDC | 349 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH5 |  |  | MvMoment | No5 AI參考點 90% |  | Y |  | AI | [6 empty] | 0321 |  |  | 3-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER |  |  |  |  | CDC | 350 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCL6 |  | Element | [12 empty] | 0384 |  |  | 4-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCL6 | AI 10%參考點 ADCL6 | OTHER |  |  |  |  | CDC | 351 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | RTU | RTU |  | ADCH6 |  | Element | [12 empty] | 0385 |  |  | 4-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍超ES.AI_ADCH6 | AI 90%參考點 ADCH6 | OTHER |  |  |  |  | CDC | 352 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 3_DCV_P | #3直流P電源 | Element | MvMoment | #3 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0312 |  |  | 3-B8 |  |  | DCV |  | #3BATT P-G | kV_-150_150(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍崎ES.#3直流P電源 | #3直流P電源電壓 | OTHER |  |  |  |  | CDC | 353 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 3_DCV_N | #3直流N電源 | Element | MvMoment | #3 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0313 |  |  | 3-B9 |  |  | DCV |  | #3BATT N-G | kV_-150_150(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍崎ES.#3直流N電源 | #3直流N電源電壓 | OTHER |  |  |  |  | CDC | 354 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 4_DCV_P | #4直流P電源 | Element | MvMoment | #4 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | DCV |  | #4 BATT P-G | kV_-150_150(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍崎ES.#4直流P電源 | #4直流P電源電壓 | OTHER |  |  |  |  | CDC | 355 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 4_DCV_N | #4直流N電源 | Element | MvMoment | #4 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | DCV |  | #4 BATT N-G | kV_-150_150(-2000_2000) |  | B3/E04_A1 | [8 empty] | 龍崎ES.#4直流N電源 | #4直流N電源電壓 | OTHER |  |  |  |  | CDC | 356 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 3-39-00 |  |  | 通訊機 |  | 通訊充電機故障 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 357 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0905 |  |  | 3-38-09 |  |  | COF |  | 消防警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.火災警報(1) | 火災警報(1) | OTHER |  |  |  |  | CDC | 358 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0911 |  |  | 3-38-15 |  |  | ACFA |  | 通訊設備AC故障 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 359 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | StaDev | 所內設施 |  | Test_CB1 | TEST_CB(S_1) | B2,Element | Status | TEST CB1 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  | 0256 | 3-30-00 |  | 3-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 龍崎ES.TEST_CB(S_1) | 345KV(S)TEST CB | OTHER |  |  |  |  | CDC | 360 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 345 | 345kV | StaDev | 所內設施 |  | RTU_R_L | RTU_S/L(S_1) | B2,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 3-30-01 |  |  | RTU |  | LOCAL/REMOTE |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.RTU_S/L(S_1) | 345KV(S)RTU S/L | OTHER |  |  |  |  | CDC | 361 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E04 | 龍崎ES | 161 | 161kV | StaDev | 所內設施 |  | Test_CB2 | TEST_CB(S_2) | B2,Element | Status | TEST CB2 | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 龍崎ES.TEST_CB(S_2) | 161KV(S)TEST CB | OTHER |  |  |  |  | CDC | 362 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 161 | 161kV | StaDev | 所內設施 |  | RTU_R_L | RTU_S/L(S_2) | B2,Element | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU |  | LOCAL/REMOTE |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.RTU_S/L(S_2) | 161KV(S)RTU S/L | OTHER |  |  |  |  | CDC | 363 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | BFS |  | Element | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 3-33-01 |  |  | 345KV | BF-S | 345KV BFS |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_BFS | 345KV(S)斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 364 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | BFA |  | Element | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0295 |  |  | 3-04-07 |  |  | 345KV | BFA | 345KV BFA |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_BFA | 345KV(S)斷路器失靈(BF)警報 | OTHER |  |  |  |  | CDC | 365 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RCA |  | Element | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 3-05-01 |  |  | 345KV | RCA | 345KV RCA |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_RCA | 345KV(S)LINE 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 366 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | OSCA |  | Element | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 3-05-00 |  |  | OSCA | A/N | 345KV示波器啟動警報OSCA(備用) |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_OSCA | 345KV(S)示波器起動 | OTHER |  |  |  |  | CDC | 367 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | OSCF |  | Element | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0904 |  |  | 3-38-08 |  |  | OSCF | A/N | 345KV示波器缺紙或故障警報OSCF(備用) |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_OSCF | 345KV(S)示波器故障,電源跳脫 | OTHER |  |  |  |  | CDC | 368 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | BFS |  | Element | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  |  | 1-30-04 |  |  | 161KV | BF-S | 161KV BFS |  |  | ELEM/E04_A1 | [8 empty] | 龍崎ES.161KV_S_BFS | 161KV(S)斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 369 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | BFA |  | Element | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 161KV | BFA | 161KV BFA |  |  | ELEM/E04_A1 | [8 empty] | 龍崎ES.161KV_S_BFA | 161KV(S)斷路器失靈(BF)RY | OTHER |  |  |  |  | CDC | 370 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | RCA |  | Element | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 161KV | RCA | 161KV RCA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161KV_S_RCA | 161KV(S)LINE 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 371 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | OSCA |  | Element | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161KV_S_OSCA | 161KV(S)示波器起動 | OTHER |  |  |  |  | CDC | 372 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | OSCF |  | Element | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0566 |  |  | 1-33-06 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161KV_S_OSCF | 161KV(S)示波器故障,電源跳脫 | OTHER |  |  |  |  | CDC | 373 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 25TA |  | Element | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0426 |  |  | 3-15-02 |  |  | 25RY | 25TA | 自動同步校核裝置超時警報 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_25TA | 345KV(S)同步電驛25TA | OTHER |  |  |  |  | CDC | 374 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 25PFA |  | Element | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0427 |  |  | 3-15-03 |  |  | 25RY | 25PFA | 自動同步校核裝置電源故障警報 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_25PFA | 345KV(S)同步電驛25PFA | OTHER |  |  |  |  | CDC | 375 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 25TA |  | Element | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0160 |  |  | 1-14-00 |  |  | 25RY | 25TA | 自動同步校核裝置超時警報 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161KV_S_25TA | 161KV(S)同步電驛25TA | OTHER |  |  |  |  | CDC | 376 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 25PFA |  | Element | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0161 |  |  | 1-14-01 |  |  | 25RY | 25PFA | 自動同步校核裝置電源故障警報 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161KV_S_25PFA | 161KV(S)同步電驛25PFA | OTHER |  |  |  |  | CDC | 377 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | CBA |  | Element | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 3-33-02 |  |  | 345KV | CBA | 345KV CB 重故障 |  |  | ELEM/E04_C | [8 empty] | 龍崎ES.345KV_S_CBA | 345KV(S)斷路器重故障 | OTHER |  |  |  |  | CDC | 378 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | CBF |  | Element | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0819 |  |  | 3-33-03 |  |  | 345KV | CBF | 345KV CB 輕故障 |  |  | ELEM/E04_C | [8 empty] | 龍崎ES.345KV_S_CBF | 345KV(S)斷路器輕故障 | OTHER |  |  |  |  | CDC | 379 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | CBA |  | Element | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0517 |  |  | 1-30-05 |  |  | 161KV | CBA | 161KV CB 重故障 |  |  | ELEM/E04_A1 | [15 empty] | CDC | 380 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | CBF |  | Element | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0518 |  |  | 1-30-06 |  |  | 161KV | CBF | 161KV CB 輕故障 |  |  | ELEM/E04_A1 | [15 empty] | CDC | 381 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | COMT |  | Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 3-33-04 |  |  | 345KV | COMT | 345KV COMT |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_COMT | 345KV(S)空壓機警報 | OTHER |  |  |  |  | CDC | 382 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | COMT |  | Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0519 |  |  | 1-30-07 |  |  | 161KV | COMT | 161KV COMT |  |  | B2/E04_A1 | [15 empty] | CDC | 383 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | E2 | 3712E_ | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0964 | 0965 | 0290 | 3-3C-04 | 3-3C-05 | 3-22 | 3712E | DS | 3712E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3712E_ES | 3712E(#6TR) ES | OTHER |  |  |  |  | CDC | 384 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | E1 | 3741E | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 1082 | 1083 |  | 4-33-10 | 4-33-11 |  | 3741E | DS | 天輪龍崎山線 3741E DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.3741E_ES | 3741E ES | OTHER |  |  |  |  | CDC | 385 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 33 | 33kV | 400 | 400 |  | ABS1 | 404_ABS | del | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1074 | 1075 | 0337 | 4-33-02 | 4-33-03 | 3-51 | 404 | DS | 404 DS AS |  |  | B2/E04_C | [8 empty] | 龍崎ES.404_ABS | 404ABS | OTHER |  |  |  |  | CDC | 386 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 33 | 33kV | 490 | #2SSTR(490) |  | DS1 | 491 | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1066 | 1067 | 0333 | 4-32-10 | 4-32-11 | 3-4D | 491 | DS | 491 DS AS |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.491_ABS | 491ABS | OTHER |  |  |  |  | CDC | 387 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 3-31-08 |  |  | NO.3 SH.R | 96B1 | NO.3 SH.R 96B1 |  |  | B3/E04_C | [8 empty] | 龍崎ES.#3ATR_SR96B1 | #3ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 388 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0793 |  |  | 3-31-09 |  |  | NO.3 SH.R | 96B1 | NO.3 SH.R 96B2 |  |  | B3/E04_C | [8 empty] | 龍崎ES.#3ATR_SR96B2 | #3ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 389 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0794 |  |  | 3-31-10 |  |  | NO.3 SH.R | 96D | NO.3 SH.R 96D |  |  | B3/E04_C | [8 empty] | 龍崎ES.#3ATR_SR96D | #3ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 390 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0795 |  |  | 3-31-11 |  |  | NO.3 SH.R | 96P | NO.3 SH.R 96P |  |  | B3/E04_C | [8 empty] | 龍崎ES.#3ATR_SR96P | #3ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 391 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 3-32-08 |  |  | NO.4 SH.R | 96B1 | NO.4 SH.R 96B1 |  |  | B3/E04_C | [8 empty] | 龍崎ES.#4ATR_SR96B1 | #4ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 392 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0809 |  |  | 3-32-09 |  |  | NO.4 SH.R | 96B2 | NO.4 SH.R 96B2 |  |  | B3/E04_C | [8 empty] | 龍崎ES.#4ATR_SR96B2 | #4ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 393 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0810 |  |  | 3-32-10 |  |  | NO.4 SH.R | 96D | NO.4 SH.R 96D |  |  | B3/E04_C | [8 empty] | 龍崎ES.#4ATR_SR96D | #4ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 394 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0811 |  |  | 3-32-11 |  |  | NO.4 SH.R | 96P | NO.4 SH.R 96P |  |  | B3/E04_C | [8 empty] | 龍崎ES.#4ATR_SR96P | #4ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 395 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 3-34-06 |  |  | 3740 | #1RY | 天輪龍崎山線 RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_87CFA | 天輪山線(3740) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 396 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 3-34-08 |  |  | 3740 | #2RY | 天輪龍崎山線 RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3740_85CFA | 天輪山線(3740) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 397 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0843 |  |  | 3-34-11 |  |  | 3760 | #1RY | 嘉民龍崎紅線 RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_87CFA | 嘉民紅線(3760) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 398 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 3-34-13 |  |  | 3760 | #2RY | 嘉民龍崎紅線 RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3760_85CFA | 嘉民紅線(3760) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 399 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0848 |  |  | 3-35-00 |  |  | 3770 | #1RY | 龍崎(北)~龍崎(南)臨時線 3770 RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_87CFA | 北南臨時線(3770) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 400 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0850 |  |  | 3-35-02 |  |  | 3770 | #2RY | 龍崎(北)~龍崎(南)臨時線 3770 RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3770_85CFA | 北南臨時線(3770) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 401 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 3-35-05 |  |  | 3790 | #1RY | 龍崎仁武山線 RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_87CFA | 仁武山線(3790) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 402 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0855 |  |  | 3-35-07 |  |  | 3790 | #2RY | 龍崎仁武山線 RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3790_85CFA | 仁武山線(3790) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 403 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0858 |  |  | 3-35-10 |  |  | 3860 | #1RY | 興達龍崎三路 RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_87CFA | 興達三路(3860) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 404 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 3-35-12 |  |  | 3860 | #2RY | 興達龍崎三路 RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3860_85CFA | 興達三路(3860) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 405 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 3-35-15 |  |  | 3870 | #1RY | 路北龍崎白線RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_87CFA | 路北白線(3870) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 406 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0865 |  |  | 3-36-01 |  |  | 3870 | #2RY | 路北龍崎白線RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3870_85CFA | 路北白線(3870) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 407 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0868 |  |  | 3-36-04 |  |  | 3890 | #1RY | 龍崎仁武海線 RAOA1 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_87CFA | 仁武海線(3890) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 408 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0870 |  |  | 3-36-06 |  |  | 3890 | #2RY | 龍崎仁武海線 RAOA2 |  |  | B2/E04_C | [8 empty] | 龍崎ES.3890_85CFA | 仁武海線(3890) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 409 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | ABS_89A | S_89A | Element | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 3-39-10 |  |  | ABS AL |  | ABS NFB跳脫警報 |  |  | ELEM/E04_A1 | [8 empty] | 龍崎ES.345KV_S_89A | 345KV(S)ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 410 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | ABS_89A | S_89A | Element | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0565 |  |  | 1-33-05 |  |  | ABS AL |  | ABS NFB跳脫警報 |  |  | ELEM/E04_A1 | [8 empty] | 龍崎ES.161KV_S_89A | 161KV(S)ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 411 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | OilLeak | S_洩油池 | Element | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0894 |  |  | 3-37-14 |  |  | Locate Empty |  |  |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_S_洩油池 | 345KV(S)洩油池水位警報 | OTHER |  |  |  |  | CDC | 412 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | ACB3 |  |  | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0896 |  | 0360 | 3-38-00 |  | 3-68 | ACB3 | ON/OFF | 所內電源ACB3 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.所內電源ACB3 | 所內電源ACB3 | OTHER |  |  |  |  | CDC | 413 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | ACB4 |  |  | Status | 所內電源ACB4 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0898 |  | 0362 | 3-38-02 |  | 3-6A | ACB4 | ON/OFF | 所內電源ACB4 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.所內電源ACB4 | 所內電源ACB4 | OTHER |  |  |  |  | CDC | 414 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | ACBT2 | ACB_TIE2 | Element | Status | 所內電源ACB TIE2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0897 |  | 0361 | 3-38-01 |  | 3-69 | ACB TIE2 | ON/OFF | 所內電源ACB TIE2 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.ACB_TIE2 | 所內電源ACB TIE2 | OTHER |  |  |  |  | CDC | 415 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 3A5Other | 所內電源ACB34A | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0913 |  |  | 3-39-01 |  |  | ACB | ACBA | ACB3.ACB4.ACB TIE所內電源ACB 故障跳脫警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.所內電源ACB34A | 所內電源#3,#4,TIE ACB故障 | OTHER |  |  |  |  | CDC | 416 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 4A5Other | 所內電源ACB12A | Element | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0560 |  |  | 1-33-00 |  |  | ACB | ACBA | ACB1,ACB2,ACB TIE1 所內電源ACB 故障跳脫警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.所內電源ACB12A | 所內電源#1,#2,TIE ACB故障 | OTHER |  |  |  |  | CDC | 417 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | STUV1 | STUVA12 | Element | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0561 |  |  | 1-33-01 |  |  | STUVA |  | ACB1,ACB2,ACB TIE1 所內電源欠壓警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.STUVA12 | #12所內電源欠壓 | OTHER |  |  |  |  | CDC | 418 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | DCA |  | Element | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0564 |  |  | 1-33-04 |  |  | DCA |  | NFB跳脫警報 |  |  | ELEM/E04_A1 | [8 empty] | 龍崎ES.直流電源DCA_S | #3,#4直流電源故障警報 | OTHER |  |  |  |  | CDC | 419 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 6A5Other | 充電機故障_S | Element | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0562 |  |  | 1-33-02 |  |  | 充電機 | CHG2 | #4,5,6充電機警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.充電機故障_S | #4,#5,#6直流充電機故障 | OTHER |  |  |  |  | CDC | 420 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | DCE |  | Element | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0563 |  |  | 1-33-03 |  |  | DCE | DCE1 | DC接地警報 |  |  | ELEM/E04_A1 | [8 empty] | 龍崎ES.直流電源DCE_S | #3,#4直流電源接地故障警報 | OTHER |  |  |  |  | CDC | 421 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | STUV2 | STUVA34 | Element | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0901 |  |  | 3-38-05 |  |  | SSTR | STUVA | ACB3.ACB4.ACB TIE 所內電源欠壓警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.STUVA34 | #34所內電源欠壓 | OTHER |  |  |  |  | CDC | 422 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | 8A5Other | 1630_DLPA | B2,B3,Element | Status | 警報等級5動作8 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0524 |  |  | 1-30-12 |  |  | 1630 | 87L CFA | 1630 DLPA DLP RY電源故障 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1630_DLPA | 龍崎聯錏線(1630)DLP電源故障 | OTHER |  |  |  |  | CDC | 423 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0525 |  |  | 1-30-13 |  |  | 1630 | 87LA | 1630 MDAR RY故障 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1630_RYFA | 龍崎聯錏線(1630)數位電驛故障 | OTHER |  |  |  |  | CDC | 424 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0528 |  |  | 1-31-00 |  |  | 1640 | 87CFA | 龍崎岡山嘉峰線1(640) 87RY通訊故障 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_87CFA | 岡山嘉峰線(1640)87RY通訊故障 | OTHER |  |  |  |  | CDC | 425 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0529 |  |  | 1-31-01 |  |  | 1640 | RYFA | 龍崎岡山嘉峰線(1640) 數位電驛故障 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1640_RYFA | 岡山嘉峰線(1640)數位電驛故障 | OTHER |  |  |  |  | CDC | 426 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0532 |  |  | 1-31-04 |  |  | 1710 | 87L CFA | 龍崎路園線 1710 87L CFA(87L通訊故障) |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_87CFA | 龍崎路園線(1710)87RY通訊故障 | OTHER |  |  |  |  | CDC | 427 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0533 |  |  | 1-31-05 |  |  | 1710 | 87LA | 龍崎路園線 1710 87LA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1710_RYFA | 龍崎路園線(1710)數位電驛故障 | OTHER |  |  |  |  | CDC | 428 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0536 |  |  | 1-31-08 |  |  | 1720 | 87L CFA | 龍崎岡山二路1720 87L CFA(87L通訊故障) |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_87CFA | 龍崎岡山二路(1720)87RY通訊故障 | OTHER |  |  |  |  | CDC | 429 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0537 |  |  | 1-31-09 |  |  | 1720 | 87LA | 龍崎岡山二路1720 87LA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1720_RYFA | 龍崎岡山二路(1720)數位電驛故障 | OTHER |  |  |  |  | CDC | 430 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0540 |  |  | 1-31-12 |  |  | 1730 | 87L CFA | 龍崎岡山三路1730 87L CFA(87L通訊故障) |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_87CFA | 龍崎岡山三路(1730)87RY通訊故障 | OTHER |  |  |  |  | CDC | 431 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0541 |  |  | 1-31-13 |  |  | 1730 | 87LA | 龍崎岡山三路1730 87LA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1730_RYFA | 龍崎岡山三路(1730)數位電驛故障 | OTHER |  |  |  |  | CDC | 432 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | 50SA |  | B2,B3,Element | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0550 |  |  | 1-32-06 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1600)50RY 測試/正常 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.1600TIE_50SA | 161KV TIE(1600) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  | Element | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0552 |  |  | 1-32-08 |  |  | 161kV #3,4Bus | RYFA | 161kV #3,4Bus RYFA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161_SBUS_RYFA | 161KV#3,4BUS 87RY數位電驛故障 | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | 87CTFA | SBUS_CTFA | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0553 |  |  | 1-32-09 |  |  | 161kV #3,4Bus | CTFA | 161kV #3,4Bus CTFA |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161_SBUS_CTFA | 161KV#3,4BUS 87RYCT迴路故障 | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E04_C | [16 empty] | 436 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E04_C | [16 empty] | 437 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E04_C | [16 empty] | 438 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E04_C | [16 empty] | 439 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E04_C | [16 empty] | 440 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E04_C | [16 empty] | 441 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | 9A5Other | 通信機房溫度 | Element | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0910 |  |  | 3-38-14 |  |  | 溫控警報 |  | 通信室溫控警報 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.通信機房溫度 | 通信機房溫度警報 | OTHER |  |  |  |  | CDC | 442 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 443 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 444 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights1 | 外燈(1) | Element | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0914 |  | 0363 | 3-39-02 |  | 3-6B | 161KV SY L1 |  | 主變三次測外燈(1) |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.外燈(1) | 主變三次側外燈(1) | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights2 | 外燈(2) | Element | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0915 |  | 0364 | 3-39-03 |  | 3-6C | 161KV SY L2 |  | 主變三次測外燈(2) |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.外燈(2) | 主變三次側外燈(2) | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights3 | 外燈(3) | Element | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0916 |  | 0365 | 3-39-04 |  | 3-6D | 345KV SY L1 |  | 屋外燈(1) |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.外燈(3) | 屋外燈(1) | OTHER |  |  |  |  | CDC | 447 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights4 | 外燈(4) | Element | Status | 照明4 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0917 |  | 0366 | 3-39-05 |  | 3-6E | 345KV SY L2 |  | 屋外燈(2) |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.外燈(4) | 屋外燈(2) | OTHER |  |  |  |  | CDC | 448 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights7 | 信號燈(1) | Element | [12 empty] | 0918 |  | 0367 | 3-39-06 |  | 3-6F | 161KV SY |  | 信號燈(1) |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.信號燈(1) | 信號燈(1) | OTHER |  |  |  |  | CDC | 449 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights8 | 信號燈(2) | Element | [12 empty] | 0919 |  | 0368 | 3-39-07 |  | 3-70 | 345KV SY |  | 信號燈(2) |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.信號燈(2) | 信號燈(2) | OTHER |  |  |  |  | CDC | 450 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights5 | 外燈(5) | Element | Status | 照明5 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0920 |  | 0369 | 3-39-08 |  | 3-71 | 161KV SY |  | 北側外燈 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.外燈(5) | 北側外燈 | OTHER |  |  |  |  | CDC | 451 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E04 | 龍崎ES | 0 |  | StaDev | 所內設施 |  | Lights6 | 外燈(6) | Element | [12 empty] | 0921 |  | 0370 | 3-39-09 |  | 3-72 | 345KV SY |  | 超超高壓外燈 |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.外燈(6) | 東開關場外燈 | OTHER |  |  |  |  | CDC | 452 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ON/OFF | OFF
E04 | 龍崎ES | 161 | 161kV | 3BUS | #3BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0514 |  | 0062 | 1-30-02 |  | 1-3E | 161KV | 87B3S | 161KV #3BUS 87RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER |  |  |  |  | CDC | 453 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 4BUS | #4BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0515 |  | 0063 | 1-30-03 |  | 1-3F | 161KV | 87B4S | 161KV #4BUS 87RY U/L |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER |  |  |  |  | CDC | 454 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 1_RYFA | #3,4BUS | Element | Status | 第1套RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 3-33-11 |  |  | 345kV #3,4Bus | RYFA1 | 345kV #3,4Bus RYFA第一套 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KVBUS_RYFA3 | 345KV #3,4BUS 第一套數位RY故障 | OTHER |  |  |  |  | CDC | 455 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 87CTFA1 | #3,4BUS | Element | Status | 第1具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 3-33-12 |  |  | 345kV #3,4Bus | CTFA1 | 345kV #3,4Bus CTFA第一套 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KVBUS_CTFA3 | 345KV #3,4BUS 第一套CT回路故障 | OTHER |  |  |  |  | CDC | 456 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3BUS | #3BUS |  | 1_87UL1 | 345#3B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0813 |  | 0371 | 3-32-13 |  | 3-73 | 345KV | #3BUS | 387B1S |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#3B_87UL1 | 345KV #3BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 457 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 4BUS | #4BUS |  | 1_87UL1 | 345#4B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0815 |  | 0372 | 3-32-15 |  | 3-74 | 345KV | #4BUS | 487B1S |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#4B_87UL1 | 345KV #4BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 458 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 2_RYFA | #3,4BUS | Element | Status | 第2套RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 3-33-13 |  |  | 345kV #3,4Bus | RYFA2 | 345kV #3,4Bus RYFA第二套 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KVBUS_RYFA4 | 345KV #3,4BUS 第二套數位RY故障 | OTHER |  |  |  |  | CDC | 459 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | 87CTFA2 | #3,4BUS | Element | Status | 第2具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 3-33-14 |  |  | 345kV #3,4Bus | CTFA2 | 345kV #3,4Bus CTFA第二套 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KVBUS_CTFA4 | 345KV #3,4BUS 第二套CT回路故障 | OTHER |  |  |  |  | CDC | 460 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3BUS | #3BUS |  | 1_87UL2 | 345#3B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0814 |  | 0373 | 3-32-14 |  | 3-75 | 345KV | #3BUS | 387B2S |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#3B_87UL2 | 345KV #3BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 461 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 4BUS | #4BUS |  | 1_87UL2 | 345#4B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0816 |  | 0374 | 3-33-00 |  | 3-76 | 345KV | #4BUS | 487B2S |  |  | B2/E04_C | [8 empty] | 龍崎ES.345#4B_87UL2 | 345KV #4BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | StaDev | 所內設施 |  | GRZ100 | BVS_RY | B2,Element | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0554 |  |  | 1-32-10 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/E04_A1 | [8 empty] | 龍崎ES.BVS_RY | 161KV #4BUS GRZ100 RY U/L | OTHER |  |  |  |  | CDC | 463 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | RYFA | 斷路器失靈電驛故障 | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0555 |  |  | 1-32-11 |  |  | 161KV | BF_RYFA | 161KV斷路器失靈電驛故障 |  |  | B2/E04_A1 | [8 empty] | 龍崎ES.161KV_SBFRYFA | 161KV(S)斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RYFA | 斷路器失靈電驛故障 | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0821 |  |  | 3-33-05 |  |  | 345KV | BF_RYFA | 345KV斷路器失靈電驛故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.345KV_SBFRYFA | 345KV(S)斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 465 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0280 | 3-30-13 |  | 3-18 | #3 ATR | ON/OFF | #3ATR 第一套87RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_87UL1 | #3ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 466 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0281 | 3-30-14 |  | 3-19 | #3 ATR | ON/OFF | #3ATR 第二套87RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_87UL2 | #3ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 467 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0877 |  | 0282 | 3-36-13 |  | 3-1A | #3ATR | 51Z U/L | #3ATR 51Z RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_51ZUL | #3ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 468 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0879 |  | 0283 | 3-36-15 |  | 3-1B | #3ATR | 87U/L | #3ATR 電抗器(530) 87RY U/L |  |  | B3/E04_C | [8 empty] | 龍崎ES.#3ATR_530_87UL | #3ATR 電抗器(530) 87RY U/L | OTHER |  |  |  |  | CDC | 469 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0878 |  |  | 3-36-14 |  |  | #3ATR | RYFA | #3ATR 數位電驛故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_RYFA | #3ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 470 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0876 |  |  | 3-36-12 |  |  | #3ATR | 86A | #3ATR 86(51Z/87/96) RY |  |  | B2/E04_C | [8 empty] | 龍崎ES.#3ATR_86A | #3ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 471 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0284 | 3-30-02 |  | 3-1C | #6 ATR | ON/OFF | #6ATR 第一套87RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_87UL1 | #6ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 472 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0285 | 3-30-03 |  | 3-1D | #6 ATR | ON/OFF | #6ATR 第二套87RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_87UL2 | #6ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 473 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0880 |  |  | 3-37-00 |  |  | #6ATR | 86A | #6ATR 86(51Z/87/96) RY |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_86A | #6ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 474 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0881 |  | 0286 | 3-37-01 |  | 3-1E | #6ATR | 51Z U/L | #6ATR 51Z RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_51ZUL | #6ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 475 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 3-37-02 |  |  | #6ATR | RYFA | #6ATR 數位電驛故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#6ATR_RYFA | #6ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 476 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0883 |  |  | 3-37-03 |  |  | #4ATR | 86A | #4ATR 86(51Z/87/96) RY |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_86A | #4ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 477 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0884 |  | 0377 | 3-37-04 |  | 3-79 | #4ATR | 51Z U/L | #4ATR 51Z RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_51ZUL | #4ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 478 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 3-37-05 |  |  | #4ATR | RYFA | #4ATR 數位電驛故障 |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_RYFA | #4ATR 數位電驛故障 | OTHER |  |  |  |  | CDC | 479 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0886 |  | 0378 | 3-37-06 |  | 3-7A | #4ATR | 87U/L | #4ATR 電抗器(540) 87RY U/L |  |  | B3/E04_C | [8 empty] | 龍崎ES.#4ATR_540_87UL | #4ATR 電抗器(540) 87RY U/L | OTHER |  |  |  |  | CDC | 480 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0797 |  | 0375 | 3-31-13 |  | 3-77 | #4 ATR | ON/OFF | #4ATR 第一套87RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_87UL1 | #4ATR 第一套 87RY U/L | OTHER |  |  |  |  | CDC | 481 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  | 0376 | 3-31-14 |  | 3-78 | #4 ATR | ON/OFF | #4ATR 第二套87RY U/L |  |  | B2/E04_C | [8 empty] | 龍崎ES.#4ATR_87UL2 | #4ATR 第二套 87RY U/L | OTHER |  |  |  |  | CDC | 482 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | ComPoint |  |  | RTU_MCT | S_MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0319 |  |  | 3-07-07 |  |  | 345_S_RTU | MCT_ SOE | 345 S RTU MASTER RY SOE |  |  | B2/E04_C | [15 empty] | CDC | 483 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 161 | 161kV | ComPoint |  |  | RTU_MCT | S_MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 161_S_RTU | MCT_ SOE | 161 S RTU MASTER RY SOE |  |  | B2/E04_A1 | [15 empty] | CDC | 484 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 33 | 33kV | ComPoint |  |  | CBA |  | Element | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 3-33-08 |  |  | 33kV | CBA | 33kV CB重故障 |  |  | ELEM/E04_C | [8 empty] | 龍崎ES.33KV_S_CBA | 33KV(S) CB重故障 | OTHER |  |  |  |  | CDC | 485 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | ComPoint |  |  | CBF |  | Element | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0825 |  |  | 3-33-09 |  |  | 33kV | CBF | 33kV CB輕故障 |  |  | ELEM/E04_C | [8 empty] | 龍崎ES.33KV_S_CBF | 33KV(S) CB輕故障 | OTHER |  |  |  |  | CDC | 486 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | ComPoint |  |  | COMT |  | Element | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 3-33-10 |  |  | 33kV | COMT | 33kV COMT |  |  | B2/E04_C | [8 empty] | 龍崎ES.33KV_S_COMT | 33KV(S) 空壓機運轉超時警報 | OTHER |  |  |  |  | CDC | 487 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | 490 | #2SSTR(490) |  | TE0 | 491TE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 490 | #2SSTR(490) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 490 | #2SSTR(490) |  | LE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 530 | #3SHR(530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | TE0 | 541TE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 33 | 33kV | 540 | #4SHR(540) |  | LE1 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E03_A1 | [8 empty] | 龍崎ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 237 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | E2 | 3842E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 265 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | LE0 | 3812E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E04_C | [16 empty] | 265 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | Vbs5 | [9 empty] | B1/E04_C | [17 empty] | v_best_161_34 | OPRD1: E04/161/3BUS/V; OPRD2: E04/161/4BUS/V
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | Vbs9 | [9 empty] | B1/E04_C | [17 empty] | v_best_345_34 | OPRD1: E04/345/3BUS/V; OPRD2: E04/345/4BUS/V
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/E04_C | [17 empty] | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: NULL; OPRD5: E04/0/CalcPoint/Vbs5; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/E04_C | [17 empty] | p_sum_15 | OPRD1: E04/161/1630/MW; OPRD2: E04/161/1640/MW; OPRD3: E04/161/1710/MW; OPRD4: E04/161/1720/MW; OPRD5: E04/161/1730/MW; OPRD6: E04/345/3730/MW; OPRD7: E04/345/3740/MW; OPRD8: E04/345/3760/MW; OPRD9: E04/345/3770/MW; OPRD10: E04/345/3790/MW; OPRD11: E04/345/3830/MW; OPRD12: E04/345/3840/MW; OPRD13: E04/345/3860/MW; OPRD14: E04/345/3870/MW; OPRD15: E04/345/3890/MW
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/E04_C | [17 empty] | pwr_cnd2 | OPRD1: E04/0/CalcPoint/OPRN2_MW
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/E04_C | [17 empty] | none
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/E04_C | [17 empty] | pwr_fail | OPRD1: E04/0/CalcPoint/OPRN1; OPRD2: E04/0/CalcPoint/OPRN2; OPRD3: E04/0/CalcPoint/PRFL_UL
E04 | 龍崎ES |  |  | 3ATR | 3ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3830/MW; OPRD2: E04/345/3830/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES |  |  | 4ATR | 4ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3840/MW; OPRD2: E04/345/3840/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES |  |  | 6ATR | 6ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3730/MW; OPRD2: E04/345/3730/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎～聯錏線(1630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_A1 | [17 empty] | amp_cal | OPRD1: E04/161/1630/MW; OPRD2: E04/161/1630/MVAR; OPRD3: E04/0/CalcPoint/Vbs5
E04 | 龍崎ES | 161 | 161kV | 1640 | 龍崎～岡山~嘉峰線(1640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_A1 | [17 empty] | amp_cal | OPRD1: E04/161/1640/MW; OPRD2: E04/161/1640/MVAR; OPRD3: E04/0/CalcPoint/Vbs5
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎～路園線(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_A1 | [17 empty] | amp_cal | OPRD1: E04/161/1710/MW; OPRD2: E04/161/1710/MVAR; OPRD3: E04/0/CalcPoint/Vbs5
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎～岡山二路(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_A1 | [17 empty] | amp_cal | OPRD1: E04/161/1720/MW; OPRD2: E04/161/1720/MVAR; OPRD3: E04/0/CalcPoint/Vbs5
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎～岡山三路(1730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_A1 | [17 empty] | amp_cal | OPRD1: E04/161/1730/MW; OPRD2: E04/161/1730/MVAR; OPRD3: E04/0/CalcPoint/Vbs5
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪～龍崎山線(3740) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3740/MW; OPRD2: E04/345/3740/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民～龍崎紅線(3760) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3760/MW; OPRD2: E04/345/3760/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 345 | 345kV | 3770 | 龍崎(北)～龍崎(南)臨時線(3770) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3770/MW; OPRD2: E04/345/3770/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 345 | 345kV | 3790 | 龍崎～仁武山線(3790) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3790/MW; OPRD2: E04/345/3790/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達～龍崎三路(3860) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3860/MW; OPRD2: E04/345/3860/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北～龍崎白線(3870) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3870/MW; OPRD2: E04/345/3870/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES | 345 | 345kV | 3890 | 龍崎～仁武海線(3890) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E04_C | [17 empty] | amp_cal | OPRD1: E04/345/3890/MW; OPRD2: E04/345/3890/MVAR; OPRD3: E04/0/CalcPoint/Vbs9
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E04_C | LG_500 | 475 | 550 | 625 | 990 |  | -475 | -550 | -625 | -990 | [7 empty] | va_million | OPRD1: E04/345/3830/MW; OPRD2: E04/345/3830/MVAR
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E04_C | LG_500 | 475 | 550 | 625 | 990 |  | -475 | -550 | -625 | -990 | [7 empty] | va_million | OPRD1: E04/345/3840/MW; OPRD2: E04/345/3840/MVAR
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E04_C | LG_500 | 475 | 550 | 625 | 990 |  | -475 | -550 | -625 | -990 | [7 empty] | va_million | OPRD1: E04/345/3730/MW; OPRD2: E04/345/3730/MVAR
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | LOAD | [9 empty] | B2/E04_C | [17 empty] | tr_loading | OPRD1: E04//3ATR/MVA; OPRD2: 500
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | LOAD | [9 empty] | B2/E04_C | [17 empty] | tr_loading | OPRD1: E04//4ATR/MVA; OPRD2: 500
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | LOAD | [9 empty] | B2/E04_C | [17 empty] | tr_loading | OPRD1: E04//6ATR/MVA; OPRD2: 500
E04 | 龍崎ES |  |  | 3ATR | #3ATR |  | PF | [9 empty] | B2/E04_C | [17 empty] | pf_cal | OPRD1: E04/345/3830/MW; OPRD2: E04/345/3830/MVAR
E04 | 龍崎ES |  |  | 4ATR | #4ATR |  | PF | [9 empty] | B2/E04_C | [17 empty] | pf_cal | OPRD1: E04/345/3840/MW; OPRD2: E04/345/3840/MVAR
E04 | 龍崎ES |  |  | 6ATR | #6ATR |  | PF | [9 empty] | B2/E04_C | [17 empty] | pf_cal | OPRD1: E04/345/3730/MW; OPRD2: E04/345/3730/MVAR
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/E04_C | [17 empty] | com_alarm_23 | OPRD1: E04//3ATR/63Q; OPRD2: E04//3ATR/96D; OPRD3: E04//3ATR/96B1; OPRD4: E04//3ATR/TRA; OPRD5: E04//3ATR/96B2; OPRD6: E04//3ATR/51ZA; OPRD7: E04//3ATR/96PA; OPRD8: E04//4ATR/96D; OPRD9: E04//4ATR/63Q; OPRD10: E04//4ATR/TRA; OPRD11: E04//4ATR/96B2; OPRD12: E04//4ATR/96B1; OPRD13: E04//4ATR/51ZA; OPRD14: E04//4ATR/96PA; OPRD15: E04//6ATR/96B1; OPRD16: E04//6ATR/96B2; OPRD17: E04//6ATR/TRA; OPRD18: E04//6ATR/63Q; OPRD19: E04//6ATR/51ZA; OPRD20: E04//6ATR/96PA; OPRD21: E04//6ATR/96D; OPRD22: E04/161/3BUS/87A; OPRD23: E04/161/4BUS/87A
E04 | 龍崎ES | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/E04_C | [17 empty] | com_alarm_3 | OPRD1: E04//3ATR/TRF; OPRD2: E04//4ATR/TRF; OPRD3: E04//6ATR/TRF
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 3_DCV_P | #3直流P電源 |  | MvMoment | #3 直流P電源電壓 |  | Y |  | AI |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/3_DCV_P
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 3_DCV_N | #3直流N電源 |  | MvMoment | #3 直流N電源電壓 |  | Y |  | AI |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/3_DCV_N
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 4_DCV_P | #4直流P電源 |  | MvMoment | #4 直流P電源電壓 |  | Y |  | AI |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/4_DCV_P
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 4_DCV_N | #4直流N電源 |  | MvMoment | #4 直流N電源電壓 |  | Y |  | AI |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/4_DCV_N
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/CHG2
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Fire1 |  |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Fire1
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/CommACF
E04 | 龍崎ES | 345 | 345kV | StaDev_C | 所內設施 |  | Test_CB1 | TEST_CB(S_1) |  | Status | TEST CB1 | Open/Close | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/345/StaDev/Test_CB1
E04 | 龍崎ES | 345 | 345kV | StaDev_C | 所內設施 |  | RTU_R_L | RTU_S/L(S_1) |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/345/StaDev/RTU_R_L
E04 | 龍崎ES | 161 | 161kV | StaDev_C | 所內設施 |  | Test_CB2 | TEST_CB(S_2) |  | Status | TEST CB2 | Open/Close | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/StaDev/Test_CB2
E04 | 龍崎ES | 161 | 161kV | StaDev_C | 所內設施 |  | RTU_R_L | RTU_S/L(S_2) |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/StaDev/RTU_R_L
E04 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | BFS | S_BFS |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/ComPoint/BFS
E04 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | BFA | 龍崎南_BFA |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/ComPoint/BFA
E04 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | CBA | S_CBA |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/ComPoint/CBA
E04 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | CBF | S_CBF |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/ComPoint/CBF
E04 | 龍崎ES | 345 | 345kV | ComPoint_C |  |  | ABS_89A | S_89A |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/345/ComPoint/ABS_89A
E04 | 龍崎ES | 161 | 161kV | ComPoint_C |  |  | ABS_89A | S_89A |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/ComPoint/ABS_89A
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | ACB3 |  |  | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/ACB3
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | ACB4 |  |  | Status | 所內電源ACB4 | Close/Open | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/ACB4
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | ACBT2 | ACB_TIE2 |  | Status | 所內電源ACB TIE2 | Close/Open | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/ACBT2
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 3A5Other | 所內電源ACB34A |  | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/3A5Other
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 4A5Other | 所內電源ACB12A |  | Status | 警報等級5動作4 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/4A5Other
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 5A5Other | STUVA12 |  | Status | 警報等級5動作5 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/5A5Other
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | DCA | 直流電源DCA_S |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/DCA
E04 | 龍崎ES | 0 |  | StaDev_D1 | 所內設施 |  | DCA | 直流電源DCA_S |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E04_D1 | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/DCA
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 6A5Other | 充電機故障_S |  | Status | 警報等級5動作6 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/6A5Other
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | DCE | 直流電源DCE_S |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/DCE
E04 | 龍崎ES | 0 |  | StaDev_D1 | 所內設施 |  | DCE | 直流電源DCE_S |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E04_D1 | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/DCE
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 7A5Other | STUVA34 |  | Status | 警報等級5動作7 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/7A5Other
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | 9A5Other | 通信機房溫度 |  | Status | 警報等級5動作9 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/9A5Other
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights1 | 外燈(1) |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights1
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights2 | 外燈(2) |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights2
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights3 | 外燈(3) |  | Status | 照明3 | OFF/ON | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights3
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights4 | 外燈(4) |  | Status | 照明4 | OFF/ON | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights4
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights7 | 信號燈(1) | [8 empty] | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights7
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights8 | 信號燈(2) | [8 empty] | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights8
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights5 | 外燈(5) |  | Status | 照明5 | OFF/ON | Y | 7 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights5
E04 | 龍崎ES | 0 |  | StaDev_C | 所內設施 |  | Lights6 | 外燈(6) | [8 empty] | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/0/StaDev/Lights6
E04 | 龍崎ES | 161 | 161kV | StaDev_C | 所內設施 |  | GRZ100 | BVS_RY |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP |  | B3/E04_C | [17 empty] | lamp2CC | OPRD1: E04/161/StaDev/GRZ100

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E04 | 龍崎ES | 345 | 345kV | 3BUS | #3BUS |  | V | [17 empty] | 3-82 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.345KV#3BUS_KV | 345KV #3BUS KV | BUS | E04/345/3BUS/V |  |  |  | CDC | 2 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | MW | [17 empty] | 3-87 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3760_MW | 嘉民紅線 MW | LINE345 | E04/345/3760/MW |  |  |  | CDC | 3 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | MVAR | [17 empty] | 3-88 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3760_MVAR | 嘉民紅線 MVAR | LINE345 | E04/345/3760/MVAR |  |  |  | CDC | 4 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | MW | [17 empty] | 3-84 | [5 empty] | MW_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3740_MW | 天輪山線 MW | LINE345 | E04/345/3740/MW |  |  |  | CDC | 5 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | MVAR | [17 empty] | 3-85 | [5 empty] | MVAR_-1200_1200(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3740_MVAR | 天輪山線 MVAR | LINE345 | E04/345/3740/MVAR |  |  |  | CDC | 6 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | MW | [17 empty] | 3-8A | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3770_MW | 北南臨時線(3770) MW | LINE345 | E04/345/3770/MW |  |  |  | CDC | 7 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | MVAR | [17 empty] | 3-8B | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3770_MVAR | 北南臨時線(3770) MVAR | LINE345 | E04/345/3770/MVAR |  |  |  | CDC | 8 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | MW | [17 empty] | 3-8D | [5 empty] | MW_-1800_1800(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3790_MW | 仁武山線 MW | LINE345 | E04/345/3790/MW |  |  |  | CDC | 9 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | MVAR | [17 empty] | 3-8E | [5 empty] | MVAR_-1800_1800(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3790_MVAR | 仁武山線 MVAR | LINE345 | E04/345/3790/MVAR |  |  |  | CDC | 10 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | MW | [17 empty] | 3-96 | [5 empty] | MW_-1800_1800(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3890_MW | 仁武海線 MW | LINE345 | E04/345/3890/MW |  |  |  | CDC | 11 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | MVAR | [17 empty] | 3-97 | [5 empty] | MVAR_-1800_1800(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3890_MVAR | 仁武海線 MVAR | LINE345 | E04/345/3890/MVAR |  |  |  | CDC | 12 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | MW | [17 empty] | 3-90 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3860_MW | 興達三路 MW | LINE345 | E04/345/3860/MW |  |  |  | CDC | 13 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | MVAR | [17 empty] | 3-91 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3860_MVAR | 興達三路 MVAR | LINE345 | E04/345/3860/MVAR |  |  |  | CDC | 14 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | MW | [17 empty] | 3-93 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3870_MW | 路北白線 MW | LINE345 | E04/345/3870/MW |  |  |  | CDC | 15 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | MVAR | [17 empty] | 3-94 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3870_MVAR | 路北白線 MVAR | LINE345 | E04/345/3870/MVAR |  |  |  | CDC | 16 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | E04/0/RTU/ADCH1 |  |  |  | CDC | 17 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | E04/0/RTU/ADCH2 |  |  |  | CDC | 18 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | E04/0/RTU/ADCH3 |  |  |  | CDC | 19 | GENERICAIPoint | ES004_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | E04/0/RTU/ADCH4 |  |  |  | CDC | 20 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCH5 | [17 empty] | 3-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCH5 | AI 90%參考點 ADCH5 | OTHER | E04/0/RTU/ADCH5 |  |  |  | CDC | 21 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCH6 | [17 empty] | 4-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCH6 | AI 90%參考點 ADCH6 | OTHER | E04/0/RTU/ADCH6 |  |  |  | CDC | 22 | GENERICAIPoint | ES004_L4 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | E04/0/RTU/ADCL1 |  |  |  | CDC | 23 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | E04/0/RTU/ADCL2 |  |  |  | CDC | 24 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | E04/0/RTU/ADCL3 |  |  |  | CDC | 25 | GENERICAIPoint | ES004_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | E04/0/RTU/ADCL4 |  |  |  | CDC | 26 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCL5 | [17 empty] | 3-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCL5 | AI 10%參考點 ADCL5 | OTHER | E04/0/RTU/ADCL5 |  |  |  | CDC | 27 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | AI | AI |  | ADCL6 | [17 empty] | 4-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍超ES.AI_ADCL6 | AI 10%參考點 ADCL6 | OTHER | E04/0/RTU/ADCL6 |  |  |  | CDC | 28 | GENERICAIPoint | ES004_L4 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 3BUS | #3BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.161KV#3BUS_KV | 161KV #3BUS KV | BUS | E04/161/3BUS/V |  |  |  | CDC | 29 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 4BUS | #4BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.161KV#4BUS_KV | 161KV #4BUS KV | BUS | E04/161/4BUS/V |  |  |  | CDC | 30 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E04 | 龍崎ES | 345 | 345kV | 4BUS | #4BUS |  | V | [17 empty] | 3-83 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.345KV#4BUS_KV | 345KV #4BUS KV | BUS | E04/345/4BUS/V |  |  |  | CDC | 31 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3740LPD | 天輪山線(3740) |  | V | [17 empty] | 3-86 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3740LPD_KV | 天輪山線(3740) LPD KV | LINE345 | E04/345/3740/V |  |  |  | CDC | 32 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3760LPD | 嘉民紅線(3760) |  | V | [17 empty] | 3-89 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3760LPD_KV | 嘉民紅線(3760) LPD KV | LINE345 | E04/345/3760/V |  |  |  | CDC | 33 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3770LPD | 北南臨時線(3770) |  | V | [17 empty] | 3-8C | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3770LPD_KV | 北南臨時線(3770) LPD KV | LINE345 | E04/345/3770/V |  |  |  | CDC | 34 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3790LPD | 仁武山線(3790) |  | V | [17 empty] | 3-8F | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3790LPD_KV | 仁武山線(3790) LPD KV | LINE345 | E04/345/3790/V |  |  |  | CDC | 35 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3860LPD | 興達三路(3860) |  | V | [17 empty] | 3-92 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3860LPD_KV | 興達三路(3860) LPD KV | LINE345 | E04/345/3860/V |  |  |  | CDC | 36 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3870LPD | 路北白線(3870) |  | V | [17 empty] | 3-95 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3870LPD_KV | 路北白線(3870) LPD KV | LINE345 | E04/345/3870/V |  |  |  | CDC | 37 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 345 | 345kV | 3890LPD | 仁武海線(3890) |  | V | [17 empty] | 3-98 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.3890LPD_KV | 仁武海線(3890) LPD KV | LINE345 | E04/345/3890/V |  |  |  | CDC | 38 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | MW | [17 empty] | 1-89 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1640_MW | 岡山嘉峰線 MW | LINE161 | E04/161/1640/MW |  |  |  | CDC | 39 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | MVAR | [17 empty] | 1-8A | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1640_MVAR | 岡山嘉峰線 MVAR | LINE161 | E04/161/1640/MVAR |  |  |  | CDC | 40 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1640LPD | 岡山嘉峰線(1640) |  | V | [17 empty] | 1-8B | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1640LPD_KV | 岡山嘉峰線(1640) LPD KV | LINE161 | E04/161/1640/V |  |  |  | CDC | 41 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1710_MW | 龍崎路園線 MW | LINE161 | E04/161/1710/MW |  |  |  | CDC | 42 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1710_MVAR | 龍崎路園線 MVAR | LINE161 | E04/161/1710/MVAR |  |  |  | CDC | 43 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1710LPD | 龍崎路園線(1710) |  | V | [17 empty] | 1-8E | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1710LPD_KV | 龍崎路園線(1710) LPD KV | LINE161 | E04/161/1710/V |  |  |  | CDC | 44 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | MW | [17 empty] | 1-8F | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1720_MW | 龍崎岡山二路 MW | LINE161 | E04/161/1720/MW |  |  |  | CDC | 45 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | MVAR | [17 empty] | 1-90 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1720_MVAR | 龍崎岡山二路 MVAR | LINE161 | E04/161/1720/MVAR |  |  |  | CDC | 46 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1720LPD | 龍崎岡山二路(1720) |  | V | [17 empty] | 1-91 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1720LPD_KV | 龍崎岡山二路(1720) LPD KV | LINE161 | E04/161/1720/V |  |  |  | CDC | 47 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1730_MW | 龍崎岡山三路 MW | LINE161 | E04/161/1730/MW |  |  |  | CDC | 48 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1730_MVAR | 龍崎岡山三路 MVAR | LINE161 | E04/161/1730/MVAR |  |  |  | CDC | 49 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1730LPD | 龍崎岡山三路(1730) |  | V | [17 empty] | 1-94 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1730LPD_KV | 龍崎岡山三路(1730) LPD KV | LINE161 | E04/161/1730/V |  |  |  | CDC | 50 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E04 | 龍崎ES | 0 |  | 1600TIE | 1600TIE |  | I | [17 empty] | 1-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1600TIE_AMP | 1600TIE AMP | TIE | E04/161/1600/I |  |  |  | CDC | 51 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | 1800TIE | 1800TIE |  | I | [17 empty] | 1-85 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1800TIE_AMP | 1800TIE AMP | TIE | E04/161/1800/I |  |  |  | CDC | 52 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR二次側 |  | MW | [17 empty] | 1-9B | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#3ATR_MW | #3ATR二次側 MW | ATR | E04/345/3830/MW |  |  |  | CDC | 53 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR二次側 |  | MVAR | [17 empty] | 1-9C | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#3ATR_MVAR | #3ATR二次側 MVAR | ATR | E04/345/3830/MVAR |  |  |  | CDC | 54 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | TapPosMv | [17 empty] | 3-9B |  | 3-59 |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_TAP | #3ATR OLTC TAP | ATR | E04//3ATR/TapPosMv |  |  |  | CDC | 55 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E04 | 龍崎ES | 0 |  | 3ATR_OIL | #3ATR |  | R | [17 empty] | 3-9D | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_OIL_R | #3ATR R相油溫 | ATR | E04//3ATR/Oil_R |  |  |  | CDC | 56 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 3ATR_COIL | #3ATR |  | R | [17 empty] | 3-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_COIL_R | #3ATR R相線溫 | ATR | E04//3ATR/Coil_R |  |  |  | CDC | 57 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 3ATR_OIL | #3ATR |  | S | [17 empty] | 3-9F | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_OIL_S | #3ATR S相油溫 | ATR | E04//3ATR/Oil_S |  |  |  | CDC | 58 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 3ATR_COIL | #3ATR |  | S | [17 empty] | 3-9E | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_COIL_S | #3ATR S相線溫 | ATR | E04//3ATR/Coil_S |  |  |  | CDC | 59 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 3ATR_OIL | #3ATR |  | T | [17 empty] | 3-A1 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_OIL_T | #3ATR T相油溫 | ATR | E04//3ATR/Oil_T |  |  |  | CDC | 60 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 3ATR_COIL | #3ATR |  | T | [17 empty] | 3-A0 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#3ATR_COIL_T | #3ATR T相線溫 | ATR | E04//3ATR/Coil_T |  |  |  | CDC | 61 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR二次側 |  | MW | [17 empty] | 1-9D | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#4ATR_MW | #4ATR二次側 MW | ATR | E04/345/3840/MW |  |  |  | CDC | 62 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR二次側 |  | MVAR | [17 empty] | 1-9E | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#4ATR_MVAR | #4ATR二次側 MVAR | ATR | E04/345/3840/MVAR |  |  |  | CDC | 63 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | TapPosMv | [17 empty] | 3-A4 |  | 3-5D |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_TAP | #4ATR OLTC TAP | ATR | E04//4ATR/TapPosMv |  |  |  | CDC | 64 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E04 | 龍崎ES | 0 |  | 4ATR_OIL | #4ATR |  | R | [17 empty] | 3-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_OIL_R | #4ATR R相油溫 | ATR | E04//4ATR/Oil_R |  |  |  | CDC | 65 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 4ATR_COIL | #4ATR |  | R | [17 empty] | 3-A5 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_COIL_R | #4ATR R相線溫 | ATR | E04//4ATR/Coil_R |  |  |  | CDC | 66 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 4ATR_OIL | #4ATR |  | S | [17 empty] | 3-A8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_OIL_S | #4ATR S相油溫 | ATR | E04//4ATR/Oil_S |  |  |  | CDC | 67 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 4ATR_COIL | #4ATR |  | S | [17 empty] | 3-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_COIL_S | #4ATR S相線溫 | ATR | E04//4ATR/Coil_S |  |  |  | CDC | 68 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 4ATR_OIL | #4ATR |  | T | [17 empty] | 3-AA | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_OIL_T | #4ATR T相油溫 | ATR | E04//4ATR/Oil_T |  |  |  | CDC | 69 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 4ATR_COIL | #4ATR |  | T | [17 empty] | 3-A9 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#4ATR_COIL_T | #4ATR T相線溫 | ATR | E04//4ATR/Coil_T |  |  |  | CDC | 70 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR二次側 |  | MW | [17 empty] | 1-A0 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#6ATR_MW | #6ATR二次側 MW | ATR | E04/345/3730/MW |  |  |  | CDC | 71 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR二次側 |  | MVAR | [17 empty] | 1-A1 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#6ATR_MVAR | #6ATR二次側 MVAR | ATR | E04/345/3730/MVAR |  |  |  | CDC | 72 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | TapPosMv | [17 empty] | 3-AD |  | 3-55 |  |  |  | TAP_0.5_16.5(0_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_TAP | #6ATR OLTC TAP | ATR | E04//6ATR/TapPosMv |  |  |  | CDC | 73 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | TAP16_0 | 15.000000 | 15.000000 | 16.000000 | 17.500000 | 0.000000 | 2.000000 | 2.000000 | 1.000000 | -0.500000 | 0.100000
E04 | 龍崎ES | 0 |  | 6ATR_OIL | #6ATR |  | R | [17 empty] | 3-AF | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_OIL_R | #6ATR R相油溫 | ATR | E04//6ATR/Oil_R |  |  |  | CDC | 74 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 6ATR_COIL | #6ATR |  | R | [17 empty] | 3-AE | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_COIL_R | #6ATR R相線溫 | ATR | E04//6ATR/Coil_R |  |  |  | CDC | 75 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 6ATR_OIL | #6ATR |  | S | [17 empty] | 3-B1 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_OIL_S | #6ATR S相油溫 | ATR | E04//6ATR/Oil_S |  |  |  | CDC | 76 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 6ATR_COIL | #6ATR |  | S | [17 empty] | 3-B0 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_COIL_S | #6ATR S相線溫 | ATR | E04//6ATR/Coil_S |  |  |  | CDC | 77 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 6ATR_OIL | #6ATR |  | T | [17 empty] | 3-B3 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_OIL_T | #6ATR T相油溫 | ATR | E04//6ATR/Oil_T |  |  |  | CDC | 78 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  | 6ATR_COIL | #6ATR |  | T | [17 empty] | 3-B2 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_S | [8 empty] | 龍崎ES.#6ATR_COIL_T | #6ATR T相線溫 | ATR | E04//6ATR/Coil_T |  |  |  | CDC | 79 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E04 | 龍崎ES | 0 |  |  |  |  | #3直流N電源 | [17 empty] | 3-B9 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#3直流N電源 | #3直流N電源電壓 | OTHER | E04/0/StaDev/3_DCV_N |  |  |  | CDC | 80 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  |  |  |  | #3直流P電源 | [17 empty] | 3-B8 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#3直流P電源 | #3直流P電源電壓 | OTHER | E04/0/StaDev/3_DCV_P |  |  |  | CDC | 81 | GENERICAIPoint | ES004_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  |  |  |  | #4直流N電源 | [17 empty] | 1-B1 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#4直流N電源 | #4直流N電源電壓 | OTHER | E04/0/StaDev/4_DCV_N |  |  |  | CDC | 82 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 0 |  |  |  |  | #4直流P電源 | [17 empty] | 1-B0 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.#4直流P電源 | #4直流P電源電壓 | OTHER | E04/0/StaDev/4_DCV_P |  |  |  | CDC | 83 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1630_MW | 龍崎聯錏線 MW | LINE161 | E04/161/1630/MW |  |  |  | CDC | 84 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 龍崎ES.1630_MVAR | 龍崎聯錏線 MVAR | LINE161 | E04/161/1630/MVAR |  |  |  | CDC | 85 | GENERICAIPoint | ES004_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | CB | [17 empty] | 3-01-05 |  | 3-0A | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3790_CB | 3790(仁武山線) CB | LINE345 | E04/345/3790/CB |  |  |  | CDC | 86 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | CB | [17 empty] | 3-04-02 |  | 3-17 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3890_CB | 3890(仁武海線) CB | LINE345 | E04/345/3890/CB |  |  |  | CDC | 87 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | CB | [17 empty] | 3-01-00 |  | 3-05 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3740_CB | 3740(天輪山線) CB | LINE345 | E04/345/3740/CB |  |  |  | CDC | 88 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | CB | [17 empty] | 3-01-03 |  | 3-08 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3770_CB | 3770(北南臨時線) CB | LINE345 | E04/345/3770/CB |  |  |  | CDC | 89 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | CB | [17 empty] | 3-03-00 |  | 3-12 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3860_CB | 3860(興達三路) CB | LINE345 | E04/345/3860/CB |  |  |  | CDC | 90 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | CB | [17 empty] | 3-04-00 |  | 3-15 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3870_CB | 3870(路北白線) CB | LINE345 | E04/345/3870/CB |  |  |  | CDC | 91 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | CB | [17 empty] | 3-01-02 |  | 3-07 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3760_CB | 3760(嘉民紅線) CB | LINE345 | E04/345/3760/CB |  |  |  | CDC | 92 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | CB | [17 empty] | 1-00-07 |  | 1-02 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1640_CB | 1640(岡山嘉峰線) CB | LINE161 | E04/161/1640/CB |  |  |  | CDC | 93 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | CB | [17 empty] | 1-01-03 |  | 1-03 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1710_CB | 1710(龍崎路園線) CB | LINE161 | E04/161/1710/CB |  |  |  | CDC | 94 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | CB | [17 empty] | 1-01-07 |  | 1-05 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1720_CB | 1720(龍崎岡山二路) CB | LINE161 | E04/161/1720/CB |  |  |  | CDC | 95 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | CB | [17 empty] | 1-02-03 |  | 1-06 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1730_CB | 1730(龍崎岡山三路) CB | LINE161 | E04/161/1730/CB |  |  |  | CDC | 96 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | CB | [17 empty] | 3-00-00 |  | 3-01 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3710_CB | 3710(#6ATR) CB | ATR | E04/345/3710/CB |  |  |  | CDC | 97 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | CB | [17 empty] | 3-00-01 |  | 3-02 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3730_CB | 3730(#6ATR) CB | LINE345 | E04/345/3730/CB |  |  |  | CDC | 98 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3750 | 3750 |  | CB | [17 empty] | 3-01-01 |  | 3-06 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3750_CB | 3750 CB | LINE345 | E04/345/3750/CB |  |  |  | CDC | 99 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3780 | 3780 |  | CB | [17 empty] | 3-01-04 |  | 3-09 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3780_CB | 3780 CB | LINE345 | E04/345/3780/CB |  |  |  | CDC | 100 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | CB | [17 empty] | 3-01-06 |  | 3-0B | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3810_CB | 3810(#3ATR) CB | ATR | E04/345/3810/CB |  |  |  | CDC | 101 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | CB | [17 empty] | 3-01-07 |  | 3-0C | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3830_CB | 3830(#3ATR) CB | LINE345 | E04/345/3830/CB |  |  |  | CDC | 102 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3880 | 3880 |  | CB | [17 empty] | 3-04-01 |  | 3-16 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3880_CB | 3880 CB | LINE345 | E04/345/3880/CB |  |  |  | CDC | 103 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | CB | [17 empty] | 3-02-06 |  | 3-10 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3840_CB | 3840(#4ATR) CB | ATR | E04/345/3840/CB |  |  |  | CDC | 104 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3850 | 3850 |  | CB | [17 empty] | 3-02-07 |  | 3-11 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.3850_CB | 3850 CB | LINE345 | E04/345/3850/CB |  |  |  | CDC | 105 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | DS1 | 3731 | [16 empty] | 3-3C-10 | 3-3C-11 | 3-23 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3731_DS | 3731(#6ATR) DS | ATR | E04/345/3730/DS1 |  |  |  | CDC | 106 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3730 | #6ATR(3730) |  | DS2 | 3732 | [16 empty] | 3-3C-12 | 3-3C-13 | 3-24 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3732_DS | 3732(#6ATR) DS | ATR | E04/345/3730/DS2 |  |  |  | CDC | 107 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | SSA11 | [17 empty] | 3-05-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3740_SSA11 | 天輪山線(3740) #1差流(87L)RY | LINE345 | E04/345/3740/1SSA1 |  |  |  | CDC | 108 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | SSA12 | [17 empty] | 3-05-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3740_SSA12 | 天輪山線(3740) #1測距(21)RY | LINE345 | E04/345/3740/1SSA2 |  |  |  | CDC | 109 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | SSA2 | [17 empty] | 3-05-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3740_SSA2 | 天輪山線(3740) #2測距(21)RY | LINE345 | E04/345/3740/2SSA |  |  |  | CDC | 110 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | RYFA1 | [17 empty] | 3-34-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_RYFA1 | 天輪山線(3740) 第一套RY故障 | LINE345 | E04/345/3740/RYFA1 |  |  |  | CDC | 111 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | RYFA2 | [17 empty] | 3-34-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_RYFA2 | 天輪山線(3740) 第二套RY故障 | LINE345 | E04/345/3740/RYFA2 |  |  |  | CDC | 112 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | 79UL | [17 empty] | 3-34-05 |  | 3-61 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_79UL | 天輪山線(3740) 79RY U/L | LINE345 | E04/345/3740/79UL |  |  |  | CDC | 113 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | DS1 | 3741 | [16 empty] | 3-3C-14 | 3-3C-15 | 3-25 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3741_DS | 3741(天輪山線) DS | LINE345 | E04/345/3740/DS1 |  |  |  | CDC | 114 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | DS2 | 3742 | [16 empty] | 3-3D-00 | 3-3D-01 | 3-26 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3742_DS | 3742(天輪山線) DS | LINE345 | E04/345/3740/DS2 |  |  |  | CDC | 115 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | E2 | 3742E | [16 empty] | 3-3D-02 | 3-3D-03 | 3-27 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3742E_ES | 3742E(天輪山線) ES | LINE345 | E04/345/3740/E2 |  |  |  | CDC | 116 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | SSA11 | [17 empty] | 3-05-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3760_SSA11 | 嘉民紅線(3760) #1差流(87L)RY | LINE345 | E04/345/3760/1SSA1 |  |  |  | CDC | 117 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | SSA12 | [17 empty] | 3-05-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3760_SSA12 | 嘉民紅線(3760) #1測距(21)RY | LINE345 | E04/345/3760/1SSA2 |  |  |  | CDC | 118 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | SSA2 | [17 empty] | 3-05-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3760_SSA2 | 嘉民紅線(3760) #2測距(21)RY | LINE345 | E04/345/3760/2SSA |  |  |  | CDC | 119 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | RYFA1 | [17 empty] | 3-34-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_RYFA1 | 嘉民紅線(3760) 第一套RY故障 | LINE345 | E04/345/3760/RYFA1 |  |  |  | CDC | 120 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | RYFA2 | [17 empty] | 3-34-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_RYFA2 | 嘉民紅線(3760) 第二套RY故障 | LINE345 | E04/345/3760/RYFA2 |  |  |  | CDC | 121 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | 79UL | [17 empty] | 3-34-10 |  | 3-62 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_79UL | 嘉民紅線(3760) 79RY U/L | LINE345 | E04/345/3760/79UL |  |  |  | CDC | 122 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | ABS1 | 3761 | [16 empty] | 3-3D-08 | 3-3D-09 | 3-2A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3761_ABS | 3761(嘉民紅線) ABS | LINE345 | E04/345/3760/ABS1 |  |  |  | CDC | 123 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | ABS2 | 3762 | [16 empty] | 3-3D-12 | 3-3D-13 | 3-2C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3762_ABS | 3762(嘉民紅線) ABS | LINE345 | E04/345/3760/ABS2 |  |  |  | CDC | 124 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3760 | 嘉民紅線(3760) |  | E1 | 3761E | [16 empty] | 3-3D-10 | 3-3D-11 | 3-2B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3761E_ES | 3761E(嘉民紅線) ES | LINE345 | E04/345/3760/E1 |  |  |  | CDC | 125 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | SSA11 | [17 empty] | 3-06-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3770_SSA11 | 北南臨時線(3770) #1(87L)RY | LINE345 | E04/345/3770/1SSA1 |  |  |  | CDC | 126 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | SSA12 | [17 empty] | 3-06-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3770_SSA12 | 北南臨時線(3770) #1(21)RY | LINE345 | E04/345/3770/1SSA2 |  |  |  | CDC | 127 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | SSA2 | [17 empty] | 3-06-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3770_SSA2 | 北南臨時線(3770) #2(21)RY | LINE345 | E04/345/3770/2SSA |  |  |  | CDC | 128 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | RYFA1 | [17 empty] | 3-35-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_RYFA1 | 北南臨時線(3770) #1RY故障 | LINE345 | E04/345/3770/RYFA1 |  |  |  | CDC | 129 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | RYFA2 | [17 empty] | 3-35-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_RYFA2 | 北南臨時線(3770) #2RY故障 | LINE345 | E04/345/3770/RYFA2 |  |  |  | CDC | 130 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | 79UL | [17 empty] | 3-34-15 |  | 3-63 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_79UL | 北南臨時線(3770) 79RY U/L | LINE345 | E04/345/3770/79UL |  |  |  | CDC | 131 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | ABS1 | 3771 | [16 empty] | 3-3D-14 | 3-3D-15 | 3-2D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3771_ABS | 3771(北南臨時線) ABS | LINE345 | E04/345/3770/ABS1 |  |  |  | CDC | 132 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | ABS2 | 3772 | [16 empty] | 3-3E-00 | 3-3E-01 | 3-2E | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3772_ABS | 3772(北南臨時線) ABS | LINE345 | E04/345/3770/ABS2 |  |  |  | CDC | 133 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3770 | 北南臨時線(3770) |  | E2 | 3772E | [16 empty] | 3-3E-02 | 3-3E-03 | 3-2F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3772E_ES | 3772E(北南臨時線) ES | LINE345 | E04/345/3770/E2 |  |  |  | CDC | 134 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | SSA11 | [17 empty] | 3-06-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3790_SSA11 | 仁武山線(3790) #1差流(87L)RY | LINE345 | E04/345/3790/1SSA1 |  |  |  | CDC | 135 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | SSA12 | [17 empty] | 3-06-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3790_SSA12 | 仁武山線(3790) #1測距(21)RY | LINE345 | E04/345/3790/1SSA2 |  |  |  | CDC | 136 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | SSA2 | [17 empty] | 3-06-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3790_SSA2 | 仁武山線(3790) #2測距(21)RY | LINE345 | E04/345/3790/2SSA |  |  |  | CDC | 137 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | RYFA1 | [17 empty] | 3-35-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_RYFA1 | 仁武山線(3790) 第一套RY故障 | LINE345 | E04/345/3790/RYFA1 |  |  |  | CDC | 138 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | RYFA2 | [17 empty] | 3-35-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_RYFA2 | 仁武山線(3790) 第二套RY故障 | LINE345 | E04/345/3790/RYFA2 |  |  |  | CDC | 139 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | 79UL | [17 empty] | 3-35-04 |  | 3-64 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_79UL | 仁武山線(3790) 79RY U/L | LINE345 | E04/345/3790/79UL |  |  |  | CDC | 140 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | ABS1 | 3791 | [16 empty] | 3-3E-08 | 3-3E-09 | 3-32 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3791_ABS | 3791(仁武山線) ABS | LINE345 | E04/345/3790/ABS1 |  |  |  | CDC | 141 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | ABS2 | 3792 | [16 empty] | 3-3E-12 | 3-3E-13 | 3-34 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3792_ABS | 3792(仁武山線) ABS | LINE345 | E04/345/3790/ABS2 |  |  |  | CDC | 142 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3790 | 仁武山線(3790) |  | E1 | 3791E | [16 empty] | 3-3E-10 | 3-3E-11 | 3-33 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3791E_ES | 3791E(仁武山線) ES | LINE345 | E04/345/3790/E1 |  |  |  | CDC | 143 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | ABS1 | 3831 | [16 empty] | 3-3F-08 | 3-3F-09 | 3-37 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3831_ABS | 3831(#3ATR) ABS | ATR | E04/345/3830/ABS1 |  |  |  | CDC | 144 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3830 | #3ATR(3830) |  | ABS2 | 3832 | [16 empty] | 3-3F-10 | 3-3F-11 | 3-38 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3832_ABS | 3832(#3ATR) ABS | ATR | E04/345/3830/ABS2 |  |  |  | CDC | 145 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | SSA11 | [17 empty] | 3-06-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3860_SSA11 | 興達三路(3860) #1差流(87L)RY | LINE345 | E04/345/3860/1SSA1 |  |  |  | CDC | 146 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | SSA12 | [17 empty] | 3-06-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3860_SSA12 | 興達三路(3860) #1測距(21)RY | LINE345 | E04/345/3860/1SSA2 |  |  |  | CDC | 147 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | SSA2 | [17 empty] | 3-07-00 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3860_SSA2 | 興達三路(3860) #2測距(21)RY | LINE345 | E04/345/3860/2SSA |  |  |  | CDC | 148 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | RYFA1 | [17 empty] | 3-35-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_RYFA1 | 興達三路(3860) 第一套RY故障 | LINE345 | E04/345/3860/RYFA1 |  |  |  | CDC | 149 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | RYFA2 | [17 empty] | 3-35-13 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_RYFA2 | 興達三路(3860) 第二套RY故障 | LINE345 | E04/345/3860/RYFA2 |  |  |  | CDC | 150 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | 79UL | [17 empty] | 3-35-09 |  | 3-65 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_79UL | 興達三路(3860) 79RY U/L | LINE345 | E04/345/3860/79UL |  |  |  | CDC | 151 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | ABS1 | 3861 | [16 empty] | 4-30-10 | 4-30-11 | 3-3D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3861_ABS | 3861(興達三路) ABS | LINE345 | E04/345/3860/ABS1 |  |  |  | CDC | 152 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | ABS2 | 3862 | [16 empty] | 4-30-12 | 4-30-13 | 3-3F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3862_ABS | 3862(興達三路) ABS | LINE345 | E04/345/3860/ABS2 |  |  |  | CDC | 153 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3860 | 興達三路(3860) |  | E1 | 3861E | [16 empty] | 4-30-08 | 4-30-09 | 3-3E | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3861E_ES | 3861E(興達三路) ES | LINE345 | E04/345/3860/E1 |  |  |  | CDC | 154 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | SSA11 | [17 empty] | 3-07-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3870_SSA11 | 路北白線(3870) #1差流(87L)RY | LINE345 | E04/345/3870/1SSA1 |  |  |  | CDC | 155 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | SSA12 | [17 empty] | 3-07-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3870_SSA12 | 路北白線(3870) #1測距(21)RY | LINE345 | E04/345/3870/1SSA2 |  |  |  | CDC | 156 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | SSA2 | [17 empty] | 3-07-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3870_SSA2 | 路北白線(3870) #2測距(21)RY | LINE345 | E04/345/3870/2SSA |  |  |  | CDC | 157 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | RYFA1 | [17 empty] | 3-36-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_RYFA1 | 路北白線(3870) 第一套RY故障 | LINE345 | E04/345/3870/RYFA1 |  |  |  | CDC | 158 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | RYFA2 | [17 empty] | 3-36-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_RYFA2 | 路北白線(3870) 第二套RY故障 | LINE345 | E04/345/3870/RYFA2 |  |  |  | CDC | 159 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | 79UL | [17 empty] | 3-35-14 |  | 3-66 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_79UL | 路北白線(3870) 79RY U/L | LINE345 | E04/345/3870/79UL |  |  |  | CDC | 160 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | ABS1 | 3871 | [16 empty] | 4-30-14 | 4-30-15 | 3-40 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3871_ABS | 3871(路北白線) ABS | LINE345 | E04/345/3870/ABS1 |  |  |  | CDC | 161 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | ABS2 | 3872 | [16 empty] | 4-31-00 | 4-31-01 | 3-41 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3872_ABS | 3872(路北白線) ABS | LINE345 | E04/345/3870/ABS2 |  |  |  | CDC | 162 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3870 | 路北白線(3870) |  | E2 | 3872E | [16 empty] | 4-31-02 | 4-31-03 | 3-42 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3872E_ES | 3872E(路北白線) ES | LINE345 | E04/345/3870/E2 |  |  |  | CDC | 163 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | SSA11 | [17 empty] | 3-07-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3890_SSA11 | 仁武海線(3890) #1差流(87L)RY | LINE345 | E04/345/3890/1SSA1 |  |  |  | CDC | 164 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | SSA12 | [17 empty] | 3-07-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3890_SSA12 | 仁武海線(3890) #1測距(21)RY | LINE345 | E04/345/3890/1SSA2 |  |  |  | CDC | 165 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | SSA2 | [17 empty] | 3-07-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.3890_SSA2 | 仁武海線(3890) #2測距(21)RY | LINE345 | E04/345/3890/2SSA |  |  |  | CDC | 166 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | RYFA1 | [17 empty] | 3-36-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_RYFA1 | 仁武海線(3890) 第一套RY故障 | LINE345 | E04/345/3890/RYFA1 |  |  |  | CDC | 167 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | RYFA2 | [17 empty] | 3-36-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_RYFA2 | 仁武海線(3890) 第二套RY故障 | LINE345 | E04/345/3890/RYFA2 |  |  |  | CDC | 168 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | 79UL | [17 empty] | 3-36-03 |  | 3-67 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_79UL | 仁武海線(3890) 79RY U/L | LINE345 | E04/345/3890/79UL |  |  |  | CDC | 169 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | ABS1 | 3891 | [16 empty] | 4-31-08 | 4-31-09 | 3-45 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3891_ABS | 3891(仁武海線) ABS | LINE345 | E04/345/3890/ABS1 |  |  |  | CDC | 170 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | ABS2 | 3892 | [16 empty] | 4-31-12 | 4-31-13 | 3-47 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3892_ABS | 3892(仁武海線) ABS | LINE345 | E04/345/3890/ABS2 |  |  |  | CDC | 171 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3890 | 仁武海線(3890) |  | E1 | 3891E | [16 empty] | 4-31-10 | 4-31-11 | 3-46 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3891E_ES | 3891E(仁武海線) ES | LINE345 | E04/345/3890/E1 |  |  |  | CDC | 172 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | PHA | [17 empty] | 1-01-01 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1640_PHA | 岡山嘉峰線(1640) 相間RY | LINE161 | E04/161/1640/PHA |  |  |  | CDC | 173 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | GDA | [17 empty] | 1-01-02 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1640_GDA | 岡山嘉峰線(1640) 接地RY | LINE161 | E04/161/1640/GDA |  |  |  | CDC | 174 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | 79UL | [17 empty] | 1-30-14 |  | 1-32 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1640_79UL | 岡山嘉峰線(1640) 79RY U/L | LINE161 | E04/161/1640/79UL |  |  |  | CDC | 175 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | ABS1 | 1641 | [16 empty] | 1-37-04 | 1-37-05 | 1-14 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1641_ABS | 1641(岡山嘉峰線) ABS | LINE161 | E04/161/1640/ABS1 |  |  |  | CDC | 176 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | ABS2 | 1642 | [16 empty] | 1-37-06 | 1-37-07 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1642_ABS | 1642(岡山嘉峰線) ABS | LINE161 | E04/161/1640/ABS2 |  |  |  | CDC | 177 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | ABS3 | 1643 | [16 empty] | 1-37-08 | 1-37-09 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1643_ABS | 1643(岡山嘉峰線) ABS | LINE161 | E04/161/1640/ABS3 |  |  |  | CDC | 178 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | E3 | 1643E | [16 empty] | 1-37-10 | 1-37-11 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1643E_ES | 1643E(岡山嘉峰線) ES | LINE161 | E04/161/1640/E3 |  |  |  | CDC | 179 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1710_PHA | 龍崎路園線(1710) 相間RY | LINE161 | E04/161/1710/PHA |  |  |  | CDC | 180 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1710_GDA | 龍崎路園線(1710) 接地RY | LINE161 | E04/161/1710/GDA |  |  |  | CDC | 181 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | 87A | [17 empty] | 1-01-04 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1710_87A | 龍崎路園線(1710) 87RY | LINE161 | E04/161/1710/85A |  |  |  | CDC | 182 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | 87UL | [17 empty] | 1-31-03 |  | 1-35 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1710_87UL | 龍崎路園線(1710) 87RY U/L | LINE161 | E04/161/1710/85UL |  |  |  | CDC | 183 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | 79UL | [17 empty] | 1-31-02 |  | 1-34 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1710_79UL | 龍崎路園線(1710) 79RY U/L | LINE161 | E04/161/1710/79UL |  |  |  | CDC | 184 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | ABS1 | 1711 | [16 empty] | 1-37-12 | 1-37-13 | 1-18 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1711_ABS | 1711(龍崎路園線) ABS | LINE161 | E04/161/1710/ABS1 |  |  |  | CDC | 185 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | ABS2 | 1712 | [16 empty] | 1-37-14 | 1-37-15 | 1-19 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1712_ABS | 1712(龍崎路園線) ABS | LINE161 | E04/161/1710/ABS2 |  |  |  | CDC | 186 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | ABS3 | 1713 | [16 empty] | 1-38-00 | 1-38-01 | 1-1A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1713_ABS | 1713(龍崎路園線) ABS | LINE161 | E04/161/1710/ABS3 |  |  |  | CDC | 187 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1710 | 龍崎路園線(1710) |  | E3 | 1713E | [16 empty] | 1-38-02 | 1-38-03 | 1-1B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1713E_ES | 1713E(龍崎路園線) ES | LINE161 | E04/161/1710/E3 |  |  |  | CDC | 188 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | PHA | [17 empty] | 1-02-01 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1720_PHA | 龍崎岡山二路(1720) 相間RY | LINE161 | E04/161/1720/PHA |  |  |  | CDC | 189 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | GDA | [17 empty] | 1-02-02 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1720_GDA | 龍崎岡山二路(1720) 接地RY | LINE161 | E04/161/1720/GDA |  |  |  | CDC | 190 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | 87A | [17 empty] | 1-02-00 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1720_87A | 龍崎岡山二路(1720) 87RY | LINE161 | E04/161/1720/85A |  |  |  | CDC | 191 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | 87UL | [17 empty] | 1-31-07 |  | 1-37 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1720_87UL | 龍崎岡山二路(1720) 87RY U/L | LINE161 | E04/161/1720/85UL |  |  |  | CDC | 192 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | 79UL | [17 empty] | 1-31-06 |  | 1-36 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1720_79UL | 龍崎岡山二路(1720) 79RY U/L | LINE161 | E04/161/1720/79UL |  |  |  | CDC | 193 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | ABS1 | 1721 | [16 empty] | 1-38-04 | 1-38-05 | 1-1E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1721_ABS | 1721(龍崎岡山二路) ABS | LINE161 | E04/161/1720/ABS1 |  |  |  | CDC | 194 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | ABS2 | 1722 | [16 empty] | 1-38-06 | 1-38-07 | 1-1F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1722_ABS | 1722(龍崎岡山二路) ABS | LINE161 | E04/161/1720/ABS2 |  |  |  | CDC | 195 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | ABS3 | 1723 | [16 empty] | 1-38-08 | 1-38-09 | 1-20 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1723_ABS | 1723(龍崎岡山二路) ABS | LINE161 | E04/161/1720/ABS3 |  |  |  | CDC | 196 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1720 | 龍崎岡山二路(1720) |  | E3 | 1723E | [16 empty] | 1-38-10 | 1-38-11 | 1-21 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1723E_ES | 1723E(龍崎岡山二路) ES | LINE161 | E04/161/1720/E3 |  |  |  | CDC | 197 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | PHA | [17 empty] | 1-02-05 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1730_PHA | 龍崎岡山三路(1730) 相間RY | LINE161 | E04/161/1730/PHA |  |  |  | CDC | 198 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | GDA | [17 empty] | 1-02-06 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1730_GDA | 龍崎岡山三路(1730) 接地RY | LINE161 | E04/161/1730/GDA |  |  |  | CDC | 199 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | 87A | [17 empty] | 1-02-04 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1730_87A | 龍崎岡山三路(1730) 87RY | LINE161 | E04/161/1730/85A |  |  |  | CDC | 200 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | 87UL | [17 empty] | 1-31-11 |  | 1-39 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1730_87UL | 龍崎岡山三路(1730) 87RY U/L | LINE161 | E04/161/1730/85UL |  |  |  | CDC | 201 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | 79UL | [17 empty] | 1-31-10 |  | 1-38 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1730_79UL | 龍崎岡山三路(1730) 79RY U/L | LINE161 | E04/161/1730/79UL |  |  |  | CDC | 202 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | ABS1 | 1731 | [16 empty] | 1-38-12 | 1-38-13 | 1-22 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1731_ABS | 1731(龍崎岡山三路) ABS | LINE161 | E04/161/1730/ABS1 |  |  |  | CDC | 203 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | ABS2 | 1732 | [16 empty] | 1-38-14 | 1-38-15 | 1-23 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1732_ABS | 1732(龍崎岡山三路) ABS | LINE161 | E04/161/1730/ABS2 |  |  |  | CDC | 204 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | ABS3 | 1733 | [16 empty] | 1-39-00 | 1-39-01 | 1-24 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1733_ABS | 1733(龍崎岡山三路) ABS | LINE161 | E04/161/1730/ABS3 |  |  |  | CDC | 205 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1730 | 龍崎岡山三路(1730) |  | E3 | 1733E | [16 empty] | 1-39-02 | 1-39-03 | 1-25 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1733E_ES | 1733E(龍崎岡山三路) ES | LINE161 | E04/161/1730/E3 |  |  |  | CDC | 206 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | CB | [17 empty] | 1-03-07 |  | 1-04 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1600_CB | 1600(TIE) CB | TIE | E04/161/1600/CB |  |  |  | CDC | 207 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 1600 | TIE(1600) |  | 50A | [17 empty] | 1-04-00 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1600_50A | 161KV TIE(1600) 50RY | TIE | E04/161/1600/50A |  |  |  | CDC | 208 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | ABS1 | 1601 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-1C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1601_ABS | 1601(TIE) ABS | TIE | E04/161/1600/ABS1 |  |  |  | CDC | 209 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1600 | TIE(1600) |  | ABS2 | 1602 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-1D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1602_ABS | 1602(TIE) ABS | TIE | E04/161/1600/ABS2 |  |  |  | CDC | 210 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | CB | [17 empty] | 1-04-01 |  | 1-09 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1800_CB | 1800(TIE) CB | TIE | E04/161/1800/CB |  |  |  | CDC | 211 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1802 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-2E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1802_DS | 1802(TIE) DS | TIE | E04/161/1800/DS1 |  |  |  | CDC | 212 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1800 | TIE(1800) |  | DS4 | 1804 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-2F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1804_DS | 1804(TIE) DS | TIE | E04/161/1800/DS2 |  |  |  | CDC | 213 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | CB | [17 empty] | 3-02-00 |  | 3-0D | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1670_CB | 1670(#3ATR) CB | ATR | E04/161/1670/CB |  |  |  | CDC | 214 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 87A1 | [17 empty] | 3-02-01 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#3ATR_87A1 | #3ATR 第一組 87RY | ATR | E04//3ATR/87A1 |  |  |  | CDC | 215 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 87A2 | [17 empty] | 3-02-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#3ATR_87A2 | #3ATR 第二組 87RY | ATR | E04//3ATR/87A2 |  |  |  | CDC | 216 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 96PA | [17 empty] | 3-02-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#3ATR_96PA | #3ATR 機械保護動作 | ATR | E04//3ATR/96PA |  |  |  | CDC | 217 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 51ZA | [17 empty] | 3-02-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#3ATR_51ZA | #3ATR 51Z(21+50,59-2,51Z) | ATR | E04//3ATR/51ZA |  |  |  | CDC | 218 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 59A | [17 empty] | 3-02-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#3ATR_59A | #3ATR 59RY | ATR | E04//3ATR/59A |  |  |  | CDC | 219 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 1_87UL1 | [17 empty] | 3-30-13 |  | 3-18 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_87UL1 | #3ATR 第一套 87RY U/L | OTHER | E04//3ATR/1_87UL1 |  |  |  | CDC | 220 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 1_87UL2 | [17 empty] | 3-30-14 |  | 3-19 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_87UL2 | #3ATR 第二套 87RY U/L | OTHER | E04//3ATR/1_87UL2 |  |  |  | CDC | 221 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 96D | [17 empty] | 3-31-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_96D | #3ATR 96D RY | ATR | E04//3ATR/96D |  |  |  | CDC | 222 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 96P | [17 empty] | 3-31-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_96P | #3ATR 96P RY | ATR | E04//3ATR/96P |  |  |  | CDC | 223 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 63Q | [17 empty] | 3-31-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_63Q | #3ATR 63Q RY | ATR | E04//3ATR/63Q |  |  |  | CDC | 224 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 96B1 | [17 empty] | 3-31-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_96B1 | #3ATR 96B1 RY | ATR | E04//3ATR/96B1 |  |  |  | CDC | 225 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 96B2 | [17 empty] | 3-31-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_96B2 | #3ATR 96B2 RY | ATR | E04//3ATR/96B2 |  |  |  | CDC | 226 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | TRA | [17 empty] | 3-31-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_TRA | #3ATR 重故障 | ATR | E04//3ATR/TRA |  |  |  | CDC | 227 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | TRF | [17 empty] | 3-31-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_TRF | #3ATR 輕故障 | ATR | E04//3ATR/TRF |  |  |  | CDC | 228 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | SupLocal | [17 empty] | 3-30-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_S/L | #3ATR OLTC S/L | ATR | E04//3ATR/SupLocal |  |  |  | CDC | 229 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | A_M | [17 empty] | 3-31-00 |  | 3-56 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_A/M | #3ATR OLTC A/M | ATR | E04/345/3830/Tap Chan |  |  |  | CDC | 230 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | M/F/I | [17 empty] | 4-33-06 | 4-33-07 | 3-57 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_M/F/I | #3ATR M/F/I | ATR | E04//3ATR/M_F_I |  |  |  | CDC | 231 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | ABS1 | 3811 | [16 empty] | 3-3E-14 | 3-3E-15 | 3-35 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3811_ABS | 3811(#3ATR) ABS | ATR | E04/345/3810/ABS1 |  |  |  | CDC | 232 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3810 | #3ATR(3810) |  | ABS2 | 3812 | [16 empty] | 3-3F-00 | 3-3F-01 | 3-36 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3812_ABS | 3812(#3ATR) ABS | ATR | E04/345/3810/ABS2 |  |  |  | CDC | 233 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | ABS1 | 1671 | [16 empty] | 4-32-04 | 4-32-05 | 3-4A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1671_ABS | 1671(#3ATR) ABS | ATR | E04/161/1670/ABS1 |  |  |  | CDC | 234 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1670 | #3ATR(1670) |  | ABS2 | 1672 | [16 empty] | 4-32-06 | 4-32-07 | 3-4B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1672_ABS | 1672(#3ATR) ABS | ATR | E04/161/1670/ABS2 |  |  |  | CDC | 235 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | CB | [17 empty] | 3-03-01 |  | 3-13 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1680_CB | 1680(#4ATR) CB | ATR | E04/161/1680/CB |  |  |  | CDC | 236 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 87A1 | [17 empty] | 3-03-02 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#4ATR_87A1 | #4ATR 第一組 87RY | ATR | E04//4ATR/87A1 |  |  |  | CDC | 237 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 87A2 | [17 empty] | 3-03-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#4ATR_87A2 | #4ATR 第二組 87RY | ATR | E04//4ATR/87A2 |  |  |  | CDC | 238 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 96PA | [17 empty] | 3-03-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#4ATR_96PA | #4ATR 機械保護動作 | ATR | E04//4ATR/96PA |  |  |  | CDC | 239 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 51ZA | [17 empty] | 3-03-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#4ATR_51ZA | #4ATR 51Z(21+50,59-2,51Z) | ATR | E04//4ATR/51ZA |  |  |  | CDC | 240 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 59A | [17 empty] | 3-03-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#4ATR_59A | #4ATR 59RY | ATR | E04//4ATR/59A |  |  |  | CDC | 241 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 1_87UL1 | [17 empty] | 3-31-13 |  | 3-77 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_87UL1 | #4ATR 第一套 87RY U/L | OTHER | E04//4ATR/1_87UL1 |  |  |  | CDC | 242 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 1_87UL2 | [17 empty] | 3-31-14 |  | 3-78 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_87UL2 | #4ATR 第二套 87RY U/L | OTHER | E04//4ATR/1_87UL2 |  |  |  | CDC | 243 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 96D | [17 empty] | 3-32-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_96D | #4ATR 96D RY | ATR | E04//4ATR/96D |  |  |  | CDC | 244 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 96P | [17 empty] | 3-32-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_96P | #4ATR 96P RY | ATR | E04//4ATR/96P |  |  |  | CDC | 245 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 63Q | [17 empty] | 3-32-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_63Q | #4ATR 63Q RY | ATR | E04//4ATR/63Q |  |  |  | CDC | 246 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 96B1 | [17 empty] | 3-32-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_96B1 | #4ATR 96B1 RY | ATR | E04//4ATR/96B1 |  |  |  | CDC | 247 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 96B2 | [17 empty] | 3-32-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_96B2 | #4ATR 96B2 RY | ATR | E04//4ATR/96B2 |  |  |  | CDC | 248 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | TRA | [17 empty] | 3-32-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_TRA | #4ATR 重故障 | ATR | E04//4ATR/TRA |  |  |  | CDC | 249 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | TRF | [17 empty] | 3-32-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_TRF | #4ATR 輕故障 | ATR | E04//4ATR/TRF |  |  |  | CDC | 250 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | SupLocal | [17 empty] | 3-31-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_S/L | #4ATR OLTC S/L | ATR | E04//4ATR/SupLocal |  |  |  | CDC | 251 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | A_M | [17 empty] | 3-32-00 |  | 3-5A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_A/M | #4ATR OLTC A/M | ATR | E04/345/3840/Tap Chan |  |  |  | CDC | 252 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | M/F/I | [17 empty] | 4-33-08 | 4-33-09 | 3-5B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_M/F/I | #4ATR M/F/I | ATR | E04//4ATR/M_F_I |  |  |  | CDC | 253 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | ABS1 | 3841 | [16 empty] | 4-30-00 | 4-30-01 | 3-39 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3841_ABS | 3841(#4ATR) ABS | ATR | E04/345/3840/ABS1 |  |  |  | CDC | 254 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3840 | #4ATR(3840) |  | ABS2 | 3842 | [16 empty] | 4-30-02 | 4-30-03 | 3-3A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3842_ABS | 3842(#4ATR) ABS | ATR | E04/345/3840/ABS2 |  |  |  | CDC | 255 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | ABS1 | 1681 | [16 empty] | 4-32-12 | 4-32-13 | 3-4E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1681_ABS | 1681(#4ATR) ABS | ATR | E04/161/1680/ABS1 |  |  |  | CDC | 256 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1680 | #4ATR(1680) |  | ABS2 | 1682 | [16 empty] | 4-32-14 | 4-32-15 | 3-4F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1682_ABS | 1682(#4ATR) ABS | ATR | E04/161/1680/ABS2 |  |  |  | CDC | 257 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | CB | [17 empty] | 3-00-02 |  | 3-03 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1780_CB | 1780(#6ATR) CB | ATR | E04/161/1780/CB |  |  |  | CDC | 258 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 87A1 | [17 empty] | 3-00-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#6ATR_87A1 | #6ATR 第一組 87RY | ATR | E04//6ATR/87A1 |  |  |  | CDC | 259 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 87A2 | [17 empty] | 3-00-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#6ATR_87A2 | #6ATR 第二組 87RY | ATR | E04//6ATR/87A2 |  |  |  | CDC | 260 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 96PA | [17 empty] | 3-00-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#6ATR_96PA | #6ATR 機械保護動作 | ATR | E04//6ATR/96PA |  |  |  | CDC | 261 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 51ZA | [17 empty] | 3-00-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#6ATR_51ZA | #6ATR 51Z(21+50,59-2,51Z) | ATR | E04//6ATR/51ZA |  |  |  | CDC | 262 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 59A | [17 empty] | 3-00-07 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.#6ATR_59A | #6ATR 59RY | ATR | E04//6ATR/59A |  |  |  | CDC | 263 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 1_87UL1 | [17 empty] | 3-30-02 |  | 3-1C | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_87UL1 | #6ATR 第一套 87RY U/L | OTHER | E04//6ATR/1_87UL1 |  |  |  | CDC | 264 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 1_87UL2 | [17 empty] | 3-30-03 |  | 3-1D | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_87UL2 | #6ATR 第二套 87RY U/L | OTHER | E04//6ATR/1_87UL2 |  |  |  | CDC | 265 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 96D | [17 empty] | 3-30-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_96D | #6ATR 96D RY | ATR | E04//6ATR/96D |  |  |  | CDC | 266 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 96P | [17 empty] | 3-30-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_96P | #6ATR 96P RY | ATR | E04//6ATR/96P |  |  |  | CDC | 267 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 63Q | [17 empty] | 3-30-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_63Q | #6ATR 63Q RY | ATR | E04//6ATR/63Q |  |  |  | CDC | 268 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 96B1 | [17 empty] | 3-30-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_96B1 | #6ATR 96B1 RY | ATR | E04//6ATR/96B1 |  |  |  | CDC | 269 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 96B2 | [17 empty] | 3-30-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_96B2 | #6ATR 96B2 RY | ATR | E04//6ATR/96B2 |  |  |  | CDC | 270 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | TRA | [17 empty] | 3-30-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_TRA | #6ATR 重故障 | ATR | E04//6ATR/TRA |  |  |  | CDC | 271 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | TRF | [17 empty] | 3-30-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_TRF | #6ATR 輕故障 | ATR | E04//6ATR/TRF |  |  |  | CDC | 272 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | SupLocal | [17 empty] | 3-30-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_S/L | #6ATR OLTC S/L | ATR | E04//6ATR/SupLocal |  |  |  | CDC | 273 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | A_M | [17 empty] | 3-30-05 |  | 3-52 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_A/M | #6ATR OLTC A/M | ATR | E04/345/3730/Tap Chan |  |  |  | CDC | 274 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | M/F/I | [17 empty] | 4-33-04 | 4-33-05 | 3-53 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.#6ATR_M/F/I | #6ATR M/F/I | ATR | E04//6ATR/M_F_I |  |  |  | CDC | 275 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | DS1 | 3711 | [16 empty] | 3-3C-00 | 3-3C-01 | 3-20 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3711_DS | 3711(#6ATR) DS | ATR | E04/345/3710/DS1 |  |  |  | CDC | 276 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | DS2 | 3712 | [16 empty] | 3-3C-02 | 3-3C-03 | 3-21 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3712_DS | 3712(#6ATR) DS | ATR | E04/345/3710/DS2 |  |  |  | CDC | 277 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | ABS1 | 1781 | [16 empty] | 4-32-00 | 4-32-01 | 3-48 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1781_ABS | 1781(#6ATR) ABS | ATR | E04/161/1780/ABS1 |  |  |  | CDC | 278 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1780 | #6ATR(1780) |  | ABS2 | 1782 | [16 empty] | 4-32-02 | 4-32-03 | 3-49 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1782_ABS | 1782(#6ATR) ABS | ATR | E04/161/1780/ABS2 |  |  |  | CDC | 279 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 0 |  | 490 | #2SSTR(490) |  | CB | [17 empty] | 3-14-05 |  | 3-0F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.490_CB | 490(#2SSTR) CB | OTHER | E04/22/490/CB |  |  |  | CDC | 280 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 3-14-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#2SSTR_51A | #2SSTR 51RY | OTHER | E04/22/490/PHA |  |  |  | CDC | 281 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 360 | #4SSTR(360) |  | CB | [17 empty] | 3-14-00 |  | 3-04 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.360_CB | 360(#4SSTR) CB | OTHER | E04/22/360/CB |  |  |  | CDC | 282 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 4SSTR | #4SSTR |  | 51A | [17 empty] | 3-14-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#4SSTR_51A | #4SSTR 51RY | OTHER | E04/22/360/PHA |  |  |  | CDC | 283 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1613BUS | #3BUS |  | VUA | [17 empty] | 1-30-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS | E04/161/3BUS/BUS_VUA |  |  |  | CDC | 284 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1613BUS | #3BUS |  | 87A | [17 empty] | 1-04-03 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.161#3BUS_87A | 161KV #3BUS 87RY | BUS | E04/161/3BUS/87A |  |  |  | CDC | 285 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1613BUS | #3BUS |  | 87UL | [17 empty] | 1-30-02 |  | 1-3E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER | E04/161/3BUS/87UL |  |  |  | CDC | 286 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 161 | 161kV | 1614BUS | #4BUS |  | VUA | [17 empty] | 1-30-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS | E04/161/4BUS/BUS_VUA |  |  |  | CDC | 287 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1614BUS | #4BUS |  | 87A | [17 empty] | 1-04-04 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.161#4BUS_87A | 161KV #4BUS 87RY | BUS | E04/161/4BUS/87A |  |  |  | CDC | 288 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1614BUS | #4BUS |  | 87UL | [17 empty] | 1-30-03 |  | 1-3F | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER | E04/161/4BUS/87UL |  |  |  | CDC | 289 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3453B | #3BUS |  | 87A1 | [17 empty] | 3-04-03 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#3B_87A1 | 345KV #3BUS 第一組 87RY | BUS | E04/345/3BUS/87A1 |  |  |  | CDC | 290 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3453B | #3BUS |  | 87A2 | [17 empty] | 3-04-04 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#3B_87A2 | 345KV #3BUS 第二組 87RY | BUS | E04/345/3BUS/87A2 |  |  |  | CDC | 291 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3453B | #3BUS |  | 1_87UL1 | [17 empty] | 3-32-13 |  | 3-73 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#3B_87UL1 | 345KV #3BUS 第一組 87RY U/L | OTHER | E04/345/3BUS/1_87UL1 |  |  |  | CDC | 292 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3453B | #3BUS |  | 1_87UL2 | [17 empty] | 3-32-14 |  | 3-75 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#3B_87UL2 | 345KV #3BUS 第二組 87RY U/L | OTHER | E04/345/3BUS/1_87UL2 |  |  |  | CDC | 293 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3454B | #4BUS |  | 87A1 | [17 empty] | 3-04-05 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#4B_87A1 | 345KV #4BUS 第一組 87RY | BUS | E04/345/4BUS/87A1 |  |  |  | CDC | 294 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3454B | #4BUS |  | 87A2 | [17 empty] | 3-04-06 | [7 empty] | 345KV_S | [8 empty] | 龍崎ES.345#4B_87A2 | 345KV #4BUS 第二組 87RY | BUS | E04/345/4BUS/87A2 |  |  |  | CDC | 295 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3454B | #4BUS |  | 1_87UL1 | [17 empty] | 3-32-15 |  | 3-74 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#4B_87UL1 | 345KV #4BUS 第一組 87RY U/L | OTHER | E04/345/4BUS/1_87UL1 |  |  |  | CDC | 296 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 345 | 345kV | 3454B | #4BUS |  | 1_87UL2 | [17 empty] | 3-33-00 |  | 3-76 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.345#4B_87UL2 | 345KV #4BUS 第二組 87RY U/L | OTHER | E04/345/4BUS/1_87UL2 |  |  |  | CDC | 297 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 530 | 530 |  | CB | [17 empty] | 3-14-02 |  | 3-0E | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.530_CB | 530 CB | OTHER | E04/33/530/CB |  |  |  | CDC | 298 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 530 | 530 |  | 87A | [17 empty] | 3-14-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.530_87A | 530 87RY | OTHER | E04/33/530/87A |  |  |  | CDC | 299 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 530 | 530 |  | PHA | [17 empty] | 3-14-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.530_PHA | 530 相間RY | OTHER | E04/33/530/PHA |  |  |  | CDC | 300 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 530 | 530 |  | ABS1 | 531 | [16 empty] | 4-32-08 | 4-32-09 | 3-4C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.531_ABS | 531 ABS | OTHER | E04/33/530/ABS1 |  |  |  | CDC | 301 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 0 |  | 540 | 540 |  | CB | [17 empty] | 3-14-07 |  | 3-14 | [5 empty] | 345KV_S | [8 empty] | 龍崎ES.540_CB | 540 CB | OTHER | E04/33/540/CB |  |  |  | CDC | 302 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 0 |  | 540 | 540 |  | 87A | [17 empty] | 3-15-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.540_87A | 540 87RY | OTHER | E04/33/540/87A |  |  |  | CDC | 303 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 540 | 540 |  | PHA | [17 empty] | 3-15-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.540_PHA | 540 相間RY | OTHER | E04/33/540/PHA |  |  |  | CDC | 304 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 540 | 540 |  | ABS1 | 541 | [16 empty] | 4-33-00 | 4-33-01 | 3-50 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.541_ABS | 541 ABS | OTHER | E04/33/540/ABS1 |  |  |  | CDC | 305 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 0 |  |  |  |  | Fire1 | [17 empty] | 3-38-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.火災警報(1) | 火災警報(1) | OTHER | E04/0/StaDev/Fire1 |  |  |  | CDC | 306 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  |  |  |  | CHG2 | [17 empty] | 3-39-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | E04/0/StaDev/CHG2 |  |  |  | CDC | 307 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  |  |  |  | CommACF | [17 empty] | 3-38-15 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.通訊設備AC故障 | 通訊設備AC故障 | OTHER | E04/0/StaDev/CommACF |  |  |  | CDC | 308 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | SR96B1 | [17 empty] | 3-31-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_SR96B1 | #3ATR 33KV 電抗器96B1 RY | OTHER | E04/33/3SHR/96B1 |  |  |  | CDC | 309 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | SR96B2 | [17 empty] | 3-31-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_SR96B2 | #3ATR 33KV 電抗器96B2 RY | OTHER | E04/33/3SHR/96B2 |  |  |  | CDC | 310 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | SR96D | [17 empty] | 3-31-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_SR96D | #3ATR 33KV 電抗器96D RY | OTHER | E04/33/3SHR/96D |  |  |  | CDC | 311 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | SR96P | [17 empty] | 3-31-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#3ATR_SR96P | #3ATR 33KV 電抗器96P RY | OTHER | E04/33/3SHR/96P |  |  |  | CDC | 312 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | SR96B1 | [17 empty] | 3-32-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_SR96B1 | #4ATR 33KV 電抗器96B1 RY | OTHER | E04/33/4SHR/96B1 |  |  |  | CDC | 313 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | SR96B2 | [17 empty] | 3-32-09 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_SR96B2 | #4ATR 33KV 電抗器96B2 RY | OTHER | E04/33/4SHR/96B2 |  |  |  | CDC | 314 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | SR96D | [17 empty] | 3-32-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_SR96D | #4ATR 33KV 電抗器96D RY | OTHER | E04/33/4SHR/96D |  |  |  | CDC | 315 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | SR96P | [17 empty] | 3-32-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.#4ATR_SR96P | #4ATR 33KV 電抗器96P RY | OTHER | E04/33/4SHR/96P |  |  |  | CDC | 316 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1600TIE | 1600 |  | 50SA | [17 empty] | 1-32-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1600TIE_50SA | 161KV TIE(1600) 50RY 測試/正常 | OTHER | E04/161/1600/50SA |  |  |  | CDC | 317 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | 25PFA | [17 empty] | 1-14-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_25PFA | 161KV(S)同步電驛25PFA | OTHER | E04/161/ComPoint/25PFA |  |  |  | CDC | 318 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | 25TA | [17 empty] | 1-14-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_25TA | 161KV(S)同步電驛25TA | OTHER | E04/161/ComPoint/25TA |  |  |  | CDC | 319 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | S |  | ABS_89A | [17 empty] | 1-33-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_89A | 161KV(S)ABS NFB 跳脫警報 | OTHER | E04/161/ComPoint/ABS_89A |  |  |  | CDC | 320 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | BFA | [17 empty] | 1-04-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_BFA | 161KV(S)斷路器失靈(BF)RY | OTHER | E04/161/ComPoint/BFA |  |  |  | CDC | 321 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | S |  | BFS | [17 empty] | 1-30-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_BFS | 161KV(S)斷路器失靈RY U/L | OTHER | E04/161/ComPoint/BFS |  |  |  | CDC | 322 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | CBA | [17 empty] | 3-33-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_CBA | 161KV(S)斷路器重故障 | OTHER |  |  |  |  | CDC | 323 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | COMT | [17 empty] | 3-33-07 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_COMT | 161KV(S)空壓機警報 | OTHER |  |  |  |  | CDC | 324 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | OSCA | [17 empty] | 1-04-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_OSCA | 161KV(S)示波器起動 | OTHER | E04/161/ComPoint/OSCA |  |  |  | CDC | 325 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | _S |  | OSCF | [17 empty] | 1-33-06 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_OSCF | 161KV(S)示波器故障,電源跳脫 | OTHER | E04/161/ComPoint/OSCF |  |  |  | CDC | 326 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | _S | S |  | RCA | [17 empty] | 1-04-07 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_S_RCA | 161KV(S)LINE 79RY(復閉)動作 | OTHER | E04/161/ComPoint/RCA |  |  |  | CDC | 327 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1640 | 岡山嘉峰線(1640) |  | RYFA | [17 empty] | 1-31-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1640_RYFA | 岡山嘉峰線(1640)數位電驛故障 | OTHER | E04/161/1640/RYFA |  |  |  | CDC | 328 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1710 | 龍崎路園線(1710) |  | 87CFA | [17 empty] | 1-31-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1710_87CFA | 龍崎路園線(1710)87RY通訊故障 | OTHER | E04/161/1710/87CFA |  |  |  | CDC | 329 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1710 | 龍崎路園線(1710) |  | RYFA | [17 empty] | 1-31-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1710_RYFA | 龍崎路園線(1710)數位電驛故障 | OTHER | E04/161/1710/RYFA |  |  |  | CDC | 330 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1720 | 龍崎岡山二路(1720) |  | 87CFA | [17 empty] | 1-31-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1720_87CFA | 龍崎岡山二路(1720)87RY通訊故障 | OTHER | E04/161/1720/87CFA |  |  |  | CDC | 331 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1720 | 龍崎岡山二路(1720) |  | RYFA | [17 empty] | 1-31-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1720_RYFA | 龍崎岡山二路(1720)數位電驛故障 | OTHER | E04/161/1720/RYFA |  |  |  | CDC | 332 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1730 | 龍崎岡山三路(1730) |  | 87CFA | [17 empty] | 1-31-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1730_87CFA | 龍崎岡山三路(1730)87RY通訊故障 | OTHER | E04/161/1730/87CFA |  |  |  | CDC | 333 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1730 | 龍崎岡山三路(1730) |  | RYFA | [17 empty] | 1-31-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1730_RYFA | 龍崎岡山三路(1730)數位電驛故障 | OTHER | E04/161/1730/RYFA |  |  |  | CDC | 334 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | 25PFA | [17 empty] | 3-15-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_25PFA | 345KV(S)同步電驛25PFA | OTHER | E04/345/ComPoint/25PFA |  |  |  | CDC | 335 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | 25TA | [17 empty] | 3-15-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_25TA | 345KV(S)同步電驛25TA | OTHER | E04/345/ComPoint/25TA |  |  |  | CDC | 336 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | S |  | ABS_89A | [17 empty] | 3-39-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_89A | 345KV(S)ABS NFB 跳脫警報 | OTHER | E04/345/ComPoint/ABS_89A |  |  |  | CDC | 337 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | BFA | [17 empty] | 3-04-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_BFA | 345KV(S)斷路器失靈(BF)警報 | OTHER | E04/345/ComPoint/BFA |  |  |  | CDC | 338 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | S |  | BFS | [17 empty] | 3-33-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_BFS | 345KV(S)斷路器失靈RY U/L | OTHER | E04/345/ComPoint/BFS |  |  |  | CDC | 339 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | CBA | [17 empty] | 3-33-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_CBA | 345KV(S)斷路器重故障 | OTHER | E04/345/ComPoint/CBA |  |  |  | CDC | 340 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | CBF | [17 empty] | 3-33-03 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_CBF | 345KV(S)斷路器輕故障 | OTHER | E04/345/ComPoint/CBF |  |  |  | CDC | 341 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | COMT | [17 empty] | 3-33-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_COMT | 345KV(S)空壓機警報 | OTHER | E04/345/ComPoint/COMT |  |  |  | CDC | 342 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | OSCA | [17 empty] | 3-05-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_OSCA | 345KV(S)示波器起動 | OTHER | E04/345/ComPoint/OSCA |  |  |  | CDC | 343 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | OSCF | [17 empty] | 3-38-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_OSCF | 345KV(S)示波器故障,電源跳脫 | OTHER | E04/345/ComPoint/OSCF |  |  |  | CDC | 344 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | S |  | RCA | [17 empty] | 3-05-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_RCA | 345KV(S)LINE 79RY(復閉)動作 | OTHER | E04/345/ComPoint/RCA |  |  |  | CDC | 345 | GENERICDIPoint | ES004_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | _S | _S |  | 洩油池 | [17 empty] | 3-37-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_S_洩油池 | 345KV(S)洩油池水位警報 | OTHER | E04/345/ComPoint/OilLeak |  |  |  | CDC | 346 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3710 | #6ATR(3710) |  | E2 | 3712E | [16 empty] | 3-3C-04 | 3-3C-05 | 3-22 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3712E_ES | 3712E(#6TR) ES | OTHER | E04/345/3710/E2 |  |  |  | CDC | 347 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 0 |  | 3740 | 天輪山線(3740) |  | 85CFA | [17 empty] | 3-34-08 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_85CFA | 天輪山線(3740) 85RY通訊故障 | OTHER | E04/345/3740/85CFA |  |  |  | CDC | 348 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3740 | 天輪山線(3740) |  | 87CFA | [17 empty] | 3-34-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3740_87CFA | 天輪山線(3740) 87RY通訊故障 | OTHER | E04/345/3740/87CFA |  |  |  | CDC | 349 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3740 | 天輪山線(3740) |  | E1 | 3741E | [16 empty] | 4-33-10 | 4-33-11 | [6 empty] | CDCS_S | [8 empty] | 龍崎ES.3741E_ES | 3741E ES | OTHER | E04/345/3740/E1 |  |  |  | CDC | 350 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 0 |  | 3760 | 嘉民紅線(3760) |  | 85CFA | [17 empty] | 3-34-13 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_85CFA | 嘉民紅線(3760) 85RY通訊故障 | OTHER | E04/345/3760/85CFA |  |  |  | CDC | 351 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3760 | 嘉民紅線(3760) |  | 87CFA | [17 empty] | 3-34-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3760_87CFA | 嘉民紅線(3760) 87RY通訊故障 | OTHER | E04/345/3760/87CFA |  |  |  | CDC | 352 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3770 | 北南臨時線(3770) |  | 85CFA | [17 empty] | 3-35-02 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_85CFA | 北南臨時線(3770) 85RY通訊故障 | OTHER | E04/345/3770/85CFA |  |  |  | CDC | 353 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3770 | 北南臨時線(3770) |  | 87CFA | [17 empty] | 3-35-00 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3770_87CFA | 北南臨時線(3770) 87RY通訊故障 | OTHER | E04/345/3770/87CFA |  |  |  | CDC | 354 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3790 | 仁武山線(3790) |  | 85CFA | [17 empty] | 3-35-07 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_85CFA | 仁武山線(3790) 85RY通訊故障 | OTHER | E04/345/3790/85CFA |  |  |  | CDC | 355 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3790 | 仁武山線(3790) |  | 87CFA | [17 empty] | 3-35-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3790_87CFA | 仁武山線(3790) 87RY通訊故障 | OTHER | E04/345/3790/87CFA |  |  |  | CDC | 356 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3860 | 興達三路(3860) |  | 85CFA | [17 empty] | 3-35-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_85CFA | 興達三路(3860) 85RY通訊故障 | OTHER | E04/345/3860/85CFA |  |  |  | CDC | 357 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3860 | 興達三路(3860) |  | 87CFA | [17 empty] | 3-35-10 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3860_87CFA | 興達三路(3860) 87RY通訊故障 | OTHER | E04/345/3860/87CFA |  |  |  | CDC | 358 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3870 | 路北白線(3870) |  | 85CFA | [17 empty] | 3-36-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_85CFA | 路北白線(3870) 85RY通訊故障 | OTHER | E04/345/3870/85CFA |  |  |  | CDC | 359 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3870 | 路北白線(3870) |  | 87CFA | [17 empty] | 3-35-15 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3870_87CFA | 路北白線(3870) 87RY通訊故障 | OTHER | E04/345/3870/87CFA |  |  |  | CDC | 360 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3890 | 仁武海線(3890) |  | 85CFA | [17 empty] | 3-36-06 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_85CFA | 仁武海線(3890) 85RY通訊故障 | OTHER | E04/345/3890/85CFA |  |  |  | CDC | 361 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3890 | 仁武海線(3890) |  | 87CFA | [17 empty] | 3-36-04 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.3890_87CFA | 仁武海線(3890) 87RY通訊故障 | OTHER | E04/345/3890/87CFA |  |  |  | CDC | 362 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 400 | 404(400) |  | ABS4 | 404 | [16 empty] | 4-33-02 | 4-33-03 | 3-51 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.404_ABS | 404ABS | OTHER | E04/33/400/ABS1 |  |  |  | CDC | 363 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 0 |  | 490 | #2SSTR(490) |  | ABS1 | 491 | [16 empty] | 4-32-10 | 4-32-11 | 3-4D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.491_ABS | 491ABS | OTHER | E04/22/490/ABS1 |  |  |  | CDC | 364 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 0 |  | RTU_S_L(S | S |  | 1) | [17 empty] | 3-30-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.RTU_S/L(S_1) | 345KV(S)RTU S/L | OTHER | E04/345/StaDev/RTU_R_L |  |  |  | CDC | 365 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E04 | 龍崎ES | 0 |  | RTU_S_L(S | S |  | 2) | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.RTU_S/L(S_2) | 161KV(S)RTU S/L | OTHER | E04/161/StaDev/RTU_R_L |  |  |  | CDC | 366 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E04 | 龍崎ES | 0 |  |  |  |  | STUVA34 | [17 empty] | 3-38-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.STUVA34 | #34所內電源欠壓 | OTHER | E04/0/StaDev/7A5Other |  |  |  | CDC | 367 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | TEST_CB(S | S(TEST_CB(S) |  | 1) | [17 empty] | 3-30-00 |  | 3-00 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.TEST_CB(S_1) | 345KV(S)TEST CB | OTHER | E04/345/StaDev/Test_CB1 |  |  |  | CDC | 368 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 0 |  | TEST_CB(S | S(TEST_CB(S) |  | 2) | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.TEST_CB(S_2) | 161KV(S)TEST CB | OTHER | E04/161/StaDev/Test_CB2 |  |  |  | CDC | 369 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E04 | 龍崎ES | 0 |  | 充電機故障 | 充電機故障 |  | S | [17 empty] | 1-33-02 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.充電機故障_S | #4,#5,#6直流充電機故障 | OTHER | E04/0/StaDev/6A5Other |  |  |  | CDC | 370 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  |  |  |  | 外燈(1) | [17 empty] | 3-39-02 |  | 3-6B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.外燈(1) | 主變三次側外燈(1) | OTHER | E04/0/StaDev/Lights1 |  |  |  | CDC | 371 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 外燈(2) | [17 empty] | 3-39-03 |  | 3-6C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.外燈(2) | 主變三次側外燈(2) | OTHER | E04/0/StaDev/Lights2 |  |  |  | CDC | 372 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 外燈(3) | [17 empty] | 3-39-04 |  | 3-6D | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.外燈(3) | 屋外燈(1) | OTHER | E04/0/StaDev/Lights3 |  |  |  | CDC | 373 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 外燈(4) | [17 empty] | 3-39-05 |  | 3-6E | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.外燈(4) | 屋外燈(2) | OTHER | E04/0/StaDev/Lights4 |  |  |  | CDC | 374 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 外燈(5) | [17 empty] | 3-39-08 |  | 3-71 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.外燈(5) | 北側外燈 | OTHER | E04/0/StaDev/Lights5 |  |  |  | CDC | 375 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 外燈(6) | [17 empty] | 3-39-09 |  | 3-72 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.外燈(6) | 東開關場外燈 | OTHER | E04/0/StaDev/Lights6 |  |  |  | CDC | 376 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | ACB3 | [17 empty] | 3-38-00 |  | 3-68 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.所內電源ACB3 | 所內電源ACB3 | OTHER | E04/0/StaDev/ACB3 |  |  |  | CDC | 377 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E04 | 龍崎ES | 0 |  |  |  |  | ACB4 | [17 empty] | 3-38-02 |  | 3-6A | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.所內電源ACB4 | 所內電源ACB4 | OTHER | E04/0/StaDev/ACB4 |  |  |  | CDC | 378 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E04 | 龍崎ES | 0 |  | 直流電源DCA | 直流電源DCA |  | S | [17 empty] | 1-33-04 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.直流電源DCA_S | #3,#4直流電源故障警報 | OTHER | E04/0/StaDev/DCA |  |  |  | CDC | 379 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 直流電源DCE | 直流電源DCE |  | S | [17 empty] | 1-33-03 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.直流電源DCE_S | #3,#4直流電源接地故障警報 | OTHER | E04/0/StaDev/DCE |  |  |  | CDC | 380 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  |  |  |  | 信號燈(1) | [17 empty] | 3-39-06 |  | 3-6F | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.信號燈(1) | 信號燈(1) | OTHER | E04/0/StaDev/Lights7 |  |  |  | CDC | 381 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 信號燈(2) | [17 empty] | 3-39-07 |  | 3-70 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.信號燈(2) | 信號燈(2) | OTHER | E04/0/StaDev/Lights8 |  |  |  | CDC | 382 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 3-38-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.通信機房溫度 | 通信機房溫度警報 | OTHER | E04/0/StaDev/9A5Other |  |  |  | CDC | 383 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 所內電源3,4,TIE | 所內電源#3,#4,TIE |  | 所內電源ACB34A | [17 empty] | 3-39-01 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.所內電源ACB34A | 所內電源#3,#4,TIE ACB故障 | OTHER | E04/0/StaDev/3A5Other |  |  |  | CDC | 384 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | 3750 | 3750 |  | ABS1 | 3751 | [16 empty] | 3-3D-04 | 3-3D-05 | 3-28 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3751_ABS | 3751 ABS | LINE345 | E04/345/3750/ABS1 |  |  |  | CDC | 385 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3750 | 3750 |  | ABS2 | 3752 | [16 empty] | 3-3D-06 | 3-3D-07 | 3-29 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3752_ABS | 3752 ABS | LINE345 | E04/345/3750/ABS2 |  |  |  | CDC | 386 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3780 | 3780 |  | ABS1 | 3781 | [16 empty] | 3-3E-04 | 3-3E-05 | 3-30 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3781_ABS | 3781 ABS | LINE345 | E04/345/3780/ABS1 |  |  |  | CDC | 387 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3780 | 3780 |  | ABS2 | 3782 | [16 empty] | 3-3E-06 | 3-3E-07 | 3-31 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3782_ABS | 3782 ABS | LINE345 | E04/345/3780/ABS2 |  |  |  | CDC | 388 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3850 | 3850 |  | ABS1 | 3851 | [16 empty] | 4-30-04 | 4-30-05 | 3-3B | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3851_ABS | 3851 ABS | LINE345 | E04/345/3850/ABS1 |  |  |  | CDC | 389 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3850 | 3850 |  | ABS2 | 3852 | [16 empty] | 4-30-06 | 4-30-07 | 3-3C | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3852_ABS | 3852 ABS | LINE345 | E04/345/3850/ABS2 |  |  |  | CDC | 390 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3880 | 3880 |  | ABS1 | 3881 | [16 empty] | 4-31-04 | 4-31-05 | 3-43 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3881_ABS | 3881 ABS | LINE345 | E04/345/3880/ABS1 |  |  |  | CDC | 391 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 345 | 345kV | 3880 | 3880 |  | ABS2 | 3882 | [16 empty] | 4-31-06 | 4-31-07 | 3-44 | [5 empty] | CDCS_S | [8 empty] | 龍崎ES.3882_ABS | 3882 ABS | LINE345 | E04/345/3880/ABS2 |  |  |  | CDC | 392 | GENERICDIPoint | ES004_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 0 |  |  |  |  | STUVA12 | [17 empty] | 1-33-01 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.STUVA12 | #12所內電源欠壓 | OTHER | E04/0/StaDev/5A5Other |  |  |  | CDC | 393 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 所內電源1,2,TIE | 所內電源#1,#2,TIE |  | 所內電源ACB12A | [17 empty] | 1-33-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.所內電源ACB12A | 所內電源#1,#2,TIE ACB故障 | OTHER | E04/0/StaDev/4A5Other |  |  |  | CDC | 394 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | PHA | [17 empty] | 1-00-05 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1630_PHA | 龍崎聯錏線(1630) 相間RY | LINE161 | E04/161/1630/PHA |  |  |  | CDC | 395 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | GDA | [17 empty] | 1-00-06 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1630_GDA | 龍崎聯錏線(1630) 接地RY | LINE161 | E04/161/1630/GDA |  |  |  | CDC | 396 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | CB | [17 empty] | 1-00-03 |  | 1-01 | [5 empty] | 161KV_S | [8 empty] | 龍崎ES.1630_CB | 1630(龍崎聯錏線) CB | LINE161 | E04/161/1630/CB |  |  |  | CDC | 397 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | ABS1 | 1631 | [16 empty] | 1-36-12 | 1-36-13 | 1-10 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1631_ABS | 1631(龍崎聯錏線) ABS | LINE161 | E04/161/1630/ABS1 |  |  |  | CDC | 398 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | ABS2 | 1632 | [16 empty] | 1-36-14 | 1-36-15 | 1-11 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1632_ABS | 1632(龍崎聯錏線) ABS | LINE161 | E04/161/1630/ABS2 |  |  |  | CDC | 399 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | ABS3 | 1633 | [16 empty] | 1-37-00 | 1-37-01 | 1-12 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1633_ABS | 1633(龍崎聯錏線) ABS | LINE161 | E04/161/1630/ABS3 |  |  |  | CDC | 400 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E04 | 龍崎ES | 161 | 161kV | 1630 | 龍崎聯錏線(1630) |  | E3 | 1633E | [16 empty] | 1-37-02 | 1-37-03 | 1-13 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1633E_ES | 1633E(龍崎聯錏線) ES | LINE161 | E04/161/1630/E3 |  |  |  | CDC | 401 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E04 | 龍崎ES | 0 |  | 1630 | 龍崎聯錏線(1630) |  | DLPA | [17 empty] | 1-30-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1630_DLPA | 龍崎聯錏線(1630)DLP電源故障 | OTHER | E04/161/1630/8A5Other |  |  |  | CDC | 402 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 1630 | 龍崎聯錏線(1630) |  | RYFA | [17 empty] | 1-30-13 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1630_RYFA | 龍崎聯錏線(1630)數位電驛故障 | OTHER | E04/161/1630/RYFA |  |  |  | CDC | 403 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 161_SBUS | #3,4BUS |  | 87CTFA | [17 empty] | 1-32-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161_SBUS_CTFA | 161KV#3,4BUS 87RYCT迴路故障 | OTHER | E04/161/ComPoint/87CTFA |  |  |  | CDC | 404 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 161_SBUS | #3,4BUS |  | RYFA | [17 empty] | 1-32-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161_SBUS_RYFA | 161KV#3,4BUS 87RY數位電驛故障 | OTHER | E04/161/ComPoint/BUS_RYFA |  |  |  | CDC | 405 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | ACB | 所內電源ACB |  | TIE2 | [17 empty] | 3-38-01 |  | 3-69 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.ACB_TIE2 | 所內電源ACB TIE2 | OTHER | E04/0/StaDev/ACBT2 |  |  |  | CDC | 406 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E04 | 龍崎ES | 345 | 345kV | BUS | #3,4BUS |  | CTFA3 | [17 empty] | 3-33-12 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_CTFA3 | 345KV #3,4BUS 第一套CT回路故障 | OTHER | E04/345/ComPoint/87CTFA1 |  |  |  | CDC | 407 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | BUS | #3,4BUS |  | CTFA4 | [17 empty] | 3-33-14 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_CTFA4 | 345KV #3,4BUS 第二套CT回路故障 | OTHER | E04/345/ComPoint/87CTFA2 |  |  |  | CDC | 408 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | BUS | #3,4BUS |  | RYFA3 | [17 empty] | 3-33-11 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_RYFA3 | 345KV #3,4BUS 第一套數位RY故障 | OTHER | E04/345/ComPoint/1_RYFA |  |  |  | CDC | 409 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV | BUS | #3,4BUS |  | RYFA4 | [17 empty] | 3-33-13 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KVBUS_RYFA4 | 345KV #3,4BUS 第二套數位RY故障 | OTHER | E04/345/ComPoint/2_RYFA |  |  |  | CDC | 410 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | BVS | #4BUS |  | RY | [17 empty] | 1-32-10 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.BVS_RY | 161KV #4BUS GRZ100 RY U/L | OTHER | E04/161/StaDev/GRZ100 |  |  |  | CDC | 411 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | 87A | [17 empty] | 1-01-00 | [7 empty] | 161KV_S | [8 empty] | 龍崎ES.1640_87A | 岡山嘉峰線(1640) 87RY | LINE161 | E04/161/1640/85A |  |  |  | CDC | 412 | GENERICDIPoint | ES004_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV | 1640 | 岡山嘉峰線(1640) |  | 87UL | [17 empty] | 1-30-15 |  | 1-33 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.1640_87UL | 岡山嘉峰線(1640) 87RY U/L | LINE161 | E04/161/1640/85UL2 |  |  |  | CDC | 413 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 1640 | 岡山嘉峰線(1640) |  | 87CFA | [17 empty] | 1-31-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.1640_87CFA | 岡山嘉峰線(1640)87RY通訊故障 | OTHER | E04/161/1640/87CFA |  |  |  | CDC | 414 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 161 | 161kV |  |  |  | SBFRYFA | [17 empty] | 1-32-11 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.161KV_SBFRYFA | 161KV(S)斷路器失靈電驛故障 | OTHER | E04/161/ComPoint/RYFA |  |  |  | CDC | 415 | GENERICDIPoint | ES004_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 345 | 345kV |  |  |  | SBFRYFA | [17 empty] | 3-33-05 | [7 empty] | CDCS_S | [8 empty] | 龍崎ES.345KV_SBFRYFA | 345KV(S)斷路器失靈電驛故障 | OTHER | E04/345/ComPoint/RYFA |  |  |  | CDC | 416 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | 51Z_UL | [17 empty] | 3-36-13 |  | 3-1A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_51ZUL | #3ATR 51ZRY U/L | OTHER | E04//3ATR/51Z_UL |  |  |  | CDC | 417 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 3ATR_530 | #3ATR |  | 87UL | [17 empty] | 3-36-15 |  | 3-1B | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_530_87UL | #3ATR 電抗器(530) 87RY U/L | OTHER | E04/33/530/87UL |  |  |  | CDC | 418 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | ATR_86A | [17 empty] | 3-36-12 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_86A | #3ATR 86(51Z/87/96)RY | OTHER | E04//3ATR/ATR_86A |  |  |  | CDC | 419 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 3ATR | #3ATR |  | RYFA | [17 empty] | 3-36-14 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#3ATR_RYFA | #3ATR 數位電驛故障 | OTHER | E04//3ATR/RYFA |  |  |  | CDC | 420 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | 51Z_UL | [17 empty] | 3-37-01 |  | 3-1E | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_51ZUL | #6ATR 51ZRY U/L | OTHER | E04//6ATR/51Z_UL |  |  |  | CDC | 421 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | ATR_86A | [17 empty] | 3-37-00 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_86A | #6ATR 86(51Z/87/96)RY | OTHER | E04//6ATR/ATR_86A |  |  |  | CDC | 422 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 6ATR | #6ATR |  | RYFA | [17 empty] | 3-37-02 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#6ATR_RYFA | #6ATR 數位電驛故障 | OTHER | E04//6ATR/RYFA |  |  |  | CDC | 423 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | 51Z_UL | [17 empty] | 3-37-04 |  | 3-79 | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_51ZUL | #4ATR 51ZRY U/L | OTHER | E04//4ATR/51Z_UL |  |  |  | CDC | 424 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 4ATR_540 | #4ATR |  | 87UL | [17 empty] | 3-37-06 |  | 3-7A | [5 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_540_87UL | #4ATR 電抗器(540) 87RY U/L | OTHER | E04/33/540/87UL |  |  |  | CDC | 425 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | ATR_86A | [17 empty] | 3-37-03 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_86A | #4ATR 86(51Z/87/96)RY | OTHER | E04//4ATR/ATR_86A |  |  |  | CDC | 426 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E04 | 龍崎ES | 0 |  | 4ATR | #4ATR |  | RYFA | [17 empty] | 3-37-05 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.#4ATR_RYFA | #4ATR 數位電驛故障 | OTHER | E04//4ATR/RYFA |  |  |  | CDC | 427 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | _S | S |  | CBA | [17 empty] | 3-33-08 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.33KV_S_CBA | 33KV(S) CB重故障 | OTHER | E04/33/ComPoint/CBA |  |  |  | CDC | 428 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | _S | S |  | CBF | [17 empty] | 3-33-09 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.33KV_S_CBF | 33KV(S) CB輕故障 | OTHER | E04/33/ComPoint/CBF |  |  |  | CDC | 429 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E04 | 龍崎ES | 33 | 33kV | _S | S |  | COMT | [17 empty] | 3-33-10 | [7 empty] | ADCS_S | [8 empty] | 龍崎ES.33KV_S_COMT | 33KV(S) 空壓機運轉超時警報 | OTHER | E04/33/ComPoint/COMT |  |  |  | CDC | 430 | GENERICDIPoint | ES004_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo