## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E05 | 嘉民ES | 345 | 345kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0258 |  |  | 3-82 |  |  | 345KV | KV | 一號 BUS PT | kV_-450_450(-2000_2000) | aaa | B2/E05_C | [8 empty] | 嘉民ES.345KV#1BUS_KV | 345KV #1BUS KV | BUS |  |  |  |  | CDC | 2 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0259 |  |  | 3-83 |  |  | 345KV | KV | 二號 BUS PT | kV_-450_450(-2000_2000) | aab | B2/E05_C | [8 empty] | 嘉民ES.345KV#2BUS_KV | 345KV #2BUS KV | BUS |  |  |  |  | CDC | 3 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 4 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E05 | 嘉民ES | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0002 |  |  | 1-82 |  |  | 161KV | KV | 一號 BUS PD | kV_-210_210(-2000_2000) | aaa | B2/E05_A1 | [8 empty] | 嘉民ES.161KV#1BUS_KV | 161KV #1BUS KV | BUS |  |  |  |  | CDC | 4 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0003 |  |  | 1-83 |  |  | 161KV | KV | 二號 BUS PD | kV_-210_210(-2000_2000) | aab | B2/E05_A1 | [8 empty] | 嘉民ES.161KV#2BUS_KV | 161KV #2BUS KV | BUS |  |  |  |  | CDC | 5 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 3BUS | #3BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0030 |  |  | 1-9E |  |  | 161KV | KV | 三號 BUS PD | kV_-210_210(-2000_2000) | aba | B2/E05_A1 | [8 empty] | 嘉民ES.161KV#3BUS_KV | 161KV #3BUS KV | BUS |  |  |  |  | CDC | 6 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 4BUS | #4BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0031 |  |  | 1-9F |  |  | 161KV | KV | 四號 BUS PD | kV_-210_210(-2000_2000) | abb | B2/E05_A1 | [8 empty] | 嘉民ES.161KV#4BUS_KV | 161KV #4BUS KV | BUS |  |  |  |  | CDC | 7 | AI_161/69KV_BUS_PT |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 3510 | MW | 麥寮二路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3510_MW | 麥寮二路 MW | LINE345 |  |  |  |  | CDC | 8 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 3510 | MVAR | 麥寮二路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3510_MVAR | 麥寮二路 MVAR | LINE345 |  |  |  |  | CDC | 9 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 3510 | KV | 麥寮二路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3510LPD_KV | 麥寮二路(3510) LPD KV | LINE345 |  |  |  |  | CDC | 10 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | 3540 | MW | 麥寮一路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3540_MW | 麥寮一路 MW | LINE345 |  |  |  |  | CDC | 11 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | 3540 | MVAR | 麥寮一路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3540_MVAR | 麥寮一路 MVAR | LINE345 |  |  |  |  | CDC | 12 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | 3540 | KV | 麥寮一路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3540LPD_KV | 麥寮一路(3540) LPD KV | LINE345 |  |  |  |  | CDC | 13 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | 3570 | MW | 中寮二路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3570_MW | 中寮二路 MW | LINE345 |  |  |  |  | CDC | 14 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | 3570 | MVAR | 中寮二路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3570_MVAR | 中寮二路 MVAR | LINE345 |  |  |  |  | CDC | 15 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | 3570 | KV | 中寮二路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3570LPD_KV | 中寮二路(3570) LPD KV | LINE345 |  |  |  |  | CDC | 16 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | 3610 | MVAR | 中寮一路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3610_MW | 中寮一路 MW | LINE345 |  |  |  |  | CDC | 17 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | 3610 | MW | 中寮一路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3610_MVAR | 中寮一路 MVAR | LINE345 |  |  |  |  | CDC | 18 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | 3610 | KV | 中寮一路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3610LPD_KV | 中寮一路(3610) LPD KV | LINE345 |  |  |  |  | CDC | 19 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | 3640 | MW | 中寮三路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3640_MW | 中寮三路 MW | LINE345 |  |  |  |  | CDC | 20 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | 3640 | MVAR | 中寮三路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3640_MVAR | 中寮三路 MVAR | LINE345 |  |  |  |  | CDC | 21 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | 3640 | KV | 中寮三路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3640LPD_KV | 中寮三路(3640) LPD KV | LINE345 |  |  |  |  | CDC | 22 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0281 |  |  | 3-99 |  |  | 3710 | MW | 龍崎紅線 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3710_MW | 龍崎紅線 MW | LINE345 |  |  |  |  | CDC | 23 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0282 |  |  | 3-9A |  |  | 3710 | MVAR | 龍崎紅線 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3710_MVAR | 龍崎紅線 MVAR | LINE345 |  |  |  |  | CDC | 24 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0283 |  |  | 3-9B |  |  | 3710 | KV | 龍崎紅線 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3710LPD_KV | 龍崎紅線(3710) LPD KV | LINE345 |  |  |  |  | CDC | 25 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | 3770 | MW | 新南科一路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3770_MW | 新南科一路 MW | LINE345 |  |  |  |  | CDC | 26 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | 3770 | MVAR | 新南科一路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3770_MVAR | 新南科一路 MVAR | LINE345 |  |  |  |  | CDC | 27 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | 3770 | KV | 新南科一路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3770LPD_KV | 新南科一路(3770) LPD KV | LINE345 |  |  |  |  | CDC | 28 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0287 |  |  | 3-9F |  |  | 3810 | MW | 新南科二路 瓦 | MW_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3810_MW | 新南科二路 MW | LINE345 |  |  |  |  | CDC | 29 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0288 |  |  | 3-A0 |  |  | 3810 | MVAR | 新南科二路 乏 | MVAR_-2400_2400(-2000_2000) |  | B2/E05_C |  |  | 4000 | [5 empty] | 嘉民ES.3810_MVAR | 新南科二路 MVAR | LINE345 |  |  |  |  | CDC | 30 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0289 |  |  | 3-A1 |  |  | 3810 | KV | 新南科二路 LPD | kV_-450_450(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.3810LPD_KV | 新南科二路(3810) LPD KV | LINE345 |  |  |  |  | CDC | 31 | AI_LINE345 |  |  |  | AI | [5 empty] | LG_345 | 362.2 | 363.2 | 364.2 | 450 | 0.5 | 327.8 | 326.8 | 325.8 | 0 | 5 | 20 | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1550 | MW | 雲林山線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1550_MW | 雲林山線 MW | LINE161 |  |  |  |  | CDC | 32 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1550 | MVAR | 雲林山線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1550_MVAR | 雲林山線 MVAR | LINE161 |  |  |  |  | CDC | 33 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1550 | KV | 雲林山線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550LPD_KV | 雲林山線(1550) LPD KV | LINE161 |  |  |  |  | CDC | 34 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1560 | MW | 雲林海線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1560_MW | 雲林海線 MW | LINE161 |  |  |  |  | CDC | 35 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1560 | MVAR | 雲林海線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1560_MVAR | 雲林海線 MVAR | LINE161 |  |  |  |  | CDC | 36 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1560 | KV | 雲林海線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560LPD_KV | 雲林海線(1560) LPD KV | LINE161 |  |  |  |  | CDC | 37 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1710 | MW | 台嘉一路 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1710_MW | 台嘉一路 MW | LINE161 |  |  |  |  | CDC | 38 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1710 | MVAR | 台嘉一路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1710_MVAR | 台嘉一路 MVAR | LINE161 |  |  |  |  | CDC | 39 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1710 | KV | 台嘉一路 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710LPD_KV | 台嘉一路(1710) LPD KV | LINE161 |  |  |  |  | CDC | 40 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1720 | MW | 台嘉二路 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1720_MW | 台嘉二路 MW | LINE161 |  |  |  |  | CDC | 41 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1720 | MVAR | 台嘉二路 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1720_MVAR | 台嘉二路 MVAR | LINE161 |  |  |  |  | CDC | 42 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1720 | KV | 台嘉二路 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720LPD_KV | 台嘉二路(1720) LPD KV | LINE161 |  |  |  |  | CDC | 43 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1640 | MW | 北港北線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1640_MW | 北港北線 MW | LINE161 |  |  |  |  | CDC | 44 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 1640 | MVAR | 北港北線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1640_MVAR | 北港北線 MVAR | LINE161 |  |  |  |  | CDC | 45 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1640 | KV | 北港北線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640LPD_KV | 北港北線(1640) LPD KV | LINE161 |  |  |  |  | CDC | 46 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-95 |  |  | 1630 | MW | 北港南線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1630_MW | 北港南線 MW | LINE161 |  |  |  |  | CDC | 47 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-96 |  |  | 1630 | MVAR | 北港南線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1630_MVAR | 北港南線 MVAR | LINE161 |  |  |  |  | CDC | 48 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 1630 | KV | 北港南線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630LPD_KV | 北港南線(1630) LPD KV | LINE161 |  |  |  |  | CDC | 49 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 1580 | MW | 嘉民雲林線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1580_MW | 嘉民雲林線 MW | LINE161 |  |  |  |  | CDC | 50 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | 1580 | MVAR | 嘉民雲林線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1580_MVAR | 嘉民雲林線 MVAR | LINE161 |  |  |  |  | CDC | 51 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 1580 | KV | 嘉民雲林線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580LPD_KV | 嘉民雲林線(1580) LPD KV | LINE161 |  |  |  |  | CDC | 52 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | 1590 | MW | 斗工紅線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1590_MW | 斗工紅線 MW | LINE161 |  |  |  |  | CDC | 53 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 1590 | MVAR | 斗工紅線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1590_MVAR | 斗工紅線 MVAR | LINE161 |  |  |  |  | CDC | 54 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 1590 | KV | 斗工紅線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590LPD_KV | 斗工紅線(1590) LPD KV | LINE161 |  |  |  |  | CDC | 55 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 1730 | MW | 嘉惠一路 瓦 | MW_-1120_1120(-2000_2000) |  | B2/E05_A1 |  |  | 4000 | [5 empty] | 嘉民ES.1730_MW | 嘉惠一路 MW | LINE161 |  |  |  |  | CDC | 56 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 1730 | MVAR | 嘉惠一路 乏 | MVAR_-1120_1120(-2000_2000) |  | B2/E05_A1 |  |  | 4000 | [5 empty] | 嘉民ES.1730_MVAR | 嘉惠一路 MVAR | LINE161 |  |  |  |  | CDC | 57 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 1730 | KV | 嘉惠一路 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730LPD_KV | 嘉惠一路(1730) LPD KV | LINE161 |  |  |  |  | CDC | 58 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 1740 | MW | 嘉惠二路 瓦 | MW_-1120_1120(-2000_2000) |  | B2/E05_A1 |  |  | 4000 | [5 empty] | 嘉民ES.1740_MW | 嘉惠二路 MW | LINE161 |  |  |  |  | CDC | 59 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 1740 | MVAR | 嘉惠二路 乏 | MVAR_-1120_1120(-2000_2000) |  | B2/E05_A1 |  |  | 4000 | [5 empty] | 嘉民ES.1740_MVAR | 嘉惠二路 MVAR | LINE161 |  |  |  |  | CDC | 60 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 2.24 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 1740 | KV | 嘉惠二路 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740LPD_KV | 嘉惠二路(1740) LPD KV | LINE161 |  |  |  |  | CDC | 61 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 1610 | MW | 嘉義南線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1610_MW | 嘉義南線 MW | LINE161 |  |  |  |  | CDC | 62 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 1610 | MVAR | 嘉義南線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1610_MVAR | 嘉義南線 MVAR | LINE161 |  |  |  |  | CDC | 63 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 1610 | KV | 嘉義南線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610LPD_KV | 嘉義南線(1610) LPD KV | LINE161 |  |  |  |  | CDC | 64 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 1620 | MW | 嘉義北線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1620_MW | 嘉義北線 MW | LINE161 |  |  |  |  | CDC | 65 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 1620 | MVAR | 嘉義北線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1620_MVAR | 嘉義北線 MVAR | LINE161 |  |  |  |  | CDC | 66 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 1620 | KV | 嘉義北線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620LPD_KV | 嘉義北線(1620) LPD KV | LINE161 |  |  |  |  | CDC | 67 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 1540 | MW | 柳營海線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1540_MW | 柳營海線 MW | LINE161 |  |  |  |  | CDC | 68 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 1540 | MVAR | 柳營海線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1540_MVAR | 柳營海線 MVAR | LINE161 |  |  |  |  | CDC | 69 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 1540 | KV | 柳營海線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540LPD_KV | 柳營海線(1540) LPD KV | LINE161 |  |  |  |  | CDC | 70 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 1530 | MW | 柳營山線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1530_MW | 柳營山線 MW | LINE161 |  |  |  |  | CDC | 71 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 1530 | MVAR | 柳營山線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1530_MVAR | 柳營山線 MVAR | LINE161 |  |  |  |  | CDC | 72 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 1530 | KV | 柳營山線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530LPD_KV | 柳營山線(1530) LPD KV | LINE161 |  |  |  |  | CDC | 73 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 1520 | MW | 嘉義海線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1520_MW | 嘉義海線 MW | LINE161 |  |  |  |  | CDC | 74 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 1520 | MVAR | 嘉義海線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1520_MVAR | 嘉義海線 MVAR | LINE161 |  |  |  |  | CDC | 75 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 1520 | KV | 嘉義海線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520LPD_KV | 嘉義海線(1520) LPD KV | LINE161 |  |  |  |  | CDC | 76 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 1510 | MW | 嘉義山線 瓦 | MW_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1510_MW | 嘉義山線 MW | LINE161 |  |  |  |  | CDC | 77 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 1510 | MVAR | 嘉義山線 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1510_MVAR | 嘉義山線 MVAR | LINE161 |  |  |  |  | CDC | 78 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.28 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | V |  | Element | MvMoment | kV |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 1510 | KV | 嘉義山線 LPD | kV_-210_210(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510LPD_KV | 嘉義山線(1510) LPD KV | LINE161 |  |  |  |  | CDC | 79 | AI_LINE161 |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1500 | A | 1500 R相電流 | A_-2000_2000(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1500TIE_AMP | 1500TIE AMP | TIE |  |  |  |  | CDC | 80 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1700 | A | 1700 R相電流 | A_-4000_4000(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1700TIE_AMP | 1700TIE AMP | TIE |  |  |  |  | CDC | 81 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C40R4000 | 3800 | 4000 | 4001 | 4002 | 1.2 | -3800 | -4000 | -4001 | -4002 | 4 | 0.01 | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 4.000000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 1600 | A | 1600 R相電流 | A_-2000_2000(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1600TIE_AMP | 1600TIE AMP | TIE |  |  |  |  | CDC | 82 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 1800 | A | 1800 R相電流 | A_-4000_4000(-2000_2000) |  | B2/E05_A1 |  |  | 2000 | [5 empty] | 嘉民ES.1800TIE_AMP | 1800TIE AMP | TIE |  |  |  |  | CDC | 83 | AI_TIE161_69 |  |  |  | AI | [5 empty] | C40R4000 | 3800 | 4000 | 4001 | 4002 | 1.2 | -3800 | -4000 | -4001 | -4002 | 4 | 0.01 | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 4.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | #1 ATR | MW | #1ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#1ATR_MW | #1ATR二次側 MW | ATR |  |  |  |  | CDC | 84 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | #1 ATR | MVAR | #1ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#1ATR_MVAR | #1ATR二次側 MVAR | ATR |  |  |  |  | CDC | 85 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | #2 ATR | MW | #2ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#2ATR_MW | #2ATR二次側 MW | ATR |  |  |  |  | CDC | 86 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | #2 ATR | MVAR | #2ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#2ATR_MVAR | #2ATR二次側 MVAR | ATR |  |  |  |  | CDC | 87 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | #3 ATR | MW | #3ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#3ATR_MW | #3ATR二次側 MW | ATR |  |  |  |  | CDC | 88 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | #3 ATR | MVAR | #3ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#3ATR_MVAR | #3ATR二次側 MVAR | ATR |  |  |  |  | CDC | 89 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | #4 ATR | MW | #4ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#4ATR_MW | #4ATR二次側 MW | ATR |  |  |  |  | CDC | 90 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | #4 ATR | MVAR | #4ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#4ATR_MVAR | #4ATR二次側 MVAR | ATR |  |  |  |  | CDC | 91 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | #5 ATR | MW | #5ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#5ATR_MW | #5ATR二次側 MW | ATR |  |  |  |  | CDC | 92 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | #5 ATR | MVAR | #5ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#5ATR_MVAR | #5ATR二次側 MVAR | ATR |  |  |  |  | CDC | 93 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | #6 ATR | MW | #6ATR 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#6ATR_MW | #6ATR二次側 MW | ATR |  |  |  |  | CDC | 94 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | #6 ATR | MVAR | #6ATR 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#6ATR_MVAR | #6ATR二次側 MVAR | ATR |  |  |  |  | CDC | 95 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | MW |  | B3 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0341 |  |  | 3-D5 |  |  | #8 ATR | MW | #8ATR二次 瓦 | MW_-840_840(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#8ATR_MW | #8ATR二次側 MW | ATR |  |  |  |  | CDC | 96 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.84 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0342 |  |  | 3-D6 |  |  | #8 ATR | MVAR | #8ATR二次 乏 | MVAR_-560_560(-2000_2000) |  | B2/E05_C | 500 |  | 2000 | 500 |  |  | 1500 | 1000 | 嘉民ES.#8ATR_MVAR | #8ATR二次側 MVAR | ATR |  |  |  |  | CDC | 97 | AI_ATR345/161 |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.56 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0696 |  | 0000 | 1-3B-08 |  | 1-00 | Locate Empty |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 嘉民ES.161KV_TEST_CB | 161KV TEST CB | OTHER |  |  |  |  | CDC | 98 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0292 |  |  | 3-A4 |  |  | #1 ATR(R) | ℃ | #1ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_OIL_R | #1ATR R相油溫 | ATR |  |  |  |  | CDC | 99 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0291 |  |  | 3-A3 |  |  | #1 ATR(R) | ℃ | #1ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_COIL_R | #1ATR R相線溫 | ATR |  |  |  |  | CDC | 100 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0294 |  |  | 3-A6 |  |  | #1 ATR(S) | ℃ | #1ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_OIL_S | #1ATR S相油溫 | ATR |  |  |  |  | CDC | 101 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0293 |  |  | 3-A5 |  |  | #1 ATR(S) | ℃ | #1ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_COIL_S | #1ATR S相線溫 | ATR |  |  |  |  | CDC | 102 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0296 |  |  | 3-A8 |  |  | #1 ATR(T) | ℃ | #1ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_OIL_T | #1ATR T相油溫 | ATR |  |  |  |  | CDC | 103 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0295 |  |  | 3-A7 |  |  | #1 ATR(T) | ℃ | #1ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_COIL_T | #1ATR T相線溫 | ATR |  |  |  |  | CDC | 104 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P03M/T1 |  | 0006 |  | 0007 | 1-00-06 |  | 1-07 | 雲林山線 | 1550 | 1550 CB AS |  | aacb | B2/E05_A1 | [8 empty] | 嘉民ES.1550_CB | 1550(雲林山線) CB | LINE161 |  |  |  |  | CDC | 105 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0299 |  |  | 3-AB |  |  | #2 ATR(R) | ℃ | #2ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_OIL_R | #2ATR R相油溫 | ATR |  |  |  |  | CDC | 106 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0298 |  |  | 3-AA |  |  | #2 ATR(R) | ℃ | #2ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_COIL_R | #2ATR R相線溫 | ATR |  |  |  |  | CDC | 107 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0301 |  |  | 3-AD |  |  | #2 ATR(S) | ℃ | #2ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_OIL_S | #2ATR S相油溫 | ATR |  |  |  |  | CDC | 108 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0300 |  |  | 3-AC |  |  | #2 ATR(S) | ℃ | #2ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_COIL_S | #2ATR S相線溫 | ATR |  |  |  |  | CDC | 109 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0303 |  |  | 3-AF |  |  | #2 ATR(T) | ℃ | #2ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_OIL_T | #2ATR T相油溫 | ATR |  |  |  |  | CDC | 110 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0302 |  |  | 3-AE |  |  | #2 ATR(T) | ℃ | #2ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_COIL_T | #2ATR T相線溫 | ATR |  |  |  |  | CDC | 111 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P03O/T1 |  | 0010 |  | 0008 | 1-01-02 |  | 1-08 | 雲林海線 | 1560 | 1560 CB AS |  | aadb | B2/E05_A1 | [8 empty] | 嘉民ES.1560_CB | 1560(雲林海線) CB | LINE161 |  |  |  |  | CDC | 112 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0306 |  |  | 3-B2 |  |  | #3 ATR(R) | ℃ | #3ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_OIL_R | #3ATR R相油溫 | ATR |  |  |  |  | CDC | 113 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0305 |  |  | 3-B1 |  |  | #3 ATR(R) | ℃ | #3ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_COIL_R | #3ATR R相線溫 | ATR |  |  |  |  | CDC | 114 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0308 |  |  | 3-B4 |  |  | #3 ATR(S) | ℃ | #3ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_OIL_S | #3ATR S相油溫 | ATR |  |  |  |  | CDC | 115 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0307 |  |  | 3-B3 |  |  | #3 ATR(S) | ℃ | #3ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_COIL_S | #3ATR S相線溫 | ATR |  |  |  |  | CDC | 116 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0310 |  |  | 3-B6 |  |  | #3 ATR(T) | ℃ | #3ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_OIL_T | #3ATR T相油溫 | ATR |  |  |  |  | CDC | 117 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0309 |  |  | 3-B5 |  |  | #3 ATR(T) | ℃ | #3ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_COIL_T | #3ATR T相線溫 | ATR |  |  |  |  | CDC | 118 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03C211/T1 |  | 0014 |  | 0009 | 1-01-06 |  | 1-09 | 台嘉一路 | 1710 | 1710 CB AS |  | aafb | B2/E05_A1 | [8 empty] | 嘉民ES.1710_CB | 1710(台嘉一路) CB | LINE161 |  |  |  |  | CDC | 119 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0313 |  |  | 3-B9 |  |  | #4 ATR(R) | ℃ | #4ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_OIL_R | #4ATR R相油溫 | ATR |  |  |  |  | CDC | 120 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0312 |  |  | 3-B8 |  |  | #4 ATR(R) | ℃ | #4ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_COIL_R | #4ATR R相線溫 | ATR |  |  |  |  | CDC | 121 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0315 |  |  | 3-BB |  |  | #4 ATR(S) | ℃ | #4ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_OIL_S | #4ATR S相油溫 | ATR |  |  |  |  | CDC | 122 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0314 |  |  | 3-BA |  |  | #4 ATR(S) | ℃ | #4ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_COIL_S | #4ATR S相線溫 | ATR |  |  |  |  | CDC | 123 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0317 |  |  | 3-BD |  |  | #4 ATR(T) | ℃ | #4ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_OIL_T | #4ATR T相油溫 | ATR |  |  |  |  | CDC | 124 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0316 |  |  | 3-BC |  |  | #4 ATR(T) | ℃ | #4ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_COIL_T | #4ATR T相線溫 | ATR |  |  |  |  | CDC | 125 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P04N/T1 |  | 0018 |  | 0010 | 1-02-02 |  | 1-0A | 北港北線 | 1640 | 1640 CB AS |  | aaib | B2/E05_A1 | [8 empty] | 嘉民ES.1640_CB | 1640(北港北線) CB | LINE161 |  |  |  |  | CDC | 126 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0324 |  |  | 3-C4 |  |  | #5 ATR(R) | ℃ | #5ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_OIL_R | #5ATR R相油溫 | ATR |  |  |  |  | CDC | 127 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0323 |  |  | 3-C3 |  |  | #5 ATR(R) | ℃ | #5ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_COIL_R | #5ATR R相線溫 | ATR |  |  |  |  | CDC | 128 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0326 |  |  | 3-C6 |  |  | #5 ATR(S) | ℃ | #5ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_OIL_S | #5ATR S相油溫 | ATR |  |  |  |  | CDC | 129 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0325 |  |  | 3-C5 |  |  | #5 ATR(S) | ℃ | #5ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_COIL_S | #5ATR S相線溫 | ATR |  |  |  |  | CDC | 130 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0328 |  |  | 3-C8 |  |  | #5 ATR(T) | ℃ | #5ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_OIL_T | #5ATR T相油溫 | ATR |  |  |  |  | CDC | 131 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0327 |  |  | 3-C7 |  |  | #5 ATR(T) | ℃ | #5ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_COIL_T | #5ATR T相線溫 | ATR |  |  |  |  | CDC | 132 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P04S/T1 |  | 0022 |  | 0011 | 1-02-06 |  | 1-0B | 北港南線 | 1630 | 1630 CB AS |  | aajb | B2/E05_A1 | [8 empty] | 嘉民ES.1630_CB | 1630(北港南線) CB | LINE161 |  |  |  |  | CDC | 133 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0331 |  |  | 3-CB |  |  | #6 ATR(R) | ℃ | #6ATR R相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_OIL_R | #6ATR R相油溫 | ATR |  |  |  |  | CDC | 134 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0330 |  |  | 3-CA |  |  | #6 ATR(R) | ℃ | #6ATR R相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_COIL_R | #6ATR R相線溫 | ATR |  |  |  |  | CDC | 135 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | Oil_S |  |  | MvMoment | S相油溫 |  | Y |  | AI | [6 empty] | 0333 |  |  | 3-CD |  |  | #6 ATR(S) | ℃ | #6ATR S相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_OIL_S | #6ATR S相油溫 | ATR |  |  |  |  | CDC | 136 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | Coil_S |  |  | MvMoment | S相線溫 |  | Y |  | AI | [6 empty] | 0332 |  |  | 3-CC |  |  | #6 ATR(S) | ℃ | #6ATR S相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_COIL_S | #6ATR S相線溫 | ATR |  |  |  |  | CDC | 137 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | Oil_T |  |  | MvMoment | T相油溫 |  | Y |  | AI | [6 empty] | 0335 |  |  | 3-CF |  |  | #6 ATR(T) | ℃ | #6ATR T相油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_OIL_T | #6ATR T相油溫 | ATR |  |  |  |  | CDC | 138 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | Coil_T |  |  | MvMoment | T相線溫 |  | Y |  | AI | [6 empty] | 0334 |  |  | 3-CE |  |  | #6 ATR(T) | ℃ | #6ATR T相二次線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_COIL_T | #6ATR T相線溫 | ATR |  |  |  |  | CDC | 139 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/E03P05O/T1 |  | 0026 |  | 0012 | 1-03-02 |  | 1-0C | 嘉義海線 | 1520 | 1520 CB AS |  | abkb | B2/E05_A1 | [8 empty] | 嘉民ES.1520_CB | 1520(嘉義海線) CB | LINE161 |  |  |  |  | CDC | 140 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | Oil_R |  |  | MvMoment | R相油溫 |  | Y |  | AI | [6 empty] | 0344 |  |  | 3-D8 |  |  | #8 ATR | ℃ | #8ATR 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_OIL_R | #8ATR 油溫 | ATR |  |  |  |  | CDC | 141 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | Coil_R |  |  | MvMoment | R相線溫 |  | Y |  | AI | [6 empty] | 0343 |  |  | 3-D7 |  |  | #8 ATR | ℃ | #8ATR 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_COIL_R | #8ATR 線溫 | ATR |  |  |  |  | CDC | 142 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER |  |  |  |  | CDC | 143 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER |  |  |  |  | CDC | 144 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER |  |  |  |  | CDC | 145 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER |  |  |  |  | CDC | 146 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0256 |  |  | 3-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER |  |  |  |  | CDC | 147 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0257 |  |  | 3-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER |  |  |  |  | CDC | 148 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0320 |  |  | 3-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER |  |  |  |  | CDC | 149 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0321 |  |  | 3-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER |  |  |  |  | CDC | 150 | AI_ADC |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | 1_DCV_P | #1直流P電源 | Element | MvMoment | #1 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0336 |  |  | 3-D0 |  |  | 345KV | DCV | P-G 電壓 | kV_-150_150(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.#1直流P電源 | #1直流P電源電壓 | OTHER |  |  |  |  | CDC | 151 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | 1_DCV_N | #1直流N電源 | Element | MvMoment | #1 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0337 |  |  | 3-D1 |  |  | 345KV | DCV | N-G 電壓 | kV_-150_150(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.#1直流N電源 | #1直流N電源電壓 | OTHER |  |  |  |  | CDC | 152 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | 2_DCV_P | #2直流P電源 | Element | MvMoment | #2 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0338 |  |  | 3-D2 |  |  | 161KV | DCV | P-G 電壓 | kV_-150_150(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.#2直流P電源 | #2直流P電源電壓 | OTHER |  |  |  |  | CDC | 153 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 |  | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | 2_DCV_N | #2直流N電源 | Element | MvMoment | #2 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0339 |  |  | 3-D3 |  |  | 161KV | DCV | N-G 電壓 | kV_-150_150(-2000_2000) |  | B3/E05_A1 | [8 empty] | 嘉民ES.#2直流N電源 | #2直流N電源電壓 | OTHER |  |  |  |  | CDC | 154 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 |  | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | #1S.R | ℃ | #1S.R 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#1ATR_SR_OIL | #1ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 155 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | #1S.R | ℃ | #1S.R 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#1ATR_SR_COIL | #1ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 156 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | #2S.R | ℃ | #2S.R 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#2ATR_SR_OIL | #2ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 157 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | #2S.R | ℃ | #2S.R 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#2ATR_SR_COIL | #2ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 158 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | #3S.R | ℃ | #3S.R 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#3ATR_SR_OIL | #3ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 159 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | #3S.R | ℃ | #3S.R 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#3ATR_SR_COIL | #3ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 160 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | #4S.R | ℃ | #4S.R 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#4ATR_SR_OIL | #4ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 161 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | #4S.R | ℃ | #4S.R 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#4ATR_SR_COIL | #4ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 162 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | #5S.R | ℃ | #5S.R 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#5ATR_SR_OIL | #5ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 163 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | #5S.R | ℃ | #5S.R 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#5ATR_SR_COIL | #5ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 164 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | OilTemp |  | Element | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | #6S.R | ℃ | #6S.R 油溫 | OIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#6ATR_SR_OIL | #6ATR 二次側 SR 油溫 | OTHER |  |  |  |  | CDC | 165 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | CoilTemp |  | Element | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | #6S.R | ℃ | #6S.R 線溫 | COIL_-120_120(-2000_2000) |  | B2/E05_A1 | [8 empty] | 嘉民ES.#6ATR_SR_COIL | #6ATR 二次側 SR 線溫 | OTHER |  |  |  |  | CDC | 166 | AI_OTHERS(1) |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aalb | B2/E05_A1 | [8 empty] | 嘉民ES.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 167 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aalb | B2/E05_A1 | [8 empty] | 嘉民ES.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 168 | DI_BUS | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3510LE | 3510LE (非取樣點) | LINE345 | [5 empty] | 169 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3510BE | 3510BE (非取樣點) | LINE345 | [5 empty] | 170 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3540LE | 3540LE (非取樣點) | LINE345 | [5 empty] | 171 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3540BE | 3540BE (非取樣點) | LINE345 | [5 empty] | 172 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | LE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3560LE | 3560LE (非取樣點) | LINE345 | [5 empty] | 173 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | BE0 | (非取樣點) | Add | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3560BE | 3560BE (非取樣點) | LINE345 | [5 empty] | 174 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3570LE | 3570LE (非取樣點) | LINE345 | [5 empty] | 175 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3570BE | 3570BE (非取樣點) | LINE345 | [5 empty] | 176 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3610LE | 3610LE (非取樣點) | LINE345 | [5 empty] | 177 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3610BE | 3610BE (非取樣點) | LINE345 | [5 empty] | 178 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3640LE | 3640LE (非取樣點) | LINE345 | [5 empty] | 179 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3640BE | 3640BE (非取樣點) | LINE345 | [5 empty] | 180 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3710LE | 3710LE (非取樣點) | LINE345 | [5 empty] | 181 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3710BE | 3710BE (非取樣點) | LINE345 | [5 empty] | 182 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3770LE | 3770LE (非取樣點) | LINE345 | [5 empty] | 183 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3770BE | 3770BE (非取樣點) | LINE345 | [5 empty] | 184 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3810LE | 3810LE (非取樣點) | LINE345 | [5 empty] | 185 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3810BE | 3810BE (非取樣點) | LINE345 | [5 empty] | 186 | DI_LINE345(4) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3580 | TIE(3580) |  | E1 | 3581E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3581E | 3581E (非取樣點) | LINE345 | [5 empty] | 187 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3580 | TIE(3580) |  | E2 | 3582E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3582E | 3582E (非取樣點) | LINE345 | [5 empty] | 188 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3620 | TIE(3620) |  | E1 | 3621E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3621E | 3621E (非取樣點) | LINE345 | [5 empty] | 189 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3620 | TIE(3620) |  | E2 | 3622E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3622E | 3622E (非取樣點) | LINE345 | [5 empty] | 190 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3650 | TIE(3650) |  | E1 | 3651E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3651E | 3651E (非取樣點) | LINE345 | [5 empty] | 191 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3650 | TIE(3650) |  | E2 | 3652E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3652E | 3652E (非取樣點) | LINE345 | [5 empty] | 192 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3720 | TIE(3720) |  | E1 | 3721E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3721E | 3721E (非取樣點) | LINE345 | [5 empty] | 193 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3720 | TIE(3720) |  | E2 | 3722E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3722E | 3722E (非取樣點) | LINE345 | [5 empty] | 194 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3780 | TIE(3780) |  | E1 | 3781E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3781E | 3781E (非取樣點) | LINE345 | [5 empty] | 195 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3780 | TIE(3780) |  | E2 | 3782E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3782E | 3782E (非取樣點) | LINE345 | [5 empty] | 196 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3820 | TIE(3820) |  | E1 | 3821E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3821E | 3821E (非取樣點) | LINE345 | [5 empty] | 197 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3820 | TIE(3820) |  | E2 | 3822E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3822E | 3822E (非取樣點) | LINE345 | [5 empty] | 198 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3520 | TIE(3520) |  | E1 | 3521E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3521E | 3521E (非取樣點) | LINE345 | [5 empty] | 199 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3520 | TIE(3520) |  | E2 | 3522E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3522E | 3522E (非取樣點) | LINE345 | [5 empty] | 200 | DI_MID_345CB(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 203 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 204 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1710LE | 1710LE (非取樣點) | LINE161 | [5 empty] | 205 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1710BE | 1710BE (非取樣點) | LINE161 | [5 empty] | 206 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1720LE | 1720LE (非取樣點) | LINE161 | [5 empty] | 207 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1720BE | 1720BE (非取樣點) | LINE161 | [5 empty] | 208 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1640LE | 1640LE (非取樣點) | LINE161 | [5 empty] | 209 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1640BE | 1640BE (非取樣點) | LINE161 | [5 empty] | 210 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1630LE | 1630LE (非取樣點) | LINE161 | [5 empty] | 211 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1630BE | 1630BE (非取樣點) | LINE161 | [5 empty] | 212 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 213 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 214 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1590LE | 1590LE (非取樣點) | LINE161 | [5 empty] | 215 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1590BE | 1590BE (非取樣點) | LINE161 | [5 empty] | 216 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1730LE | 1730LE (非取樣點) | LINE161 | [5 empty] | 217 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1730BE | 1730BE (非取樣點) | LINE161 | [5 empty] | 218 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1740LE | 1740LE (非取樣點) | LINE161 | [5 empty] | 219 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1740BE | 1740BE (非取樣點) | LINE161 | [5 empty] | 220 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1610LE | 1610LE (非取樣點) | LINE161 | [5 empty] | 221 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1610BE | 1610BE (非取樣點) | LINE161 | [5 empty] | 222 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1620LE | 1620LE (非取樣點) | LINE161 | [5 empty] | 223 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1620BE | 1620BE (非取樣點) | LINE161 | [5 empty] | 224 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 225 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 226 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 227 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 228 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 229 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 230 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 231 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 232 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3590TE | 3590TE (非取樣點) | ATR | [5 empty] | 233 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3590BE | 3590BE (非取樣點) | ATR | [5 empty] | 234 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3630TE | 3630TE (非取樣點) | ATR | [5 empty] | 235 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3630BE | 3630BE (非取樣點) | ATR | [5 empty] | 236 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3660TE | 3660TE (非取樣點) | ATR | [5 empty] | 237 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3660BE | 3660BE (非取樣點) | ATR | [5 empty] | 238 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3730TE | 3730TE (非取樣點) | ATR | [5 empty] | 239 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3730BE | 3730BE (非取樣點) | ATR | [5 empty] | 240 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3790TE | 3790TE (非取樣點) | ATR | [5 empty] | 241 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3790BE | 3790BE (非取樣點) | ATR | [5 empty] | 242 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3830TE | 3830TE (非取樣點) | ATR | [5 empty] | 243 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3830BE | 3830BE (非取樣點) | ATR | [5 empty] | 244 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3530TE | 3530TE (非取樣點) | ATR | [5 empty] | 245 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_C | [8 empty] | 嘉民ES.3530BE | 3530BE (非取樣點) | ATR | [5 empty] | 246 | DI_ATR345/161(1) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1650BE | 1650BE(#1ATR)(非取樣點) | OTHER | [5 empty] | 247 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1650TE | 1650TE(#1ATR)(非取樣點) | OTHER | [5 empty] | 248 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1660BE | 1660BE(#2ATR)(非取樣點) | OTHER | [5 empty] | 249 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1660TE | 1660TE(#2ATR)(非取樣點) | OTHER | [5 empty] | 250 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1670BE | 1670BE(#3ATR)(非取樣點) | OTHER | [5 empty] | 251 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1670TE | 1670TE(#3ATR)(非取樣點) | OTHER | [5 empty] | 252 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1830BE | 1830BE(#3ATR)(非取樣點) | OTHER | [5 empty] | 253 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1830TE | 1830TE(#3ATR)(非取樣點) | OTHER | [5 empty] | 254 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1680BE | 1680BE(#4ATR)(非取樣點) | OTHER | [5 empty] | 255 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1680TE | 1680TE(#4ATR)(非取樣點) | OTHER | [5 empty] | 256 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1690BE | 1690BE(#5ATR)(非取樣點) | OTHER | [5 empty] | 257 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1690TE | 1690TE(#5ATR)(非取樣點) | OTHER | [5 empty] | 258 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1860BE | 1860BE(#6ATR)(非取樣點) | OTHER | [5 empty] | 259 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1860TE | 1860TE(#6ATR)(非取樣點) | OTHER | [5 empty] | 260 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | BE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1880BE | 1880BE(#8ATR)(非取樣點) | OTHER | [5 empty] | 261 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | TE0 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/E05_C | [8 empty] | 嘉民ES.1880TE | 1880TE(#8ATR)(非取樣點) | OTHER | [5 empty] | 262 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1650RE | #1ATR(1650) |  | NE0 | 1650SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/1ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1650SRE | 1650SRE(#1ATR)(非取樣點) | OTHER | [5 empty] | 263 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1660RE | #2ATR(1660) |  | NE0 | 1660SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/2ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1660SRE | 1660SRE(#2ATR)(非取樣點) | OTHER | [5 empty] | 264 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1670RE | #3ATR(1670) |  | NE0 | 1670SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/3ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1670SRE | 1670SRE(#3ATR)(非取樣點) | OTHER | [5 empty] | 265 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1830RE | #3ATR(1830) |  | NE0 | 1830SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/3ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1830SRE | 1830SRE(#3ATR)(非取樣點) | OTHER | [5 empty] | 266 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1680RE | #4ATR(1680) |  | NE0 | 1680SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/4ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1680SRE | 1680SRE(#4ATR)(非取樣點) | OTHER | [5 empty] | 267 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1690RE | #5ATR(1690) |  | NE0 | 1690SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/5ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1690SRE | 1690SRE(#5ATR)(非取樣點) | OTHER | [5 empty] | 268 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1860RE | #6ATR(1860) |  | NE0 | 1860SRE(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/6ATR161 | [13 empty] | no rule | B3/E05_C | [8 empty] | 嘉民ES.1860SRE | 1860SRE(#6ATR)(非取樣點) | OTHER | [5 empty] | 269 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/E03P05M/T1 |  | 0030 |  | 0013 | 1-03-06 |  | 1-0D | 嘉義山線 | 1510 | 1510 CB AS |  | ablb | B2/E05_A1 | [8 empty] | 嘉民ES.1510_CB | 1510(嘉義山線) CB | LINE161 |  |  |  |  | CDC | 270 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 雲林山線 | 1550 | 1550 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_87A | 雲林山線(1550) 87RY | LINE161 |  |  |  |  | CDC | 271 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 雲林山線 | 1550 | 1550 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_PHA | 雲林山線(1550) 相間RY | LINE161 |  |  |  |  | CDC | 272 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 雲林山線 | 1550 | 1550 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_GDA | 雲林山線(1550) 接地RY | LINE161 |  |  |  |  | CDC | 273 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/E03P05S/T1 |  | 0034 |  | 0014 | 1-04-02 |  | 1-0E | 嘉義南線 | 1610 | 1610 CB AS |  | abeb | B2/E05_A1 | [8 empty] | 嘉民ES.1610_CB | 1610(嘉義南線) CB | LINE161 |  |  |  |  | CDC | 274 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 雲林海線 | 1560 | 1560 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_87A | 雲林海線(1560) 87RY | LINE161 |  |  |  |  | CDC | 275 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 雲林海線 | 1560 | 1560 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_PHA | 雲林海線(1560) 相間RY | LINE161 |  |  |  |  | CDC | 276 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 雲林海線 | 1560 | 1560 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_GDA | 雲林海線(1560) 接地RY | LINE161 |  |  |  |  | CDC | 277 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/E03P05N/T1 |  | 0038 |  | 0015 | 1-04-06 |  | 1-0F | 嘉義北線 | 1620 | 1620 CB AS |  | abfb | B2/E05_A1 | [8 empty] | 嘉民ES.1620_CB | 1620(嘉義北線) CB | LINE161 |  |  |  |  | CDC | 278 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 台嘉一路 | 1710 | 1710 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_PHA | 台嘉一路(1710) 相間RY | LINE161 |  |  |  |  | CDC | 279 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 台嘉一路 | 1710 | 1710 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_GDA | 台嘉一路(1710) 接地RY | LINE161 |  |  |  |  | CDC | 280 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/E03D06O/T1 |  | 0042 |  | 0016 | 1-05-02 |  | 1-10 | 柳營海線 | 1540 | 1540 CB AS |  | abhb | B2/E05_A1 | [8 empty] | 嘉民ES.1540_CB | 1540(柳營海線) CB | LINE161 |  |  |  |  | CDC | 281 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 北港北線 | 1640 | 1640 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_87A | 北港北線(1640) 87RY | LINE161 |  |  |  |  | CDC | 282 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 北港北線 | 1640 | 1640 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_PHA | 北港北線(1640) 相間RY | LINE161 |  |  |  |  | CDC | 283 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 北港北線 | 1640 | 1640 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_GDA | 北港北線(1640) 接地RY | LINE161 |  |  |  |  | CDC | 284 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/E03D06M/T1 |  | 0046 |  | 0017 | 1-05-06 |  | 1-11 | 柳營山線 | 1530 | 1530 CB AS |  | abib | B2/E05_A1 | [8 empty] | 嘉民ES.1530_CB | 1530(柳營山線) CB | LINE161 |  |  |  |  | CDC | 285 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 北港南線 | 1630 | 1630 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_87A | 北港南線(1630) 87RY | LINE161 |  |  |  |  | CDC | 286 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 |  |  | 1-03-00 |  |  | 北港南線 | 1630 | 1630 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_PHA | 北港南線(1630) 相間RY | LINE161 |  |  |  |  | CDC | 287 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 北港南線 | 1630 | 1630 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_GDA | 北港南線(1630) 接地RY | LINE161 |  |  |  |  | CDC | 288 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03D09R/T1 |  | 0050 |  | 0018 | 1-06-02 |  | 1-12 | 斗工紅線 | 1590 | 1590 CB AS |  | aanb | B2/E05_A1 | [8 empty] | 嘉民ES.1590_CB | 1590(斗工紅線) CB | LINE161 |  |  |  |  | CDC | 289 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 嘉義海線 | 1520 | 1520 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_87A | 嘉義海線(1520) 87RY | LINE161 |  |  |  |  | CDC | 290 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 嘉義海線 | 1520 | 1520 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_PHA | 嘉義海線(1520) 相間RY | LINE161 |  |  |  |  | CDC | 291 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 嘉義海線 | 1520 | 1520 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_GDA | 嘉義海線(1520) 接地RY | LINE161 |  |  |  |  | CDC | 292 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P03/T1 |  | 0054 |  | 0019 | 1-06-06 |  | 1-13 | 嘉民雲林線 | 1580 | 1580 CB AS |  | aamb | B2/E05_A1 | [8 empty] | 嘉民ES.1580_CB | 1580(嘉民雲林線) CB | LINE161 |  |  |  |  | CDC | 293 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 嘉義山線 | 1510 | 1510 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_87A | 嘉義山線(1510) 87RY | LINE161 |  |  |  |  | CDC | 294 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 嘉義山線 | 1510 | 1510 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_PHA | 嘉義山線(1510) 相間RY | LINE161 |  |  |  |  | CDC | 295 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 嘉義山線 | 1510 | 1510 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_GDA | 嘉義山線(1510) 接地RY | LINE161 |  |  |  |  | CDC | 296 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03C212/T1 |  | 0075 |  | 0020 | 1-09-03 |  | 1-14 | 台嘉二路 | 1720 | 1720 CB AS |  | aagb | B2/E05_A1 | [8 empty] | 嘉民ES.1720_CB | 1720(台嘉二路) CB | LINE161 |  |  |  |  | CDC | 297 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 嘉義南線 | 1610 | 1610 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_87A | 嘉義南線(1610) 87RY | LINE161 |  |  |  |  | CDC | 298 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 嘉義南線 | 1610 | 1610 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_PHA | 嘉義南線(1610) 相間RY | LINE161 |  |  |  |  | CDC | 299 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 嘉義南線 | 1610 | 1610 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_GDA | 嘉義南線(1610) 接地RY | LINE161 |  |  |  |  | CDC | 300 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/T10E031/T2 |  | 0104 |  | 0021 | 1-0D-00 |  | 1-15 | 嘉惠一路 | 1730 | 1730 CB AS |  | abab | B2/E05_A1 | [8 empty] | 嘉民ES.1730_CB | 1730(嘉惠一路) CB | LINE161 |  |  |  |  | CDC | 301 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | 嘉義北線 | 1620 | 1620 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_87A | 嘉義北線(1620) 87RY | LINE161 |  |  |  |  | CDC | 302 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 嘉義北線 | 1620 | 1620 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_PHA | 嘉義北線(1620) 相間RY | LINE161 |  |  |  |  | CDC | 303 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 嘉義北線 | 1620 | 1620 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_GDA | 嘉義北線(1620) 接地RY | LINE161 |  |  |  |  | CDC | 304 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/3Bus | B/4Bus | L/T10E032/T2 |  | 0105 |  | 0022 | 1-0D-01 |  | 1-16 | 嘉惠二路 | 1740 | 1740 CB AS |  | abbb | B2/E05_A1 | [8 empty] | 嘉民ES.1740_CB | 1740(嘉惠二路) CB | LINE161 |  |  |  |  | CDC | 305 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 柳營海線 | 1540 | 1540 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_87A | 柳營海線(1540) 87RY | LINE161 |  |  |  |  | CDC | 306 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 柳營海線 | 1540 | 1540 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_PHA | 柳營海線(1540) 相間RY | LINE161 |  |  |  |  | CDC | 307 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 柳營海線 | 1540 | 1540 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_GDA | 柳營海線(1540) 接地RY | LINE161 |  |  |  |  | CDC | 308 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | no type |  |  |  |  | 0058 |  | 0024 | 1-07-02 |  | 1-18 | Locate Empty | 1500 | 1500 CB AS |  | aaaz | B2/E05_A1 | [8 empty] | 嘉民ES.1500_CB | 1500(TIE) CB | TIE |  |  |  |  | CDC | 309 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | 柳營山線 | 1530 | 1530 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_87A | 柳營山線(1530) 87RY | LINE161 |  |  |  |  | CDC | 310 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0048 |  |  | 1-06-00 |  |  | 柳營山線 | 1530 | 1530 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_PHA | 柳營山線(1530) 相間RY | LINE161 |  |  |  |  | CDC | 311 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 柳營山線 | 1530 | 1530 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_GDA | 柳營山線(1530) 接地RY | LINE161 |  |  |  |  | CDC | 312 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | no type |  |  |  |  | 0060 |  | 0025 | 1-07-04 |  | 1-19 | Locate Empty | 1600 | 1600 CB AS |  | abmz | B2/E05_A1 | [8 empty] | 嘉民ES.1600_CB | 1600(TIE) CB | TIE |  |  |  |  | CDC | 313 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 斗工紅線 | 1590 | 1590 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_87A | 斗工紅線(1590) 87RY | LINE161 |  |  |  |  | CDC | 314 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 斗工紅線 | 1590 | 1590 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_PHA | 斗工紅線(1590) 相間RY | LINE161 |  |  |  |  | CDC | 315 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 斗工紅線 | 1590 | 1590 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_GDA | 斗工紅線(1590) 接地RY | LINE161 |  |  |  |  | CDC | 316 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/1Bus | B/3Bus |  |  | 0062 |  | 0026 | 1-07-06 |  | 1-1A | Locate Empty | 1700 | 1700 CB AS |  | no rule | B2/E05_A1 | [8 empty] | 嘉民ES.1700_CB | 1700(TIE) CB | TIE |  |  |  |  | CDC | 317 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 嘉民雲林線 | 1580 | 1580 87A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_87A | 嘉民雲林線(1580) 87RY | LINE161 |  |  |  |  | CDC | 318 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 嘉民雲林線 | 1580 | 1580 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_PHA | 嘉民雲林線(1580) 相間RY | LINE161 |  |  |  |  | CDC | 319 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0057 |  |  | 1-07-01 |  |  | 嘉民雲林線 | 1580 | 1580 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_GDA | 嘉民雲林線(1580) 接地RY | LINE161 |  |  |  |  | CDC | 320 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Sect2B | B/2Bus | B/4Bus |  |  | 0064 |  | 0027 | 1-08-00 |  | 1-1B | Locate Empty | 1800 | 1800 CB AS |  | no rule | B2/E05_A1 | [8 empty] | 嘉民ES.1800_CB | 1800(TIE) CB | TIE |  |  |  |  | CDC | 321 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | Locate Empty | 1500 | 1500 50A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1500_50A | 161KV TIE(1500) 50RY | TIE |  |  |  |  | CDC | 322 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | ABS1 | 1551 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0536 | 0537 | 0040 | 1-31-08 | 1-31-09 | 1-28 | 雲林山線 |  | 1551 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1551_ABS | 1551(雲林山線) ABS | LINE161 |  |  |  |  | CDC | 323 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | Locate Empty | 1600 | 1600 50A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1600_50A | 161KV TIE(1600) 50RY | TIE |  |  |  |  | CDC | 324 | DI_TIE(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | ABS2 | 1552 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0538 | 0539 | 0041 | 1-31-10 | 1-31-11 | 1-29 | 雲林山線 |  | 1552 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1552_ABS | 1552(雲林山線) ABS | LINE161 |  |  |  |  | CDC | 325 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | ABS3 | 1553 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0540 | 0541 | 0042 | 1-31-12 | 1-31-13 | 1-2A | 雲林山線 |  | 1553 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1553_ABS | 1553(雲林山線) ABS | LINE161 |  |  |  |  | CDC | 326 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | Locate Empty | 161KV | 87B1A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#1BUS_87A | 161KV #1BUS 87RY | BUS |  |  |  |  | CDC | 327 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | Locate Empty | 161KV | 87B2A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#2BUS_87A | 161KV #2BUS 87RY | BUS |  |  |  |  | CDC | 328 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 3BUS | #3BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | Locate Empty | 161KV | 87B3A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#3BUS_87A | 161KV #3BUS 87RY | BUS |  |  |  |  | CDC | 329 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 4BUS | #4BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | Locate Empty | 161KV | 87B4A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#4BUS_87A | 161KV #4BUS 87RY | BUS |  |  |  |  | CDC | 330 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | Locate Empty | 161KV | 161KV RCA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER |  |  |  |  | CDC | 331 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | BFA |  |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | Locate Empty | 161KV | 161KV BFA |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.161KV_BFA | 161KV斷路器失靈(BF)RY | OTHER |  |  |  |  | CDC | 332 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161KV_OSCA | 161KV示波器啟動警報 | OTHER |  |  |  |  | CDC | 333 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | RTU_MCT | MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 161RTU | MCT_ SOE | 161 RTU MASTER RY SOE |  |  | B2/E05_A1 | [15 empty] | CDC | 334 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | ES3 | 1553E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0542 | 0543 | 0043 | 1-31-14 | 1-31-15 | 1-2B | 雲林山線 |  | 1553E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1553E_ES | 1553E(雲林山線) ES | LINE161 |  |  |  |  | CDC | 335 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 台嘉二路 | 1720 | 1720 285A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_85BA | 台嘉二路(1720) 85RY(B) | LINE161 |  |  |  |  | CDC | 336 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 台嘉二路 | 1720 | 1720 185A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_85MA | 台嘉二路(1720) 85RY(M) | LINE161 |  |  |  |  | CDC | 337 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 台嘉二路 | 1720 | 1720 PHA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_PHA | 台嘉二路(1720) 相間RY | LINE161 |  |  |  |  | CDC | 338 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 台嘉二路 | 1720 | 1720 GDA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_GDA | 台嘉二路(1720) 接地RY | LINE161 |  |  |  |  | CDC | 339 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 台嘉一路 | 1710 | 1710 285A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_85BA | 台嘉一路(1710) 85RY(B) | LINE161 |  |  |  |  | CDC | 340 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 台嘉一路 | 1710 | 1710 185A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_85MA | 台嘉一路(1710) 85RY(M) | LINE161 |  |  |  |  | CDC | 341 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | DTTA |  | B2,B3,Element | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 柳營山線 | 1530 | 1530 遠方遙跳 DTTA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_DTTA | 嘉民柳營山線(1530)遠方遙跳 | OTHER |  |  |  |  | CDC | 342 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | DTTA |  | B2,B3,Element | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 柳營海線 | 1540 | 1540 遠方遙跳 DTTA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_DTTA | 嘉民柳營海線(1540)遠方遙跳 | OTHER |  |  |  |  | CDC | 343 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | ABS1 | 1561 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0544 | 0545 | 0044 | 1-32-00 | 1-32-01 | 1-2C | 雲林海線 |  | 1561 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1561_ABS | 1561(雲林海線) ABS | LINE161 |  |  |  |  | CDC | 344 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | ABS2 | 1562 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0546 | 0547 | 0045 | 1-32-02 | 1-32-03 | 1-2D | 雲林海線 |  | 1562 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1562_ABS | 1562(雲林海線) ABS | LINE161 |  |  |  |  | CDC | 345 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | 嘉惠一路 | 1730 | 1730 87L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730_87A | 嘉惠一路(1730) 87RY | LINE161 |  |  |  |  | CDC | 346 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | 嘉惠一路 | 1730 | 1730 21 RY |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730_21A | 嘉惠一路(1730) 21RY | LINE161 |  |  |  |  | CDC | 347 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0108 |  |  | 1-0D-04 |  |  | 嘉惠二路 | 1740 | 1740 87L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740_87A | 嘉惠二路(1740) 87RY | LINE161 |  |  |  |  | CDC | 348 | DI_LINE161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | 21A |  |  | Status | 21RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0109 |  |  | 1-0D-05 |  |  | 嘉惠二路 | 1740 | 1740 21 RY |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740_21A | 嘉惠二路(1740) 21RY | LINE161 |  |  |  |  | CDC | 349 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 25RY | 25PFA | 自動同步校核裝置電源故障警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER |  |  |  |  | CDC | 350 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 25RY | 25TA | 自動同步校核裝置超時警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER |  |  |  |  | CDC | 351 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | ABS3 | 1563 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0548 | 0549 | 0046 | 1-32-04 | 1-32-05 | 1-2E | 雲林海線 |  | 1563 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1563_ABS | 1563(雲林海線) ABS | LINE161 |  |  |  |  | CDC | 352 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | ES3 | 1563E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0550 | 0551 | 0047 | 1-32-06 | 1-32-07 | 1-2F | 雲林海線 |  | 1563E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1563E_ES | 1563E(雲林海線) ES | LINE161 |  |  |  |  | CDC | 353 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | ABS1 | 1711 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0552 | 0553 | 0048 | 1-32-08 | 1-32-09 | 1-30 | 台嘉一路 |  | 1711 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1711_ABS | 1711(台嘉一路) ABS | LINE161 |  |  |  |  | CDC | 354 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | ABS2 | 1712 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0554 | 0555 | 0049 | 1-32-10 | 1-32-11 | 1-31 | 台嘉一路 |  | 1712 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1712_ABS | 1712(台嘉一路) ABS | LINE161 |  |  |  |  | CDC | 355 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | ABS3 | 1713 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0556 | 0557 | 0050 | 1-32-12 | 1-32-13 | 1-32 | 台嘉一路 |  | 1713 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1713_ABS | 1713(台嘉一路) ABS | LINE161 |  |  |  |  | CDC | 356 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | ES3 | 1713E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0558 | 0559 | 0051 | 1-32-14 | 1-32-15 | 1-33 | 台嘉一路 |  | 1713E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1713E_ES | 1713E(台嘉一路) ES | LINE161 |  |  |  |  | CDC | 357 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | ABS1 | 1721 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0688 | 0689 | 0052 | 1-3B-00 | 1-3B-01 | 1-34 | 台嘉二路 |  | 1721 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1721_ABS | 1721(台嘉二路) ABS | LINE161 |  |  |  |  | CDC | 358 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | ABS2 | 1722 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0690 | 0691 | 0053 | 1-3B-02 | 1-3B-03 | 1-35 | 台嘉二路 |  | 1722 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1722_ABS | 1722(台嘉二路) ABS | LINE161 |  |  |  |  | CDC | 359 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | ABS3 | 1723 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0692 | 0693 | 0054 | 1-3B-04 | 1-3B-05 | 1-36 | 台嘉二路 |  | 1723 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1723_ABS | 1723(台嘉二路) ABS | LINE161 |  |  |  |  | CDC | 360 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | ES3 | 1723E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0694 | 0695 | 0055 | 1-3B-06 | 1-3B-07 | 1-37 | 台嘉二路 |  | 1723E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1723E_ES | 1723E(台嘉二路) ES | LINE161 |  |  |  |  | CDC | 361 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ABS1 | 1641 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0560 | 0561 | 0056 | 1-33-00 | 1-33-01 | 1-38 | 北港北線 |  | 1641 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1641_ABS | 1641(北港北線) ABS | LINE161 |  |  |  |  | CDC | 362 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ABS2 | 1642 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0562 | 0563 | 0057 | 1-33-02 | 1-33-03 | 1-39 | 北港北線 |  | 1642 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1642_ABS | 1642(北港北線) ABS | LINE161 |  |  |  |  | CDC | 363 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ABS3 | 1643 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0564 | 0565 | 0058 | 1-33-04 | 1-33-05 | 1-3A | 北港北線 |  | 1643 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1643_ABS | 1643(北港北線) ABS | LINE161 |  |  |  |  | CDC | 364 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ES3 | 1643E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0566 | 0567 | 0059 | 1-33-06 | 1-33-07 | 1-3B | 北港北線 |  | 1643E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1643E_ES | 1643E(北港北線) ES | LINE161 |  |  |  |  | CDC | 365 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ABS1 | 1631 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0568 | 0569 | 0060 | 1-33-08 | 1-33-09 | 1-3C | 北港南線 |  | 1631 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1631_ABS | 1631(北港南線) ABS | LINE161 |  |  |  |  | CDC | 366 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ABS2 | 1632 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0570 | 0571 | 0061 | 1-33-10 | 1-33-11 | 1-3D | 北港南線 |  | 1632 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1632_ABS | 1632(北港南線) ABS | LINE161 |  |  |  |  | CDC | 367 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ABS3 | 1633 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0572 | 0573 | 0062 | 1-33-12 | 1-33-13 | 1-3E | 北港南線 |  | 1633 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1633_ABS | 1633(北港南線) ABS | LINE161 |  |  |  |  | CDC | 368 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ES3 | 1633E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0574 | 0575 | 0063 | 1-33-14 | 1-33-15 | 1-3F | 北港南線 |  | 1633E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1633E_ES | 1633E(北港南線) ES | LINE161 |  |  |  |  | CDC | 369 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | ABS1 | 1521 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0576 | 0577 | 0064 | 1-34-00 | 1-34-01 | 1-40 | 嘉義海線 |  | 1521 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1521_ABS | 1521(嘉義海線) ABS | LINE161 |  |  |  |  | CDC | 370 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | ABS2 | 1522 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0578 | 0579 | 0065 | 1-34-02 | 1-34-03 | 1-41 | 嘉義海線 |  | 1522 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1522_ABS | 1522(嘉義海線) ABS | LINE161 |  |  |  |  | CDC | 371 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | ABS3 | 1523 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0580 | 0581 | 0066 | 1-34-04 | 1-34-05 | 1-42 | 嘉義海線 |  | 1523 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1523_ABS | 1523(嘉義海線) ABS | LINE161 |  |  |  |  | CDC | 372 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | ES3 | 1523E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0582 | 0583 | 0067 | 1-34-06 | 1-34-07 | 1-43 | 嘉義海線 |  | 1523E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1523E_ES | 1523E(嘉義海線) ES | LINE161 |  |  |  |  | CDC | 373 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | ABS1 | 1511 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0584 | 0585 | 0068 | 1-34-08 | 1-34-09 | 1-44 | 嘉義山線 |  | 1511 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1511_ABS | 1511(嘉義山線) ABS | LINE161 |  |  |  |  | CDC | 374 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | ABS2 | 1512 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0586 | 0587 | 0069 | 1-34-10 | 1-34-11 | 1-45 | 嘉義山線 |  | 1512 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1512_ABS | 1512(嘉義山線) ABS | LINE161 |  |  |  |  | CDC | 375 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | ABS3 | 1513 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0588 | 0589 | 0070 | 1-34-12 | 1-34-13 | 1-46 | 嘉義山線 |  | 1513 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1513_ABS | 1513(嘉義山線) ABS | LINE161 |  |  |  |  | CDC | 376 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | ES3 | 1513E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0590 | 0591 | 0071 | 1-34-14 | 1-34-15 | 1-47 | 嘉義山線 |  | 1513E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1513E_ES | 1513E(嘉義山線) ES | LINE161 |  |  |  |  | CDC | 377 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | ABS1 | 1611 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0592 | 0593 | 0072 | 1-35-00 | 1-35-01 | 1-48 | 嘉義南線 |  | 1611 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1611_ABS | 1611(嘉義南線) ABS | LINE161 |  |  |  |  | CDC | 378 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | ABS2 | 1612 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0594 | 0595 | 0073 | 1-35-02 | 1-35-03 | 1-49 | 嘉義南線 |  | 1612 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1612_ABS | 1612(嘉義南線) ABS | LINE161 |  |  |  |  | CDC | 379 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | ABS3 | 1613 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0596 | 0597 | 0074 | 1-35-04 | 1-35-05 | 1-4A | 嘉義南線 |  | 1613 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1613_ABS | 1613(嘉義南線) ABS | LINE161 |  |  |  |  | CDC | 380 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | ES3 | 1613E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0598 | 0599 | 0075 | 1-35-06 | 1-35-07 | 1-4B | 嘉義南線 |  | 1613E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1613E_ES | 1613E(嘉義南線) ES | LINE161 |  |  |  |  | CDC | 381 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | ABS1 | 1621 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0600 | 0601 | 0076 | 1-35-08 | 1-35-09 | 1-4C | 嘉義北線 |  | 1621 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1621_ABS | 1621(嘉義北線) ABS | LINE161 |  |  |  |  | CDC | 382 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | ABS2 | 1622 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0602 | 0603 | 0077 | 1-35-10 | 1-35-11 | 1-4D | 嘉義北線 |  | 1622 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1622_ABS | 1622(嘉義北線) ABS | LINE161 |  |  |  |  | CDC | 383 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | ABS3 | 1623 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0604 | 0605 | 0078 | 1-35-12 | 1-35-13 | 1-4E | 嘉義北線 |  | 1623 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1623_ABS | 1623(嘉義北線) ABS | LINE161 |  |  |  |  | CDC | 384 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | ES3 | 1623E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0606 | 0607 | 0079 | 1-35-14 | 1-35-15 | 1-4F | 嘉義北線 |  | 1623E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1623E_ES | 1623E(嘉義北線) ES | LINE161 |  |  |  |  | CDC | 385 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | ABS1 | 1541 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0608 | 0609 | 0080 | 1-36-00 | 1-36-01 | 1-50 | 柳營海線 |  | 1541 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1541_ABS | 1541(柳營海線) ABS | LINE161 |  |  |  |  | CDC | 386 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | ABS2 | 1542 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0610 | 0611 | 0081 | 1-36-02 | 1-36-03 | 1-51 | 柳營海線 |  | 1542 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1542_ABS | 1542(柳營海線) ABS | LINE161 |  |  |  |  | CDC | 387 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | ABS3 | 1543 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0612 | 0613 | 0082 | 1-36-04 | 1-36-05 | 1-52 | 柳營海線 |  | 1543 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1543_ABS | 1543(柳營海線) ABS | LINE161 |  |  |  |  | CDC | 388 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | ES3 | 1543E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0614 | 0615 | 0083 | 1-36-06 | 1-36-07 | 1-53 | 柳營海線 |  | 1543E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1543E_ES | 1543E(柳營海線) ES | LINE161 |  |  |  |  | CDC | 389 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | ABS1 | 1531 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0616 | 0617 | 0084 | 1-36-08 | 1-36-09 | 1-54 | 柳營山線 |  | 1531 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1531_ABS | 1531(柳營山線) ABS | LINE161 |  |  |  |  | CDC | 390 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | ABS2 | 1532 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0618 | 0619 | 0085 | 1-36-10 | 1-36-11 | 1-55 | 柳營山線 |  | 1532 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1532_ABS | 1532(柳營山線) ABS | LINE161 |  |  |  |  | CDC | 391 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | ABS3 | 1533 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0620 | 0621 | 0086 | 1-36-12 | 1-36-13 | 1-56 | 柳營山線 |  | 1533 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1533_ABS | 1533(柳營山線) ABS | LINE161 |  |  |  |  | CDC | 392 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | ES3 | 1533E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0622 | 0623 | 0087 | 1-36-14 | 1-36-15 | 1-57 | 柳營山線 |  | 1533E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1533E_ES | 1533E(柳營山線) ES | LINE161 |  |  |  |  | CDC | 393 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | ABS1 | 1591 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0624 | 0625 | 0088 | 1-37-00 | 1-37-01 | 1-58 | 斗工紅線 |  | 1591 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1591_ABS | 1591(斗工紅線) ABS | LINE161 |  |  |  |  | CDC | 394 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | ABS2 | 1592 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0626 | 0627 | 0089 | 1-37-02 | 1-37-03 | 1-59 | 斗工紅線 |  | 1592 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1592_ABS | 1592(斗工紅線) ABS | LINE161 |  |  |  |  | CDC | 395 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | ABS3 | 1593 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | 0629 | 0090 | 1-37-04 | 1-37-05 | 1-5A | 斗工紅線 |  | 1593 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1593_ABS | 1593(斗工紅線) ABS | LINE161 |  |  |  |  | CDC | 396 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | ES3 | 1593E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0630 | 0631 | 0091 | 1-37-06 | 1-37-07 | 1-5B | 斗工紅線 |  | 1593E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1593E_ES | 1593E(斗工紅線) ES | LINE161 |  |  |  |  | CDC | 397 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | ABS1 | 1581 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0632 | 0633 | 0092 | 1-37-08 | 1-37-09 | 1-5C | 嘉民雲林線 |  | 1581 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1581_ABS | 1581(嘉民雲林線) ABS | LINE161 |  |  |  |  | CDC | 398 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | ABS2 | 1582 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0634 | 0635 | 0093 | 1-37-10 | 1-37-11 | 1-5D | 嘉民雲林線 |  | 1582 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1582_ABS | 1582(嘉民雲林線) ABS | LINE161 |  |  |  |  | CDC | 399 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | ABS3 | 1583 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | 0637 | 0094 | 1-37-12 | 1-37-13 | 1-5E | 嘉民雲林線 |  | 1583 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1583_ABS | 1583(嘉民雲林線) ABS | LINE161 |  |  |  |  | CDC | 400 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | ES3 | 1583E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0638 | 0639 | 0095 | 1-37-14 | 1-37-15 | 1-5F | 嘉民雲林線 |  | 1583E EABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1583E_ES | 1583E(嘉民雲林線) ES | LINE161 |  |  |  |  | CDC | 401 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 0641 | 0096 | 1-38-00 | 1-38-01 | 1-60 | Locate Empty |  | 1501 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1501_DS | 1501(TIE) DS | TIE |  |  |  |  | CDC | 402 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0646 | 0647 | 0097 | 1-38-06 | 1-38-07 | 1-61 | Locate Empty |  | 1502 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1502_DS | 1502(TIE) DS | TIE |  |  |  |  | CDC | 403 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | ABS1 | 1503_ABS | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 0653 | 0098 | 1-38-12 | 1-38-13 | 1-62 | Locate Empty |  | 1503 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1503_ABS | 1503 ABS | OTHER |  |  |  |  | CDC | 404 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | BE1 | 1501BE | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0642 | 0643 |  | 1-38-02 | 1-38-03 |  | Locate Empty |  | 1501BE ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1501BE_DS | 1501BE DS | OTHER |  |  |  |  | CDC | 405 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0644 | 0645 |  | 1-38-04 | 1-38-05 |  | Locate Empty |  | 1501E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1501E_DS | 1501E DS | OTHER |  |  |  |  | CDC | 406 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS1 | 1601 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0656 | 0657 | 0100 | 1-39-00 | 1-39-01 | 1-64 | Locate Empty |  | 1601 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1601_DS | 1601(TIE) DS | TIE |  |  |  |  | CDC | 407 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | BE2 | 1502BE | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0648 | 0649 |  | 1-38-08 | 1-38-09 |  | Locate Empty |  | 1502BE ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1502BE_DS | 1502BE DS | OTHER |  |  |  |  | CDC | 408 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0650 | 0651 |  | 1-38-10 | 1-38-11 |  | Locate Empty |  | 1502E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1502E_DS | 1502E DS | OTHER |  |  |  |  | CDC | 409 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS2 | 1602 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0662 | 0663 | 0101 | 1-39-06 | 1-39-07 | 1-65 | Locate Empty |  | 1602 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1602_DS | 1602(TIE) DS | TIE |  |  |  |  | CDC | 410 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | ABS1 | 1603_ABS | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 0669 | 0102 | 1-39-12 | 1-39-13 | 1-66 | Locate Empty |  | 1603 ABS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1603_ABS | 1603 ABS | OTHER |  |  |  |  | CDC | 411 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | BE1 | 1601BE | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0658 | 0659 |  | 1-39-02 | 1-39-03 |  | Locate Empty |  | 1601BE ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1601BE_DS | 1601BE DS | OTHER |  |  |  |  | CDC | 412 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | E1 | 1601E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0660 | 0661 |  | 1-39-04 | 1-39-05 |  | Locate Empty |  | 1601E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1601E_DS | 1601E DS | OTHER |  |  |  |  | CDC | 413 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0672 | 0673 | 0104 | 1-3A-00 | 1-3A-01 | 1-68 | Locate Empty |  | 1701 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1701_DS | 1701(TIE) DS | TIE |  |  |  |  | CDC | 414 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | E2 | 1602E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0666 | 0667 |  | 1-39-10 | 1-39-11 |  | Locate Empty |  | 1602E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1602E_DS | 1602E DS | OTHER |  |  |  |  | CDC | 415 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | DS2 | 1703 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0676 | 0677 | 0105 | 1-3A-04 | 1-3A-05 | 1-69 | Locate Empty |  | 1703 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1703_DS | 1703(TIE) DS | TIE |  |  |  |  | CDC | 416 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | DS1 | 1802 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 0681 | 0106 | 1-3A-08 | 1-3A-09 | 1-6A | Locate Empty |  | 1802 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1802_DS | 1802(TIE) DS | TIE |  |  |  |  | CDC | 417 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | E1 | 1701E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0674 | 0675 |  | 1-3A-02 | 1-3A-03 |  | Locate Empty |  | 1701E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1701E_DS | 1701E DS | OTHER |  |  |  |  | CDC | 418 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1804 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 0685 | 0107 | 1-3A-12 | 1-3A-13 | 1-6B | Locate Empty |  | 1804 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1804_DS | 1804(TIE) DS | TIE |  |  |  |  | CDC | 419 | DI_TIE(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | E2 | 1703E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0678 | 0679 |  | 1-3A-06 | 1-3A-07 |  | Locate Empty |  | 1703E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1703E_DS | 1703E DS | OTHER |  |  |  |  | CDC | 420 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | DS1 | 1731 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0704 | 0705 | 0112 | 1-3C-00 | 1-3C-01 | 1-70 | 嘉惠一路 | 1731 | 1731 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1731_DS | 1731(嘉惠一路) DS | LINE161 |  |  |  |  | CDC | 421 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | E1 | 1802E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0682 | 0683 |  | 1-3A-10 | 1-3A-11 |  | Locate Empty |  | 1802E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1802E_DS | 1802E DS | OTHER |  |  |  |  | CDC | 422 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | DS2 | 1732 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0706 | 0707 | 0113 | 1-3C-02 | 1-3C-03 | 1-71 | 嘉惠一路 | 1732 | 1732 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1732_DS | 1732(嘉惠一路) DS | LINE161 |  |  |  |  | CDC | 423 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | E2 | 1804E_DS | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP | [6 empty] | 0686 | 0687 |  | 1-3A-14 | 1-3A-15 |  | Locate Empty |  | 1804E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1804E_DS | 1804E DS | OTHER |  |  |  |  | CDC | 424 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | DS3 | 1733 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0708 | 0709 | 0114 | 1-3C-04 | 1-3C-05 | 1-72 | 嘉惠一路 | 1733 | 1733 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1733_DS | 1733(嘉惠一路) DS | LINE161 |  |  |  |  | CDC | 425 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | ES3 | 1733E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0710 | 0711 | 0115 | 1-3C-06 | 1-3C-07 | 1-73 | 嘉惠一路 | 1733E | 1733E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1733E_ES | 1733E(嘉惠一路) ES | LINE161 |  |  |  |  | CDC | 426 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | DS1 | 1741 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0712 | 0713 | 0116 | 1-3C-08 | 1-3C-09 | 1-74 | 嘉惠二路 | 1741 | 1741 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1741_DS | 1741(嘉惠二路) DS | LINE161 |  |  |  |  | CDC | 427 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | DS2 | 1742 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0714 | 0715 | 0117 | 1-3C-10 | 1-3C-11 | 1-75 | 嘉惠二路 | 1742 | 1742 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1742_DS | 1742(嘉惠二路) DS | LINE161 |  |  |  |  | CDC | 428 | DI_LINE161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | DS3 | 1743 |  | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0716 | 0717 | 0118 | 1-3C-12 | 1-3C-13 | 1-76 | 嘉惠二路 | 1743 | 1743 DS AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1743_DS | 1743(嘉惠二路) DS | LINE161 |  |  |  |  | CDC | 429 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0697 |  |  | 1-3B-09 |  |  | Locate Empty |  | LOCAL/REMOTE |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161KV_RTU_S/L | 161KV RTU S/L | OTHER |  |  |  |  | CDC | 430 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | 87CFA | TONE故障 | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0698 |  |  | 1-3B-10 |  |  | 嘉惠一路 |  | 1730 音頻警報 RAOA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730_RAOA | 嘉民嘉惠一路(1730)TONE故障 | OTHER |  |  |  |  | CDC | 431 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0699 |  |  | 1-3B-11 |  |  | 嘉惠一路 |  | 1730 RY1A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730_RY1A | 嘉民嘉惠一路(1730)第一套RY故障 | OTHER |  |  |  |  | CDC | 432 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | RYFA2 |  | B2,B3,Element | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0700 |  |  | 1-3B-12 |  |  | 嘉惠一路 |  | 1730 RY2A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730_RY2A | 嘉民嘉惠一路(1730)第二套RY故障 | OTHER |  |  |  |  | CDC | 433 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | 87CFA | TONE故障 | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0701 |  |  | 1-3B-13 |  |  | 嘉惠二路 |  | 1740 音頻警報 RAOA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740_RAOA | 嘉民嘉惠二路(1740)TONE故障 | OTHER |  |  |  |  | CDC | 434 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0702 |  |  | 1-3B-14 |  |  | 嘉惠二路 |  | 1740 RY1A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740_RY1A | 嘉民嘉惠二路(1740)第一套RY故障 | OTHER |  |  |  |  | CDC | 435 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | RYFA2 |  | B2,B3,Element | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0703 |  |  | 1-3B-15 |  |  | 嘉惠二路 |  | 1740 RY2A |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740_RY2A | 嘉民嘉惠二路(1740)第二套RY故障 | OTHER |  |  |  |  | CDC | 436 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | ES3 | 1743E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0718 | 0719 | 0119 | 1-3C-14 | 1-3C-15 | 1-77 | 嘉惠二路 | 1743E | 1743E ES AS |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1743E_ES | 1743E(嘉惠二路) ES | LINE161 |  |  |  |  | CDC | 437 | DI_LINE161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0770 |  | 0128 | 2-30-02 |  | 2-00 | 1550 | U/L | 雲林山線 1550 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_79UL | 雲林山線(1550) 79RY U/L | LINE161 |  |  |  |  | CDC | 438 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0771 |  | 0129 | 2-30-03 |  | 2-01 | 1550 | U/L | 雲林山線 1550 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_87UL | 雲林山線(1550) 87RY U/L | LINE161 |  |  |  |  | CDC | 439 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0772 |  | 0130 | 2-30-04 |  | 2-02 | 1560 | U/L | 雲林海線 1560 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_79UL | 雲林海線(1560) 79RY U/L | LINE161 |  |  |  |  | CDC | 440 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0773 |  | 0131 | 2-30-05 |  | 2-03 | 1560 | U/L | 雲林海線 1560 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_87UL | 雲林海線(1560) 87RY U/L | LINE161 |  |  |  |  | CDC | 441 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0774 |  | 0132 | 2-30-06 |  | 2-04 | 北港北線 |  | 1640 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_79UL | 北港北線(1640) 79RY U/L | LINE161 |  |  |  |  | CDC | 442 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0775 |  | 0133 | 2-30-07 |  | 2-05 | 北港北線 |  | 1640 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_87UL | 北港北線(1640) 87RY U/L | LINE161 |  |  |  |  | CDC | 443 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0776 |  | 0134 | 2-30-08 |  | 2-06 | 北港南線 |  | 1630 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_79UL | 北港南線(1630) 79RY U/L | LINE161 |  |  |  |  | CDC | 444 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 161B3E | #3BUS(161B3E) |  | BE1 |  | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/3Bus |  |  |  | 0720 | 0721 |  | 1-3D-00 | 1-3D-01 |  | Locate Empty | ES | 161B3E ES AS |  | abcz | B2/E05_A1 | [8 empty] | 嘉民ES.161B3E | 161B3E | OTHER |  |  |  |  | CDC | 445 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 161B4E | #4BUS(161B4E) |  | BE2 |  | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/4Bus |  |  |  | 0722 | 0723 |  | 1-3D-02 | 1-3D-03 |  | Locate Empty | ES | 161B4E ES AS |  | abcz | B2/E05_A1 | [8 empty] | 嘉民ES.161B4E | 161B4E | OTHER |  |  |  |  | CDC | 446 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0777 |  | 0135 | 2-30-09 |  | 2-07 | 北港南線 |  | 1630 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_87UL | 北港南線(1630) 87RY U/L | LINE161 |  |  |  |  | CDC | 447 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0778 |  | 0136 | 2-30-10 |  | 2-08 | 嘉義海線 |  | 1520 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_79UL | 嘉義海線(1520) 79RY U/L | LINE161 |  |  |  |  | CDC | 448 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0779 |  | 0137 | 2-30-11 |  | 2-09 | 嘉義海線 |  | 1520 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_87UL | 嘉義海線(1520) 87RY U/L | LINE161 |  |  |  |  | CDC | 449 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0780 |  | 0138 | 2-30-12 |  | 2-0A | 嘉義山線 |  | 1510 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_79UL | 嘉義山線(1510) 79RY U/L | LINE161 |  |  |  |  | CDC | 450 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0781 |  | 0139 | 2-30-13 |  | 2-0B | 嘉義山線 |  | 1510 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_87UL | 嘉義山線(1510) 87RY U/L | LINE161 |  |  |  |  | CDC | 451 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  | 0140 | 2-30-14 |  | 2-0C | 嘉義南線 |  | 1610 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_79UL | 嘉義南線(1610) 79RY U/L | LINE161 |  |  |  |  | CDC | 452 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  | 0141 | 2-30-15 |  | 2-0D | 嘉義南線 |  | 1610 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_87UL | 嘉義南線(1610) 87RY U/L | LINE161 |  |  |  |  | CDC | 453 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0784 |  | 0142 | 2-31-00 |  | 2-0E | 嘉義北線 |  | 1620 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_79UL | 嘉義北線(1620) 79RY U/L | LINE161 |  |  |  |  | CDC | 454 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0785 |  | 0143 | 2-31-01 |  | 2-0F | 嘉義北線 |  | 1620 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_87UL | 嘉義北線(1620) 87RY U/L | LINE161 |  |  |  |  | CDC | 455 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0786 |  | 0144 | 2-31-02 |  | 2-10 | 柳營海線 |  | 1540 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_79UL | 柳營海線(1540) 79RY U/L | LINE161 |  |  |  |  | CDC | 456 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0788 |  | 0146 | 2-31-04 |  | 2-12 | 柳營山線 |  | 1530 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_79UL | 柳營山線(1530) 79RY U/L | LINE161 |  |  |  |  | CDC | 457 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0790 |  | 0148 | 2-31-06 |  | 2-14 | 斗工紅線 |  | 1590 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_79UL | 斗工紅線(1590) 79RY U/L | LINE161 |  |  |  |  | CDC | 458 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0791 |  | 0149 | 2-31-07 |  | 2-15 | 斗工紅線 |  | 1590 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_87UL | 斗工紅線(1590) 87RY U/L | LINE161 |  |  |  |  | CDC | 459 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0792 |  | 0150 | 2-31-08 |  | 2-16 | 嘉民雲林線 |  | 1580 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_79UL | 嘉民雲林線(1580) 79RY U/L | LINE161 |  |  |  |  | CDC | 460 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0793 |  | 0151 | 2-31-09 |  | 2-17 | 嘉民雲林線 |  | 1580 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_87UL | 嘉民雲林線(1580) 87RY U/L | LINE161 |  |  |  |  | CDC | 461 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 |  | 0152 | 2-32-00 |  | 2-18 | Locate Empty | 87B1S | 161KV #1BUS 87RY U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER |  |  |  |  | CDC | 462 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  | 0153 | 2-32-01 |  | 2-19 | Locate Empty | 87B2S | 161KV #2BUS 87RY U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER |  |  |  |  | CDC | 463 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 3BUS | #3BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  | 0154 | 2-32-02 |  | 2-1A | Locate Empty | 87B3S | 161KV #3BUS 87RY U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER |  |  |  |  | CDC | 464 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0833 |  | 0155 | 2-34-01 |  | 2-1B | 台嘉一路 | 185S | 1710 185 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_85U1 | 台嘉一路(1710) 85RY(M) U/L | LINE161 |  |  |  |  | CDC | 465 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0787 |  |  | 2-31-03 |  |  | 柳營海線 |  | 1540 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_87UL | 柳營海線(1540) 87RY U/L | LINE161 |  |  |  |  | CDC | 466 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0834 |  | 0156 | 2-34-02 |  | 2-1C | 台嘉一路 | 285S | 1710 285 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_85U2 | 台嘉一路(1710) 85RY(B) U/L | LINE161 |  |  |  |  | CDC | 467 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0789 |  |  | 2-31-05 |  |  | 柳營山線 |  | 1530 87 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_87UL | 柳營山線(1530) 87RY U/L | LINE161 |  |  |  |  | CDC | 468 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0835 |  | 0157 | 2-34-03 |  | 2-1D | 台嘉二路 | 185S | 1720 185 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_85U1 | 台嘉二路(1720) 85RY(M) U/L | LINE161 |  |  |  |  | CDC | 469 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | 1_87UL2 | 87UL(BA) | Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0836 |  | 0158 | 2-34-04 |  | 2-1E | 台嘉二路 | 285S | 1720 285 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_85U2 | 台嘉二路(1720) 85RY(B) U/L | LINE161 |  |  |  |  | CDC | 470 | DI_LINE161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 4BUS | #4BUS |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0803 |  | 0159 | 2-32-03 |  | 2-1F | Locate Empty | 87B4S | 161KV #4BUS 87RY U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER |  |  |  |  | CDC | 471 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0768 |  | 0168 | 2-30-00 |  | 2-28 | 嘉惠一路 |  | 1730 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1730_79UL | 嘉惠一路(1730) 79RY U/L | LINE161 |  |  |  |  | CDC | 472 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0796 |  |  | 2-31-12 |  |  | Locate Empty |  | 161KV #1BUS VUA1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS |  |  |  |  | CDC | 473 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0797 |  |  | 2-31-13 |  |  | Locate Empty |  | 161KV #2BUS VUA2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS |  |  |  |  | CDC | 474 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 3BUS | #3BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0798 |  |  | 2-31-14 |  |  | Locate Empty |  | 161KV #3BUS VUA3 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS |  |  |  |  | CDC | 475 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 4BUS | #4BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0799 |  |  | 2-31-15 |  |  | Locate Empty |  | 161KV #4BUS VUA4 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS |  |  |  |  | CDC | 476 | DI_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0769 |  | 0169 | 2-30-01 |  | 2-29 | 嘉惠二路 |  | 1740 79 U/L |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1740_79UL | 嘉惠二路(1740) 79RY U/L | LINE161 |  |  |  |  | CDC | 477 | DI_LINE161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 1024 |  | 0256 | 3-30-00 |  | 3-00 | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 嘉民ES.345KV_TEST_CB | 345KV TEST CB | OTHER |  |  |  |  | CDC | 478 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaE | B/1Bus | L/T09E032/T2 |  |  | 0256 |  | 0257 | 3-00-00 |  | 3-01 | 麥寮二路 | CB | 3510 CB AS |  | aaaa | B2/E05_C | [8 empty] | 嘉民ES.3510_CB | 3510(麥寮二路) CB | LINE345 |  |  |  |  | CDC | 479 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3520 | TIE(3520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3510 | A/3530 |  |  | 0257 |  | 0258 | 3-00-01 |  | 3-02 | #8 ATR | CB | 3520 CB AS |  | aaab | B2/E05_C | [8 empty] | 嘉民ES.3520_CB | 3520 CB | LINE345 |  |  |  |  | CDC | 480 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 2-32-04 |  |  | 嘉義山線 | 87CFA | 電驛通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_87CFA | 嘉民嘉義山線(1510)87RY通訊故障 | OTHER |  |  |  |  | CDC | 481 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 2-32-05 |  |  | 嘉義山線 | RYFA | 電驛故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1510_RYFA | 嘉民嘉義山線(1510)數位電驛故障 | OTHER |  |  |  |  | CDC | 482 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0806 |  |  | 2-32-06 |  |  | 嘉義海線 | 87CFA | 電驛通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_87CFA | 嘉民嘉義海線(1520)87RY通訊故障 | OTHER |  |  |  |  | CDC | 483 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0807 |  |  | 2-32-07 |  |  | 嘉義海線 | RYFA | 電驛故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1520_RYFA | 嘉民嘉義海線(1520)數位電驛故障 | OTHER |  |  |  |  | CDC | 484 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 2-32-08 |  |  | 柳營山線 |  | 87L 通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_87CFA | 嘉民柳營山線(1530)87RY通訊故障 | OTHER |  |  |  |  | CDC | 485 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0809 |  |  | 2-32-09 |  |  | 柳營山線 |  | 87L RY故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1530_RYFA | 嘉民柳營山線(1530)數位電驛故障 | OTHER |  |  |  |  | CDC | 486 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0810 |  |  | 2-32-10 |  |  | 柳營海線 |  | 87L 通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_87CFA | 嘉民柳營海線(1540)87RY通訊故障 | OTHER |  |  |  |  | CDC | 487 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0811 |  |  | 2-32-11 |  |  | 柳營海線 |  | 87L RY故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1540_RYFA | 嘉民柳營海線(1540)數位電驛故障 | OTHER |  |  |  |  | CDC | 488 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 2-32-12 |  |  | 1550 | A/N | 雲林山線 1550 87CFA(87L通訊故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_87CFA | 嘉民雲林山線(1550)87RY通訊故障 | OTHER |  |  |  |  | CDC | 489 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0813 |  |  | 2-32-13 |  |  | 1550 | A/N | 雲林山線 1550 RYFA(電驛故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1550_RYFA | 嘉民雲林山線(1550)數位電驛故障 | OTHER |  |  |  |  | CDC | 490 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0814 |  |  | 2-32-14 |  |  | 1560 |  | 雲林海線 1560 87CFA(87L通訊故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_87CFA | 嘉民雲林海線(1560)87RY通訊故障 | OTHER |  |  |  |  | CDC | 491 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0815 |  |  | 2-32-15 |  |  | 1560 |  | 雲林海線 1560 RYFA(電驛故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1560_RYFA | 嘉民雲林海線(1560)數位電驛故障 | OTHER |  |  |  |  | CDC | 492 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | 嘉民雲林線 | 87CFA | 嘉民雲林線1580 87Ry電驛通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_87CFA | 嘉民雲林線(1580)87RY通訊故障 | OTHER |  |  |  |  | CDC | 493 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | 嘉民雲林線 | RYFA | 嘉民雲林線1580 電驛故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1580_RYFA | 嘉民雲林線(1580)數位電驛故障 | OTHER |  |  |  |  | CDC | 494 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | 斗工紅線 | 87CFA | 電驛通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_87CFA | 嘉民斗工紅線(1590)87RY通訊故障 | OTHER |  |  |  |  | CDC | 495 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 2-33-03 |  |  | 斗工紅線 | RYFA | 電驛故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1590_RYFA | 嘉民斗工紅線(1590)數位電驛故障 | OTHER |  |  |  |  | CDC | 496 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 2-33-04 |  |  | 嘉義南線 | 1610 | 87CFA(87L通訊故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_87CFA | 嘉民嘉義南線(1610)87RY通訊故障 | OTHER |  |  |  |  | CDC | 497 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0821 |  |  | 2-33-05 |  |  | 嘉義南線 | 1610 | RYFA(電驛故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1610_RYFA | 嘉民嘉義南線(1610)數位電驛故障 | OTHER |  |  |  |  | CDC | 498 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 2-33-06 |  |  | 嘉義北線 | 87CFA | 電驛通訊故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_87CFA | 嘉民嘉義北線(1620)87RY通訊故障 | OTHER |  |  |  |  | CDC | 499 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 2-33-07 |  |  | 嘉義北線 | RYFA | 電驛故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1620_RYFA | 嘉民嘉義北線(1620)數位電驛故障 | OTHER |  |  |  |  | CDC | 500 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 2-33-08 |  |  | 北港南線 | 1630 | 87CFA(87L通訊故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_87CFA | 嘉民北港南線(1630)87RY通訊故障 | OTHER |  |  |  |  | CDC | 501 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 2-33-09 |  |  | 北港南線 | 1630 | RYFA(電驛故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1630_RYFA | 嘉民北港南線(1630)數位電驛故障 | OTHER |  |  |  |  | CDC | 502 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 2-33-10 |  |  | 北港北線 | 1640 | 87CFA(87L通訊故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_87CFA | 嘉民北港北線(1640)87RY通訊故障 | OTHER |  |  |  |  | CDC | 503 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 2-33-11 |  |  | 北港北線 | 1640 | RYFA(電驛故障) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1640_RYFA | 嘉民北港北線(1640)數位電驛故障 | OTHER |  |  |  |  | CDC | 504 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 2-33-12 |  |  | 台嘉一路 |  | 音頻警報 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_85CFA | 嘉民台嘉一路(1710)85RY通訊故障 | OTHER |  |  |  |  | CDC | 505 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0829 |  |  | 2-33-13 |  |  | 台嘉一路 |  | 85RY 故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1710_RYFA | 嘉民台嘉一線(1710)數位電驛故障 | OTHER |  |  |  |  | CDC | 506 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 2-33-14 |  |  | 台嘉二路 |  | 音頻警報 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_85CFA | 嘉民台嘉二路(1720)85RY通訊故障 | OTHER |  |  |  |  | CDC | 507 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0831 |  |  | 2-33-15 |  |  | 台嘉二路 |  | 85RY 故障 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1720_RYFA | 嘉民台嘉二線(1720)數位電驛故障 | OTHER |  |  |  |  | CDC | 508 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaM | T/8ATR345 | B/2Bus |  |  | 0258 |  | 0259 | 3-00-02 |  | 3-03 | #8 ATR | CB | 3530 CB AS |  | aaac | B2/E05_C | [8 empty] | 嘉民ES.3530_CB | 3530(#8ATR) CB | ATR |  |  |  |  | CDC | 509 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/T09E031/T2 |  |  | 0259 |  | 0260 | 3-00-03 |  | 3-04 | 麥寮一路 | CB | 3540 CB AS |  | aaba | B2/E05_C | [8 empty] | 嘉民ES.3540_CB | 3540(麥寮一路) CB | LINE345 |  |  |  |  | CDC | 510 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | L/T09E031/T2 | B/2Bus |  |  | 0261 |  | 0262 | 3-00-05 |  | 3-06 | Locate Empty | CB | 3560 CB AS |  | aabc | B2/E05_C | [8 empty] | 嘉民ES.3560_CB | 3560 CB | LINE345 |  |  |  |  | CDC | 511 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E09E032/T2 |  |  | 0262 |  | 0263 | 3-00-06 |  | 3-07 | 中寮二路 | CB | 3570 CB AS |  | aaca | B2/E05_C | [8 empty] | 嘉民ES.3570_CB | 3570(中寮二路) CB | LINE345 |  |  |  |  | CDC | 512 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0837 |  |  | 2-34-05 |  |  | Locate Empty | CB | 161KV CB COMT |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER |  |  |  |  | CDC | 513 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | BFS |  |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 2-34-06 |  |  | Locate Empty | BFS | 161KV BF U/L |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.161KV_BFS | 161KV 斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 514 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0840 |  |  | 2-34-08 |  |  | Locate Empty | 161_89A | 161KV ABS Alarm |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER |  |  |  |  | CDC | 515 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0841 |  |  | 2-34-09 |  |  | Locate Empty | 161_CBA | 161KV CB 重故障 |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.161KV_CBA | 161KV斷路器重故障 | OTHER |  |  |  |  | CDC | 516 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0842 |  |  | 2-34-10 |  |  | Locate Empty | 161_CBF | 161KV CB 輕故障 |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.161KV_CBF | 161KV斷路器輕故障 | OTHER |  |  |  |  | CDC | 517 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | StaDev | 所內設施 |  | DCA2 | 直流電源DCA(2) | B2,Element | Status | 直流電源故障2 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0843 |  |  | 2-34-11 |  |  | Locate Empty | 161_DCA | 161KV 直流電源跳脫 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.直流電源DCA(2) | 161KV直流電源跳脫警報 | OTHER |  |  |  |  | CDC | 518 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | 34B_RYFA |  | Element | Status | #3#4 BUS RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0844 |  |  | 2-34-12 |  |  | 161kV#3,4Bus | RYFA | 161kV#3,#4Bus 87B RYFA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161_SBUS_RYFA | 161KV#3,4BUS 87RY數位電驛故障 | OTHER |  |  |  |  | CDC | 519 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | 34B_CTFA |  | Element | Status | #3#4 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 2-34-13 |  |  | 161kV#3,4Bus | CTFA | 161kV#3,#4Bus CTFA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161_SBUS_CTFA | 161KV#3,4BUS 87RYCT迴路故障 | OTHER |  |  |  |  | CDC | 520 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | 12B_RYFA |  | Element | Status | #1#2 BUS RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0846 |  |  | 2-34-14 |  |  | 161kV#1,2Bus | RYFA | 161kV#1,#2Bus 87B RYFA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161_NBUS_RYFA | 161KV#1,2BUS 87RY數位電驛故障 | OTHER |  |  |  |  | CDC | 521 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | 12B_CTFA |  | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0847 |  |  | 2-34-15 |  |  | 161kV#1,2Bus | CTFA | 161kV#1,#2Bus CTFA |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161_NBUS_CTFA | 161KV#1,2BUS 87RYCT迴路故障 | OTHER |  |  |  |  | CDC | 522 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  | B2,B3,Element | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0848 |  |  | 2-35-00 |  |  | 161KV TIE | 1500 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 523 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | 50SA |  | B2,B3,Element | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0849 |  |  | 2-35-01 |  |  | 161KV TIE | 1600 | 161KV TIE (1600)50RY 測試/正常 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.1600TIE_50SA | 161KV TIE(1600) 50RY 測試/正常 | OTHER |  |  |  |  | CDC | 524 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 2-35-04 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER |  |  |  |  | CDC | 525 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | StaDev | 所內設施 |  | GRZ100 | BVS_RY | B2,Element | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 2-35-05 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.BVS_RY | 161KV #34BUS GRZ100 RY U/L | OTHER |  |  |  |  | CDC | 526 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | RYFA | 斷路器失靈電驛故障 | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0854 |  |  | 2-35-06 |  |  | 161KV | RYFA | 161KV BF RY電驛故障(RYFA) |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.161KV_BFRYFA | 161KV斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 527 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | EQA | 有感地震警報 | INSERT | [12 empty] | 0856 |  |  | 2-35-08 |  |  | Locate Empty |  |  |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.EQA | 有感地震警報 EQA | OTHER |  | PointList_NULL |  |  |  | 528 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3580 | TIE(3580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3570 | A/3590 |  |  | 0263 |  | 0264 | 3-00-07 |  | 3-08 | Locate Empty | CB | 3580 CB AS |  | aacc | B2/E05_C | [8 empty] | 嘉民ES.3580_CB | 3580 CB | LINE345 |  |  |  |  | CDC | 529 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/1ATR345 | B/2Bus |  |  | 0264 |  | 0265 | 3-01-00 |  | 3-09 | #1 ATR | CB | 3590 CB AS |  | aacc | B2/E05_C | [8 empty] | 嘉民ES.3590_CB | 3590(#1ATR) CB | ATR |  |  |  |  | CDC | 530 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1ATR161 |  | 0265 |  | 0266 | 3-01-01 |  | 3-0A | #1 ATR 二次側 | CB | 1650 CB AS |  | aaea | B3/E05_C | [8 empty] | 嘉民ES.1650_CB | 1650(#1ATR) CB | ATR |  |  |  |  | CDC | 531 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | R/1SHR | T/1ATR33 |  |  | 0416 |  | 0267 | 3-14-00 |  | 3-0B | #1 ATR 三次側 | CB | 510 CB AS |  | abab | B3/E05_C | [8 empty] | 嘉民ES.510_CB | 510 CB | OTHER |  |  |  |  | CDC | 532 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaE | B/1Bus | L/E09E031/T2 |  |  | 0266 |  | 0268 | 3-01-02 |  | 3-0C | 中寮一路 | CB | 3610 CB AS |  | aada | B2/E05_C | [8 empty] | 嘉民ES.3610_CB | 3610(中寮一路) CB | LINE345 |  |  |  |  | CDC | 533 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3620 | TIE(3620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3610 | A/3630 |  |  | 0267 |  | 0269 | 3-01-03 |  | 3-0D | Locate Empty | CB | 3620 CB AS |  | aadb | B2/E05_C | [8 empty] | 嘉民ES.3620_CB | 3620 CB | LINE345 |  |  |  |  | CDC | 534 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaM | T/2ATR345 | B/2Bus |  |  | 0268 |  | 0270 | 3-01-04 |  | 3-0E | #2 ATR | CB | 3630 CB AS |  | aadc | B2/E05_C | [8 empty] | 嘉民ES.3630_CB | 3630(#2ATR) CB | ATR |  |  |  |  | CDC | 535 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2ATR161 |  | 0269 |  | 0271 | 3-01-05 |  | 3-0F | #2 ATR 二次側 | CB | 1660 CB AS |  | aaha | B3/E05_C | [8 empty] | 嘉民ES.1660_CB | 1660(#2ATR) CB | ATR |  |  |  |  | CDC | 536 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | R/2SHR | T/2ATR33 |  |  | 0419 |  | 0272 | 3-14-03 |  | 3-10 | #2 ATR 三次側 | CB | 520 CB AS |  | acab | B3/E05_C | [8 empty] | 嘉民ES.520_CB | 520 CB | OTHER |  |  |  |  | CDC | 537 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E09E033/T2 |  |  | 0270 |  | 0273 | 3-01-06 |  | 3-11 | 中寮三路 | CB | 3640 CB AS |  | aaea | B2/E05_C | [8 empty] | 嘉民ES.3640_CB | 3640(中寮三路) CB | LINE345 |  |  |  |  | CDC | 538 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3650 | TIE(3650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3640 | A/3660 |  |  | 0271 |  | 0274 | 3-01-07 |  | 3-12 | Locate Empty | CB | 3650 CB AS |  | aaeb | B2/E05_C | [8 empty] | 嘉民ES.3650_CB | 3650 CB | LINE345 |  |  |  |  | CDC | 539 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/3ATR345 | B/2Bus |  |  | 0272 |  | 0275 | 3-02-00 |  | 3-13 | #3 ATR | CB | 3660 CB AS |  | aaec | B2/E05_C | [8 empty] | 嘉民ES.3660_CB | 3660(#3ATR) CB | ATR |  |  |  |  | CDC | 540 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3ATR161 |  | 0273 |  | 0276 | 3-02-01 |  | 3-14 | #3 ATR 二次側 | CB | 1670 CB AS |  | aaka | B3/E05_C | [8 empty] | 嘉民ES.1670_CB | 1670(#3ATR) CB | ATR |  |  |  |  | CDC | 541 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | T/3ATR33 | T/3SSTR |  |  | 0422 |  | 0277 | 3-14-06 |  | 3-15 | #3 ATR 三次側 | CB | 330 CB AS |  | adab | B3/E05_C | [8 empty] | 嘉民ES.330_CB | 330(#3SSTR) CB | OTHER |  |  |  |  | CDC | 542 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E03E02R/T1 |  |  | 0274 |  | 0278 | 3-02-02 |  | 3-16 | 龍崎紅線 | CB | 3710 CB AS |  | aafa | B2/E05_C | [8 empty] | 嘉民ES.3710_CB | 3710(龍崎紅線) CB | LINE345 |  |  |  |  | CDC | 543 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3720 | TIE(3720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3710 | A/3730 |  |  | 0275 |  | 0279 | 3-02-03 |  | 3-17 | Locate Empty | CB | 3720 CB AS |  | aafb | B2/E05_C | [8 empty] | 嘉民ES.3720_CB | 3720 CB | LINE345 |  |  |  |  | CDC | 544 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/4ATR345 | B/2Bus |  |  | 0276 |  | 0280 | 3-02-04 |  | 3-18 | #4 ATR | CB | 3730 CB AS |  | aafc | B2/E05_C | [8 empty] | 嘉民ES.3730_CB | 3730(#4ATR) CB | ATR |  |  |  |  | CDC | 545 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/4ATR161 |  | 0277 |  | 0281 | 3-02-05 |  | 3-19 | #4 ATR 二次側 | CB | 1680 CB AS |  | abda | B3/E05_C | [8 empty] | 嘉民ES.1680_CB | 1680(#4ATR) CB | ATR |  |  |  |  | CDC | 546 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 340 | #4SSTR(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | T/4ATR33 | T/4SSTR |  |  | 0424 |  | 0282 | 3-15-00 |  | 3-1A | #4 ATR 三次側 | CB | 340 CB AS |  | aeab | B3/E05_C | [8 empty] | 嘉民ES.340_CB | 340(#4SSTR) CB | OTHER |  |  |  |  | CDC | 547 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaE | B/1Bus | L/E03E011/T1 |  |  | 0278 |  | 0283 | 3-02-06 |  | 3-1B | 新南科一路 | CB | 新南科一路 3770 CB AS |  | aaga | B2/E05_C | [8 empty] | 嘉民ES.3770_CB | 3770(新南科一路) CB | LINE345 |  |  |  |  | CDC | 548 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3780 | TIE(3780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3770 | A/3790 |  |  | 0279 |  | 0284 | 3-02-07 |  | 3-1C | Locate Empty | CB | 3780 CB AS |  | aagb | B2/E05_C | [8 empty] | 嘉民ES.3780_CB | 3780 CB | LINE345 |  |  |  |  | CDC | 549 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaM | T/5ATR345 | B/2Bus |  |  | 0280 |  | 0285 | 3-03-00 |  | 3-1D | #5 ATR | CB | 3790 CB AS |  | aagc | B2/E05_C | [8 empty] | 嘉民ES.3790_CB | 3790(#5ATR) CB | ATR |  |  |  |  | CDC | 550 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/5ATR161 |  | 0281 |  | 0286 | 3-03-01 |  | 3-1E | #5 ATR 二次側 | CB | 1690 CB AS |  | abga | B3/E05_C | [8 empty] | 嘉民ES.1690_CB | 1690(#5ATR) CB | ATR |  |  |  |  | CDC | 551 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | R/5SHR | T/5ATR33 |  |  | 0426 |  | 0287 | 3-15-02 |  | 3-1F | #5 ATR 三次側 | CB | 550 CB AS |  | afab | B3/E05_C | [8 empty] | 嘉民ES.550_CB | 550 CB | OTHER |  |  |  |  | CDC | 552 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | TopDiaK | B/1Bus | L/E03E012/T1 |  |  | 0282 |  | 0288 | 3-03-02 |  | 3-20 | 新南科二路 | CB | 新南科二路3810 CB AS |  | aaha | B2/E05_C | [8 empty] | 嘉民ES.3810_CB | 3810(新南科二路) CB | LINE345 |  |  |  |  | CDC | 553 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3820 | TIE(3820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | MidDia | A/3810 | A/3830 |  |  | 0283 |  | 0289 | 3-03-03 |  | 3-21 | Locate Empty | CB | 3820 CB AS |  | aahb | B2/E05_C | [8 empty] | 嘉民ES.3820_CB | 3820 CB | LINE345 |  |  |  |  | CDC | 554 | DI_MID_345CB(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BotDiaK | T/6ATR345 | B/2Bus |  |  | 0284 |  | 0290 | 3-03-04 |  | 3-22 | #6 ATR | CB | 3830 CB AS |  | aahc | B2/E05_C | [8 empty] | 嘉民ES.3830_CB | 3830(#6ATR) CB | ATR |  |  |  |  | CDC | 555 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/6ATR161 |  | 0285 |  | 0291 | 3-03-05 |  | 3-23 | #6 ATR 二次側 | CB | 1860 CB AS |  | abja | B3/E05_C | [8 empty] | 嘉民ES.1860_CB | 1860(#6ATR) CB | ATR |  |  |  |  | CDC | 556 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | R/6SHR | T/6ATR33 |  |  | 0429 |  | 0292 | 3-15-05 |  | 3-24 | #6 ATR 三次側 | CB | 560 CB AS |  | agab | B3/E05_C | [8 empty] | 嘉民ES.560_CB | 560 CB | OTHER |  |  |  |  | CDC | 557 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0286 |  |  | 3-03-06 |  |  | Locate Empty | 87T1A | #1 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_87A1 | #1ATR 第一組 87RY | ATR |  |  |  |  | CDC | 558 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 3-03-07 |  |  | Locate Empty | 87T2A | #1 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_87A2 | #1ATR 第二組 87RY | ATR |  |  |  |  | CDC | 559 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 3-04-00 |  |  | Locate Empty | 96PA | #1 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_96PA | #1ATR 機械保護動作 | ATR |  |  |  |  | CDC | 560 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0289 |  |  | 3-04-01 |  |  | Locate Empty | 51ZA | #1 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_51ZA | #1ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 561 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0290 |  |  | 3-04-02 |  |  | Locate Empty | 59A | #1 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_59A | #1ATR 59RY | ATR |  |  |  |  | CDC | 562 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 3-04-03 |  |  | Locate Empty | 87T1A | #2 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_87A1 | #2ATR 第一組 87RY | ATR |  |  |  |  | CDC | 563 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0292 |  |  | 3-04-04 |  |  | Locate Empty | 87T2A | #2 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_87A2 | #2ATR 第二組 87RY | ATR |  |  |  |  | CDC | 564 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 3-04-05 |  |  | Locate Empty | 96PA | #2 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_96PA | #2ATR 機械保護動作 | ATR |  |  |  |  | CDC | 565 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 3-04-06 |  |  | Locate Empty | 51ZA | #2 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_51ZA | #2ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 566 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0295 |  |  | 3-04-07 |  |  | Locate Empty | 59A | #2 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_59A | #2ATR 59RY | ATR |  |  |  |  | CDC | 567 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0296 |  |  | 3-05-00 |  |  | Locate Empty | 87T1A | #3 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_87A1 | #3ATR 第一組 87RY | ATR |  |  |  |  | CDC | 568 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0297 |  |  | 3-05-01 |  |  | Locate Empty | 87T2A | #3 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_87A2 | #3ATR 第二組 87RY | ATR |  |  |  |  | CDC | 569 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0298 |  |  | 3-05-02 |  |  | Locate Empty | 96PA | #3 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_96PA | #3ATR 機械保護動作 | ATR |  |  |  |  | CDC | 570 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 3-05-03 |  |  | Locate Empty | 51ZA | #3 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_51ZA | #3ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 571 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0300 |  |  | 3-05-04 |  |  | Locate Empty | 59A | #3 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_59A | #3ATR 59RY | ATR |  |  |  |  | CDC | 572 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0301 |  |  | 3-05-05 |  |  | Locate Empty | 87T1A | #4 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_87A1 | #4ATR 第一組 87RY | ATR |  |  |  |  | CDC | 573 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 3-05-06 |  |  | Locate Empty | 87T2A | #4 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_87A2 | #4ATR 第二組 87RY | ATR |  |  |  |  | CDC | 574 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 3-05-07 |  |  | Locate Empty | 96PA | #4 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_96PA | #4ATR 機械保護動作 | ATR |  |  |  |  | CDC | 575 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0304 |  |  | 3-06-00 |  |  | Locate Empty | 51ZA | #4 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_51ZA | #4ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 576 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0305 |  |  | 3-06-01 |  |  | Locate Empty | 59A | #4 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_59A | #4ATR 59RY | ATR |  |  |  |  | CDC | 577 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 3-06-02 |  |  | Locate Empty | 87T1A | #5 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_87A1 | #5ATR 第一組 87RY | ATR |  |  |  |  | CDC | 578 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0307 |  |  | 3-06-03 |  |  | Locate Empty | 87T2A | #5 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_87A2 | #5ATR 第二組 87RY | ATR |  |  |  |  | CDC | 579 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 3-06-04 |  |  | Locate Empty | 96PA | #5 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_96PA | #5ATR 機械保護動作 | ATR |  |  |  |  | CDC | 580 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 3-06-05 |  |  | Locate Empty | 51ZA | #5 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_51ZA | #5ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 581 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0310 |  |  | 3-06-06 |  |  | Locate Empty | 59A | #5 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_59A | #5ATR 59RY | ATR |  |  |  |  | CDC | 582 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0311 |  |  | 3-06-07 |  |  | Locate Empty | 87T1A | #6 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_87A1 | #6ATR 第一組 87RY | ATR |  |  |  |  | CDC | 583 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0312 |  |  | 3-07-00 |  |  | Locate Empty | 87T2A | #6 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_87A2 | #6ATR 第二組 87RY | ATR |  |  |  |  | CDC | 584 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0313 |  |  | 3-07-01 |  |  | Locate Empty | 96PA | #6 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_96PA | #6ATR 機械保護動作 | ATR |  |  |  |  | CDC | 585 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 3-07-02 |  |  | Locate Empty | 51ZA | #6 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_51ZA | #6ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 586 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0315 |  |  | 3-07-03 |  |  | Locate Empty | 59A | #6 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_59A | #6ATR 59RY | ATR |  |  |  |  | CDC | 587 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 1BUS | #1BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0316 |  |  | 3-07-04 |  |  | Locate Empty | #1BUS | 187B1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#1B_87A1 | 345KV #1BUS 第一組 87RY | BUS |  |  |  |  | CDC | 588 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 1BUS | #1BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 3-07-05 |  |  | Locate Empty | #1BUS | 187B2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#1B_87A2 | 345KV #1BUS 第二組 87RY | BUS |  |  |  |  | CDC | 589 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 2BUS | #2BUS |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 3-07-06 |  |  | Locate Empty | #2BUS | 287B1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#2B_87A1 | 345KV #2BUS 第一組 87RY | BUS |  |  |  |  | CDC | 590 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 2BUS | #2BUS |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0319 |  |  | 3-07-07 |  |  | Locate Empty | #2BUS | 287B2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#2B_87A2 | 345KV #2BUS 第二組 87RY | BUS |  |  |  |  | CDC | 591 | DI_345KV_BUS |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | BFA |  | INSERT | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 3-08-00 |  |  | Locate Empty | BFA | 345KV BFA 斷路器失敗警報 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_BFA | 345KV斷路器失靈(BF)警報 | OTHER | [5 empty] | 592 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | OSCA |  | INSERT | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0321 |  |  | 3-08-01 |  |  | Locate Empty | ON/OFF | 345KV示波器啟動警報OSCA |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_OSCA | 345KV 示波器啟動警報 | OTHER | [5 empty] | 593 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | RCA |  | INSERT | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0322 |  |  | 3-08-02 |  |  | Locate Empty | RCA | 345KV RCA 復閉電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_RCA | 345KV 79RY(復閉) 動作 | OTHER | [5 empty] | 594 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 1_87A |  | Element | Status | 第1套87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 3-08-03 |  |  | 麥寮二路 | #1 RY | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA11 | 麥寮二路(3510) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 595 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0325 |  |  | 3-08-05 |  |  | 麥寮二路 | #2 RY | 1SSA_21_51 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA12 | 麥寮二路(3510) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 596 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 2_87A |  | INSERT | Status | 第2套87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 3-08-06 |  |  | Locate Empty | #2 RY | 2SSA_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA21 | 麥寮二路(3510) #2差流(87L)RY | LINE345 | [5 empty] | 597 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0328 |  |  | 3-09-00 |  |  | Locate Empty | #2 RY | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA22 | 麥寮二路(3510) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 598 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 3-09-01 |  |  | 麥寮一路 | #1 RY | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA11 | 麥寮一路(3540) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 599 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0331 |  |  | 3-09-03 |  |  | 麥寮一路 | #1 RY | 1SSA_21_51 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA12 | 麥寮一路(3540) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 600 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 3-09-04 |  |  | Locate Empty | #2 RY | 2SSA_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA21 | 麥寮一路(3540) #2差流(87L)RY | LINE345 |  |  |  |  | CDC | 601 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0334 |  |  | 3-09-06 |  |  | Locate Empty | #2 RY | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA22 | 麥寮一路(3540) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 602 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0335 |  |  | 3-09-07 |  |  | 中寮二路 | #1 RY | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_SSA11 | 中寮二路(3570) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 603 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 3-0A-00 |  |  | 中寮二路 | #1RY | 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_SSA12 | 中寮二路(3570) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 604 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 3-0A-01 |  |  | 中寮二路 | #2 RY | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_SSA2 | 中寮二路(3570) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 605 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 3-0A-02 |  |  | 中寮一路 | #1 RY | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_SSA11 | 中寮一路(3610) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 606 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0339 |  |  | 3-0A-03 |  |  | 中寮一路 | #1RY | 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_SSA12 | 中寮一路(3610) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 607 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0340 |  |  | 3-0A-04 |  |  | 中寮一路 | #2 RY | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_SSA2 | 中寮一路(3610) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 608 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 3-0A-05 |  |  | 中寮三路 | #1 RY | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_SSA11 | 中寮三路(3640) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 609 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0342 |  |  | 3-0A-06 |  |  | 中寮三路 | #1RY | 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_SSA12 | 中寮三路(3640) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 610 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0343 |  |  | 3-0A-07 |  |  | 中寮三路 | #2 RY | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_SSA2 | 中寮三路(3640) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 611 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 3-0B-00 |  |  | 龍崎紅線 | #1 RY | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_SSA11 | 龍崎紅線(3710) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 612 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 3-0B-01 |  |  | 龍崎紅線 | #1RY | 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_SSA12 | 龍崎紅線(3710) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 613 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0346 |  |  | 3-0B-02 |  |  | 龍崎紅線 | #2 RY | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_SSA2 | 龍崎紅線(3710) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 614 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 3-0B-03 |  |  | 新南科一路 | #1 RY | 新南科一路 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_SSA11 | 新南科一路(3770) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 615 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 3-0B-04 |  |  | 新南科一路 | #1RY | 新南科一路 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_SSA12 | 新南科一路(3770) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 616 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0349 |  |  | 3-0B-05 |  |  | 新南科一路 | #2 RY | 新南科一路 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_SSA2 | 新南科一路(3770) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 617 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | 1SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 3-0B-06 |  |  | 新南科二路 | #1 RY | 新南科二路1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_SSA11 | 新南科二路(3810) #1差流(87L)RY | LINE345 |  |  |  |  | CDC | 618 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | 1SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 3-0B-07 |  |  | 新南科二路 | #1RY | 新南科二路1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_SSA12 | 新南科二路(3810) #1測距(21)RY | LINE345 |  |  |  |  | CDC | 619 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | 2SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 3-0C-00 |  |  | 新南科二路 | #2 RY | 新南科二路2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_SSA2 | 新南科二路(3810) #2測距(21)RY | LINE345 |  |  |  |  | CDC | 620 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 3SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 3-0C-01 |  |  | Locate Empty |  | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA31 | 麥寮二路(3510) #3差流(87L)RY | LINE345 |  |  |  |  | CDC | 621 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 3SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 3-0C-02 |  |  | Locate Empty |  | 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA32 | 麥寮二路(3510) #3測距(21)RY | LINE345 |  |  |  |  | CDC | 622 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 4SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0355 |  |  | 3-0C-03 |  |  | Locate Empty |  | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_SSA4 | 麥寮二路(3510) #4測距(21)RY | LINE345 |  |  |  |  | CDC | 623 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 3SSA1 |  | Element | Status | 1SSA1 差流(87L)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0357 |  |  | 3-0C-05 |  |  | Locate Empty |  | 1SSA1_87 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA31 | 麥寮一路(3540) #3差流(87L)RY | LINE345 |  |  |  |  | CDC | 624 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 3SSA2 |  | Element | Status | 1SSA2 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0358 |  |  | 3-0C-06 |  |  | Locate Empty |  | 1SSA2_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA32 | 麥寮一路(3540) #3測距(21)RY | LINE345 |  |  |  |  | CDC | 625 | DI_LINE345(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 4SSA |  | Element | Status | 2SSA 測距(21)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0359 |  |  | 3-0C-07 |  |  | Locate Empty |  | 2SSA_21 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_SSA4 | 麥寮一路(3540) #4測距(21)RY | LINE345 |  |  |  |  | CDC | 626 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/8ATR161 |  | 0362 |  | 0293 | 3-0D-02 |  | 3-25 | #8 ATR 二次側 | CB | 1880 CB AS |  | aaba | B3/E05_C | [8 empty] | 嘉民ES.1880_CB | 1880(#8ATR) CB | ATR |  |  |  |  | CDC | 627 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0363 |  |  | 3-0D-03 |  |  | Locate Empty | 87T1A | #8 ATR 87T1A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_87A1 | #8ATR 第一組 87RY | ATR |  |  |  |  | CDC | 628 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0364 |  |  | 3-0D-04 |  |  | Locate Empty | 87T2A | #8 ATR 87T2A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_87A2 | #8ATR 第二組 87RY | ATR |  |  |  |  | CDC | 629 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0365 |  |  | 3-0D-05 |  |  | Locate Empty | 96PA | #8 ATR 機械保護動作(96PA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_96PA | #8ATR 機械保護動作 | ATR |  |  |  |  | CDC | 630 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0366 |  |  | 3-0D-06 |  |  | Locate Empty | 51ZA | #8 ATR 51ZA |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_51ZA | #8ATR 51Z(21+50,59-2,51Z) | ATR |  |  |  |  | CDC | 631 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 59A |  |  | Status | 59RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0367 |  |  | 3-0D-07 |  |  | Locate Empty | 59A | #8 ATR 59A |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_59A | #8ATR 59RY | ATR |  |  |  |  | CDC | 632 | DI_ATR345/161(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0368 |  |  | 3-0E-00 |  |  | Locate Empty | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_96P | #8ATR 96P RY | OTHER |  | CDC_Mon1_DPC |  |  | CDC | 633 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 2A7Other | EQA | Element | Status | 警報等級7動作2 | Normal/Alarm | Y | 7 | DI-SP | [6 empty] | 0369 |  |  | 3-0E-01 |  |  | Locate Empty | EQA1 | 地震檢知器(100gal)動作 |  |  | B1/E05_C | [8 empty] | 嘉民ES.#8ATR_EQA | #8ATR 地震檢知 RY 動作 | OTHER |  |  |  |  | CDC | 634 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrC | R/8SHR | T/8ATR33 |  |  | 0434 |  | 0294 | 3-16-02 |  | 3-26 | #8 ATR 三次側 | CB | 580 CB AS |  | aaab | B3/E05_C | [8 empty] | 嘉民ES.580_CB | 580 CB | OTHER |  |  |  |  | CDC | 635 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0374 |  |  | 3-0E-06 |  |  | #3ATR | 51A | #3ATR 51RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_51A | #3ATR 51RY | OTHER |  |  |  |  | CDC | 636 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0375 |  |  | 3-0E-07 |  |  | #3ATR | 86A | #3ATR 86RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_86A | #3ATR 86RY | OTHER |  |  |  |  | CDC | 637 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | RTU_MCT | MCT | Element | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0376 |  |  | 3-0F-00 |  |  | 345RTU | MCT_ SOE | 345 RTU MASTER RY SOE |  |  | B2/E05_C | [15 empty] | CDC | 638 | DI_OTHERS(2) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/3Bus | B/4Bus | T/3ATR161 |  | 0373 |  | 0295 | 3-0E-05 |  | 3-27 | #3ATR二次側 | CB | 1830 CB |  | abna | B3/E05_C | [8 empty] | 嘉民ES.1830_CB | 1830(#3ATR) CB | ATR |  |  |  |  | CDC | 639 | DI_ATR345/161(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0417 |  |  | 3-14-01 |  |  | #1 ATR 三次側 | 51A | 510 CB 51A |  |  | B3/E05_C | [8 empty] | 嘉民ES.510_PHA | 510 相間RY | OTHER |  |  |  |  | CDC | 640 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0418 |  |  | 3-14-02 |  |  | #1 ATR 三次側 | 87A | 510 CB 87A |  |  | B3/E05_C | [8 empty] | 嘉民ES.510_87A | 510 87RY | OTHER |  |  |  |  | CDC | 641 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | DS1 | 3511 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1216 | 1217 | 0296 | 3-3C-00 | 3-3C-01 | 3-28 | 3511 | DS | 3511 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3511_DS | 3511(麥寮二路) DS | LINE345 |  |  |  |  | CDC | 642 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0420 |  |  | 3-14-04 |  |  | #2 ATR 三次側 | 51A | 520 CB 51A |  |  | B3/E05_C | [8 empty] | 嘉民ES.520_PHA | 520 相間RY | OTHER |  |  |  |  | CDC | 643 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0421 |  |  | 3-14-05 |  |  | #2 ATR 三次側 | 87A | 520 CB 87A |  |  | B3/E05_C | [8 empty] | 嘉民ES.520_87A | 520 87RY | OTHER |  |  |  |  | CDC | 644 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | DS2 | 3512 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1218 | 1219 | 0297 | 3-3C-02 | 3-3C-03 | 3-29 | 3512 | DS | 3512 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3512_DS | 3512(麥寮二路) DS | LINE345 |  |  |  |  | CDC | 645 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | E2 | 3512E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1220 | 1221 | 0298 | 3-3C-04 | 3-3C-05 | 3-2A | 3512E | ES | 3512E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3512E_ES | 3512E(麥寮二路) ES | LINE345 |  |  |  |  | CDC | 646 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3520 | TIE(3520) |  | DS1 | 3521 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1222 | 1223 | 0299 | 3-3C-06 | 3-3C-07 | 3-2B | 3521 | DS | 3521 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3521_DS | 3521 DS | LINE345 |  |  |  |  | CDC | 647 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0427 |  |  | 3-15-03 |  |  | #5 ATR 三次側 | 51A | 550 CB 51A |  |  | B3/E05_C | [8 empty] | 嘉民ES.550_51A | 550 51A | OTHER |  |  |  |  | CDC | 648 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0428 |  |  | 3-15-04 |  |  | #5 ATR 三次側 | CB | 550 CB 87A |  |  | B3/E05_C | [8 empty] | 嘉民ES.550_87A | 550 87RY | OTHER |  |  |  |  | CDC | 649 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3520 | TIE(3520) |  | DS2 | 3522 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1224 | 1225 | 0300 | 3-3C-08 | 3-3C-09 | 3-2C | 3522 | DS | 3522 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3522_DS | 3522 DS | LINE345 |  |  |  |  | CDC | 650 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0430 |  |  | 3-15-06 |  |  | #6 ATR 三次側 | 51A | 560 CB 51A |  |  | B3/E05_C | [8 empty] | 嘉民ES.560_51A | 560 51A | OTHER |  |  |  |  | CDC | 651 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0431 |  |  | 3-15-07 |  |  | #6 ATR 三次側 | CB | 560 CB 87A |  |  | B3/E05_C | [8 empty] | 嘉民ES.560_87A | 560 87RY | OTHER |  |  |  |  | CDC | 652 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | 25TA |  | INSERT | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0432 |  |  | 3-16-00 |  |  | 345KV | 25TA | 自動同步校核裝置超時警報 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_25TA | 345KV 25RY 超時動作警報 | OTHER | [5 empty] | 653 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | 25PFA |  | INSERT | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0433 |  |  | 3-16-01 |  |  | 345KV | 25PFA | 自動同步校核裝置電源故障警報 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_25PFA | 345KV 25RY 電源故障警報 | OTHER | [5 empty] | 654 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | ES1 | 3531E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1226 | 1227 | 0301 | 3-3C-10 | 3-3C-11 | 3-2D | 3531E | ES | 3531E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3531E_ES | #8ATR 3531E ES | OTHER |  |  |  |  | CDC | 655 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0435 |  |  | 3-16-03 |  |  | #8 ATR 三次側 | 51A | 580 CB 51A |  |  | B3/E05_C | [8 empty] | 嘉民ES.580_51A | 580 51A | OTHER |  |  |  |  | CDC | 656 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0436 |  |  | 3-16-04 |  |  | #8 ATR 三次側 | CB | 580 CB 87A |  |  | B3/E05_C | [8 empty] | 嘉民ES.580_87A | 580 87RY | OTHER |  |  |  |  | CDC | 657 | DI_ATR_REC69(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | DS1 | 3531 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1228 | 1229 | 0302 | 3-3C-12 | 3-3C-13 | 3-2E | 3531 | DS | 3531 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3531_DS | 3531(#8ATR) DS | ATR |  |  |  |  | CDC | 658 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 310 | #1SSTR(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0438 |  |  | 3-16-06 |  |  | #1 ATR 三次側 | 51A | 310 CB 51RY |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1SSTR_51A | #1SSTR 51RY | OTHER |  |  |  |  | CDC | 659 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | DS2 | 3532 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1230 | 1231 | 0303 | 3-3C-14 | 3-3C-15 | 3-2F | 3532 | DS | 3532 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3532_DS | 3532(#8ATR) DS | ATR |  |  |  |  | CDC | 660 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 320 | #2SSTR(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0440 |  |  | 3-17-00 |  |  | #2 ATR 三次側 | 51A | 320 CB 51RY |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2SSTR_51A | #2SSTR 51RY | OTHER |  |  |  |  | CDC | 661 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | PHA1 |  | B2,B3,Element | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0441 |  |  | 3-17-01 |  |  | #3 ATR 三次側 | 151A | 330 CB #1 51RY |  |  | B3/E05_C | [8 empty] | 嘉民ES.330_151A | #3ATR 330#1 51RY | OTHER |  |  |  |  | CDC | 662 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | PHA2 |  | B2,B3,Element | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0442 |  |  | 3-17-02 |  |  | #3 ATR 三次側 | 251A | 330 CB #2 51RY |  |  | B3/E05_C | [8 empty] | 嘉民ES.330_251A | #3ATR 330#2 51RY | OTHER |  |  |  |  | CDC | 663 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | DS1 | 3541 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1232 | 1233 | 0304 | 3-3D-00 | 3-3D-01 | 3-30 | 3541 | DS | 3541 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3541_DS | 3541(麥寮一路) DS | LINE345 |  |  |  |  | CDC | 664 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 1025 |  |  | 3-30-01 |  |  | RTU |  | LOCAL/REMOTE |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_RTU_S/L | 345KV RTU S/L | OTHER |  |  |  |  | CDC | 665 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | DS2 | 3542 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1234 | 1235 | 0305 | 3-3D-02 | 3-3D-03 | 3-31 | 3542 | DS | 3542 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3542_DS | 3542(麥寮一路) DS | LINE345 |  |  |  |  | CDC | 666 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | ES2 | 3542E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1236 | 1237 | 0306 | 3-3D-04 | 3-3D-05 | 3-32 | 3542E | ES | 3542E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3542E_ES | 3542E(麥寮一路) ES | LINE345 |  |  |  |  | CDC | 667 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1028 |  |  | 3-30-04 |  |  | #1 ATR | S/L | #1 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_S/L | #1ATR OLTC S/L | ATR |  |  |  |  | CDC | 668 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | ES1 | 3561E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1242 | 1243 | 0309 | 3-3D-10 | 3-3D-11 | 3-35 | 3561E | ES | 3561E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3561E_ES | 3561E ES | LINE345 |  |  |  |  | CDC | 669 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1030 |  |  | 3-30-06 |  |  | #1 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_96B1 | #1ATR 96B1 RY | ATR |  |  |  |  | CDC | 670 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1031 |  |  | 3-30-07 |  |  | #1 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_96B2 | #1ATR 96B2 RY | ATR |  |  |  |  | CDC | 671 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1032 |  |  | 3-30-08 |  |  | #1 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_96D | #1ATR 96D RY | ATR |  |  |  |  | CDC | 672 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1033 |  |  | 3-30-09 |  |  | #1 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_96P | #1ATR 96P RY | ATR |  |  |  |  | CDC | 673 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1034 |  |  | 3-30-10 |  |  | #1 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_63Q | #1ATR 63Q RY | ATR |  |  |  |  | CDC | 674 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1035 |  |  | 3-30-11 |  |  | #1 ATR | TRF | #1 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_TRF | #1ATR 輕故障 | ATR |  |  |  |  | CDC | 675 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1036 |  |  | 3-30-12 |  |  | #1 ATR | TRA | #1 ATR 重故障 |  | a | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_TRA | #1ATR 重故障 | ATR |  |  |  |  | CDC | 676 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1037 |  |  | 3-30-13 |  |  | 510 SH.R | 96B1 | 510 SH.R 96B1 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1ATR_SHR96B1 | #1ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 677 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1038 |  |  | 3-30-14 |  |  | 510 SH.R | 96B2 | 510 SH.R 96B2 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1ATR_SHR96B2 | #1ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 678 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1039 |  |  | 3-30-15 |  |  | 510 SH.R | 96D | 510 SH.R 96D |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1ATR_SHR96D | #1ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 679 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1040 |  |  | 3-31-00 |  |  | 510 SH.R | 96P | 510 SH.R 96P |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1ATR_SHR96P | #1ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 680 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | SHRA | SHRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1041 |  |  | 3-31-01 |  |  | 510 SH.R | TRA | 510 SH.R TRA |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1ATR_SHRTRA | #1ATR 33KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 681 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | DS1 | 3561 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1244 | 1245 | 0310 | 3-3D-12 | 3-3D-13 | 3-36 | 3561 | DS | 3561 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3561_DS | 3561 DS | LINE345 |  |  |  |  | CDC | 682 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | DS2 | 3562 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1246 | 1247 | 0311 | 3-3D-14 | 3-3D-15 | 3-37 | 3562 | DS | 3562 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3562_DS | 3562 DS | LINE345 |  |  |  |  | CDC | 683 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1044 |  |  | 3-31-04 |  |  | #2 ATR | S/L | #2 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_S/L | #2ATR OLTC S/L | ATR |  |  |  |  | CDC | 684 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | DS1 | 3571 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1248 | 1249 | 0312 | 3-3E-00 | 3-3E-01 | 3-38 | 3571 | DS | 3571 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3571_DS | 3571(中寮二路) DS | LINE345 |  |  |  |  | CDC | 685 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1046 |  |  | 3-31-06 |  |  | #2 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_96B1 | #2ATR 96B1 RY | ATR |  |  |  |  | CDC | 686 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1047 |  |  | 3-31-07 |  |  | #2 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_96B2 | #2ATR 96B2 RY | ATR |  |  |  |  | CDC | 687 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1048 |  |  | 3-31-08 |  |  | #2 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_96D | #2ATR 96D RY | ATR |  |  |  |  | CDC | 688 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1049 |  |  | 3-31-09 |  |  | #2 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_96P | #2ATR 96P RY | ATR |  |  |  |  | CDC | 689 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1050 |  |  | 3-31-10 |  |  | #2 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_63Q | #2ATR 63Q RY | ATR |  |  |  |  | CDC | 690 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1051 |  |  | 3-31-11 |  |  | #2 ATR | TRF | #2 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_TRF | #2ATR 輕故障 | ATR |  |  |  |  | CDC | 691 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1052 |  |  | 3-31-12 |  |  | #2 ATR | TRA | #2 ATR 重故障 |  | a | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_TRA | #2ATR 重故障 | ATR |  |  |  |  | CDC | 692 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1053 |  |  | 3-31-13 |  |  | 520 SH.R | 96B1 | 520 SH.R 96B1 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2ATR_SHR96B1 | #2ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 693 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1054 |  |  | 3-31-14 |  |  | 520 SH.R | 96B2 | 520 SH.R 96B2 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2ATR_SHR96B2 | #2ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 694 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1055 |  |  | 3-31-15 |  |  | 520 SH.R | 96D | 520 SH.R 96D |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2ATR_SHR96D | #2ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 695 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1056 |  |  | 3-32-00 |  |  | 520 SH.R | 96P | 520 SH.R 96P |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2ATR_SHR96P | #2ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 696 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | SHRA |  | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1057 |  |  | 3-32-01 |  |  | 520 SH.R | TRA | 520 SH.R TRA |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2ATR_SHRTRA | #2ATR 33KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 697 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | DS2 | 3572 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1250 | 1251 | 0313 | 3-3E-02 | 3-3E-03 | 3-39 | 3572 | DS | 3572 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3572_DS | 3572(中寮二路) DS | LINE345 |  |  |  |  | CDC | 698 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | ES2 | 3572E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1252 | 1253 | 0314 | 3-3E-04 | 3-3E-05 | 3-3A | 3572E | ES | 3572E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3572E_ES | 3572E(中寮二路) ES | LINE345 |  |  |  |  | CDC | 699 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1060 |  |  | 3-32-04 |  |  | #3 ATR | S/L | #3 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_S/L | #3ATR OLTC S/L | ATR |  |  |  |  | CDC | 700 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3580 | TIE(3580) |  | DS1 | 3581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1254 | 1255 | 0315 | 3-3E-06 | 3-3E-07 | 3-3B | 3581 | DS | 3581 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3581_DS | 3581 DS | LINE345 |  |  |  |  | CDC | 701 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1062 |  |  | 3-32-06 |  |  | #3 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_96B1 | #3ATR 96B1 RY | ATR |  |  |  |  | CDC | 702 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1063 |  |  | 3-32-07 |  |  | #3 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_96B2 | #3ATR 96B2 RY | ATR |  |  |  |  | CDC | 703 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1064 |  |  | 3-32-08 |  |  | #3 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_96D | #3ATR 96D RY | ATR |  |  |  |  | CDC | 704 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1065 |  |  | 3-32-09 |  |  | #3 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_96P | #3ATR 96P RY | ATR |  |  |  |  | CDC | 705 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1066 |  |  | 3-32-10 |  |  | #3 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_63Q | #3ATR 63Q RY | ATR |  |  |  |  | CDC | 706 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1067 |  |  | 3-32-11 |  |  | #3 ATR | TRF | #3 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_TRF | #3ATR 輕故障 | ATR |  |  |  |  | CDC | 707 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1068 |  |  | 3-32-12 |  |  | #3 ATR | TRA | #3 ATR 重故障 |  | a | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_TRA | #3ATR 重故障 | ATR |  |  |  |  | CDC | 708 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3580 | TIE(3580) |  | DS2 | 3582 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1256 | 1257 | 0316 | 3-3E-08 | 3-3E-09 | 3-3C | 3582 | DS | 3582 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3582_DS | 3582 DS | LINE345 |  |  |  |  | CDC | 709 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | DS1 | 3591 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1258 | 1259 | 0317 | 3-3E-10 | 3-3E-11 | 3-3D | 3591 | DS | 3591 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3591_DS | 3591(#1ATR) DS | ATR |  |  |  |  | CDC | 710 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1071 |  |  | 3-32-15 |  |  | #4 ATR | S/L | #4 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_S/L | #4ATR OLTC S/L | ATR |  |  |  |  | CDC | 711 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | DS2 | 3592 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1260 | 1261 | 0318 | 3-3E-12 | 3-3E-13 | 3-3E | 3592 | DS | 3592 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3592_DS | 3592(#1ATR) DS | ATR |  |  |  |  | CDC | 712 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1073 |  |  | 3-33-01 |  |  | #4 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_96B1 | #4ATR 96B1 RY | ATR |  |  |  |  | CDC | 713 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1074 |  |  | 3-33-02 |  |  | #4 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_96B2 | #4ATR 96B2 RY | ATR |  |  |  |  | CDC | 714 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1075 |  |  | 3-33-03 |  |  | #4 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_96D | #4ATR 96D RY | ATR |  |  |  |  | CDC | 715 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1076 |  |  | 3-33-04 |  |  | #4 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_96P | #4ATR 96P RY | ATR |  |  |  |  | CDC | 716 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1077 |  |  | 3-33-05 |  |  | #4 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_63Q | #4ATR 63Q RY | ATR |  |  |  |  | CDC | 717 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1078 |  |  | 3-33-06 |  |  | #4 ATR | TRF | #4 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_TRF | #4ATR 輕故障 | ATR |  |  |  |  | CDC | 718 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1079 |  |  | 3-33-07 |  |  | #4 ATR | TRA | #4 ATR 重故障 |  | a | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_TRA | #4ATR 重故障 | ATR |  |  |  |  | CDC | 719 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | DS1 | 3611 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1262 | 1263 | 0319 | 3-3E-14 | 3-3E-15 | 3-3F | 3611 | DS | 3611 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3611_DS | 3611(中寮一路) DS | LINE345 |  |  |  |  | CDC | 720 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | DS2 | 3612 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1264 | 1265 | 0320 | 3-3F-00 | 3-3F-01 | 3-40 | 3612 | DS | 3612 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3612_DS | 3612(中寮一路) DS | LINE345 |  |  |  |  | CDC | 721 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1082 |  |  | 3-33-10 |  |  | #5 ATR | S/L | #5 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_S/L | #5ATR OLTC S/L | ATR |  |  |  |  | CDC | 722 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | E2 | 3612E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1266 | 1267 | 0321 | 3-3F-02 | 3-3F-03 | 3-41 | 3612E | ES | 3612E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3612E_ES | 3612E(中寮一路) ES | LINE345 |  |  |  |  | CDC | 723 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1084 |  |  | 3-33-12 |  |  | #5 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_96B1 | #5ATR 96B1 RY | ATR |  |  |  |  | CDC | 724 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1085 |  |  | 3-33-13 |  |  | #5 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_96B2 | #5ATR 96B2 RY | ATR |  |  |  |  | CDC | 725 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1086 |  |  | 3-33-14 |  |  | #5 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_96D | #5ATR 96D RY | ATR |  |  |  |  | CDC | 726 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1087 |  |  | 3-33-15 |  |  | #5 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_96P | #5ATR 96P RY | ATR |  |  |  |  | CDC | 727 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1088 |  |  | 3-34-00 |  |  | #5 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_63Q | #5ATR 63Q RY | ATR |  |  |  |  | CDC | 728 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1089 |  |  | 3-34-01 |  |  | #5 ATR | TRF | #5 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_TRF | #5ATR 輕故障 | ATR |  |  |  |  | CDC | 729 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1090 |  |  | 3-34-02 |  |  | #5 ATR | TRA | #5 ATR 重故障 |  | a | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_TRA | #5ATR 重故障 | ATR |  |  |  |  | CDC | 730 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1091 |  |  | 3-34-03 |  |  | 550 SH.R | 96B1 | 550 SH.R 96B1 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#5ATR_SHR96B1 | #5ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 731 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1092 |  |  | 3-34-04 |  |  | 550 SH.R | 96B2 | 550 SH.R 96B2 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#5ATR_SHR96B2 | #5ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 732 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1093 |  |  | 3-34-05 |  |  | 550 SH.R | 96D | 550 SH.R 96D |  |  | B3/E05_C | [8 empty] | 嘉民ES.#5ATR_SHR96D | #5ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 733 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1094 |  |  | 3-34-06 |  |  | 550 SH.R | 96P | 550 SH.R 96P |  |  | B3/E05_C | [8 empty] | 嘉民ES.#5ATR_SHR96P | #5ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 734 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | SHRA | SHRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1095 |  |  | 3-34-07 |  |  | 550 SH.R | TRA | 550 SH.R TRA |  |  | B3/E05_C | [8 empty] | 嘉民ES.#5ATR_SHRTRA | #5ATR 33KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 735 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3620 | TIE(3620) |  | DS1 | 3621 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1268 | 1269 | 0322 | 3-3F-04 | 3-3F-05 | 3-42 | 3621 | DS | 3621 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3621_DS | 3621 DS | LINE345 |  |  |  |  | CDC | 736 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3620 | TIE(3620) |  | DS2 | 3622 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1270 | 1271 | 0323 | 3-3F-06 | 3-3F-07 | 3-43 | 3622 | DS | 3622 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3622_DS | 3622 DS | LINE345 |  |  |  |  | CDC | 737 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1098 |  |  | 3-34-10 |  |  | #6 ATR | S/L | #6 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_S/L | #6ATR OLTC S/L | ATR |  |  |  |  | CDC | 738 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | DS1 | 3631 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1272 | 1273 | 0324 | 3-3F-08 | 3-3F-09 | 3-44 | 3631 | DS | 3631 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3631_DS | 3631(#2ATR) DS | ATR |  |  |  |  | CDC | 739 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1100 |  |  | 3-34-12 |  |  | #6 ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_96B1 | #6ATR 96B1 RY | ATR |  |  |  |  | CDC | 740 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1101 |  |  | 3-34-13 |  |  | #6 ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_96B2 | #6ATR 96B2 RY | ATR |  |  |  |  | CDC | 741 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1102 |  |  | 3-34-14 |  |  | #6 ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_96D | #6ATR 96D RY | ATR |  |  |  |  | CDC | 742 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1103 |  |  | 3-34-15 |  |  | #6 ATR | 96P | 本體突壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_96P | #6ATR 96P RY | ATR |  |  |  |  | CDC | 743 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1104 |  |  | 3-35-00 |  |  | #6 ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_63Q | #6ATR 63Q RY | ATR |  |  |  |  | CDC | 744 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1105 |  |  | 3-35-01 |  |  | #6 ATR | TRF | #6 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_TRF | #6ATR 輕故障 | ATR |  |  |  |  | CDC | 745 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1106 |  |  | 3-35-02 |  |  | #6 ATR | TRA | #6 ATR 重故障 |  | a | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_TRA | #6ATR 重故障 | ATR |  |  |  |  | CDC | 746 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1107 |  |  | 3-35-03 |  |  | 560 SH.R | 96B1 | 560 SH.R 96B1 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#6ATR_SHR96B1 | #6ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 747 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1108 |  |  | 3-35-04 |  |  | 560 SH.R | 96B2 | 560 SH.R 96B2 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#6ATR_SHR96B2 | #6ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 748 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1109 |  |  | 3-35-05 |  |  | 560 SH.R | 96D | 560 SH.R 96D |  |  | B3/E05_C | [8 empty] | 嘉民ES.#6ATR_SHR96D | #6ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 749 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1110 |  |  | 3-35-06 |  |  | 560 SH.R | 96P | 560 SH.R 96P |  |  | B3/E05_C | [8 empty] | 嘉民ES.#6ATR_SHR96P | #6ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 750 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | SHRA | SHRTRA | B2,Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1111 |  |  | 3-35-07 |  |  | 560 SH.R | TRA | 560 SH.R TRA |  |  | B3/E05_C | [8 empty] | 嘉民ES.#6ATR_SHRTRA | #6ATR 33KV 電抗器 重故障 | OTHER |  |  |  |  | CDC | 751 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | DS2 | 3632 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1274 | 1275 | 0325 | 3-3F-10 | 3-3F-11 | 3-45 | 3632 | DS | 3632 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3632_DS | 3632(#2ATR) DS | ATR |  |  |  |  | CDC | 752 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | DS1 | 3641 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1280 | 1281 | 0326 | 4-30-00 | 4-30-01 | 3-46 | 3641 | DS | 3641 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3641_DS | 3641(中寮三路) DS | LINE345 |  |  |  |  | CDC | 753 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | DS2 | 3642 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1282 | 1283 | 0327 | 4-30-02 | 4-30-03 | 3-47 | 3642 | DS | 3642 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3642_DS | 3642(中寮三路) DS | LINE345 |  |  |  |  | CDC | 754 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | ES2 | 3642E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1284 | 1285 | 0328 | 4-30-04 | 4-30-05 | 3-48 | 3642E | ES | 3642E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3642E_ES | 3642E(中寮三路) ES | LINE345 |  |  |  |  | CDC | 755 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | BFS |  |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1116 |  |  | 3-35-12 |  |  | 345KV | BF-S | 345KV BFS |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_BFS | 345KV 斷路器失靈RY U/L | OTHER |  |  |  |  | CDC | 756 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | CBA |  | INSERT | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1117 |  |  | 3-35-13 |  |  | 345KV | CBA | 345KV CB 重故障 |  |  | ELEM/E05_C | [8 empty] | 嘉民ES.345KV_CBA | 345KV 斷路器重故障 | OTHER | [5 empty] | 757 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | CBF |  | INSERT | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1118 |  |  | 3-35-14 |  |  | 345KV | CBF | 345KV CB 輕故障 |  |  | ELEM/E05_C | [8 empty] | 嘉民ES.345KV_CBF | 345KV 斷路器輕故障 | OTHER | [5 empty] | 758 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | COMT |  | INSERT | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1119 |  |  | 3-35-15 |  |  | 345KV | COMT | 345KV COMT 空壓機運轉超時警報 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_COMT | 345KV 空壓機運轉超時警報 | OTHER | [5 empty] | 759 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | ComPoint |  |  | CBA |  | Element | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1120 |  |  | 3-36-00 |  |  | 33KV | CBA | 33KV CB 重故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.33KV_CBA | 33KV CB 重故障 | OTHER |  |  |  |  | CDC | 760 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1121 |  |  | 3-36-01 |  |  | 33KV | CBF | 33KV CB 輕故障 |  |  | ELEM/E05_C | [8 empty] | 嘉民ES.33KV_CBF | 33KV CB 輕故障 | OTHER |  |  |  |  | CDC | 761 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1122 |  |  | 3-36-02 |  |  | 33KV | COMT | 33KV COMT 空壓機運轉超時警報 |  |  | B2/E05_C | [8 empty] | 嘉民ES.33KV_COMT | 33KV 空壓機警報 | OTHER |  |  |  |  | CDC | 762 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | RYFA | BF RY電驛故障 | Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1123 |  |  | 3-36-03 |  |  | 345KV | RYFA | 345KVBF RY電驛故障(RYFA) |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_BFRYFA | 345KV斷路器失靈電驛故障 | OTHER |  |  |  |  | CDC | 763 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3650 | TIE(3650) |  | DS1 | 3651 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1286 | 1287 | 0329 | 4-30-06 | 4-30-07 | 3-49 | 3651 | DS | 3651 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3651_DS | 3651 DS | LINE345 |  |  |  |  | CDC | 764 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 87CFA1 |  | B2,B3,Element | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1126 |  |  | 3-36-06 |  |  | 3510 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_87CFA(1) | 麥寮二路(3510)#1 87RY通訊故障 | OTHER |  |  |  |  | CDC | 765 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1127 |  |  | 3-36-07 |  |  | 3510 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_RYFA11 | 麥寮二路(3510) 第一套87RY故障 | LINE345 |  |  |  |  | CDC | 766 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 85CFA1 |  | B2,B3,Element | Status | 第1具85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1128 |  |  | 3-36-08 |  |  | 3510 | #2RY | 第二套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_85CFA(1) | 麥寮二路(3510)#2 87RY通訊故障 | OTHER |  |  |  |  | CDC | 767 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1129 |  |  | 3-36-09 |  |  | 3510 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_RYFA12 | 麥寮二路(3510) 第一套21RY故障 | LINE345 |  |  |  |  | CDC | 768 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3650 | TIE(3650) |  | DS2 | 3652 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1288 | 1289 | 0330 | 4-30-08 | 4-30-09 | 3-4A | 3652 | DS | 3652 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3652_DS | 3652 DS | LINE345 |  |  |  |  | CDC | 769 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | DS1 | 3661 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1290 | 1291 | 0331 | 4-30-10 | 4-30-11 | 3-4B | 3661 | DS | 3661 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3661_DS | 3661(#3ATR) DS | ATR |  |  |  |  | CDC | 770 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 87CFA1 |  | B2,B3,Element | Status | 第1具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1136 |  |  | 3-37-00 |  |  | 3540 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_87CFA(1) | 麥寮一路(3540)#1 87RY通訊故障 | OTHER |  |  |  |  | CDC | 771 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1137 |  |  | 3-37-01 |  |  | 3540 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_RYFA11 | 麥寮一路(3540) 第一套87RY故障 | LINE345 |  |  |  |  | CDC | 772 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 85CFA1 |  | B2,B3,Element | Status | 第1具85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1138 |  |  | 3-37-02 |  |  | 3540 | #2RY | 第二套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_85CFA(1) | 麥寮一路(3540)#2 87RY通訊故障 | OTHER |  |  |  |  | CDC | 773 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1139 |  |  | 3-37-03 |  |  | 3540 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_RYFA12 | 麥寮一路(3540) 第一套21RY故障 | LINE345 |  |  |  |  | CDC | 774 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | DS2 | 3662 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1292 | 1293 | 0332 | 4-30-12 | 4-30-13 | 3-4C | 3662 | DS | 3662 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3662_DS | 3662(#3ATR) DS | ATR |  |  |  |  | CDC | 775 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 87CFA2 |  | B2,B3,Element | Status | 第2具87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1141 |  |  | 3-37-05 |  |  | 3560 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_87CFA(2) | 麥寮一路(3560)#1 87RY通訊故障 | OTHER |  |  |  |  | CDC | 776 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1142 |  |  | 3-37-06 |  |  | 3560 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_RYFA21 | 麥寮一路(3540) 第二套87RY故障 | LINE345 |  |  |  |  | CDC | 777 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 85CFA2 |  | B2,B3,Element | Status | 第2具85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1143 |  |  | 3-37-07 |  |  | 3560 | #2RY | 第二套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_85CFA(2) | 麥寮一路(3560)#2 87RY通訊故障 | OTHER |  |  |  |  | CDC | 778 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1144 |  |  | 3-37-08 |  |  | 3560 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_RYFA22 | 麥寮一路(3540) 第二套21RY故障 | LINE345 |  |  |  |  | CDC | 779 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | DS1 | 3711 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1294 | 1295 | 0333 | 4-30-14 | 4-30-15 | 3-4D | 3711 | DS | 3711 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3711_DS | 3711(龍崎紅線) DS | LINE345 |  |  |  |  | CDC | 780 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1146 |  |  | 3-37-10 |  |  | 3570 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_87CFA | 中寮二路(3570) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 781 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1147 |  |  | 3-37-11 |  |  | 3570 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_RYFA1 | 中寮二路(3570) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 782 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1148 |  |  | 3-37-12 |  |  | 3570 | #2RY | 第二套音頻機組 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_85CFA | 中寮二路(3570) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 783 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1149 |  |  | 3-37-13 |  |  | 3570 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_RYFA2 | 中寮二路(3570) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 784 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | DS2 | 3712 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1296 | 1297 | 0334 | 4-31-00 | 4-31-01 | 3-4E | 3712 | DS | 3712 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3712_DS | 3712(龍崎紅線) DS | LINE345 |  |  |  |  | CDC | 785 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1151 |  |  | 3-37-15 |  |  | 3610 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_87CFA | 中寮一路(3610) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 786 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1152 |  |  | 3-38-00 |  |  | 3610 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_RYFA1 | 中寮一路(3610) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 787 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1153 |  |  | 3-38-01 |  |  | 3610 | #2RY | 第二套音頻機組 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_85CFA | 中寮一路(3610) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 788 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1154 |  |  | 3-38-02 |  |  | 3610 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_RYFA2 | 中寮一路(3610) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 789 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | ES2 | 3712E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1298 | 1299 | 0335 | 4-31-02 | 4-31-03 | 3-4F | 3712E | ES | 3712E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3712E_ES | 3712E(龍崎紅線) ES | LINE345 |  |  |  |  | CDC | 790 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1156 |  |  | 3-38-04 |  |  | 3640 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_87CFA | 中寮三路(3640) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 791 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1157 |  |  | 3-38-05 |  |  | 3640 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_RYFA1 | 中寮三路(3640) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 792 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1158 |  |  | 3-38-06 |  |  | 3640 | #2RY | 第二套音頻機組 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_85CFA | 中寮三路(3640) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 793 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1159 |  |  | 3-38-07 |  |  | 3640 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_RYFA2 | 中寮三路(3640) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 794 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3720 | TIE(3720) |  | DS1 | 3721 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1300 | 1301 | 0336 | 4-31-04 | 4-31-05 | 3-50 | 3721 | DS | 3721 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3721_DS | 3721 DS | LINE345 |  |  |  |  | CDC | 795 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1161 |  |  | 3-38-09 |  |  | 3710 | #1RY | 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_87CFA | 龍崎紅線(3710) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 796 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1162 |  |  | 3-38-10 |  |  | 3710 | #1RY | 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_RYFA1 | 龍崎紅線(3710) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 797 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1163 |  |  | 3-38-11 |  |  | 3710 | #2RY | 第二套音頻機組 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_85CFA | 龍崎紅線(3710) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 798 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1164 |  |  | 3-38-12 |  |  | 3710 | #2RY | 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_RYFA2 | 龍崎紅線(3710) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 799 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3720 | TIE(3720) |  | DS2 | 3722 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1302 | 1303 | 0337 | 4-31-06 | 4-31-07 | 3-51 | 3722 | DS | 3722 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3722_DS | 3722 DS | LINE345 |  |  |  |  | CDC | 800 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1166 |  |  | 3-38-14 |  |  | 3770 | #1RY | 新南科一路 第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_87CFA | 新南科一路(3770) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 801 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1167 |  |  | 3-38-15 |  |  | 3770 | #1RY | 新南科一路 第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_RYFA1 | 新南科一路(3770) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 802 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1168 |  |  | 3-39-00 |  |  | 3770 | #2RY | 新南科一路 第二套音頻機組 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_85CFA | 新南科一路(3770) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 803 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1169 |  |  | 3-39-01 |  |  | 3770 | #2RY | 新南科一路 第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_RYFA2 | 新南科一路(3770) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 804 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | DS1 | 3731 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1304 | 1305 | 0338 | 4-31-08 | 4-31-09 | 3-52 | 3731 | DS | 3731 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3731_DS | 3731(#4ATR) DS | ATR |  |  |  |  | CDC | 805 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | 87CFA |  | B2,B3,Element | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1171 |  |  | 3-39-03 |  |  | 3810 | #1RY | 新南科二路第一套87L通訊故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_87CFA | 新南科二路(3810) 87RY通訊故障 | OTHER |  |  |  |  | CDC | 806 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | RYFA1 |  |  | Status | 第1具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1172 |  |  | 3-39-04 |  |  | 3810 | #1RY | 新南科二路第一套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_RYFA1 | 新南科二路(3810) 第一套RY故障 | LINE345 |  |  |  |  | CDC | 807 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | 85CFA |  | B2,B3,Element | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1173 |  |  | 3-39-05 |  |  | 3810 | #2RY | 新南科二路第二套音頻機組 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_85CFA | 新南科二路(3810) 85RY通訊故障 | OTHER |  |  |  |  | CDC | 808 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | RYFA2 |  |  | Status | 第2具RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1174 |  |  | 3-39-06 |  |  | 3810 | #2RY | 新南科二路第二套 RY 故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_RYFA2 | 新南科二路(3810) 第二套RY故障 | LINE345 |  |  |  |  | CDC | 809 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | DS2 | 3732 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1306 | 1307 | 0339 | 4-31-10 | 4-31-11 | 3-53 | 3732 | DS | 3732 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3732_DS | 3732(#4ATR) DS | ATR |  |  |  |  | CDC | 810 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | DS1 | 3771 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1308 | 1309 | 0340 | 4-31-12 | 4-31-13 | 3-54 | 3771 | DS | 新南科一路 3771 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3771_DS | 3771(新南科一路) DS | LINE345 |  |  |  |  | CDC | 811 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | DS2 | 3772 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1310 | 1311 | 0341 | 4-31-14 | 4-31-15 | 3-55 | 3772 | DS | 新南科一路 3772 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3772_DS | 3772(新南科一路) DS | LINE345 |  |  |  |  | CDC | 812 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1178 |  |  | 3-39-10 |  |  | Locate Empty |  | 門禁 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.無人化門禁(1) | 無人化門禁(1) | OTHER |  |  |  |  | CDC | 813 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | OPEN/CLOSE | CLOSE
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | AIRCON | 空調機故障 | Element | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1179 |  |  | 3-39-11 |  |  | Locate Empty |  | 冷氣空調故障 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.空調機故障 | 空調機故障或電源跳脫 | OTHER |  |  |  |  | CDC | 814 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1180 |  |  | 3-39-12 |  |  | 洩油池警報 |  | 液面過高 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.洩油池水位警報 | 洩油池水位警報 | OTHER |  |  |  |  | CDC | 815 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Water1 | 地下室水位0.5M | Element | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1181 |  |  | 3-39-13 |  |  | 水位輕故障 |  | 地下室水位0.5M |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.水位警報(1) | 地下室水位0.5M警報 | OTHER |  |  |  |  | CDC | 816 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Water2 | 地下室水位1M | Element | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1182 |  |  | 3-39-14 |  |  | 水位重故障 |  | 地下室水位1M |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.水位警報(2) | 地下室水位1M警報 | OTHER |  |  |  |  | CDC | 817 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | STUV2 | ACB3,ACB4,ACBT2所內電源欠壓 | Element | Status | 所內電源欠壓2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1183 |  |  | 3-39-15 |  |  | SSTR | STUVA | ACB3,ACB4,ACB TIE2 所內電源欠壓警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源欠壓2 | ACB3,ACB4,ACBT2所內電源欠壓 | OTHER |  |  |  |  | CDC | 818 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1184 |  |  | 3-3A-00 |  |  | 充電機 | CHG1-1 | #1 充電機警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.直流充電機故障 | 變電所#1直流充電機故障 | OTHER |  |  |  |  | CDC | 819 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1185 |  |  | 3-3A-01 |  |  | CHG2(SP) |  | 通訊室充電機警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.通訊充電機故障 | 變電所通訊充電機故障 | OTHER |  |  |  |  | CDC | 820 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1186 |  |  | 3-3A-02 |  |  | 345KV | DCE | 直流接地故障警報 |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.直流電源DCE | 345KV直流接地故障警報 | OTHER |  |  |  |  | CDC | 821 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1187 |  |  | 3-3A-03 |  |  | 345KV | DCA | 直流電源故障警報 |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.直流電源DCA | 345KV直流電源故障警報 | OTHER |  |  |  |  | CDC | 822 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Fire |  | Element | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1188 |  |  | 3-3A-04 |  |  | COF |  | 消防警報 |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.COF | 消防警報 | OTHER |  |  |  |  | CDC | 823 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1194 |  |  | 3-3A-10 |  |  | ACFA(SP) |  | 通訊設備AC故障 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.通訊設備AC故障 | 通訊設備AC故障 | OTHER |  |  |  |  | CDC | 824 | DI_OTHERS(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1196 |  |  | 3-3A-12 |  |  | OSCF | ON/OFF | 345KV示波器缺紙或故障警報OSCF |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KV_OSCF | 345KV 示波器故障/缺紙 | OTHER |  |  |  |  | CDC | 825 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | R_Temp1 | 電驛室溫度 | Element | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1197 |  |  | 3-3A-13 |  |  | 靜態電驛室 |  | 電驛室溫度警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.電驛室溫度 | 電驛室溫度警報 | OTHER |  |  |  |  | CDC | 826 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | R_Temp | 通訊室溫度 | Element | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1198 |  |  | 3-3A-14 |  |  | 通訊室 |  | 通訊室溫度警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.通訊室溫度 | 通訊室溫度警報 | OTHER |  |  |  |  | CDC | 827 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACBA2 | ACB3,ACB4,ACBT2所內電源故障 | Element | Status | 第二套所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1199 |  |  | 3-3A-15 |  |  | SSTR | ACBA | ACB3,ACB4,ACB TIE2所內電源故障警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACB(2) | ACB3,ACB4,ACBT2所內電源故障 | OTHER |  |  |  |  | CDC | 828 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | E2 | 3772E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1312 | 1313 | 0342 | 4-32-00 | 4-32-01 | 3-56 | 3772E | ES | 新南科一路 3772E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3772E_ES | 3772E(新南科一路) ES | LINE345 |  |  |  |  | CDC | 829 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3780 | TIE(3780) |  | DS1 | 3781 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1314 | 1315 | 0343 | 4-32-02 | 4-32-03 | 3-57 | 3781 | DS | 3781 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3781_DS | 3781 DS | LINE345 |  |  |  |  | CDC | 830 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3780 | TIE(3780) |  | DS2 | 3782 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1316 | 1317 | 0344 | 4-32-04 | 4-32-05 | 3-58 | 3782 | DS | 3782 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3782_DS | 3782 DS | LINE345 |  |  |  |  | CDC | 831 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | DS1 | 3791 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1318 | 1319 | 0345 | 4-32-06 | 4-32-07 | 3-59 | 3791 | DS | 3791 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3791_DS | 3791(#5ATR) DS | ATR |  |  |  |  | CDC | 832 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | DS2 | 3792 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1320 | 1321 | 0346 | 4-32-08 | 4-32-09 | 3-5A | 3792 | DS | 3792 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3792_DS | 3792(#5ATR) DS | ATR |  |  |  |  | CDC | 833 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | DS1 | 3811 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1322 | 1323 | 0347 | 4-32-10 | 4-32-11 | 3-5B | 3811 | DS | 新南科二路3811 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3811_DS | 3811(新南科二路) DS | LINE345 |  |  |  |  | CDC | 834 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | DS2 | 3812 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1324 | 1325 | 0348 | 4-32-12 | 4-32-13 | 3-5C | 3812 | DS | 新南科二路3812 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3812_DS | 3812(新南科二路) DS | LINE345 |  |  |  |  | CDC | 835 | DI_LINE345(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | ES2 | 3812E |  | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1326 | 1327 | 0349 | 4-32-14 | 4-32-15 | 3-5D | 3812E | ES | 新南科二路3812E ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3812E_ES | 3812E(新南科二路) ES | LINE345 |  |  |  |  | CDC | 836 | DI_LINE345(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3820 | TIE(3820) |  | DS1 | 3821 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1328 | 1329 | 0350 | 4-33-00 | 4-33-01 | 3-5E | 3821 | DS | 3821 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3821_DS | 3821 DS | LINE345 |  |  |  |  | CDC | 837 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | CHG1_1 | #2充電機故障 | Element | Status | #1 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1209 |  |  | 3-3B-09 |  |  | 充電機 | CHG1-2 | #2 充電機警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.#2充電機故障 | 變電所#2直流充電機故障 | OTHER |  |  |  |  | CDC | 838 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | CHG1_2 | #3充電機故障 | Element | Status | #2 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1210 |  |  | 3-3B-10 |  |  | 充電機 | CHG1-3 | #3 充電機警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.#3充電機故障 | 變電所#3直流充電機故障 | OTHER |  |  |  |  | CDC | 839 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1211 |  |  | 3-3B-11 |  |  | Locate Empty |  | Power Meter 故障警報 PMA |  |  | ELEM/E05_A1 | [8 empty] | 嘉民ES.PMA | 電力量測表計警報 | OTHER |  |  |  |  | CDC | 840 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | 12B_RYFA1 | #1,2BUS 第一套數位RY故障 | [13 empty] | 1212 |  |  | 3-3B-12 |  |  | Locate Empty | RYFA1 | 345kV #1,2Bus RYFA第一套 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KVBUS_RYFA1 | 345KV #1,2BUS 第一套數位RY故障 | OTHER |  |  |  |  | CDC | 841 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | 87CTFA1 | CTFA1 | Element | Status | 第1具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1213 |  |  | 3-3B-13 |  |  | Locate Empty | CTFA1 | 345kV #1,2Bus CTFA第一套 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KVBUS_CTFA1 | 345KV #1,2BUS 第一套CT回路故障 | OTHER |  |  |  |  | CDC | 842 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | 12B_RYFA2 | #1,2BUS 第二套數位RY故障 | [13 empty] | 1214 |  |  | 3-3B-14 |  |  | Locate Empty | RYFA2 | 345kV #1,2Bus RYFA第二套 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KVBUS_RYFA2 | 345KV #1,2BUS 第二套數位RY故障 | OTHER |  |  |  |  | CDC | 843 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | ComPoint |  |  | 87CTFA2 | CTFA2 | Element | Status | 第2具87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1215 |  |  | 3-3B-15 |  |  | Locate Empty | CTFA2 | 345kV #1,2Bus CTFA第二套 |  |  | B2/E05_C | [8 empty] | 嘉民ES.345KVBUS_CTFA2 | 345KV #1,2BUS 第二套CT回路故障 | OTHER |  |  |  |  | CDC | 844 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3820 | TIE(3820) |  | DS2 | 3822 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1330 | 1331 | 0351 | 4-33-02 | 4-33-03 | 3-5F | 3822 | DS | 3822 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3822_DS | 3822 DS | LINE345 |  |  |  |  | CDC | 845 | DI_MID_345CB(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | DS1 | 3831 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1332 | 1333 | 0352 | 4-33-04 | 4-33-05 | 3-60 | 3831 | DS | 3831 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3831_DS | 3831(#6ATR) DS | ATR |  |  |  |  | CDC | 846 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | DS2 | 3832 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1334 | 1335 | 0353 | 4-33-06 | 4-33-07 | 3-61 | 3832 | DS | 3832 DS AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3832_DS | 3832(#6ATR) DS | ATR |  |  |  |  | CDC | 847 | DI_ATR345/161(5) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | DS1 | 1651 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1336 | 1337 | 0354 | 4-33-08 | 4-33-09 | 3-62 | 1651 | DS | 1651 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1651_ABS | 1651(#1ATR) ABS | ATR |  |  |  |  | CDC | 848 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | DS2 | 1652 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1338 | 1339 | 0355 | 4-33-10 | 4-33-11 | 3-63 | 1652 | DS | 1652 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1652_ABS | 1652(#1ATR) ABS | ATR |  |  |  |  | CDC | 849 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | DS1 | 511 | B3 | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1340 | 1341 | 0356 | 4-33-12 | 4-33-13 | 3-64 | 511 | ABS | 511 ABS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.511_ABS | 511 ABS | OTHER |  |  |  |  | CDC | 850 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | DS1 | 1661 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1342 | 1343 | 0357 | 4-33-14 | 4-33-15 | 3-65 | 1661 | DS | 1661 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1661_ABS | 1661(#2ATR) ABS | ATR |  |  |  |  | CDC | 851 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | DS2 | 1662 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1344 | 1345 | 0358 | 4-34-00 | 4-34-01 | 3-66 | 1662 | DS | 1662 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1662_ABS | 1662(#2ATR) ABS | ATR |  |  |  |  | CDC | 852 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | DS1 | 521 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1346 | 1347 | 0359 | 4-34-02 | 4-34-03 | 3-67 | 521 | ABS | 521 ABS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.521_ABS | 521 ABS | OTHER |  |  |  |  | CDC | 853 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | DS1 | 1671 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1348 | 1349 | 0360 | 4-34-04 | 4-34-05 | 3-68 | 1671 | DS | 1671 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1671_ABS | 1671(#3ATR) ABS | ATR |  |  |  |  | CDC | 854 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | DS2 | 1672 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1350 | 1351 | 0361 | 4-34-06 | 4-34-07 | 3-69 | 1672 | DS | 1672 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1672_ABS | 1672(#3ATR) ABS | ATR |  |  |  |  | CDC | 855 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | DS1 | 331_ABS | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1352 | 1353 | 0362 | 4-34-08 | 4-34-09 | 3-6A | 331 | DS | 331 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.331_ABS | 331 ABS | OTHER |  |  |  |  | CDC | 856 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | DS1 | 1681 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1354 | 1355 | 0363 | 4-34-10 | 4-34-11 | 3-6B | 1681 | DS | 1681 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1681_ABS | 1681(#4ATR) ABS | ATR |  |  |  |  | CDC | 857 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | DS2 | 1682 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1356 | 1357 | 0364 | 4-34-12 | 4-34-13 | 3-6C | 1682 | DS | 1682 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1682_ABS | 1682(#4ATR) ABS | ATR |  |  |  |  | CDC | 858 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 340 | #4SSTR(340) |  | DS1 | 341_ABS | B2,B3,Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1358 | 1359 | 0365 | 4-34-14 | 4-34-15 | 3-6D | 341 | DS | 341 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.341_ABS | 341 ABS | OTHER |  |  |  |  | CDC | 859 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | DS1 | 1691 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1360 | 1361 | 0366 | 4-35-00 | 4-35-01 | 3-6E | 1691 | DS | 1691 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1691_ABS | 1691(#5ATR) ABS | ATR |  |  |  |  | CDC | 860 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | DS2 | 1692 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1362 | 1363 | 0367 | 4-35-02 | 4-35-03 | 3-6F | 1692 | DS | 1692 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1692_ABS | 1692(#5ATR) ABS | ATR |  |  |  |  | CDC | 861 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | DS1 | 551 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1364 | 1365 | 0368 | 4-35-04 | 4-35-05 | 3-70 | 551 | ABS | 551 ABS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.551_ABS | 551 ABS | OTHER |  |  |  |  | CDC | 862 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | DS1 | 1861 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1366 | 1367 | 0369 | 4-35-06 | 4-35-07 | 3-71 | 1861 | DS | 1861 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1861_ABS | 1861(#6ATR) ABS | ATR |  |  |  |  | CDC | 863 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | DS2 | 1862 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1368 | 1369 | 0370 | 4-35-08 | 4-35-09 | 3-72 | 1862 | DS | 1862 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1862_ABS | 1862(#6ATR) ABS | ATR |  |  |  |  | CDC | 864 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | DS1 | 561 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1370 | 1371 | 0371 | 4-35-10 | 4-35-11 | 3-73 | 561 | ABS | 561 ABS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.561_ABS | 561 ABS | OTHER |  |  |  |  | CDC | 865 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1029 |  | 0372 | 3-30-05 |  | 3-74 | #1 ATR | A/M | #1 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_A/M | #1ATR OLTC A/M | ATR |  |  |  |  | CDC | 866 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1372 | 1373 | 0373 | 4-35-12 | 4-35-13 | 3-75 | #1 ATR | MY-S | #1 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_M/F/I | #1ATR M/F/I | ATR |  |  |  |  | CDC | 867 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0290 |  | 0375 | 3-A2 |  | 3-77 | #1 ATR | TAP | #1ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_TAP | #1ATR OLTC TAP | ATR |  |  |  |  | CDC | 868 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1045 |  | 0376 | 3-31-05 |  | 3-78 | #2 ATR | A/M | #2 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_A/M | #2ATR OLTC A/M | ATR |  |  |  |  | CDC | 869 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | M_F_I |  | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1374 | 1375 | 0377 | 4-35-14 | 4-35-15 | 3-79 | #2 ATR | MY-S | #2 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_M/F/I | #2ATR M/F/I | ATR |  |  |  |  | CDC | 870 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0297 |  | 0379 | 3-A9 |  | 3-7B | #2 ATR | TAP | #2ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_TAP | #2ATR OLTC TAP | ATR |  |  |  |  | CDC | 871 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1061 |  | 0380 | 3-32-05 |  | 3-7C | #3 ATR | A/M | #3 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_A/M | #3ATR OLTC A/M | ATR |  |  |  |  | CDC | 872 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1376 | 1377 | 0381 | 4-36-00 | 4-36-01 | 3-7D | #3 ATR | MY-S | #3 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_M/F/I | #3ATR M/F/I | ATR |  |  |  |  | CDC | 873 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0304 |  | 0383 | 3-B0 |  | 3-7F | #3 ATR | TAP | #3ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_TAP | #3ATR OLTC TAP | ATR |  |  |  |  | CDC | 874 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1072 |  | 0384 | 3-33-00 |  | 4-00 | #4 ATR | A/M | #4 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_A/M | #4ATR OLTC A/M | ATR |  |  |  |  | CDC | 875 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1378 | 1379 | 0385 | 4-36-02 | 4-36-03 | 4-01 | #4 ATR | MY-S | #4 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_M/F/I | #4ATR M/F/I | ATR |  |  |  |  | CDC | 876 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0311 |  | 0387 | 3-B7 |  | 4-03 | #4 ATR | TAP | #4ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_TAP | #4ATR OLTC TAP | ATR |  |  |  |  | CDC | 877 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1083 |  | 0388 | 3-33-11 |  | 4-04 | #5 ATR | A/M | #5 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_A/M | #5ATR OLTC A/M | ATR |  |  |  |  | CDC | 878 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1380 | 1381 | 0389 | 4-36-04 | 4-36-05 | 4-05 | #5 ATR | MY-S | #5 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_M/F/I | #5ATR M/F/I | ATR |  |  |  |  | CDC | 879 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0322 |  | 0391 | 3-C2 |  | 4-07 | #5 ATR | TAP | #5ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_TAP | #5ATR OLTC TAP | ATR |  |  |  |  | CDC | 880 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1099 |  | 0392 | 3-34-11 |  | 4-08 | #6 ATR | A/M | #6 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_A/M | #6ATR OLTC A/M | ATR |  |  |  |  | CDC | 881 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1382 | 1383 | 0393 | 4-36-06 | 4-36-07 | 4-09 | #6 ATR | MY-S | #6 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_M/F/I | #6ATR M/F/I | ATR |  |  |  |  | CDC | 882 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0329 |  | 0395 | 3-C9 |  | 4-0B | #6 ATR | TAP | #6ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_TAP | #6ATR OLTC TAP | ATR |  |  |  |  | CDC | 883 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1125 |  | 0396 | 3-36-05 |  | 4-0C | 3510 | 179S | 第一套 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3510_79UL | 麥寮二路(3510) 79RY U/L | LINE345 |  |  |  |  | CDC | 884 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1135 |  | 0398 | 3-36-15 |  | 4-0E | 3540 | 179S | 3540 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3540_79UL | 麥寮一路(3540) 79RY U/L | LINE345 |  |  |  |  | CDC | 885 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1140 |  | 0399 | 3-37-04 |  | 4-0F | 3560 | 279S | 3560 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3560_79UL | 3560 79RY U/L | LINE345 |  |  |  |  | CDC | 886 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1145 |  | 0400 | 3-37-09 |  | 4-10 | 3570 | 79S | 3570 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3570_79UL | 中寮二路(3570) 79RY U/L | LINE345 |  |  |  |  | CDC | 887 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1150 |  | 0401 | 3-37-14 |  | 4-11 | 3610 | 79S | 3610 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3610_79UL | 中寮一路(3610) 79RY U/L | LINE345 |  |  |  |  | CDC | 888 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1155 |  | 0402 | 3-38-03 |  | 4-12 | 3640 | 79S | 3640 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3640_79UL | 中寮三路(3640) 79RY U/L | LINE345 |  |  |  |  | CDC | 889 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1160 |  | 0403 | 3-38-08 |  | 4-13 | 3710 | 79S | 3710 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3710_79UL | 龍崎紅線(3710) 79RY U/L | LINE345 |  |  |  |  | CDC | 890 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1165 |  | 0404 | 3-38-13 |  | 4-14 | 3770 | 79S | 新南科一路 3770 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3770_79UL | 新南科一路(3770) 79RY U/L | LINE345 |  |  |  |  | CDC | 891 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1170 |  | 0405 | 3-39-02 |  | 4-15 | 3810 | 79S | 新南科二路3810 79RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.3810_79UL | 新南科二路(3810) 79RY U/L | LINE345 |  |  |  |  | CDC | 892 | DI_LINE345(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 33 | 33kV | 310 | #1SSTR(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/1ATR33 | T/1SSTR |  |  | 0437 |  | 0406 | 3-16-05 |  | 4-16 | #1 ATR 三次側 | CB | 310 CB |  | abbb | B3/E05_C | [8 empty] | 嘉民ES.310_CB | 310(#1SSTR) CB | OTHER |  |  |  |  | CDC | 893 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 310 | #1SSTR(310) |  | DS1 | 311_DS | B2,B3,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1452 | 1453 | 0407 | 4-3A-12 | 4-3A-13 | 4-17 | 311 | DS | 311 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.311_DS | 311 DS | OTHER |  |  |  |  | CDC | 894 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACB3 |  |  | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1175 |  | 0408 | 3-39-07 |  | 4-18 | ACB3 | CB ON/OFF | 所內電源ACB3 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACB3 | 所內電源ACB3 | OTHER |  |  |  |  | CDC | 895 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACBT2 |  |  | Status | 所內電源ACB TIE2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1176 |  | 0409 | 3-39-08 |  | 4-19 | ACB TIE2 | CB ON/OFF | 所內電源ACB TIE2 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACBT2 | 所內電源ACBT2 | OTHER |  |  |  |  | CDC | 896 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACB4 |  |  | Status | 所內電源ACB4 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1177 |  | 0410 | 3-39-09 |  | 4-1A | ACB4 | CB ON/OFF | 所內電源ACB4 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACB4 | 所內電源ACB4 | OTHER |  |  |  |  | CDC | 897 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights | 通訊塔防情信號燈 | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1200 |  | 0411 | 3-3B-00 |  | 4-1B | 通訊塔 |  | 防情信號燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.信號燈(1) | 通訊塔防情信號燈 | OTHER |  |  |  |  | CDC | 898 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 | Y |  | ON/OFF | ON
E05 | 嘉民ES | 161 | 161kV | StaDev | 所內設施 |  | Lights | 161KV防情信號燈 | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1201 |  | 0412 | 3-3B-01 |  | 4-1C | 161KV |  | 防情信號燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.信號燈(2) | 161KV防情信號燈 | OTHER |  |  |  |  | CDC | 899 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 | Y |  | ON/OFF | ON
E05 | 嘉民ES | 345 | 345kV | StaDev | 所內設施 |  | Lights | 345KV防情信號燈 | Element | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1202 |  | 0413 | 3-3B-02 |  | 4-1D | 345 KV |  | 防情信號燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.信號燈(3) | 345KV防情信號燈 | OTHER |  |  |  |  | CDC | 900 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | ON | 1 | Y |  | ON/OFF | ON
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights1 | 3570側開關場長夜燈 | Element | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1203 |  | 0414 | 3-3B-03 |  | 4-1E | 3570 側 |  | 開關場長夜燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.外燈(1) | 3570側開關場長夜燈 | OTHER |  |  |  |  | CDC | 901 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights2 | 3720側開關場長夜燈 | Element | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1204 |  | 0415 | 3-3B-04 |  | 4-1F | 3720 側 |  | 開關場長夜燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.外燈(2) | 3720側開關場長夜燈 | OTHER |  |  |  |  | CDC | 902 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights3 | 3820側開關場長夜燈 | Element | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1205 |  | 0416 | 3-3B-05 |  | 4-20 | 3820 側 |  | 開關場長夜燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.外燈(3) | 3820側開關場長夜燈 | OTHER |  |  |  |  | CDC | 903 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights4 | 1711側開關場長夜燈 | Element | Status | 照明4 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1206 |  | 0417 | 3-3B-06 |  | 4-21 | 1711 側 |  | 開關場長夜燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.外燈(4) | 1711側開關場長夜燈 | OTHER |  |  |  |  | CDC | 904 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights5 | 1700側開關場長夜燈 | Element | Status | 照明5 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1207 |  | 0418 | 3-3B-07 |  | 4-22 | 1700 側 |  | 開關場長夜燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.外燈(5) | 1700側開關場長夜燈 | OTHER |  |  |  |  | CDC | 905 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | Lights6 | 1542側開關場長夜燈 | Element | [12 empty] | 1208 |  | 0419 | 3-3B-08 |  | 4-23 | 1542 側 |  | 開關場長夜燈 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.外燈(6) | 1542側開關場長夜燈 | OTHER |  |  |  |  | CDC | 906 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ON/OFF | OFF
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | Tap Chan |  | B3 | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1411 |  | 0420 | 4-38-03 |  | 4-24 | #8ATR | A/M | #8 ATR 自動/手動 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_A/M | #8ATR OLTC A/M | ATR |  |  |  |  | CDC | 907 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | M_F_I | M/F/I | B2,Element | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 1446 | 1447 | 0421 | 4-3A-06 | 4-3A-07 | 4-25 | #8 ATR | MY-S | #8 ATR MY-S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_M/F/I | #8ATR M/F/I | ATR |  |  |  |  | CDC | 908 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0340 |  | 0423 | 3-D4 |  | 4-27 | #8 ATR | TAP | #8ATR TAP | TAP_-5.5_10.5(0_2000) |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_TAP | #8ATR OLTC TAP | ATR |  |  |  |  | CDC | 909 | AI_ATR345/161(2) |  |  |  | AI | [5 empty] | TAP10_5 | 9 | 10 | 11 | 12 | 0 | -4 | -5 | -6 | -7 | 0.1 |  | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | ES1 | 3591E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1396 | 1397 | 0424 | 4-37-04 | 4-37-05 | 4-28 | 3591E | ES | 3591 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3591E_ES | #1ATR 3591E ES | OTHER |  |  |  |  | CDC | 910 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | ES1 | 3631E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1398 | 1399 | 0425 | 4-37-06 | 4-37-07 | 4-29 | 3631E | ES | 3631 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3631E_ES | #2ATR 3631E ES | OTHER |  |  |  |  | CDC | 911 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | ES1 | 3661E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1400 | 1401 | 0426 | 4-37-08 | 4-37-09 | 4-2A | 3661E | ES | 3661 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3661E_ES | #3ATR 3661E ES | OTHER |  |  |  |  | CDC | 912 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | ES1 | 3731E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1402 | 1403 | 0427 | 4-37-10 | 4-37-11 | 4-2B | 3731E | ES | 3731 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3731E_ES | #4ATR 3731E ES | OTHER |  |  |  |  | CDC | 913 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | ES1 | 3791E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1404 | 1405 | 0428 | 4-37-12 | 4-37-13 | 4-2C | 3791E | ES | 3791 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3791E_ES | #5ATR 3791E ES | OTHER |  |  |  |  | CDC | 914 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | ES1 | 3831E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1406 | 1407 | 0429 | 4-37-14 | 4-37-15 | 4-2D | 3831E | ES | 3831 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3831E_ES | #6ATR 3831E ES | OTHER |  |  |  |  | CDC | 915 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS1 | 1831 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1448 | 1449 | 0430 | 4-3A-08 | 4-3A-09 | 4-2E | 1831 | DS | 1831 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1831_DS | 1831(#3ATR) DS | ATR |  |  |  |  | CDC | 916 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS2 | 1832 |  | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1450 | 1451 | 0431 | 4-3A-10 | 4-3A-11 | 4-2F | 1832 | DS | 1832 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1832_DS | 1832(#3ATR) DS | ATR |  |  |  |  | CDC | 917 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | DS1 | 1881 |  | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1440 | 1441 | 0432 | 4-3A-00 | 4-3A-01 | 4-30 | 1881 | DS | 1881 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1881_ABS | 1881(#8ATR) ABS | ATR |  |  |  |  | CDC | 918 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | DS2 | 1882 |  | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1442 | 1443 | 0433 | 4-3A-02 | 4-3A-03 | 4-31 | 1881 | DS | 1882 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.1882_ABS | 1882(#8ATR) ABS | ATR |  |  |  |  | CDC | 919 | DI_ATR345/161(6) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | DS1 | 581 |  | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1444 | 1445 | 0434 | 4-3A-04 | 4-3A-05 | 4-32 | 581 | ABS | 581 ABS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.581_DS | 581 DS | OTHER |  |  |  |  | CDC | 920 | DI_ATR_REC69(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 1BUS | #1BUS |  | 1_87UL1 | 345#1B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1112 |  | 0435 | 3-35-08 |  | 4-33 | 345KV | #1BUS | 187B1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#1B_87UL1 | 345KV #1BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 921 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 2BUS | #2BUS |  | 1_87UL1 | 345#2B_87UL1 | B2,B3,Element | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1114 |  | 0436 | 3-35-10 |  | 4-34 | 345KV | #2BUS | 287B1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#2B_87UL1 | 345KV #2BUS 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 922 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 1BUS | #1BUS |  | 1_87UL2 | 345#1B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1113 |  | 0437 | 3-35-09 |  | 4-35 | 345KV | #1BUS | 187B2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#1B_87UL2 | 345KV #1BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 923 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | E1 | 3511E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1384 | 1385 |  | 4-36-08 | 4-36-09 |  | 3511E | ES | 3511 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3511E_ES | 麥寮二路 3511E ES | OTHER |  |  |  |  | CDC | 924 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | E1 | 3611E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1386 | 1387 |  | 4-36-10 | 4-36-11 |  | 3611E | ES | 3611 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3611E_ES | 中寮一路 3611E ES | OTHER |  |  |  |  | CDC | 925 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | E1 | 3771E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1388 | 1389 |  | 4-36-12 | 4-36-13 |  | 3771E | ES | 3771 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3771E_ES | 新南科一路 3771E ES | OTHER |  |  |  |  | CDC | 926 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | BE2 | 3532E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1390 | 1391 |  | 4-36-14 | 4-36-15 |  | 3532E | ES | 3532 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3532E_ES | #8ATR 3532E ES | OTHER |  |  |  |  | CDC | 927 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | BE2 | 3632E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1392 | 1393 |  | 4-37-00 | 4-37-01 |  | 3632E | ES | 3632 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3632E_ES | #2ATR 3632E ES | OTHER |  |  |  |  | CDC | 928 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | BE2 | 3792E_ES | B2,B3,Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1394 | 1395 |  | 4-37-02 | 4-37-03 |  | 3792E | ES | 3792 ES AS |  |  | B2/E05_C | [8 empty] | 嘉民ES.3792E_ES | #5ATR 3792E ES | OTHER |  |  |  |  | CDC | 929 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 2BUS | #2BUS |  | 1_87UL2 | 345#2B_87UL2 | B2,B3,Element | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1115 |  | 0438 | 3-35-11 |  | 4-36 | 345KV | #2BUS | 287B2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.345#2B_87UL2 | 345KV #2BUS 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 930 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 33 | 33kV | 320 | #2SSTR(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | T/2ATR33 | T/2SSTR |  |  | 0439 |  | 0439 | 3-16-07 |  | 4-37 | #2 ATR 三次側 | CB | 320 CB |  | acbb | B3/E05_C | [8 empty] | 嘉民ES.320_CB | 320(#2SSTR) CB | OTHER |  |  |  |  | CDC | 931 | DI_SSTR(1) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1436 |  | 0440 | 4-39-12 |  | 4-38 | ACB1 | ON/OFF | 所內電源ACB1 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACB1 | 所內電源ACB1 | OTHER |  |  |  |  | CDC | 932 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACBT1 |  | Element | Status | 所內電源ACB TIE1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1437 |  | 0441 | 4-39-13 |  | 4-39 | ACB TIE1 | ON/OFF | 所內電源ACB TIE1 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACBT1 | 所內電源ACBT1 | OTHER |  |  |  |  | CDC | 933 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1438 |  | 0442 | 4-39-14 |  | 4-3A | ACB2 | ON/OFF | 所內電源ACB2 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACB2 | 所內電源ACB2 | OTHER |  |  |  |  | CDC | 934 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1058 |  | 0443 | 3-32-02 |  | 4-3B | #3 ATR | 87T1S | #3 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_87UL1 | #3ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 935 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1439 |  | 0444 | 4-39-15 |  | 4-3C | Locate Empty | 51ZUL | #3 ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_51ZUL | #3ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 936 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1059 |  | 0446 | 3-32-03 |  | 4-3E | #3 ATR | 87T2S | #3 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_87UL2 | #3ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 937 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1410 |  |  | 4-38-02 |  |  | #8ATR | S/L | #8 ATR 遙測/本地 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_S/L | #8ATR OLTC S/L | ATR |  |  |  |  | CDC | 938 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 33 | 33kV | 320 | #2SSTR(320) |  | DS1 | 321_DS | B2,B3,Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1456 | 1457 | 0447 | 4-3B-00 | 4-3B-01 | 4-3F | 321 | DS | 321 DS AS |  |  | B3/E05_C | [8 empty] | 嘉民ES.321_DS | 321 DS | OTHER |  |  |  |  | CDC | 939 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1412 |  |  | 4-38-04 |  |  | #8ATR | 96B1 | 樸氣電驛第一段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_96B1 | #8ATR 96B1 RY | ATR |  |  |  |  | CDC | 940 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1413 |  |  | 4-38-05 |  |  | #8ATR | 96B2 | 樸氣電驛第二段動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_96B2 | #8ATR 96B2 RY | ATR |  |  |  |  | CDC | 941 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1414 |  |  | 4-38-06 |  |  | #8ATR | 96D | 本體釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_96D | #8ATR 96D RY | ATR |  |  |  |  | CDC | 942 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1416 |  |  | 4-38-08 |  |  | #8ATR | 63Q | OLTC釋壓電驛動作 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_63Q | #8ATR 63Q RY | ATR |  |  |  |  | CDC | 943 | DI_ATR345/161(3) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1417 |  |  | 4-38-09 |  |  | #8ATR | TRF | #8 ATR 輕故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_TRF | #8ATR 輕故障 | ATR |  |  |  |  | CDC | 944 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ATR |  |  |  |  | 1418 |  |  | 4-38-10 |  |  | #8ATR | TRA | #8 ATR 重故障 |  | acbb | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_TRA | #8ATR 重故障 | ATR |  |  |  |  | CDC | 945 | DI_ATR345/161(4) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1419 |  |  | 4-38-11 |  |  | 580 SH.R | 96B1 | 580 SH.R 96B1 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#8ATR_SHR96B1 | #8ATR 33KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 946 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1420 |  |  | 4-38-12 |  |  | 580 SH.R | 96B2 | 580 SH.R 96B2 |  |  | B3/E05_C | [8 empty] | 嘉民ES.#8ATR_SHR96B2 | #8ATR 33KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 947 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1421 |  |  | 4-38-13 |  |  | 580 SH.R | 96D | 580 SH.R 96D |  |  | B3/E05_C | [8 empty] | 嘉民ES.#8ATR_SHR96D | #8ATR 33KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 948 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1422 |  |  | 4-38-14 |  |  | 580 SH.R | 96P | 580 SH.R 96P |  |  | B3/E05_C | [8 empty] | 嘉民ES.#8ATR_SHR96P | #8ATR 33KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 949 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1424 |  |  | 4-39-00 |  |  | NO.1 S.R. | 96B1 | NO.1 S.R.96B1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#1ATR_SR96B1 | #1ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 950 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1425 |  |  | 4-39-01 |  |  | NO.1 S.R. | 96B2 | NO.1 S.R.96B2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#1ATR_SR96B2 | #1ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 951 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1426 |  |  | 4-39-02 |  |  | NO.1 S.R. | 96D | NO.1 S.R.96D |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#1ATR_SR96D | #1ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 952 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1427 |  |  | 4-39-03 |  |  | NO.1 S.R. | 96PA | NO.1 S.R.96P |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#1ATR_SR96P | #1ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 953 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1428 |  |  | 4-39-04 |  |  | NO.2 S.R. | 96B1 | NO.2 S.R.96B1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#2ATR_SR96B1 | #2ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 954 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1429 |  |  | 4-39-05 |  |  | NO.2 S.R. | 96B2 | NO.2 S.R.96B2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#2ATR_SR96B2 | #2ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 955 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1430 |  |  | 4-39-06 |  |  | NO.2 S.R. | 96D | NO.2 S.R.96D |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#2ATR_SR96D | #2ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 956 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1431 |  |  | 4-39-07 |  |  | NO.2 S.R. | 96PA | NO.2 S.R.96P |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#2ATR_SR96P | #2ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 957 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1432 |  |  | 4-39-08 |  |  | NO.3 S.R. | 96B1 | NO.3 S.R.96B1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#3ATR_SR96B1 | #3ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 958 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1433 |  |  | 4-39-09 |  |  | NO.3 S.R. | 96B2 | NO.3 S.R.96B2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#3ATR_SR96B2 | #3ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 959 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1434 |  |  | 4-39-10 |  |  | NO.3 S.R. | 96D | NO.3 S.R.96D |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#3ATR_SR96D | #3ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 960 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1435 |  |  | 4-39-11 |  |  | NO.3 S.R. | 96PA | NO.3 S.R.96P |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#3ATR_SR96P | #3ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 961 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1026 |  | 0448 | 3-30-02 |  | 4-40 | #1 ATR | 87T1S | #1 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_87UL1 | #1ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 962 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1027 |  | 0449 | 3-30-03 |  | 4-41 | #1 ATR | 87T2S | #1 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_87UL2 | #1ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 963 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1493 |  | 0450 | 4-3D-05 |  | 4-42 | Locate Empty | 51ZUL | #1ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_51ZUL | #1ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 964 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1495 |  | 0451 | 4-3D-07 |  | 4-43 | 510 | 87UL | #1ATR 電抗器(510) 87RY U/L |  |  | B3/E05_C | [8 empty] | 嘉民ES.#1ATR_510_87UL | #1ATR 電抗器(510) 87RY U/L | OTHER |  |  |  |  | CDC | 965 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1042 |  | 0452 | 3-31-02 |  | 4-44 | #2 ATR | 87T1S | #2 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_87UL1 | #2ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 966 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1043 |  | 0453 | 3-31-03 |  | 4-45 | #2 ATR | 87T2S | #2 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_87UL2 | #2ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 967 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1497 |  | 0454 | 4-3D-09 |  | 4-46 | Locate Empty | 51ZUL | #2ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_51ZUL | #2ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 968 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1499 |  | 0455 | 4-3D-11 |  | 4-47 | 520 | 87UL | #2ATR 電抗器(520) 87RY U/L |  |  | B3/E05_C | [8 empty] | 嘉民ES.#2ATR_520_87UL | #2ATR 電抗器(520) 87RY U/L | OTHER |  |  |  |  | CDC | 969 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1069 |  | 0456 | 3-32-13 |  | 4-48 | #4 ATR | 87T1S | #4 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_87UL1 | #4ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 970 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1070 |  | 0457 | 3-32-14 |  | 4-49 | #4 ATR | 87T2S | #4 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_87UL2 | #4ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 971 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1501 |  | 0458 | 4-3D-13 |  | 4-4A | Locate Empty | 51ZUL | #4ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_51ZUL | #4ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 972 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1080 |  | 0459 | 3-33-08 |  | 4-4B | #5 ATR | 87T1S | #5 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_87UL1 | #5ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 973 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1472 |  |  | 4-3C-00 |  |  | NO.4 S.R. | 96B1 | NO.4 S.R.96B1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#4ATR_SR96B1 | #4ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 974 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1473 |  |  | 4-3C-01 |  |  | NO.4 S.R. | 96B2 | NO.4 S.R.96B2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#4ATR_SR96B2 | #4ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 975 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1474 |  |  | 4-3C-02 |  |  | NO.4 S.R. | 96D | NO.4 S.R.96D |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#4ATR_SR96D | #4ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 976 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1475 |  |  | 4-3C-03 |  |  | NO.4 S.R. | 96P | NO.4 S.R.96P |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#4ATR_SR96P | #4ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 977 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1476 |  |  | 4-3C-04 |  |  | NO.5 S.R. | 96B1 | NO.5 S.R.96B1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#5ATR_SR96B1 | #5ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 978 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1477 |  |  | 4-3C-05 |  |  | NO.5 S.R. | 96B2 | NO.5 S.R.96B2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#5ATR_SR96B2 | #5ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 979 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1478 |  |  | 4-3C-06 |  |  | NO.5 S.R. | 96D | NO.5 S.R.96D |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#5ATR_SR96D | #5ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 980 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1479 |  |  | 4-3C-07 |  |  | NO.5 S.R. | 96P | NO.5 S.R.96P |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#5ATR_SR96P | #5ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 981 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | 96B1 |  | B2,Element | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1480 |  |  | 4-3C-08 |  |  | NO.6 S.R. | 96B1 | NO.6 S.R.96B1 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#6ATR_SR96B1 | #6ATR 161KV 電抗器96B1 RY | OTHER |  |  |  |  | CDC | 982 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | 96B2 |  | B2,Element | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1481 |  |  | 4-3C-09 |  |  | NO.6 S.R. | 96B2 | NO.6 S.R.96B2 |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#6ATR_SR96B2 | #6ATR 161KV 電抗器96B2 RY | OTHER |  |  |  |  | CDC | 983 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | 96D |  | B2,Element | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1482 |  |  | 4-3C-10 |  |  | NO.6 S.R. | 96D | NO.6 S.R.96D |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#6ATR_SR96D | #6ATR 161KV 電抗器96D RY | OTHER |  |  |  |  | CDC | 984 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | 96P |  | B2,Element | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1483 |  |  | 4-3C-11 |  |  | NO.6 S.R. | 96P | NO.6 S.R.96P |  |  | B2/E05_A1 | [8 empty] | 嘉民ES.#6ATR_SR96P | #6ATR 161KV 電抗器96P RY | OTHER |  |  |  |  | CDC | 985 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | STUV1 | ACB1,ACB2,ACB TIE 所內電源欠壓警報 | Element | Status | 所內電源欠壓1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1484 |  |  | 4-3C-12 |  |  | SSTR | STUVA | ACB1,ACB2,ACB TIE 所內電源欠壓警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源欠壓1 | ACB1,ACB2,ACBT1所內電源欠壓 | OTHER |  |  |  |  | CDC | 986 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | StaDev | 所內設施 |  | ACBA1 | ACB1,ACB2,ACB TIE所內電源故障警報 | Element | Status | 第一套所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1485 |  |  | 4-3C-13 |  |  | SSTR | ACBA | ACB1,ACB2,ACB TIE所內電源故障警報 |  |  | B3/E05_A1 | [8 empty] | 嘉民ES.所內電源ACB(1) | ACB1,ACB2,ACBT1所內電源故障 | OTHER |  |  |  |  | CDC | 987 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 310 | #1SSTR(310) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1486 |  |  | 4-3C-14 |  |  | 310 | RYFA | 310 數位電驛故障 |  |  | B3/E05_C | [8 empty] | 嘉民ES.310_RYFA | (310)數位電驛故障 | OTHER |  |  |  |  | CDC | 988 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 320 | #2SSTR(320) |  | RYFA |  | B2,B3,Element | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1487 |  |  | 4-3C-15 |  |  | 320 | RYFA | 320 數位電驛故障 |  |  | B3/E05_C | [8 empty] | 嘉民ES.320_RYFA | (320)數位電驛故障 | OTHER |  |  |  |  | CDC | 989 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1488 |  |  | 4-3D-00 |  |  | Locate Empty | RYFA | #3ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#3ATR_RYFA | (#3ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 990 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1492 |  |  | 4-3D-04 |  |  | Locate Empty | 86A | #1ATR 86(51Z/87/96) RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_86A | #1ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 991 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1081 |  | 0460 | 3-33-09 |  | 4-4C | #5 ATR | 87T2S | #5 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_87UL2 | #5ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 992 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1494 |  |  | 4-3D-06 |  |  | Locate Empty | RYFA | #1ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#1ATR_RYFA | (#1ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 993 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1504 |  | 0461 | 4-3E-00 |  | 4-4D | Locate Empty | 51ZUL | #5ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_51ZUL | #5ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 994 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1496 |  |  | 4-3D-08 |  |  | Locate Empty | 86A | #2ATR 86(51Z/87/96) RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_86A | #2ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 995 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1506 |  | 0462 | 4-3E-02 |  | 4-4E | 550 | 87UL | #5ATR 電抗器(550) 87RY U/L |  |  | B3/E05_C | [8 empty] | 嘉民ES.#5ATR_550_87UL | #5ATR 電抗器(550) 87RY U/L | OTHER |  |  |  |  | CDC | 996 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1498 |  |  | 4-3D-10 |  |  | Locate Empty | RYFA | #2ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#2ATR_RYFA | (#2ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 997 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1096 |  | 0463 | 3-34-08 |  | 4-4F | #6 ATR | 87T1S | #6 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_87UL1 | #6ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 998 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1500 |  |  | 4-3D-12 |  |  | Locate Empty | 86A | #4ATR 86(51Z/87/96) RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_86A | #4ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 999 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1097 |  | 0464 | 3-34-09 |  | 4-50 | #6 ATR | 87T2S | #6 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_87UL2 | #6ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 1000 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1502 |  |  | 4-3D-14 |  |  | Locate Empty | RYFA | #4ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#4ATR_RYFA | (#4ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 1001 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1503 |  |  | 4-3D-15 |  |  | Locate Empty | 86A | #5ATR 86(51Z/87/96) RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_86A | #5ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 1002 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1508 |  | 0465 | 4-3E-04 |  | 4-51 | Locate Empty | 51ZUL | #6ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_51ZUL | #6ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1003 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1505 |  |  | 4-3E-01 |  |  | Locate Empty | RYFA | #5ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#5ATR_RYFA | (#5ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 1004 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1510 |  | 0466 | 4-3E-06 |  | 4-52 | 560 | 87UL | #6ATR 電抗器(560) 87RY U/L |  |  | B3/E05_C | [8 empty] | 嘉民ES.#6ATR_560_87UL | #6ATR 電抗器(560) 87RY U/L | OTHER |  |  |  |  | CDC | 1005 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1507 |  |  | 4-3E-03 |  |  | Locate Empty | 86A | #6ATR 86(51Z/87/96) RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_86A | #6ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 1006 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 1_87UL1 |  | B2 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1408 |  | 0467 | 4-38-00 |  | 4-53 | #8ATR | 87T1S | #8 ATR 87T1S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_87UL1 | #8ATR 第一組 87RY U/L | OTHER |  |  |  |  | CDC | 1007 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1509 |  |  | 4-3E-05 |  |  | Locate Empty | RYFA | #6ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#6ATR_RYFA | (#6ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 1008 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 1_87UL2 |  | B2 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1409 |  | 0468 | 4-38-01 |  | 4-54 | #8ATR | 87T2S | #8 ATR 87T2S |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_87UL2 | #8ATR 第二組 87RY U/L | OTHER |  |  |  |  | CDC | 1009 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | ATR_86A |  | B2 | Status | 86RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1511 |  |  | 4-3E-07 |  |  | Locate Empty | 86A | #8ATR 86(51Z/87/96) RY |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_86A | #8ATR 86(51Z/87/96)RY | OTHER |  |  |  |  | CDC | 1010 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | 51Z_UL |  | B2 | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1512 |  | 0469 | 4-3E-08 |  | 4-55 | Locate Empty | 51ZUL | #8ATR 51Z RY U/L |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_51ZUL | #8ATR 51ZRY U/L | OTHER |  |  |  |  | CDC | 1011 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1513 |  |  | 4-3E-09 |  |  | Locate Empty | RYFA | #8ATR 數位電驛故障 |  |  | B2/E05_C | [8 empty] | 嘉民ES.#8ATR_RYFA | (#8ATR)數位電驛故障 | OTHER |  |  |  |  | CDC | 1012 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | 87UL |  | B2,B3,Element | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1514 |  | 0470 | 4-3E-10 |  | 4-56 | 580 | 87UL | #8ATR 電抗器(580) 87RY U/L |  |  | B3/E05_C | [8 empty] | 嘉民ES.#8ATR_580_87UL | #8ATR 電抗器(580) 87RY U/L | OTHER |  |  |  |  | CDC | 1013 | DI_OTHERS(2) |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0850 | [10 empty] | B2/E05_A1 | [16 empty] | 1014 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0851 | [10 empty] | B2/E05_A1 | [16 empty] | 1015 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | 12B_87UL |  |  | Status | #1#2 BUS 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0832 | [10 empty] | B2/E05_A1 | [16 empty] | 1016 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
E05 | 嘉民ES | 161 | 161kV | ComPoint |  |  | 34B_87UL |  |  | Status | #3#4 BUS 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0839 | [10 empty] | B2/E05_A1 | [16 empty] | 1017 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | MW |  | INSERT | MvMoment | MW |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 1510 有效電力P | MW | 0~+/-210MW | MW_-210_210(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.1510_MW | 嘉民台嘉一路 MW | LINE161 | [5 empty] | 1018 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.57 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.570000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | MVAR |  | INSERT | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 1510 無效電力Q | MVAR | 0~+/-210MVAR | MVAR_-210_210(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.1510_MVAR | 嘉民台嘉一路 MVAR | LINE161 | [5 empty] | 1019 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.57 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.570000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 1510 ST線電壓 | KV | 0~210KV | kV_-210_210(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.1510LPD_KV | 嘉民台嘉一路(1510) LPD KV | LINE161 | [5 empty] | 1020 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | MW |  | INSERT | MvMoment | MW |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 1520 有效電力P | MW | 0~+/-210MW | MW_-210_210(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.1520_MW | 嘉民台嘉二路 MW | LINE161 | [5 empty] | 1021 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.544 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.544000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | MVAR |  | INSERT | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 1520 無效電力Q | MVAR | 0~+/-210MVAR | MVAR_-210_210(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.1520_MVAR | 嘉民台嘉二路 MVAR | LINE161 | [5 empty] | 1022 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.544 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.544000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 1520 ST線電壓 | KV | 0~210KV | kV_-210_210(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.1520LPD_KV | 嘉民台嘉二路(1520) LPD KV | LINE161 | [5 empty] | 1023 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
C21 | 台嘉CS | 161 | 161kV | 3GTR | #3GTR |  | MW |  | INSERT | MvMoment | MW |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | #3 GTR 有效電力P | MW | 0~+/-120MW | MW_-120_120(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.#3GTR_MW | 台嘉CS #3GTR MW | LINE161 | [5 empty] | 1024 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.31 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.310000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 3GTR | #3GTR |  | MVAR |  | INSERT | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | #3 GTR 無效電力Q | MVAR | 0~+/-120MVAR | MVAR_-120_120(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.#3GTR_MVAR | 台嘉CS #3GTR MVAR | LINE161 | [5 empty] | 1025 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.31 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.310000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 3GTR | #3GTR |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | #3 GTR ST線電壓 | KV | 0~120KV | kV_-120_120(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.#3GTRLPD_KV | 台嘉CS #3GTR LPD KV | LINE161 | [5 empty] | 1026 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
C21 | 台嘉CS | 161 | 161kV | 4GTR | #4GTR |  | MW |  | INSERT | MvMoment | MW |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | #4 GTR 有效電力P | MW | 0~+/-36MW | MW_-36_36(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.#4GTR_MW | 台嘉CS #4GTR MW | LINE161 | [5 empty] | 1027 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.976 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.976000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 4GTR | #4GTR |  | MVAR |  | INSERT | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | #4 GTR 無效電力Q | MVAR | 0~+/-36MVAR | MVAR_-36_36(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.#4GTR_MVAR | 台嘉CS #4GTR MVAR | LINE161 | [5 empty] | 1028 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.976 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.976000 | 0.010000
C21 | 台嘉CS | 161 | 161kV | 4GTR | #4GTR |  | V |  | INSERT | MvMoment | kV |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | #4 GTR ST線電壓 | KV | 0~36KV | kV_-36_36(-2000_2000) |  | B1/C21_A1 | [8 empty] | 台嘉CS.#4GTRLPD_KV | 台嘉CS #4GTR LPD KV | LINE161 | [5 empty] | 1029 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | BE0 | 1510BE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1510BE | 1510BE (非取樣點) | LINE161 | C21/161/1510/BE0 |  |  |  |  | 1030 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | LE0 | 1510LE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1510LE | 1510LE (非取樣點) | LINE161 | C21/161/1510/LE0 |  |  |  |  | 1031 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | CB | 1510_CB(非取樣點) | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1510_CB | 1510(嘉民台嘉一路)(非取樣點) | OTHER | C21/161/1510/CB |  |  |  |  | 1032 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | E2 | 1512E(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1512E_ES | 1512E(嘉民台嘉一路)(非取樣點) | OTHER | C21/161/1510/E2 |  |  |  |  | 1033 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | DS2 | 1512(非取樣點) | DEL | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1512_DS | 1512(嘉民台嘉一路)(非取樣點) | OTHER | C21/161/1510/DS2 |  |  |  |  | 1034 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | BE0 | 1520BE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1520BE | 1520BE (非取樣點) | LINE161 | C21/161/1520/BE0 |  |  |  |  | 1035 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | LE0 | 1520LE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1520LE | 1520LE (非取樣點) | LINE161 | C21/161/1520/LE0 |  |  |  |  | 1036 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | CB | 1520_CB(非取樣點) | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1520_CB | 1520(嘉民台嘉二路)(非取樣點) | OTHER | C21/161/1520/CB |  |  |  |  | 1037 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | E2 | 1522E(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1522E_ES | 1522E(嘉民台嘉二路)(非取樣點) | OTHER | C21/161/1520/E2 |  |  |  |  | 1038 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | DS2 | 1522(非取樣點) | DEL | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1522_DS | 1522(嘉民台嘉二路)(非取樣點) | OTHER | C21/161/1520/DS2 |  |  |  |  | 1039 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501(非取樣點) | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1501_DS | 1501(TIE) DS(非取樣點) | OTHER | C21/161/1500/DS1 |  |  |  |  | 1040 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | 1650BE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1650BE | 1650BE(#1ATR)(非取樣點) | OTHER | C21/161/1650/BE0 |  |  |  |  | 1041 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | 1650TE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1650TE | 1650TE(#1ATR)(非取樣點) | OTHER | C21/161/1650/TE0 |  |  |  |  | 1042 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB | 1650_CB(非取樣點) | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1650_CB | 1650(#1MTR) CB(非取樣點) | OTHER | C21/161/1650/CB |  |  |  |  | 1043 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651(非取樣點) | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1651_DS | 1651(#1MTR) DS(非取樣點) | OTHER | C21/161/1650/DS1 |  |  |  |  | 1044 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1660BE | 1660BE(#2ATR)(非取樣點) | OTHER | C21/161/1660/BE0 |  |  |  |  | 1045 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1660TE | 1660TE(#2ATR)(非取樣點) | OTHER | C21/161/1660/TE0 |  |  |  |  | 1046 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | 1660_CB(非取樣點) | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1660_CB | 1660(#2MTR) CB(非取樣點) | OTHER | C21/161/1660/CB |  |  |  |  | 1047 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661(非取樣點) | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1661_DS | 1661(#2MTR) DS(非取樣點) | OTHER | C21/161/1660/DS1 |  |  |  |  | 1048 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | BE0 | 1680BE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1680BE | 1680BE(#4ATR)(非取樣點) | OTHER | C21/161/1680/BE0 |  |  |  |  | 1049 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | TE0 | 1680TE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1680TE | 1680TE(#4ATR)(非取樣點) | OTHER | C21/161/1680/TE0 |  |  |  |  | 1050 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | CB | 1680_CB(非取樣點) | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1680_CB | 1680(#4GTR) CB(非取樣點) | OTHER | C21/161/1680/CB |  |  |  |  | 1051 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | DS1 | 1681(非取樣點) | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1681_DS | 1681(#4GTR) DS(非取樣點) | OTHER | C21/161/1680/DS1 |  |  |  |  | 1052 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | E2 | 1682E(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1682E_ES | 1682E(#4GTR) ES(非取樣點) | OTHER | C21/161/1680/E2 |  |  |  |  | 1053 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | DS2 | 1682(非取樣點) | DEL | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1682_DS | 1682(#4GTR) DS(非取樣點) | OTHER | C21/161/1680/DS2 |  |  |  |  | 1054 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1501E_ES | 1501E(TIE) ES(非取樣點) | OTHER | C21/161/1500/E1 |  |  |  |  | 1055 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | BE0 | 1670BE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1670BE | 1670BE(#3ATR)(非取樣點) | OTHER | C21/161/1670/BE0 |  |  |  |  | 1056 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | TE0 | 1670TE(非取樣點) | DEL | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 嘉民ES.1670TE | 1670TE(#3ATR)(非取樣點) | OTHER | C21/161/1670/TE0 |  |  |  |  | 1057 | NotelDIPoint |  |  |  |  | D_P_KEY | [5 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | CB | 1670_CB(非取樣點) | DEL | Status | CB | Close/Open | Y | 1 | DI-SP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1670_CB | 1670(#2MTR) CB(非取樣點) | OTHER | C21/161/1670/CB |  |  |  |  | 1058 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | DS1 | 1671(非取樣點) | DEL | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B1/C21_A1 | [8 empty] | 台嘉CS.1671_DS | 1671(#2MTR) DS(非取樣點) | OTHER | C21/161/1670/DS1 |  |  |  |  | 1059 | NotelDIPoint | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 510 | #1SHR(510) |  | LE1 | 511E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 520 | #2SHR(520) |  | LE1 | 521E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 550 | #5SHR(550) |  | LE1 | 551E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 560 | #6SHR(560) |  | LE1 | 561E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 580 | #8SHR(580) |  | LE1 | 581E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 330 | #3SSTR(330) |  | LE1 | 331E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 340 | #4SSTR(340) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 340 | #4SSTR(340) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 340 | #4SSTR(340) |  | LE1 | 341E(非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 310 | #1SSTR(310) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 310 | #1SSTR(310) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 320 | #1SSTR(320) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 201 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 33 | 33kV | 320 | #1SSTR(320) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/E05_A1 | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 202 | DI_LINE161(5) | [10 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/E05_C | [12 empty] | 嘉民ES.161KV_12BUS_KV | 161KV #1,#2 BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: E05/161/1BUS/V; OPRD2: E05/161/2BUS/V
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | Vbs5 | [9 empty] | B1/E05_C | [12 empty] | 嘉民ES.161KV_12BUS_KV | 161KV #1,#2 BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_34 | OPRD1: E05/161/3BUS/V; OPRD2: E05/161/4BUS/V
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | Vbs8 | [9 empty] | B1/E05_C | [15 empty] | BEST_SOURCE_35KV_1 |  | v_best_345_12 | OPRD1: E05/345/1BUS/V; OPRD2: E05/345/2BUS/V
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/E05_C | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: NULL; OPRD3: NULL; OPRD4: E05/0/CalcPoint/Vbs4; OPRD5: E05/0/CalcPoint/Vbs5; OPRD6: NULL; OPRD7: NULL; OPRD8: E05/0/CalcPoint/Vbs8; OPRD9: NULL
C21 | 台嘉CS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/C21_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_4 | OPRD1: C21/161/1510/MW; OPRD2: C21/161/1520/MW; OPRD3: C21/161/3GTR/MW; OPRD4: C21/161/4GTR/MW
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/E05_C | [15 empty] | TOT_1MTR_CAL |  | p_sum_31 | E05/161/1510/MW | E05/161/1520/MW | E05/161/1530/MW | E05/161/1540/MW | E05/161/1550/MW | E05/161/1560/MW | E05/161/1580/MW | E05/161/1590/MW | E05/161/1610/MW | E05/161/1620/MW | E05/161/1630/MW | E05/161/1640/MW | E05/161/1710/MW | E05/161/1720/MW | E05/161/1730/MW | E05/161/1740/MW | E05/345/3510/MW | E05/345/3530/MW | E05/345/3540/MW | E05/345/3570/MW | E05/345/3590/MW | E05/345/3610/MW | E05/345/3630/MW | E05/345/3640/MW | E05/345/3660/MW | E05/345/3710/MW | E05/345/3730/MW | E05/345/3770/MW | E05/345/3790/MW | E05/345/3810/MW | E05/345/3830/MW
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/E05_C | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: E05/0/CalcPoint/OPRN2_MW
C21 | 台嘉CS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/C21_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: C21/0/CalcPoint/OPRN2_MW
C21 | 台嘉CS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/C21_A1 | [17 empty] | none
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/E05_C | [17 empty] | none
C21 | 台嘉CS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/C21_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: NULL; OPRD2: C21/0/CalcPoint/OPRN2; OPRD3: C21/0/CalcPoint/PRFL_UL
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/E05_C | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: E05/0/CalcPoint/OPRN1; OPRD2: E05/0/CalcPoint/OPRN2; OPRD3: E05/0/CalcPoint/PRFL_UL
E05 | 嘉民ES |  |  | 1ATR | 1ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#1ATR_AMP | #1ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3590/MW; OPRD2: E05/345/3590/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 2ATR | 2ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#2ATR_AMP | #2ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3630/MW; OPRD2: E05/345/3630/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 3ATR | 3ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#3ATR_AMP | #3ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3660/MW; OPRD2: E05/345/3660/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 4ATR | 4ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#4ATR_AMP | #4ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3730/MW; OPRD2: E05/345/3730/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 5ATR | 5ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#5ATR_AMP | #5ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3790/MW; OPRD2: E05/345/3790/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 6ATR | 6ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#6ATR_AMP | #6ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3830/MW; OPRD2: E05/345/3830/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 8ATR | 8ATR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.#8ATR_AMP | #8ATR 二次側 AMP | ATR | AMP_CAL | LG_1797 | amp_cal | OPRD1: E05/345/3530/MW; OPRD2: E05/345/3530/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民～台嘉一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/C21_A1 | [12 empty] | 台嘉CS.1510_AMP | 嘉民台嘉一路 AMP | LINE161 | AMP_CAL | C20R1600 | amp_cal | OPRD1: C21/161/1510/MW; OPRD2: C21/161/1510/MVAR; OPRD3: NULL
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民～台嘉二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/C21_A1 | [12 empty] | 台嘉CS.1520_AMP | 嘉民台嘉二路 AMP | LINE161 | AMP_CAL | C20R1600 | amp_cal | OPRD1: C21/161/1520/MW; OPRD2: C21/161/1520/MVAR; OPRD3: NULL
C21 | 台嘉CS | 161 | 161kV | 3GTR | #3GTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/C21_A1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: C21/161/3GTR/MW; OPRD2: C21/161/3GTR/MVAR; OPRD3: NULL
C21 | 台嘉CS | 161 | 161kV | 4GTR | #4GTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/C21_A1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: C21/161/4GTR/MW; OPRD2: C21/161/4GTR/MVAR; OPRD3: NULL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民～嘉義山線(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1510_AMP | 嘉義山線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: E05/161/1510/MW; OPRD2: E05/161/1510/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民～嘉義海線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1520_AMP | 嘉義海線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: E05/161/1520/MW; OPRD2: E05/161/1520/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1530 | 嘉民～柳營山線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1530_AMP | 柳營山線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: E05/161/1530/MW; OPRD2: E05/161/1530/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1540 | 嘉民～柳營海線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1540_AMP | 柳營海線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: E05/161/1540/MW; OPRD2: E05/161/1540/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1550 | 嘉民～雲林山線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1550_AMP | 雲林山線 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E05/161/1550/MW; OPRD2: E05/161/1550/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1560 | 嘉民～雲林海線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1560_AMP | 雲林海線 AMP | LINE161 | AMP_CAL | C20R2000 | amp_cal | OPRD1: E05/161/1560/MW; OPRD2: E05/161/1560/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民~雲林線(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1580_AMP | 嘉民雲林線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: E05/161/1580/MW; OPRD2: E05/161/1580/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1590 | 嘉民～斗工紅線(1590) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1590_AMP | 斗工紅線 AMP | LINE161 | AMP_CAL | C20R1576 | amp_cal | OPRD1: E05/161/1590/MW; OPRD2: E05/161/1590/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉民～嘉義南線(1610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1610_AMP | 嘉義南線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E05/161/1610/MW; OPRD2: E05/161/1610/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉民～嘉義北線(1620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1620_AMP | 嘉義北線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E05/161/1620/MW; OPRD2: E05/161/1620/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1630_AMP | 北港南線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E05/161/1630/MW; OPRD2: E05/161/1630/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1640_AMP | 北港北線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E05/161/1640/MW; OPRD2: E05/161/1640/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1710 | 嘉民～台嘉一路(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1710_AMP | 台嘉一路 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E05/161/1710/MW; OPRD2: E05/161/1710/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1720 | 嘉民～台嘉二路(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1720_AMP | 台嘉二路 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: E05/161/1720/MW; OPRD2: E05/161/1720/MVAR; OPRD3: E05/0/CalcPoint/Vbs4
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠～嘉民一路(1730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1730_AMP | 嘉惠一路 AMP | LINE161 | AMP_CAL | C40R4000 | amp_cal | OPRD1: E05/161/1730/MW; OPRD2: E05/161/1730/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠～嘉民二路(1740) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_A1 | [12 empty] | 嘉民ES.1740_AMP | 嘉惠二路 AMP | LINE161 | AMP_CAL | C40R4000 | amp_cal | OPRD1: E05/161/1740/MW; OPRD2: E05/161/1740/MVAR; OPRD3: E05/0/CalcPoint/Vbs5
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮～嘉民二路(3510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3510_AMP | 麥寮二路 AMP | LINE345 | AMP_CAL | C40R4000 | amp_cal | OPRD1: E05/345/3510/MW; OPRD2: E05/345/3510/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮～嘉民一路(3540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3540_AMP | 麥寮一路 AMP | LINE345 | AMP_CAL | C40R4000 | amp_cal | OPRD1: E05/345/3540/MW; OPRD2: E05/345/3540/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮～嘉民二路(3570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3570_AMP | 中寮二路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E05/345/3570/MW; OPRD2: E05/345/3570/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮～嘉民一路(3610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3610_AMP | 中寮一路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E05/345/3610/MW; OPRD2: E05/345/3610/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮～嘉民三路(3640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3640_AMP | 中寮三路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E05/345/3640/MW; OPRD2: E05/345/3640/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3710 | 嘉民～龍崎紅線(3710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3710_AMP | 龍崎紅線 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E05/345/3710/MW; OPRD2: E05/345/3710/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3770 | 新嘉民～南科一路(3770) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3770_AMP | 新南科一路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E05/345/3770/MW; OPRD2: E05/345/3770/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES | 345 | 345kV | 3810 | 新嘉民～南科二路(3810) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/E05_C | [12 empty] | 嘉民ES.3810_AMP | 新南科二路 AMP | LINE345 | AMP_CAL | C40R3652 | amp_cal | OPRD1: E05/345/3810/MW; OPRD2: E05/345/3810/MVAR; OPRD3: E05/0/CalcPoint/Vbs8
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#1ATR_MVA | #1ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3590/MW; OPRD2: E05/345/3590/MVAR
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#2ATR_MVA | #2ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3630/MW; OPRD2: E05/345/3630/MVAR
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#3ATR_MVA | #3ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3660/MW; OPRD2: E05/345/3660/MVAR
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#4ATR_MVA | #4ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3730/MW; OPRD2: E05/345/3730/MVAR
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#5ATR_MVA | #5ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3790/MW; OPRD2: E05/345/3790/MVAR
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#6ATR_MVA | #6ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3830/MW; OPRD2: E05/345/3830/MVAR
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B2/E05_C | LG_500 | 475 | 550 | 625 | 990 | 2.5 | -475 | -550 | -625 | -990 |  |  | 嘉民ES.#8ATR_MVA | #8ATR二次側 MVA | ATR | MVA_CAL | LG_500 | va_million | OPRD1: E05/345/3530/MW; OPRD2: E05/345/3530/MVAR
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#1ATR_LOAD | #1ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//1ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#2ATR_LOAD | #2ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//2ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#3ATR_LOAD | #3ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//3ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#4ATR_LOAD | #4ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//4ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#5ATR_LOAD | #5ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//5ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#6ATR_LOAD | #6ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//6ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | LOAD | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#8ATR_LOAD | #8ATR 負載率 | ATR | TR_LOAD_500 | LG_LOAD | tr_loading | OPRD1: E05//8ATR/MVA; OPRD2: 500
E05 | 嘉民ES |  |  | 1ATR | #1ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#1ATR_PF | #1ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3590/MW; OPRD2: E05/345/3590/MVAR
E05 | 嘉民ES |  |  | 2ATR | #2ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#2ATR_PF | #2ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3630/MW; OPRD2: E05/345/3630/MVAR
E05 | 嘉民ES |  |  | 3ATR | #3ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#3ATR_PF | #3ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3660/MW; OPRD2: E05/345/3660/MVAR
E05 | 嘉民ES |  |  | 4ATR | #4ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#4ATR_PF | #4ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3730/MW; OPRD2: E05/345/3730/MVAR
E05 | 嘉民ES |  |  | 5ATR | #5ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#5ATR_PF | #5ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3790/MW; OPRD2: E05/345/3790/MVAR
E05 | 嘉民ES |  |  | 6ATR | #6ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#6ATR_PF | #6ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3830/MW; OPRD2: E05/345/3830/MVAR
E05 | 嘉民ES |  |  | 8ATR | #8ATR |  | PF | [9 empty] | B2/E05_C | [12 empty] | 嘉民ES.#8ATR_PF | #8ATR 功率因素 | ATR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: E05/345/3530/MW; OPRD2: E05/345/3530/MVAR
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/E05_C | [15 empty] | STATION_FAULT_1 |  | com_alarm_53 | E05//1ATR/63Q | E05//1ATR/TRA | E05//1ATR/96D | E05//1ATR/96B1 | E05//1ATR/96B2 | E05//1ATR/51ZA | E05//1ATR/96PA | E05//2ATR/63Q | E05//2ATR/TRA | E05//2ATR/96D | E05//2ATR/96B1 | E05//2ATR/96B2 | E05//2ATR/96PA | E05//2ATR/51ZA | E05//3ATR/96B1 | E05//3ATR/96PA | E05//3ATR/63Q | E05//3ATR/TRA | E05//3ATR/96B2 | E05//3ATR/96D | E05//3ATR/51ZA | E05//4ATR/96B2 | E05//4ATR/96B1 | E05//4ATR/96D | E05//4ATR/TRA | E05//4ATR/63Q | E05//4ATR/96PA | E05//4ATR/51ZA | E05//5ATR/96B1 | E05//5ATR/96B2 | E05//5ATR/TRA | E05//5ATR/63Q | E05//5ATR/96D | E05//5ATR/96PA | E05//5ATR/51ZA | E05//6ATR/96D | E05//6ATR/51ZA | E05//6ATR/96B1 | E05//6ATR/96B2 | E05//6ATR/TRA | E05//6ATR/63Q | E05//6ATR/96PA | E05//8ATR/96B1 | E05//8ATR/51ZA | E05//8ATR/63Q | E05//8ATR/TRA | E05//8ATR/96D | E05//8ATR/96B2 | E05//8ATR/96PA | E05/161/1BUS/87A
E05 | 嘉民ES | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/E05_C | [15 empty] | STATION_FAULT_1 |  | com_alarm_7 | OPRD1: E05//1ATR/TRF; OPRD2: E05//2ATR/TRF; OPRD3: E05//3ATR/TRF; OPRD4: E05//4ATR/TRF; OPRD5: E05//5ATR/TRF; OPRD6: E05//6ATR/TRF; OPRD7: E05//8ATR/TRF
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | 1_DCV_P | #1直流P電源 |  | MvMoment | #1 直流P電源電壓 |  | Y |  | AI |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/1_DCV_P
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | 1_DCV_N | #1直流N電源 |  | MvMoment | #1 直流N電源電壓 |  | Y |  | AI |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/1_DCV_N
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | 2_DCV_P | #2直流P電源 |  | MvMoment | #2 直流P電源電壓 |  | Y |  | AI |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/2_DCV_P
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | 2_DCV_N | #2直流N電源 |  | MvMoment | #2 直流N電源電壓 |  | Y |  | AI |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/2_DCV_N
E05 | 嘉民ES | 161 | 161kV | ComPoint_C |  |  | BFA |  |  | Status | 斷路器失靈(BF) RY | Normal/Fault | Y | 1 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/ComPoint/BFA
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/25PFA
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/25TA
E05 | 嘉民ES | 161 | 161kV | ComPoint_C |  |  | BFS |  |  | Status | 斷路器失靈RY U/L | Use/Lock | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/ComPoint/BFS
E05 | 嘉民ES | 161 | 161kV | ComPoint_C |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/ComPoint/ABS_89A
E05 | 嘉民ES | 161 | 161kV | ComPoint_C |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/ComPoint/CBA
E05 | 嘉民ES | 161 | 161kV | ComPoint_C |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/ComPoint/CBF
E05 | 嘉民ES | 161 | 161kV | StaDev_C | 所內設施 |  | DCA2 | 直流電源DCA(2) |  | Status | 直流電源故障2 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/StaDev/DCA2
E05 | 嘉民ES | 161 | 161kV | StaDev_C | 所內設施 |  | GRZ100 | BVS_RY |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/StaDev/GRZ100
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | EQA | 有感地震警報 | [8 empty] | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/EQA
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Door1 |  |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Door1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | AIRCON | 空調機故障 |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/AIRCON
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | OilLeak |  |  | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/OilLeak
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Water1 | 地下室水位0.5M |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Water1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Water2 | 地下室水位1M |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Water2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | STUV2 | ACB3,ACB4,ACBT2所內電源欠壓 |  | Status | 所內電源欠壓2 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/STUV2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/CHG1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/CHG2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/DCE
E05 | 嘉民ES | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_D1 | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/DCE
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/DCA
E05 | 嘉民ES | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_D1 | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/DCA
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Fire
E05 | 嘉民ES | 0 |  | StaDev_D1 | 所內設施 |  | Fire |  |  | Status | 火災警報 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/E05_D1 | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Fire
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/CommACF
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | R_Temp1 | 電驛室溫度 |  | Status | 溫度警報1 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/R_Temp1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | R_Temp | 通訊室溫度 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/R_Temp
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACBA2 | ACB3,ACB4,ACBT2所內電源故障 |  | Status | 第二套所內電源故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACBA2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | CHG1_1 | #2充電機故障 |  | Status | #1 直流充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/CHG1_1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | CHG1_2 | #3充電機故障 |  | Status | #2 直流充電機 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/CHG1_2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/PMA
E05 | 嘉民ES | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/E05_D1 | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/PMA
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACB3 |  |  | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACB3
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACBT2 |  |  | Status | 所內電源ACB TIE2 | Close/Open | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACBT2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACB4 |  |  | Status | 所內電源ACB4 | Close/Open | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACB4
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights | 通訊塔防情信號燈 |  | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights
E05 | 嘉民ES | 161 | 161kV | StaDev_C | 所內設施 |  | Lights | 161KV防情信號燈 |  | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/161/StaDev/Lights
E05 | 嘉民ES | 345 | 345kV | StaDev_C | 所內設施 |  | Lights | 345KV防情信號燈 |  | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/345/StaDev/Lights
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights1 | 3570側開關場長夜燈 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights2 | 3720側開關場長夜燈 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights3 | 3820側開關場長夜燈 |  | Status | 照明3 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights3
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights4 | 1711側開關場長夜燈 |  | Status | 照明4 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights4
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights5 | 1700側開關場長夜燈 |  | Status | 照明5 | OFF/ON | Y | 7 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights5
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | Lights6 | 1542側開關場長夜燈 | [8 empty] | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/Lights6
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACB1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACBT1 | 所內電源ACBT1 |  | Status | 所內電源ACB TIE1 | Close/Open | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACBT1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACB2
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | STUV1 | ACB1,ACB2,ACB TIE 所內電源欠壓警報 |  | Status | 所內電源欠壓1 | Normal/Alarm | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/STUV1
E05 | 嘉民ES | 0 |  | StaDev_C | 所內設施 |  | ACBA1 | ACB1,ACB2,ACB TIE所內電源故障警報 |  | Status | 第一套所內電源故障 | Normal/Fault | Y | 3 | DI-SP |  | B3/E05_C | [17 empty] | lamp2CC | OPRD1: E05/0/StaDev/ACBA1

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
E05 | 嘉民ES | 161 | 161kV | _12BUS | #1,#2 |  | V | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_12BUS_KV | 161KV #1,#2 BUS BEST SOURCE | BUS | E05/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
E05 | 嘉民ES | 161 | 161kV | _34BUS | #3,#4 |  | V | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_34BUS_KV | 161KV #3,#4 BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_161KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
E05 | 嘉民ES | 345 | 345kV | _12BUS | #1,#2 |  | V | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_12BUS_KV | 345KV #1,#2 BUS BEST SOURCE | BUS |  |  | BEST_SOURCE_345KV_2 |  |  | 4 | CalcAIPoint | [21 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_AMP | 麥寮二路 AMP | LINE345 | E05/345/3510/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_AMP | 麥寮一路 AMP | LINE345 | E05/345/3540/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_AMP | 中寮二路 AMP | LINE345 | E05/345/3570/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_AMP | 中寮一路 AMP | LINE345 | E05/345/3610/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_AMP | 中寮三路 AMP | LINE345 | E05/345/3640/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_AMP | 龍崎紅線 AMP | LINE345 | E05/345/3710/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3770_AMP | 新南科一路 AMP | LINE345 | E05/345/3770/I |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | I | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.3810_AMP | 新南科二路 AMP | LINE345 | E05/345/3810/I |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C40R3652 | 3286.800049 | 3286.800049 | 3652.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1510_AMP | 嘉義山線 AMP | LINE161 | E05/161/1510/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1520_AMP | 嘉義海線 AMP | LINE161 | E05/161/1520/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_AMP | 柳營山線 AMP | LINE161 | E05/161/1530/I |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_AMP | 柳營海線 AMP | LINE161 | E05/161/1540/I |  | AMP_CAL |  |  | 16 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1550_AMP | 雲林山線 AMP | LINE161 | E05/161/1550/I |  | AMP_CAL |  |  | 17 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1560_AMP | 雲林海線 AMP | LINE161 | E05/161/1560/I |  | AMP_CAL |  |  | 18 | CalcAIPoint | [21 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1580_AMP | 嘉民雲林線 AMP | LINE161 | E05/161/1580/I |  | AMP_CAL |  |  | 19 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1590_AMP | 斗工紅線 AMP | LINE161 | E05/161/1590/I |  | AMP_CAL |  |  | 20 | CalcAIPoint | [21 empty] | C20R1576 | 1418.000000 | 1418.000000 | 1576.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1610_AMP | 嘉義南線 AMP | LINE161 | E05/161/1610/I |  | AMP_CAL |  |  | 21 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1620_AMP | 嘉義北線 AMP | LINE161 | E05/161/1620/I |  | AMP_CAL |  |  | 22 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1630_AMP | 北港南線 AMP | LINE161 | E05/161/1630/I |  | AMP_CAL |  |  | 23 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1640_AMP | 北港北線 AMP | LINE161 | E05/161/1640/I |  | AMP_CAL |  |  | 24 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1710_AMP | 台嘉一路 AMP | LINE161 | E05/161/1710/I |  | AMP_CAL |  |  | 25 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1720_AMP | 台嘉二路 AMP | LINE161 | E05/161/1720/I |  | AMP_CAL |  |  | 26 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1730_AMP | 嘉惠一路 AMP | LINE161 | E05/161/1730/I |  | AMP_CAL |  |  | 27 | CalcAIPoint | [21 empty] | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.1740_AMP | 嘉惠二路 AMP | LINE161 | E05/161/1740/I |  | AMP_CAL |  |  | 28 | CalcAIPoint | [21 empty] | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_MVA | #1ATR二次側 MVA | ATR | E05//1ATR/MVA |  | MVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_LOAD | #1ATR 負載率 | ATR | E05//1ATR/Loading |  | TR_LOAD_500 |  |  | 30 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_PF | #1ATR 功率因素 | ATR | E05//1ATR/PF |  | RPDC_PF_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_AMP | #1ATR 二次側 AMP | ATR | E05//1ATR/I |  | AMP_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_MVA | #2ATR二次側 MVA | ATR | E05//2ATR/MVA |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_LOAD | #2ATR 負載率 | ATR | E05//2ATR/Loading |  | TR_LOAD_500 |  |  | 34 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_PF | #2ATR 功率因素 | ATR | E05//2ATR/PF |  | RPDC_PF_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_AMP | #2ATR 二次側 AMP | ATR | E05//2ATR/I |  | AMP_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_MVA | #3ATR二次側 MVA | ATR | E05//3ATR/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_LOAD | #3ATR 負載率 | ATR | E05//3ATR/Loading |  | TR_LOAD_500 |  |  | 38 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_PF | #3ATR 功率因素 | ATR | E05//3ATR/PF |  | RPDC_PF_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_AMP | #3ATR 二次側 AMP | ATR | E05//3ATR/I |  | AMP_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_MVA | #4ATR二次側 MVA | ATR | E05//4ATR/MVA |  | MVA_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_LOAD | #4ATR 負載率 | ATR | E05//4ATR/Loading |  | TR_LOAD_500 |  |  | 42 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_PF | #4ATR 功率因素 | ATR | E05//4ATR/PF |  | RPDC_PF_CAL |  |  | 43 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_AMP | #4ATR 二次側 AMP | ATR | E05//4ATR/I |  | AMP_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_MVA | #5ATR二次側 MVA | ATR | E05//5ATR/MVA |  | MVA_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_LOAD | #5ATR 負載率 | ATR | E05//5ATR/Loading |  | TR_LOAD_500 |  |  | 46 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_PF | #5ATR 功率因素 | ATR | E05//5ATR/PF |  | RPDC_PF_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_AMP | #5ATR 二次側 AMP | ATR | E05//5ATR/I |  | AMP_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_MVA | #6ATR二次側 MVA | ATR | E05//6ATR/MVA |  | MVA_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_LOAD | #6ATR 負載率 | ATR | E05//6ATR/Loading |  | TR_LOAD_500 |  |  | 50 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_PF | #6ATR 功率因素 | ATR | E05//6ATR/PF |  | RPDC_PF_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_AMP | #6ATR 二次側 AMP | ATR | E05//6ATR/I |  | AMP_CAL |  |  | 52 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | TRTOT | 嘉民主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.TRTOT_MW | 嘉民主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_7 |  |  | 53 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | STOTAL | 嘉民南轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.STOTAL_MW | 嘉民南轄區瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 54 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | STOTAL | 嘉民南轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 嘉民ES.STOTAL_MVAR | 嘉民南轄區瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | NTOTAL | 嘉民北轄區瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.NTOTAL_MW | 嘉民北轄區瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 56 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | NTOTAL | 嘉民北轄區瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 嘉民ES.NTOTAL_MVAR | 嘉民北轄區瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | SIPPTOTAL | 嘉民南轄區IPP瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.SIPPTOTAL_MW | 嘉民南轄區IPP瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 58 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | SIPPTOTAL | 嘉民南轄區IPP瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 嘉民ES.SIPPTOTAL_MVAR | 嘉民南轄區IPP瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | NIPPTOTAL | 嘉民北轄區IPP瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.NIPPTOTAL_MW | 嘉民北轄區IPP瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 60 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | NIPPTOTAL | 嘉民北轄區IPP瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 嘉民ES.NIPPTOTAL_MVAR | 嘉民北轄區IPP瞬時供電量 MVAR |  |  |  | MTR_PQ_CAL |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | TEN_DAYS02 | (1710+1720 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.TEN_DAYS02_MW | (1710+1720 MW) |  |  |  | MTR_PQ_CAL |  |  | 62 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_MVA | #8ATR二次側 MVA | ATR | E05//8ATR/MVA |  | MVA_CAL |  |  | 63 | CalcAIPoint | [21 empty] | LG_500 | 450.000000 | 500.000000 | 625.000000 | 650.000000 | 2.500000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_LOAD | #8ATR 負載率 | ATR | E05//8ATR/Loading |  | TR_LOAD_500 |  |  | 64 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | PF | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_PF | #8ATR 功率因素 | ATR | E05//8ATR/PF |  | RPDC_PF_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | I | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_AMP | #8ATR 二次側 AMP | ATR | E05//8ATR/I |  | AMP_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_1797 | 1617.000000 | 1797.000000 | 2246.000000 | 2336.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -200.000000
E05 | 嘉民ES | 0 |  | NIPPTOT | 嘉民北轄區IPP瞬時P(-) |  | MW(-) | [25 empty] | CDCS | [8 empty] | 嘉民ES.NIPPTOT_MW(-) | 嘉民北轄區IPP瞬時P(-) MW |  |  |  | ESIPP_HYV_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | 3NATR | #3ATR |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.#3NATR_MW | #3ATR 1670 CLOSE | ATR |  |  | 3NSATR_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | 3SATR | #3ATR |  | MW | [25 empty] | CDCS | [8 empty] | 嘉民ES.#3SATR_MW | #3ATR 1830 CLOSE | ATR |  |  | 3NSATR_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
E05 | 嘉民ES | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 嘉民ES.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_ES_6 |  |  | 70 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510_AMP | 麥寮二路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_AMP_A | 麥寮二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 71 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540_AMP | 麥寮一路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_AMP_A | 麥寮一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 72 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570_AMP | 中寮二路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_AMP_A | 中寮二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 73 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610_AMP | 中寮一路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_AMP_A | 中寮一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 74 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640_AMP | 中寮三路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_AMP_A | 中寮三路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710_AMP | 龍崎紅線 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_AMP_A | 龍崎紅線 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 76 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770_AMP | 新南科一路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3770_AMP_A | 新南科一路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810_AMP | 新南科二路 | [27 empty] | CDCS_N | [8 empty] | 嘉民ES.3810_AMP_A | 新南科二路 AMP 點燈 (AD) | LINE345 |  |  | MAP_SET |  |  | 78 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510_AMP | 嘉義山線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1510_AMP_A | 嘉義山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520_AMP | 嘉義海線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1520_AMP_A | 嘉義海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530_AMP | 柳營山線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_AMP_A | 柳營山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540_AMP | 柳營海線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_AMP_A | 柳營海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 82 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550_AMP | 雲林山線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1550_AMP_A | 雲林山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560_AMP | 雲林海線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1560_AMP_A | 雲林海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580_AMP | 嘉民雲林線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1580_AMP_A | 嘉民雲林線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590_AMP | 斗工紅線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1590_AMP_A | 斗工紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610_AMP | 嘉義南線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1610_AMP_A | 嘉義南線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620_AMP | 嘉義北線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1620_AMP_A | 嘉義北線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630_AMP | 北港南線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1630_AMP_A | 北港南線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640_AMP | 北港北線 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1640_AMP_A | 北港北線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710_AMP | 台嘉一路 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1710_AMP_A | 台嘉一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720_AMP | 台嘉二路 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1720_AMP_A | 台嘉二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730_AMP | 嘉惠一路 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1730_AMP_A | 嘉惠一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740_AMP | 嘉惠二路 | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.1740_AMP_A | 嘉惠二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR_MVA | #1ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_MVA_A | #1ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_PERM | #1ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR_MVA | #2ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_MVA_A | #2ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 97 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_PERM | #2ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR_MVA | #3ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_MVA_A | #3ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_PERM | #3ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 100 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR_MVA | #4ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_MVA_A | #4ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 101 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_PERM | #4ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 102 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR_MVA | #5ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_MVA_A | #5ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 103 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_PERM | #5ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 104 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR_MVA | #6ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_MVA_A | #6ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 105 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_PERM | #6ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 106 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR_MVA | #8ATR | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_MVA_A | #8ATR MVA 點燈 (AD) | ATR |  |  | MAP_SET |  |  | 107 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | PERM | [25 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_PERM | #8ATR TAP PERMISSION POINT | ATR |  |  | MTR_PERM |  |  | 108 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
E05 | 嘉民ES | 0 |  | DCP | 嘉民ES | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.DCP_A | 嘉民ES DC 二組P電源混接 | OTHER |  |  | DCPN_1 |  |  | 109 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | DCN | 嘉民ES | [27 empty] | ADCS_N | [8 empty] | 嘉民ES.DCN_A | 嘉民ES DC 二組N電源混接 | OTHER |  |  | DCPN_1 |  |  | 110 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 1BUS | #1BUS |  | V | [17 empty] | 3-82 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.345KV#1BUS_KV | 345KV #1BUS KV | BUS | E05/345/1BUS/V |  |  |  | CDC | 111 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 2BUS | #2BUS |  | V | [17 empty] | 3-83 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.345KV#2BUS_KV | 345KV #2BUS KV | BUS | E05/345/2BUS/V |  |  |  | CDC | 112 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 4.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | MW | [17 empty] | 3-93 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3610_MW | 中寮一路 MW | LINE345 | E05/345/3610/MW |  |  |  | CDC | 113 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | MVAR | [17 empty] | 3-94 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3610_MVAR | 中寮一路 MVAR | LINE345 | E05/345/3610/MVAR |  |  |  | CDC | 114 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | MW | [17 empty] | 3-90 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3570_MW | 中寮二路 MW | LINE345 | E05/345/3570/MW |  |  |  | CDC | 115 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | MVAR | [17 empty] | 3-91 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3570_MVAR | 中寮二路 MVAR | LINE345 | E05/345/3570/MVAR |  |  |  | CDC | 116 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | MW | [17 empty] | 3-96 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3640_MW | 中寮三路 MW | LINE345 | E05/345/3640/MW |  |  |  | CDC | 117 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | MVAR | [17 empty] | 3-97 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3640_MVAR | 中寮三路 MVAR | LINE345 | E05/345/3640/MVAR |  |  |  | CDC | 118 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | MW | [17 empty] | 3-9C | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3770_MW | 新南科一路 MW | LINE345 | E05/345/3770/MW |  |  |  | CDC | 119 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | MVAR | [17 empty] | 3-9D | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3770_MVAR | 新南科一路 MVAR | LINE345 | E05/345/3770/MVAR |  |  |  | CDC | 120 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | MW | [17 empty] | 3-99 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3710_MW | 龍崎紅線 MW | LINE345 | E05/345/3710/MW |  |  |  | CDC | 121 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | MVAR | [17 empty] | 3-9A | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3710_MVAR | 龍崎紅線 MVAR | LINE345 | E05/345/3710/MVAR |  |  |  | CDC | 122 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | MW | [17 empty] | 3-8A | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3540_MW | 麥寮一路 MW | LINE345 | E05/345/3540/MW |  |  |  | CDC | 123 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | MVAR | [17 empty] | 3-8B | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3540_MVAR | 麥寮一路 MVAR | LINE345 | E05/345/3540/MVAR |  |  |  | CDC | 124 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | MW | [17 empty] | 3-84 | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3510_MW | 麥寮二路 MW | LINE345 | E05/345/3510/MW |  |  |  | CDC | 125 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | MVAR | [17 empty] | 3-85 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3510_MVAR | 麥寮二路 MVAR | LINE345 | E05/345/3510/MVAR |  |  |  | CDC | 126 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | MW | [17 empty] | 3-9F | [5 empty] | MW_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3810_MW | 新南科二路 MW | LINE345 | E05/345/3810/MW |  |  |  | CDC | 127 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | MVAR | [17 empty] | 3-A0 | [5 empty] | MVAR_-2400_2400(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3810_MVAR | 新南科二路 MVAR | LINE345 | E05/345/3810/MVAR |  |  |  | CDC | 128 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1550_MW | 雲林山線 MW | LINE161 | E05/161/1550/MW |  |  |  | CDC | 129 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1550_MVAR | 雲林山線 MVAR | LINE161 | E05/161/1550/MVAR |  |  |  | CDC | 130 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | MW | [17 empty] | 1-89 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1560_MW | 雲林海線 MW | LINE161 | E05/161/1560/MW |  |  |  | CDC | 131 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | MVAR | [17 empty] | 1-8A | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1560_MVAR | 雲林海線 MVAR | LINE161 | E05/161/1560/MVAR |  |  |  | CDC | 132 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1640_MW | 北港北線 MW | LINE161 | E05/161/1640/MW |  |  |  | CDC | 133 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1640_MVAR | 北港北線 MVAR | LINE161 | E05/161/1640/MVAR |  |  |  | CDC | 134 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | MW | [17 empty] | 1-95 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1630_MW | 北港南線 MW | LINE161 | E05/161/1630/MW |  |  |  | CDC | 135 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | MVAR | [17 empty] | 1-96 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1630_MVAR | 北港南線 MVAR | LINE161 | E05/161/1630/MVAR |  |  |  | CDC | 136 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | MW | [17 empty] | 1-AB | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1620_MW | 嘉義北線 MW | LINE161 | E05/161/1620/MW |  |  |  | CDC | 137 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | MVAR | [17 empty] | 1-AC | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1620_MVAR | 嘉義北線 MVAR | LINE161 | E05/161/1620/MVAR |  |  |  | CDC | 138 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | MW | [17 empty] | 1-A8 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1610_MW | 嘉義南線 MW | LINE161 | E05/161/1610/MW |  |  |  | CDC | 139 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | MVAR | [17 empty] | 1-A9 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1610_MVAR | 嘉義南線 MVAR | LINE161 | E05/161/1610/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | MW | [17 empty] | 1-AE | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1540_MW | 柳營海線 MW | LINE161 | E05/161/1540/MW |  |  |  | CDC | 141 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | MVAR | [17 empty] | 1-AF | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1540_MVAR | 柳營海線 MVAR | LINE161 | E05/161/1540/MVAR |  |  |  | CDC | 142 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | MW | [17 empty] | 1-B7 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1510_MW | 嘉義山線 MW | LINE161 | E05/161/1510/MW |  |  |  | CDC | 143 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | MVAR | [17 empty] | 1-B8 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1510_MVAR | 嘉義山線 MVAR | LINE161 | E05/161/1510/MVAR |  |  |  | CDC | 144 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | MW | [17 empty] | 1-B4 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1520_MW | 嘉義海線 MW | LINE161 | E05/161/1520/MW |  |  |  | CDC | 145 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | MVAR | [17 empty] | 1-B5 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1520_MVAR | 嘉義海線 MVAR | LINE161 | E05/161/1520/MVAR |  |  |  | CDC | 146 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | MW | [17 empty] | 1-B1 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1530_MW | 柳營山線 MW | LINE161 | E05/161/1530/MW |  |  |  | CDC | 147 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | MVAR | [17 empty] | 1-B2 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1530_MVAR | 柳營山線 MVAR | LINE161 | E05/161/1530/MVAR |  |  |  | CDC | 148 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | MW | [17 empty] | 1-9B | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1590_MW | 斗工紅線 MW | LINE161 | E05/161/1590/MW |  |  |  | CDC | 149 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | MVAR | [17 empty] | 1-9C | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1590_MVAR | 斗工紅線 MVAR | LINE161 | E05/161/1590/MVAR |  |  |  | CDC | 150 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | MW | [17 empty] | 1-98 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1580_MW | 嘉民雲林線 MW | LINE161 | E05/161/1580/MW |  |  |  | CDC | 151 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | MVAR | [17 empty] | 1-99 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1580_MVAR | 嘉民雲林線 MVAR | LINE161 | E05/161/1580/MVAR |  |  |  | CDC | 152 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1710_MW | 台嘉一路 MW | LINE161 | E05/161/1710/MW |  |  |  | CDC | 153 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1710_MVAR | 台嘉一路 MVAR | LINE161 | E05/161/1710/MVAR |  |  |  | CDC | 154 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | MW | [17 empty] | 1-8F | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1720_MW | 台嘉二路 MW | LINE161 | E05/161/1720/MW |  |  |  | CDC | 155 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | MVAR | [17 empty] | 1-90 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1720_MVAR | 台嘉二路 MVAR | LINE161 | E05/161/1720/MVAR |  |  |  | CDC | 156 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | MW | [17 empty] | 1-A2 | [5 empty] | MW_-1120_1120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1730_MW | 嘉惠一路 MW | LINE161 | E05/161/1730/MW |  |  |  | CDC | 157 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | MVAR | [17 empty] | 1-A3 | [5 empty] | MVAR_-1120_1120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1730_MVAR | 嘉惠一路 MVAR | LINE161 | E05/161/1730/MVAR |  |  |  | CDC | 158 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | MW | [17 empty] | 1-A5 | [5 empty] | MW_-1120_1120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1740_MW | 嘉惠二路 MW | LINE161 | E05/161/1740/MW |  |  |  | CDC | 159 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | MVAR | [17 empty] | 1-A6 | [5 empty] | MVAR_-1120_1120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1740_MVAR | 嘉惠二路 MVAR | LINE161 | E05/161/1740/MVAR |  |  |  | CDC | 160 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 2.240000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | E05/0/RTU/ADCH1 |  |  |  | CDC | 161 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | E05/0/RTU/ADCH2 |  |  |  | CDC | 162 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 3-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | E05/0/RTU/ADCH3 |  |  |  | CDC | 163 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 3-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | E05/0/RTU/ADCH4 |  |  |  | CDC | 164 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | E05/0/RTU/ADCL1 |  |  |  | CDC | 165 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | E05/0/RTU/ADCL2 |  |  |  | CDC | 166 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 3-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | E05/0/RTU/ADCL3 |  |  |  | CDC | 167 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 3-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | E05/0/RTU/ADCL4 |  |  |  | CDC | 168 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-82 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.161KV#1BUS_KV | 161KV #1BUS KV | BUS | E05/161/1BUS/V |  |  |  | CDC | 169 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-83 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.161KV#2BUS_KV | 161KV #2BUS KV | BUS | E05/161/2BUS/V |  |  |  | CDC | 170 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 3BUS | #3BUS |  | V | [17 empty] | 1-9E | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.161KV#3BUS_KV | 161KV #3BUS KV | BUS | E05/161/3BUS/V |  |  |  | CDC | 171 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 4BUS | #4BUS |  | V | [17 empty] | 1-9F | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.161KV#4BUS_KV | 161KV #4BUS KV | BUS | E05/161/4BUS/V |  |  |  | CDC | 172 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
E05 | 嘉民ES | 345 | 345kV | 3510LPD | 麥寮二路(3510) |  | V | [17 empty] | 3-86 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3510LPD_KV | 麥寮二路(3510) LPD KV | LINE345 | E05/345/3510/V |  |  |  | CDC | 173 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3540LPD | 麥寮一路(3540) |  | V | [17 empty] | 3-8C | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3540LPD_KV | 麥寮一路(3540) LPD KV | LINE345 | E05/345/3540/V |  |  |  | CDC | 174 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3570LPD | 中寮二路(3570) |  | V | [17 empty] | 3-92 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3570LPD_KV | 中寮二路(3570) LPD KV | LINE345 | E05/345/3570/V |  |  |  | CDC | 175 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3610LPD | 中寮一路(3610) |  | V | [17 empty] | 3-95 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3610LPD_KV | 中寮一路(3610) LPD KV | LINE345 | E05/345/3610/V |  |  |  | CDC | 176 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3640LPD | 中寮三路(3640) |  | V | [17 empty] | 3-98 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3640LPD_KV | 中寮三路(3640) LPD KV | LINE345 | E05/345/3640/V |  |  |  | CDC | 177 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3710LPD | 龍崎紅線(3710) |  | V | [17 empty] | 3-9B | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3710LPD_KV | 龍崎紅線(3710) LPD KV | LINE345 | E05/345/3710/V |  |  |  | CDC | 178 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3770LPD | 新南科一路(3770) |  | V | [17 empty] | 3-9E | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3770LPD_KV | 新南科一路(3770) LPD KV | LINE345 | E05/345/3770/V |  |  |  | CDC | 179 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 345 | 345kV | 3810LPD | 新南科二路(3810) |  | V | [17 empty] | 3-A1 | [5 empty] | kV_-450_450(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.3810LPD_KV | 新南科二路(3810) LPD KV | LINE345 | E05/345/3810/V |  |  |  | CDC | 180 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_345 | 362.250000 | 362.250000 | 362.250000 | 450.000000 | 0.500000 | 327.750000 | 327.750000 | 327.750000 | 0.000000 | 5.000000 | 20.000000
E05 | 嘉民ES | 161 | 161kV | 1510LPD | 嘉義山線(1510) |  | V | [17 empty] | 1-B9 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1510LPD_KV | 嘉義山線(1510) LPD KV | LINE161 | E05/161/1510/V |  |  |  | CDC | 181 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1520LPD | 嘉義海線(1520) |  | V | [17 empty] | 1-B6 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1520LPD_KV | 嘉義海線(1520) LPD KV | LINE161 | E05/161/1520/V |  |  |  | CDC | 182 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1530LPD | 柳營山線(1530) |  | V | [17 empty] | 1-B3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1530LPD_KV | 柳營山線(1530) LPD KV | LINE161 | E05/161/1530/V |  |  |  | CDC | 183 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1540LPD | 柳營海線(1540) |  | V | [17 empty] | 1-B0 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1540LPD_KV | 柳營海線(1540) LPD KV | LINE161 | E05/161/1540/V |  |  |  | CDC | 184 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1550LPD | 雲林山線(1550) |  | V | [17 empty] | 1-88 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1550LPD_KV | 雲林山線(1550) LPD KV | LINE161 | E05/161/1550/V |  |  |  | CDC | 185 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1560LPD | 雲林海線(1560) |  | V | [17 empty] | 1-8B | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1560LPD_KV | 雲林海線(1560) LPD KV | LINE161 | E05/161/1560/V |  |  |  | CDC | 186 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1580LPD | 嘉民雲林線(1580) |  | V | [17 empty] | 1-9A | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1580LPD_KV | 嘉民雲林線(1580) LPD KV | LINE161 | E05/161/1580/V |  |  |  | CDC | 187 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1590LPD | 斗工紅線(1590) |  | V | [17 empty] | 1-9D | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1590LPD_KV | 斗工紅線(1590) LPD KV | LINE161 | E05/161/1590/V |  |  |  | CDC | 188 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1610LPD | 嘉義南線(1610) |  | V | [17 empty] | 1-AA | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1610LPD_KV | 嘉義南線(1610) LPD KV | LINE161 | E05/161/1610/V |  |  |  | CDC | 189 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1620LPD | 嘉義北線(1620) |  | V | [17 empty] | 1-AD | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1620LPD_KV | 嘉義北線(1620) LPD KV | LINE161 | E05/161/1620/V |  |  |  | CDC | 190 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1630LPD | 北港南線(1630) |  | V | [17 empty] | 1-97 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1630LPD_KV | 北港南線(1630) LPD KV | LINE161 | E05/161/1630/V |  |  |  | CDC | 191 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1640LPD | 北港北線(1640) |  | V | [17 empty] | 1-94 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1640LPD_KV | 北港北線(1640) LPD KV | LINE161 | E05/161/1640/V |  |  |  | CDC | 192 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1710LPD | 台嘉一路(1710) |  | V | [17 empty] | 1-8E | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1710LPD_KV | 台嘉一路(1710) LPD KV | LINE161 | E05/161/1710/V |  |  |  | CDC | 193 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1720LPD | 台嘉二路(1720) |  | V | [17 empty] | 1-91 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1720LPD_KV | 台嘉二路(1720) LPD KV | LINE161 | E05/161/1720/V |  |  |  | CDC | 194 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1730LPD | 嘉惠一路(1730) |  | V | [17 empty] | 1-A4 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1730LPD_KV | 嘉惠一路(1730) LPD KV | LINE161 | E05/161/1730/V |  |  |  | CDC | 195 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1740LPD | 嘉惠二路(1740) |  | V | [17 empty] | 1-A7 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1740LPD_KV | 嘉惠二路(1740) LPD KV | LINE161 | E05/161/1740/V |  |  |  | CDC | 196 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1500TIE_AMP | 1500TIE AMP | TIE | E05/161/1500/I |  |  |  | CDC | 197 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | 1600TIE | 1600TIE |  | I | [17 empty] | 1-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1600TIE_AMP | 1600TIE AMP | TIE | E05/161/1600/I |  |  |  | CDC | 198 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
E05 | 嘉民ES | 0 |  | 1700TIE | 1700TIE |  | I | [17 empty] | 1-85 | [5 empty] | A_-4000_4000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1700TIE_AMP | 1700TIE AMP | TIE | E05/161/1700/I |  |  |  | CDC | 199 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 4.000000 | 0.010000
E05 | 嘉民ES | 0 |  | 1800TIE | 1800TIE |  | I | [17 empty] | 1-A1 | [5 empty] | A_-4000_4000(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.1800TIE_AMP | 1800TIE AMP | TIE | E05/161/1800/I |  |  |  | CDC | 200 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | C40R4000 | 3600.000000 | 3600.000000 | 4000.000000 | 4000.000000 | 1.200000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 4.000000 | 0.010000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR二次側 |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#1ATR_MW | #1ATR二次側 MW | ATR | E05/345/3590/MW |  |  |  | CDC | 201 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR二次側 |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#1ATR_MVAR | #1ATR二次側 MVAR | ATR | E05/345/3590/MVAR |  |  |  | CDC | 202 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | TapPosMv | [17 empty] | 3-A2 |  | 3-77 |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_TAP | #1ATR OLTC TAP | ATR | E05//1ATR/TapPosMv |  |  |  | CDC | 203 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 1ATR_OIL | #1ATR |  | R | [17 empty] | 3-A4 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_OIL_R | #1ATR R相油溫 | ATR | E05//1ATR/Oil_R |  |  |  | CDC | 204 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_COIL | #1ATR |  | R | [17 empty] | 3-A3 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_COIL_R | #1ATR R相線溫 | ATR | E05//1ATR/Coil_R |  |  |  | CDC | 205 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_OIL | #1ATR |  | S | [17 empty] | 3-A6 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_OIL_S | #1ATR S相油溫 | ATR | E05//1ATR/Oil_S |  |  |  | CDC | 206 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_COIL | #1ATR |  | S | [17 empty] | 3-A5 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_COIL_S | #1ATR S相線溫 | ATR | E05//1ATR/Coil_S |  |  |  | CDC | 207 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_OIL | #1ATR |  | T | [17 empty] | 3-A8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_OIL_T | #1ATR T相油溫 | ATR | E05//1ATR/Oil_T |  |  |  | CDC | 208 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_COIL | #1ATR |  | T | [17 empty] | 3-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#1ATR_COIL_T | #1ATR T相線溫 | ATR | E05//1ATR/Coil_T |  |  |  | CDC | 209 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR二次側 |  | MW | [17 empty] | 1-C4 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#2ATR_MW | #2ATR二次側 MW | ATR | E05/345/3630/MW |  |  |  | CDC | 210 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR二次側 |  | MVAR | [17 empty] | 1-C5 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#2ATR_MVAR | #2ATR二次側 MVAR | ATR | E05/345/3630/MVAR |  |  |  | CDC | 211 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | TapPosMv | [17 empty] | 3-A9 |  | 3-7B |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_TAP | #2ATR OLTC TAP | ATR | E05//2ATR/TapPosMv |  |  |  | CDC | 212 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 2ATR_OIL | #2ATR |  | R | [17 empty] | 3-AB | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_OIL_R | #2ATR R相油溫 | ATR | E05//2ATR/Oil_R |  |  |  | CDC | 213 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_COIL | #2ATR |  | R | [17 empty] | 3-AA | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_COIL_R | #2ATR R相線溫 | ATR | E05//2ATR/Coil_R |  |  |  | CDC | 214 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_OIL | #2ATR |  | S | [17 empty] | 3-AD | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_OIL_S | #2ATR S相油溫 | ATR | E05//2ATR/Oil_S |  |  |  | CDC | 215 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_COIL | #2ATR |  | S | [17 empty] | 3-AC | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_COIL_S | #2ATR S相線溫 | ATR | E05//2ATR/Coil_S |  |  |  | CDC | 216 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_OIL | #2ATR |  | T | [17 empty] | 3-AF | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_OIL_T | #2ATR T相油溫 | ATR | E05//2ATR/Oil_T |  |  |  | CDC | 217 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_COIL | #2ATR |  | T | [17 empty] | 3-AE | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#2ATR_COIL_T | #2ATR T相線溫 | ATR | E05//2ATR/Coil_T |  |  |  | CDC | 218 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR二次側 |  | MW | [17 empty] | 1-C6 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#3ATR_MW | #3ATR二次側 MW | ATR | E05/345/3660/MW |  |  |  | CDC | 219 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR二次側 |  | MVAR | [17 empty] | 1-C7 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#3ATR_MVAR | #3ATR二次側 MVAR | ATR | E05/345/3660/MVAR |  |  |  | CDC | 220 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | TapPosMv | [17 empty] | 3-B0 |  | 3-7F |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_TAP | #3ATR OLTC TAP | ATR | E05//3ATR/TapPosMv |  |  |  | CDC | 221 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 3ATR_OIL | #3ATR |  | R | [17 empty] | 3-B2 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_OIL_R | #3ATR R相油溫 | ATR | E05//3ATR/Oil_R |  |  |  | CDC | 222 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_COIL | #3ATR |  | R | [17 empty] | 3-B1 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_COIL_R | #3ATR R相線溫 | ATR | E05//3ATR/Coil_R |  |  |  | CDC | 223 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_OIL | #3ATR |  | S | [17 empty] | 3-B4 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_OIL_S | #3ATR S相油溫 | ATR | E05//3ATR/Oil_S |  |  |  | CDC | 224 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_COIL | #3ATR |  | S | [17 empty] | 3-B3 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_COIL_S | #3ATR S相線溫 | ATR | E05//3ATR/Coil_S |  |  |  | CDC | 225 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_OIL | #3ATR |  | T | [17 empty] | 3-B6 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_OIL_T | #3ATR T相油溫 | ATR | E05//3ATR/Oil_T |  |  |  | CDC | 226 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_COIL | #3ATR |  | T | [17 empty] | 3-B5 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#3ATR_COIL_T | #3ATR T相線溫 | ATR | E05//3ATR/Coil_T |  |  |  | CDC | 227 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR二次側 |  | MW | [17 empty] | 1-C8 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#4ATR_MW | #4ATR二次側 MW | ATR | E05/345/3730/MW |  |  |  | CDC | 228 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR二次側 |  | MVAR | [17 empty] | 1-C9 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#4ATR_MVAR | #4ATR二次側 MVAR | ATR | E05/345/3730/MVAR |  |  |  | CDC | 229 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | TapPosMv | [17 empty] | 3-B7 |  | 4-03 |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_TAP | #4ATR OLTC TAP | ATR | E05//4ATR/TapPosMv |  |  |  | CDC | 230 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 4ATR_OIL | #4ATR |  | R | [17 empty] | 3-B9 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_OIL_R | #4ATR R相油溫 | ATR | E05//4ATR/Oil_R |  |  |  | CDC | 231 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_COIL | #4ATR |  | R | [17 empty] | 3-B8 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_COIL_R | #4ATR R相線溫 | ATR | E05//4ATR/Coil_R |  |  |  | CDC | 232 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_OIL | #4ATR |  | S | [17 empty] | 3-BB | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_OIL_S | #4ATR S相油溫 | ATR | E05//4ATR/Oil_S |  |  |  | CDC | 233 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_COIL | #4ATR |  | S | [17 empty] | 3-BA | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_COIL_S | #4ATR S相線溫 | ATR | E05//4ATR/Coil_S |  |  |  | CDC | 234 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_OIL | #4ATR |  | T | [17 empty] | 3-BD | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_OIL_T | #4ATR T相油溫 | ATR | E05//4ATR/Oil_T |  |  |  | CDC | 235 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_COIL | #4ATR |  | T | [17 empty] | 3-BC | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#4ATR_COIL_T | #4ATR T相線溫 | ATR | E05//4ATR/Coil_T |  |  |  | CDC | 236 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR二次側 |  | MW | [17 empty] | 1-CA | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#5ATR_MW | #5ATR二次側 MW | ATR | E05/345/3790/MW |  |  |  | CDC | 237 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR二次側 |  | MVAR | [17 empty] | 1-CB | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#5ATR_MVAR | #5ATR二次側 MVAR | ATR | E05/345/3790/MVAR |  |  |  | CDC | 238 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | TapPosMv | [17 empty] | 3-C2 |  | 4-07 |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_TAP | #5ATR OLTC TAP | ATR | E05//5ATR/TapPosMv |  |  |  | CDC | 239 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 5ATR_OIL | #5ATR |  | R | [17 empty] | 3-C4 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_OIL_R | #5ATR R相油溫 | ATR | E05//5ATR/Oil_R |  |  |  | CDC | 240 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_COIL | #5ATR |  | R | [17 empty] | 3-C3 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_COIL_R | #5ATR R相線溫 | ATR | E05//5ATR/Coil_R |  |  |  | CDC | 241 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_OIL | #5ATR |  | S | [17 empty] | 3-C6 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_OIL_S | #5ATR S相油溫 | ATR | E05//5ATR/Oil_S |  |  |  | CDC | 242 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_COIL | #5ATR |  | S | [17 empty] | 3-C5 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_COIL_S | #5ATR S相線溫 | ATR | E05//5ATR/Coil_S |  |  |  | CDC | 243 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_OIL | #5ATR |  | T | [17 empty] | 3-C8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_OIL_T | #5ATR T相油溫 | ATR | E05//5ATR/Oil_T |  |  |  | CDC | 244 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_COIL | #5ATR |  | T | [17 empty] | 3-C7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#5ATR_COIL_T | #5ATR T相線溫 | ATR | E05//5ATR/Coil_T |  |  |  | CDC | 245 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR二次側 |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#6ATR_MW | #6ATR二次側 MW | ATR | E05/345/3830/MW |  |  |  | CDC | 246 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR二次側 |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#6ATR_MVAR | #6ATR二次側 MVAR | ATR | E05/345/3830/MVAR |  |  |  | CDC | 247 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | TapPosMv | [17 empty] | 3-C9 |  | 4-0B |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_TAP | #6ATR OLTC TAP | ATR | E05//6ATR/TapPosMv |  |  |  | CDC | 248 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 6ATR_OIL | #6ATR |  | R | [17 empty] | 3-CB | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_OIL_R | #6ATR R相油溫 | ATR | E05//6ATR/Oil_R |  |  |  | CDC | 249 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_COIL | #6ATR |  | R | [17 empty] | 3-CA | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_COIL_R | #6ATR R相線溫 | ATR | E05//6ATR/Coil_R |  |  |  | CDC | 250 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_OIL | #6ATR |  | S | [17 empty] | 3-CD | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_OIL_S | #6ATR S相油溫 | ATR | E05//6ATR/Oil_S |  |  |  | CDC | 251 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_COIL | #6ATR |  | S | [17 empty] | 3-CC | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_COIL_S | #6ATR S相線溫 | ATR | E05//6ATR/Coil_S |  |  |  | CDC | 252 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_OIL | #6ATR |  | T | [17 empty] | 3-CF | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_OIL_T | #6ATR T相油溫 | ATR | E05//6ATR/Oil_T |  |  |  | CDC | 253 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_COIL | #6ATR |  | T | [17 empty] | 3-CE | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#6ATR_COIL_T | #6ATR T相線溫 | ATR | E05//6ATR/Coil_T |  |  |  | CDC | 254 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  |  |  |  | #2直流N電源 | [17 empty] | 3-D3 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#2直流N電源 | #2直流N電源電壓 | OTHER | E05/0/StaDev/2_DCV_N |  |  |  | CDC | 255 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 0 |  |  |  |  | #2直流P電源 | [17 empty] | 3-D2 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#2直流P電源 | #2直流P電源電壓 | OTHER | E05/0/StaDev/2_DCV_P |  |  |  | CDC | 256 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 0 |  |  |  |  | #1直流N電源 | [17 empty] | 3-D1 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#1直流N電源 | #1直流N電源電壓 | OTHER | E05/0/StaDev/1_DCV_N |  |  |  | CDC | 257 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 0 |  |  |  |  | #1直流P電源 | [17 empty] | 3-D0 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#1直流P電源 | #1直流P電源電壓 | OTHER | E05/0/StaDev/1_DCV_P |  |  |  | CDC | 258 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民台嘉一路(1510) |  | MW | [17 empty] | 1-E0 | [5 empty] | MW_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.1510_MW | 嘉民台嘉一路 MW | LINE161 | C21/161/1510/MW |  |  |  | CDC | 259 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.570000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉民台嘉一路(1510) |  | MVAR | [17 empty] | 1-E1 | [5 empty] | MVAR_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.1510_MVAR | 嘉民台嘉一路 MVAR | LINE161 | C21/161/1510/MVAR |  |  |  | CDC | 260 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.570000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1510LPD | 嘉民台嘉一路(1510) |  | V | [17 empty] | 1-E2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.1510LPD_KV | 嘉民台嘉一路(1510) LPD KV | LINE161 | C21/161/1510/V |  |  |  | CDC | 261 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民台嘉二路(1520) |  | MW | [17 empty] | 1-E3 | [5 empty] | MW_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.1520_MW | 嘉民台嘉二路 MW | LINE161 | C21/161/1520/MW |  |  |  | CDC | 262 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.544000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉民台嘉二路(1520) |  | MVAR | [17 empty] | 1-E4 | [5 empty] | MVAR_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.1520_MVAR | 嘉民台嘉二路 MVAR | LINE161 | C21/161/1520/MVAR |  |  |  | CDC | 263 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.544000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 1520LPD | 嘉民台嘉二路(1520) |  | V | [17 empty] | 1-E5 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.1520LPD_KV | 嘉民台嘉二路(1520) LPD KV | LINE161 | C21/161/1520/V |  |  |  | CDC | 264 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | D_KEY | [16 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 3GTR | 台嘉CS |  | MW | [17 empty] | 1-E6 | [5 empty] | MW_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.#3GTR_MW | 台嘉CS #3GTR MW | LINE161 | C21/161/3GTR/MW |  |  |  | CDC | 265 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.310000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 3GTR | 台嘉CS |  | MVAR | [17 empty] | 1-E7 | [5 empty] | MVAR_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.#3GTR_MVAR | 台嘉CS #3GTR MVAR | LINE161 | C21/161/3GTR/MVAR |  |  |  | CDC | 266 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.310000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 3GTRLPD | 台嘉CS |  | V | [17 empty] | 1-E8 | [5 empty] | kV_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.#3GTRLPD_KV | 台嘉CS #3GTR LPD KV | LINE161 | C21/161/3GTR/V |  |  |  | CDC | 267 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 161 | 161kV | 4GTR | 台嘉CS |  | MW | [17 empty] | 1-E9 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.#4GTR_MW | 台嘉CS #4GTR MW | LINE161 | C21/161/4GTR/MW |  |  |  | CDC | 268 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.976000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 4GTR | 台嘉CS |  | MVAR | [17 empty] | 1-EA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.#4GTR_MVAR | 台嘉CS #4GTR MVAR | LINE161 | C21/161/4GTR/MVAR |  |  |  | CDC | 269 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.976000 | 0.010000
E05 | 嘉民ES | 161 | 161kV | 4GTRLPD | 台嘉CS |  | V | [17 empty] | 1-EB | [5 empty] | kV_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 台嘉CS.#4GTRLPD_KV | 台嘉CS #4GTR LPD KV | LINE161 | C21/161/4GTR/V |  |  |  | CDC | 270 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR二次側 |  | MW | [17 empty] | 3-D5 | [5 empty] | MW_-840_840(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#8ATR_MW | #8ATR二次側 MW | ATR | E05/345/3530/MW |  |  |  | CDC | 271 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.840000 | 0.010000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR二次側 |  | MVAR | [17 empty] | 3-D6 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#8ATR_MVAR | #8ATR二次側 MVAR | ATR | E05/345/3530/MVAR |  |  |  | CDC | 272 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.560000 | 0.010000
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | TapPosMv | [17 empty] | 3-D4 |  | 4-27 |  |  |  | TAP_-5.5_10.5(0_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#8ATR_TAP | #8ATR OLTC TAP | ATR | E05//8ATR/TapPosMv |  |  |  | CDC | 273 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | TAP10_5 | 9.000000 | 9.000000 | 10.000000 | 10.500000 | 0.000000 | -4.000000 | -4.000000 | -5.000000 | -5.500000 | 0.100000
E05 | 嘉民ES | 0 |  | 8ATR_OIL | #8ATR |  | R | [17 empty] | 3-D8 | [5 empty] | OIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#8ATR_OIL_R | #8ATR 油溫 | ATR | E05//8ATR/Oil_R |  |  |  | CDC | 274 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 8ATR_COIL | #8ATR |  | R | [17 empty] | 3-D7 | [5 empty] | COIL_-120_120(-2000_2000) |  | CDCS_N | [8 empty] | 嘉民ES.#8ATR_COIL_R | #8ATR 線溫 | ATR | E05//8ATR/Coil_R |  |  |  | CDC | 275 | GENERICAIPoint | ES005_L3 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_SR | #1ATR |  | CoilTemp | [17 empty] | 1-D0 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SR_COIL | #1ATR 二次側 SR 線溫 | OTHER | E05/161/1SR/CoilTemp |  |  |  | CDC | 276 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 1ATR_SR | #1ATR |  | OilTemp | [17 empty] | 1-D1 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SR_OIL | #1ATR 二次側 SR 油溫 | OTHER | E05/161/1SR/OilTemp |  |  |  | CDC | 277 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_SR | #2ATR |  | CoilTemp | [17 empty] | 1-D2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SR_COIL | #2ATR 二次側 SR 線溫 | OTHER | E05/161/2SR/CoilTemp |  |  |  | CDC | 278 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 2ATR_SR | #2ATR |  | OilTemp | [17 empty] | 1-D3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SR_OIL | #2ATR 二次側 SR 油溫 | OTHER | E05/161/2SR/OilTemp |  |  |  | CDC | 279 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_SR | #3ATR |  | CoilTemp | [17 empty] | 1-D4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#3ATR_SR_COIL | #3ATR 二次側 SR 線溫 | OTHER | E05/161/3SR/CoilTemp |  |  |  | CDC | 280 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 3ATR_SR | #3ATR |  | OilTemp | [17 empty] | 1-D5 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#3ATR_SR_OIL | #3ATR 二次側 SR 油溫 | OTHER | E05/161/3SR/OilTemp |  |  |  | CDC | 281 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_SR | #4ATR |  | CoilTemp | [17 empty] | 1-D6 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#4ATR_SR_COIL | #4ATR 二次側 SR 線溫 | OTHER | E05/161/4SR/CoilTemp |  |  |  | CDC | 282 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 4ATR_SR | #4ATR |  | OilTemp | [17 empty] | 1-D7 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#4ATR_SR_OIL | #4ATR 二次側 SR 油溫 | OTHER | E05/161/4SR/OilTemp |  |  |  | CDC | 283 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_SR | #5ATR |  | CoilTemp | [17 empty] | 1-D8 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SR_COIL | #5ATR 二次側 SR 線溫 | OTHER | E05/161/5SR/CoilTemp |  |  |  | CDC | 284 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 5ATR_SR | #5ATR |  | OilTemp | [17 empty] | 1-D9 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SR_OIL | #5ATR 二次側 SR 油溫 | OTHER | E05/161/5SR/OilTemp |  |  |  | CDC | 285 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_SR | #6ATR |  | CoilTemp | [17 empty] | 1-DA | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SR_COIL | #6ATR 二次側 SR 線溫 | OTHER | E05/161/6SR/CoilTemp |  |  |  | CDC | 286 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 0 |  | 6ATR_SR | #6ATR |  | OilTemp | [17 empty] | 1-DB | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SR_OIL | #6ATR 二次側 SR 油溫 | OTHER | E05/161/6SR/OilTemp |  |  |  | CDC | 287 | GENERICAIPoint | ES005_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | CB | [17 empty] | 3-00-00 |  | 3-01 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_CB | 3510(麥寮二路) CB | LINE345 | E05/345/3510/CB |  |  |  | CDC | 288 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | CB | [17 empty] | 3-00-02 |  | 3-03 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3530_CB | 3530(#8ATR) CB | ATR | E05/345/3530/CB |  |  |  | CDC | 289 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | CB | [17 empty] | 3-00-03 |  | 3-04 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_CB | 3540(麥寮一路) CB | LINE345 | E05/345/3540/CB |  |  |  | CDC | 290 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | CB | [17 empty] | 3-00-05 |  | 3-06 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3560_CB | 3560 CB | LINE345 | E05/345/3560/CB |  |  |  | CDC | 291 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | CB | [17 empty] | 3-00-06 |  | 3-07 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3570_CB | 3570(中寮二路) CB | LINE345 | E05/345/3570/CB |  |  |  | CDC | 292 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3580 | 3580 |  | CB | [17 empty] | 3-00-07 |  | 3-08 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3580_CB | 3580 CB | LINE345 | E05/345/3580/CB |  |  |  | CDC | 293 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | CB | [17 empty] | 3-01-00 |  | 3-09 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3590_CB | 3590(#1ATR) CB | ATR | E05/345/3590/CB |  |  |  | CDC | 294 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | CB | [17 empty] | 3-01-02 |  | 3-0C | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3610_CB | 3610(中寮一路) CB | LINE345 | E05/345/3610/CB |  |  |  | CDC | 295 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3620 | 3620 |  | CB | [17 empty] | 3-01-03 |  | 3-0D | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3620_CB | 3620 CB | LINE345 | E05/345/3620/CB |  |  |  | CDC | 296 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | CB | [17 empty] | 3-01-04 |  | 3-0E | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3630_CB | 3630(#2ATR) CB | ATR | E05/345/3630/CB |  |  |  | CDC | 297 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | CB | [17 empty] | 3-01-06 |  | 3-11 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3640_CB | 3640(中寮三路) CB | LINE345 | E05/345/3640/CB |  |  |  | CDC | 298 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3650 | 3650 |  | CB | [17 empty] | 3-01-07 |  | 3-12 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3650_CB | 3650 CB | LINE345 | E05/345/3650/CB |  |  |  | CDC | 299 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | CB | [17 empty] | 3-02-00 |  | 3-13 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3660_CB | 3660(#3ATR) CB | ATR | E05/345/3660/CB |  |  |  | CDC | 300 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | CB | [17 empty] | 3-02-02 |  | 3-16 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3710_CB | 3710(龍崎紅線) CB | LINE345 | E05/345/3710/CB |  |  |  | CDC | 301 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3720 | 3720 |  | CB | [17 empty] | 3-02-03 |  | 3-17 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3720_CB | 3720 CB | LINE345 | E05/345/3720/CB |  |  |  | CDC | 302 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | CB | [17 empty] | 3-02-04 |  | 3-18 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3730_CB | 3730(#4ATR) CB | ATR | E05/345/3730/CB |  |  |  | CDC | 303 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | CB | [17 empty] | 3-02-06 |  | 3-1B | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3770_CB | 3770(新南科一路) CB | LINE345 | E05/345/3770/CB |  |  |  | CDC | 304 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3780 | 3780 |  | CB | [17 empty] | 3-02-07 |  | 3-1C | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3780_CB | 3780 CB | LINE345 | E05/345/3780/CB |  |  |  | CDC | 305 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | CB | [17 empty] | 3-03-00 |  | 3-1D | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3790_CB | 3790(#5ATR) CB | ATR | E05/345/3790/CB |  |  |  | CDC | 306 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | CB | [17 empty] | 3-03-02 |  | 3-20 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3810_CB | 3810(新南科二路) CB | LINE345 | E05/345/3810/CB |  |  |  | CDC | 307 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3820 | 3820 |  | CB | [17 empty] | 3-03-03 |  | 3-21 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3820_CB | 3820 CB | LINE345 | E05/345/3820/CB |  |  |  | CDC | 308 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | CB | [17 empty] | 3-03-04 |  | 3-22 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3830_CB | 3830(#6ATR) CB | ATR | E05/345/3830/CB |  |  |  | CDC | 309 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-07-02 |  | 1-18 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1500_CB | 1500(TIE) CB | TIE | E05/161/1500/CB |  |  |  | CDC | 310 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | CB | [17 empty] | 1-03-06 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1510_CB | 1510(嘉義山線) CB | LINE161 | E05/161/1510/CB |  |  |  | CDC | 311 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | CB | [17 empty] | 1-03-02 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1520_CB | 1520(嘉義海線) CB | LINE161 | E05/161/1520/CB |  |  |  | CDC | 312 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | CB | [17 empty] | 1-05-06 |  | 1-11 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1530_CB | 1530(柳營山線) CB | LINE161 | E05/161/1530/CB |  |  |  | CDC | 313 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | CB | [17 empty] | 1-05-02 |  | 1-10 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1540_CB | 1540(柳營海線) CB | LINE161 | E05/161/1540/CB |  |  |  | CDC | 314 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | CB | [17 empty] | 1-00-06 |  | 1-07 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1550_CB | 1550(雲林山線) CB | LINE161 | E05/161/1550/CB |  |  |  | CDC | 315 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | CB | [17 empty] | 1-01-02 |  | 1-08 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1560_CB | 1560(雲林海線) CB | LINE161 | E05/161/1560/CB |  |  |  | CDC | 316 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | CB | [17 empty] | 1-06-06 |  | 1-13 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1580_CB | 1580(嘉民雲林線) CB | LINE161 | E05/161/1580/CB |  |  |  | CDC | 317 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | CB | [17 empty] | 1-06-02 |  | 1-12 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1590_CB | 1590(斗工紅線) CB | LINE161 | E05/161/1590/CB |  |  |  | CDC | 318 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | CB | [17 empty] | 1-07-04 |  | 1-19 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1600_CB | 1600(TIE) CB | TIE | E05/161/1600/CB |  |  |  | CDC | 319 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | CB | [17 empty] | 1-04-02 |  | 1-0E | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1610_CB | 1610(嘉義南線) CB | LINE161 | E05/161/1610/CB |  |  |  | CDC | 320 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | CB | [17 empty] | 1-04-06 |  | 1-0F | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1620_CB | 1620(嘉義北線) CB | LINE161 | E05/161/1620/CB |  |  |  | CDC | 321 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | CB | [17 empty] | 1-02-06 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1630_CB | 1630(北港南線) CB | LINE161 | E05/161/1630/CB |  |  |  | CDC | 322 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | CB | [17 empty] | 1-02-02 |  | 1-0A | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1640_CB | 1640(北港北線) CB | LINE161 | E05/161/1640/CB |  |  |  | CDC | 323 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | CB | [17 empty] | 3-01-01 |  | 3-0A | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1650_CB | 1650(#1ATR) CB | ATR | E05/161/1650/CB |  |  |  | CDC | 324 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | CB | [17 empty] | 3-01-05 |  | 3-0F | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1660_CB | 1660(#2ATR) CB | ATR | E05/161/1660/CB |  |  |  | CDC | 325 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | CB | [17 empty] | 3-02-01 |  | 3-14 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1670_CB | 1670(#3ATR) CB | ATR | E05/161/1670/CB |  |  |  | CDC | 326 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | CB | [17 empty] | 3-02-05 |  | 3-19 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1680_CB | 1680(#4ATR) CB | ATR | E05/161/1680/CB |  |  |  | CDC | 327 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | CB | [17 empty] | 3-03-01 |  | 3-1E | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1690_CB | 1690(#5ATR) CB | ATR | E05/161/1690/CB |  |  |  | CDC | 328 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | CB | [17 empty] | 1-07-06 |  | 1-1A | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1700_CB | 1700(TIE) CB | TIE | E05/161/1700/CB |  |  |  | CDC | 329 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | CB | [17 empty] | 1-01-06 |  | 1-09 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1710_CB | 1710(台嘉一路) CB | LINE161 | E05/161/1710/CB |  |  |  | CDC | 330 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | CB | [17 empty] | 1-09-03 |  | 1-14 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1720_CB | 1720(台嘉二路) CB | LINE161 | E05/161/1720/CB |  |  |  | CDC | 331 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | CB | [17 empty] | 1-08-00 |  | 1-1B | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1800_CB | 1800(TIE) CB | TIE | E05/161/1800/CB |  |  |  | CDC | 332 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | CB | [17 empty] | 3-03-05 |  | 3-23 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1860_CB | 1860(#6ATR) CB | ATR | E05/161/1860/CB |  |  |  | CDC | 333 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | CB | [17 empty] | 1-0D-00 |  | 1-15 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1730_CB | 1730(嘉惠一路) CB | LINE161 | E05/161/1730/CB |  |  |  | CDC | 334 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | CB | [17 empty] | 1-0D-01 |  | 1-16 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1740_CB | 1740(嘉惠二路) CB | LINE161 | E05/161/1740/CB |  |  |  | CDC | 335 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA11 | [17 empty] | 3-08-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA11 | 麥寮二路(3510) #1差流(87L)RY | LINE345 | E05/345/3510/1_87A |  |  |  | CDC | 336 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA12 | [17 empty] | 3-08-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA12 | 麥寮二路(3510) #1測距(21)RY | LINE345 | E05/345/3510/1SSA2 |  |  |  | CDC | 337 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA22 | [17 empty] | 3-09-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA22 | 麥寮二路(3510) #2測距(21)RY | LINE345 | E05/345/3510/2SSA |  |  |  | CDC | 338 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | RYFA11 | [17 empty] | 3-36-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_RYFA11 | 麥寮二路(3510) 第一套87RY故障 | LINE345 | E05/345/3510/RYFA1 |  |  |  | CDC | 339 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | RYFA12 | [17 empty] | 3-36-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_RYFA12 | 麥寮二路(3510) 第一套21RY故障 | LINE345 | E05/345/3510/RYFA2 |  |  |  | CDC | 340 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | 79UL | [17 empty] | 3-36-05 |  | 4-0C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_79UL | 麥寮二路(3510) 79RY U/L | LINE345 | E05/345/3510/79UL |  |  |  | CDC | 341 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | DS1 | 3511 | [16 empty] | 3-3C-00 | 3-3C-01 | 3-28 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3511_DS | 3511(麥寮二路) DS | LINE345 | E05/345/3510/DS1 |  |  |  | CDC | 342 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | DS2 | 3512 | [16 empty] | 3-3C-02 | 3-3C-03 | 3-29 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3512_DS | 3512(麥寮二路) DS | LINE345 | E05/345/3510/DS2 |  |  |  | CDC | 343 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | E2 | 3512E | [16 empty] | 3-3C-04 | 3-3C-05 | 3-2A | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3512E_ES | 3512E(麥寮二路) ES | LINE345 | E05/345/3510/ES2 |  |  |  | CDC | 344 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA21 | [17 empty] | 3-08-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA21 | 麥寮二路(3510) #2差流(87L)RY | LINE345 | E05/345/3510/2_87A |  |  |  | CDC | 345 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | DS1 | 3531 | [16 empty] | 3-3C-12 | 3-3C-13 | 3-2E | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3531_DS | 3531(#8ATR) DS | ATR | E05/345/3530/DS1 |  |  |  | CDC | 346 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | DS2 | 3532 | [16 empty] | 3-3C-14 | 3-3C-15 | 3-2F | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3532_DS | 3532(#8ATR) DS | ATR | E05/345/3530/DS2 |  |  |  | CDC | 347 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | E1 | 3531E | [16 empty] | 3-3C-10 | 3-3C-11 | 3-2D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3531E_ES | #8ATR 3531E ES | OTHER | E05/345/3530/ES1 |  |  |  | CDC | 348 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA11 | [17 empty] | 3-09-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA11 | 麥寮一路(3540) #1差流(87L)RY | LINE345 | E05/345/3540/1SSA1 |  |  |  | CDC | 349 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA12 | [17 empty] | 3-09-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA12 | 麥寮一路(3540) #1測距(21)RY | LINE345 | E05/345/3540/1SSA2 |  |  |  | CDC | 350 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA22 | [17 empty] | 3-09-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA22 | 麥寮一路(3540) #2測距(21)RY | LINE345 | E05/345/3540/2SSA |  |  |  | CDC | 351 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | RYFA11 | [17 empty] | 3-37-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_RYFA11 | 麥寮一路(3540) 第一套87RY故障 | LINE345 | E05/345/3540/RYFA1 |  |  |  | CDC | 352 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | RYFA12 | [17 empty] | 3-37-03 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_RYFA12 | 麥寮一路(3540) 第一套21RY故障 | LINE345 | E05/345/3540/RYFA2 |  |  |  | CDC | 353 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | 79UL | [17 empty] | 3-36-15 |  | 4-0E | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_79UL | 麥寮一路(3540) 79RY U/L | LINE345 | E05/345/3540/79UL |  |  |  | CDC | 354 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | DS1 | 3541 | [16 empty] | 3-3D-00 | 3-3D-01 | 3-30 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3541_DS | 3541(麥寮一路) DS | LINE345 | E05/345/3540/DS1 |  |  |  | CDC | 355 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | DS2 | 3542 | [16 empty] | 3-3D-02 | 3-3D-03 | 3-31 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3542_DS | 3542(麥寮一路) DS | LINE345 | E05/345/3540/DS2 |  |  |  | CDC | 356 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | E2 | 3542E | [16 empty] | 3-3D-04 | 3-3D-05 | 3-32 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3542E_ES | 3542E(麥寮一路) ES | LINE345 | E05/345/3540/ES2 |  |  |  | CDC | 357 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA21 | [17 empty] | 3-09-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA21 | 麥寮一路(3540) #2差流(87L)RY | LINE345 | E05/345/3560/1SSA1 |  |  |  | CDC | 358 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | RYFA21 | [17 empty] | 3-37-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_RYFA21 | 麥寮一路(3540) 第二套87RY故障 | LINE345 | E05/345/3560/RYFA1 |  |  |  | CDC | 359 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | RYFA22 | [17 empty] | 3-37-08 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_RYFA22 | 麥寮一路(3540) 第二套21RY故障 | LINE345 | E05/345/3560/RYFA2 |  |  |  | CDC | 360 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | 79UL | [17 empty] | 3-37-04 |  | 4-0F | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3560_79UL | 3560 79RY U/L | LINE345 | E05/345/3560/79UL |  |  |  | CDC | 361 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | DS1 | 3561 | [16 empty] | 3-3D-12 | 3-3D-13 | 3-36 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3561_DS | 3561 DS | LINE345 | E05/345/3560/DS1 |  |  |  | CDC | 362 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | DS2 | 3562 | [16 empty] | 3-3D-14 | 3-3D-15 | 3-37 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3562_DS | 3562 DS | LINE345 | E05/345/3560/DS2 |  |  |  | CDC | 363 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | E1 | 3561E | [16 empty] | 3-3D-10 | 3-3D-11 | 3-35 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3561E_ES | 3561E ES | LINE345 | E05/345/3560/ES1 |  |  |  | CDC | 364 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | SSA11 | [17 empty] | 3-09-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3570_SSA11 | 中寮二路(3570) #1差流(87L)RY | LINE345 | E05/345/3570/1SSA1 |  |  |  | CDC | 365 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | SSA12 | [17 empty] | 3-0A-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3570_SSA12 | 中寮二路(3570) #1測距(21)RY | LINE345 | E05/345/3570/1SSA2 |  |  |  | CDC | 366 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | SSA2 | [17 empty] | 3-0A-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3570_SSA2 | 中寮二路(3570) #2測距(21)RY | LINE345 | E05/345/3570/2SSA |  |  |  | CDC | 367 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | RYFA1 | [17 empty] | 3-37-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_RYFA1 | 中寮二路(3570) 第一套RY故障 | LINE345 | E05/345/3570/RYFA1 |  |  |  | CDC | 368 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | RYFA2 | [17 empty] | 3-37-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_RYFA2 | 中寮二路(3570) 第二套RY故障 | LINE345 | E05/345/3570/RYFA2 |  |  |  | CDC | 369 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | 79UL | [17 empty] | 3-37-09 |  | 4-10 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_79UL | 中寮二路(3570) 79RY U/L | LINE345 | E05/345/3570/79UL |  |  |  | CDC | 370 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | DS1 | 3571 | [16 empty] | 3-3E-00 | 3-3E-01 | 3-38 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3571_DS | 3571(中寮二路) DS | LINE345 | E05/345/3570/DS1 |  |  |  | CDC | 371 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | DS2 | 3572 | [16 empty] | 3-3E-02 | 3-3E-03 | 3-39 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3572_DS | 3572(中寮二路) DS | LINE345 | E05/345/3570/DS2 |  |  |  | CDC | 372 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | E2 | 3572E | [16 empty] | 3-3E-04 | 3-3E-05 | 3-3A | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3572E_ES | 3572E(中寮二路) ES | LINE345 | E05/345/3570/ES2 |  |  |  | CDC | 373 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | SSA11 | [17 empty] | 3-0A-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3610_SSA11 | 中寮一路(3610) #1差流(87L)RY | LINE345 | E05/345/3610/1SSA1 |  |  |  | CDC | 374 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | SSA12 | [17 empty] | 3-0A-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3610_SSA12 | 中寮一路(3610) #1測距(21)RY | LINE345 | E05/345/3610/1SSA2 |  |  |  | CDC | 375 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | SSA2 | [17 empty] | 3-0A-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3610_SSA2 | 中寮一路(3610) #2測距(21)RY | LINE345 | E05/345/3610/2SSA |  |  |  | CDC | 376 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | RYFA1 | [17 empty] | 3-38-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_RYFA1 | 中寮一路(3610) 第一套RY故障 | LINE345 | E05/345/3610/RYFA1 |  |  |  | CDC | 377 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | RYFA2 | [17 empty] | 3-38-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_RYFA2 | 中寮一路(3610) 第二套RY故障 | LINE345 | E05/345/3610/RYFA2 |  |  |  | CDC | 378 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | 79UL | [17 empty] | 3-37-14 |  | 4-11 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_79UL | 中寮一路(3610) 79RY U/L | LINE345 | E05/345/3610/79UL |  |  |  | CDC | 379 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | DS1 | 3611 | [16 empty] | 3-3E-14 | 3-3E-15 | 3-3F | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3611_DS | 3611(中寮一路) DS | LINE345 | E05/345/3610/DS1 |  |  |  | CDC | 380 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | DS2 | 3612 | [16 empty] | 3-3F-00 | 3-3F-01 | 3-40 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3612_DS | 3612(中寮一路) DS | LINE345 | E05/345/3610/DS2 |  |  |  | CDC | 381 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | E2 | 3612E | [16 empty] | 3-3F-02 | 3-3F-03 | 3-41 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3612E_ES | 3612E(中寮一路) ES | LINE345 | E05/345/3610/ES2 |  |  |  | CDC | 382 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | SSA11 | [17 empty] | 3-0A-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3640_SSA11 | 中寮三路(3640) #1差流(87L)RY | LINE345 | E05/345/3640/1SSA1 |  |  |  | CDC | 383 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | SSA12 | [17 empty] | 3-0A-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3640_SSA12 | 中寮三路(3640) #1測距(21)RY | LINE345 | E05/345/3640/1SSA2 |  |  |  | CDC | 384 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | SSA2 | [17 empty] | 3-0A-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3640_SSA2 | 中寮三路(3640) #2測距(21)RY | LINE345 | E05/345/3640/2SSA |  |  |  | CDC | 385 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | RYFA1 | [17 empty] | 3-38-05 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_RYFA1 | 中寮三路(3640) 第一套RY故障 | LINE345 | E05/345/3640/RYFA1 |  |  |  | CDC | 386 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | RYFA2 | [17 empty] | 3-38-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_RYFA2 | 中寮三路(3640) 第二套RY故障 | LINE345 | E05/345/3640/RYFA2 |  |  |  | CDC | 387 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | 79UL | [17 empty] | 3-38-03 |  | 4-12 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_79UL | 中寮三路(3640) 79RY U/L | LINE345 | E05/345/3640/79UL |  |  |  | CDC | 388 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | DS1 | 3641 | [16 empty] | 4-30-00 | 4-30-01 | 3-46 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3641_DS | 3641(中寮三路) DS | LINE345 | E05/345/3640/DS1 |  |  |  | CDC | 389 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | DS2 | 3642 | [16 empty] | 4-30-02 | 4-30-03 | 3-47 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3642_DS | 3642(中寮三路) DS | LINE345 | E05/345/3640/DS2 |  |  |  | CDC | 390 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | E2 | 3642E | [16 empty] | 4-30-04 | 4-30-05 | 3-48 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3642E_ES | 3642E(中寮三路) ES | LINE345 | E05/345/3640/ES2 |  |  |  | CDC | 391 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | SSA11 | [17 empty] | 3-0B-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3710_SSA11 | 龍崎紅線(3710) #1差流(87L)RY | LINE345 | E05/345/3710/1SSA1 |  |  |  | CDC | 392 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | SSA12 | [17 empty] | 3-0B-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3710_SSA12 | 龍崎紅線(3710) #1測距(21)RY | LINE345 | E05/345/3710/1SSA2 |  |  |  | CDC | 393 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | SSA2 | [17 empty] | 3-0B-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3710_SSA2 | 龍崎紅線(3710) #2測距(21)RY | LINE345 | E05/345/3710/2SSA |  |  |  | CDC | 394 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | RYFA1 | [17 empty] | 3-38-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_RYFA1 | 龍崎紅線(3710) 第一套RY故障 | LINE345 | E05/345/3710/RYFA1 |  |  |  | CDC | 395 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | RYFA2 | [17 empty] | 3-38-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_RYFA2 | 龍崎紅線(3710) 第二套RY故障 | LINE345 | E05/345/3710/RYFA2 |  |  |  | CDC | 396 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | 79UL | [17 empty] | 3-38-08 |  | 4-13 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_79UL | 龍崎紅線(3710) 79RY U/L | LINE345 | E05/345/3710/79UL |  |  |  | CDC | 397 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | DS1 | 3711 | [16 empty] | 4-30-14 | 4-30-15 | 3-4D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3711_DS | 3711(龍崎紅線) DS | LINE345 | E05/345/3710/DS1 |  |  |  | CDC | 398 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | DS2 | 3712 | [16 empty] | 4-31-00 | 4-31-01 | 3-4E | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3712_DS | 3712(龍崎紅線) DS | LINE345 | E05/345/3710/DS2 |  |  |  | CDC | 399 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | E2 | 3712E | [16 empty] | 4-31-02 | 4-31-03 | 3-4F | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3712E_ES | 3712E(龍崎紅線) ES | LINE345 | E05/345/3710/ES2 |  |  |  | CDC | 400 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | SSA11 | [17 empty] | 3-0B-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3770_SSA11 | 新南科一路(3770) #1差流(87L)RY | LINE345 | E05/345/3770/1SSA1 |  |  |  | CDC | 401 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | SSA12 | [17 empty] | 3-0B-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3770_SSA12 | 新南科一路(3770) #1測距(21)RY | LINE345 | E05/345/3770/1SSA2 |  |  |  | CDC | 402 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | SSA2 | [17 empty] | 3-0B-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3770_SSA2 | 新南科一路(3770) #2測距(21)RY | LINE345 | E05/345/3770/2SSA |  |  |  | CDC | 403 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | RYFA1 | [17 empty] | 3-38-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3770_RYFA1 | 新南科一路(3770) 第一套RY故障 | LINE345 | E05/345/3770/RYFA1 |  |  |  | CDC | 404 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | RYFA2 | [17 empty] | 3-39-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3770_RYFA2 | 新南科一路(3770) 第二套RY故障 | LINE345 | E05/345/3770/RYFA2 |  |  |  | CDC | 405 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | 79UL | [17 empty] | 3-38-13 |  | 4-14 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3770_79UL | 新南科一路(3770) 79RY U/L | LINE345 | E05/345/3770/79UL |  |  |  | CDC | 406 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | DS1 | 3771 | [16 empty] | 4-31-12 | 4-31-13 | 3-54 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3771_DS | 3771(新南科一路) DS | LINE345 | E05/345/3770/DS1 |  |  |  | CDC | 407 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | DS2 | 3772 | [16 empty] | 4-31-14 | 4-31-15 | 3-55 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3772_DS | 3772(新南科一路) DS | LINE345 | E05/345/3770/DS2 |  |  |  | CDC | 408 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | E2 | 3772E | [16 empty] | 4-32-00 | 4-32-01 | 3-56 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3772E_ES | 3772E(新南科一路) ES | LINE345 | E05/345/3770/ES2 |  |  |  | CDC | 409 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | SSA11 | [17 empty] | 3-0B-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3810_SSA11 | 新南科二路(3810) #1差流(87L)RY | LINE345 | E05/345/3810/1SSA1 |  |  |  | CDC | 410 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | SSA12 | [17 empty] | 3-0B-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3810_SSA12 | 新南科二路(3810) #1測距(21)RY | LINE345 | E05/345/3810/1SSA2 |  |  |  | CDC | 411 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | SSA2 | [17 empty] | 3-0C-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3810_SSA2 | 新南科二路(3810) #2測距(21)RY | LINE345 | E05/345/3810/2SSA |  |  |  | CDC | 412 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | RYFA1 | [17 empty] | 3-39-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3810_RYFA1 | 新南科二路(3810) 第一套RY故障 | LINE345 | E05/345/3810/RYFA1 |  |  |  | CDC | 413 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | RYFA2 | [17 empty] | 3-39-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3810_RYFA2 | 新南科二路(3810) 第二套RY故障 | LINE345 | E05/345/3810/RYFA2 |  |  |  | CDC | 414 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | 79UL | [17 empty] | 3-39-02 |  | 4-15 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3810_79UL | 新南科二路(3810) 79RY U/L | LINE345 | E05/345/3810/79UL |  |  |  | CDC | 415 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | DS1 | 3811 | [16 empty] | 4-32-10 | 4-32-11 | 3-5B | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3811_DS | 3811(新南科二路) DS | LINE345 | E05/345/3810/DS1 |  |  |  | CDC | 416 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | DS2 | 3812 | [16 empty] | 4-32-12 | 4-32-13 | 3-5C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3812_DS | 3812(新南科二路) DS | LINE345 | E05/345/3810/DS2 |  |  |  | CDC | 417 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | E2 | 3812E | [16 empty] | 4-32-14 | 4-32-15 | 3-5D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3812E_ES | 3812E(新南科二路) ES | LINE345 | E05/345/3810/ES2 |  |  |  | CDC | 418 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3580 | 3580 |  | DS1 | 3581 | [16 empty] | 3-3E-06 | 3-3E-07 | 3-3B | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3581_DS | 3581 DS | LINE345 | E05/345/3580/DS1 |  |  |  | CDC | 419 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3580 | 3580 |  | DS2 | 3582 | [16 empty] | 3-3E-08 | 3-3E-09 | 3-3C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3582_DS | 3582 DS | LINE345 | E05/345/3580/DS2 |  |  |  | CDC | 420 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3620 | 3620 |  | DS1 | 3621 | [16 empty] | 3-3F-04 | 3-3F-05 | 3-42 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3621_DS | 3621 DS | LINE345 | E05/345/3620/DS1 |  |  |  | CDC | 421 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3620 | 3620 |  | DS2 | 3622 | [16 empty] | 3-3F-06 | 3-3F-07 | 3-43 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3622_DS | 3622 DS | LINE345 | E05/345/3620/DS2 |  |  |  | CDC | 422 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3650 | 3650 |  | DS1 | 3651 | [16 empty] | 4-30-06 | 4-30-07 | 3-49 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3651_DS | 3651 DS | LINE345 | E05/345/3650/DS1 |  |  |  | CDC | 423 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3650 | 3650 |  | DS2 | 3652 | [16 empty] | 4-30-08 | 4-30-09 | 3-4A | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3652_DS | 3652 DS | LINE345 | E05/345/3650/DS2 |  |  |  | CDC | 424 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3720 | 3720 |  | DS1 | 3721 | [16 empty] | 4-31-04 | 4-31-05 | 3-50 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3721_DS | 3721 DS | LINE345 | E05/345/3720/DS1 |  |  |  | CDC | 425 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3720 | 3720 |  | DS2 | 3722 | [16 empty] | 4-31-06 | 4-31-07 | 3-51 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3722_DS | 3722 DS | LINE345 | E05/345/3720/DS2 |  |  |  | CDC | 426 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3780 | 3780 |  | DS1 | 3781 | [16 empty] | 4-32-02 | 4-32-03 | 3-57 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3781_DS | 3781 DS | LINE345 | E05/345/3780/DS1 |  |  |  | CDC | 427 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3780 | 3780 |  | DS2 | 3782 | [16 empty] | 4-32-04 | 4-32-05 | 3-58 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3782_DS | 3782 DS | LINE345 | E05/345/3780/DS2 |  |  |  | CDC | 428 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3820 | 3820 |  | DS1 | 3821 | [16 empty] | 4-33-00 | 4-33-01 | 3-5E | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3821_DS | 3821 DS | LINE345 | E05/345/3820/DS1 |  |  |  | CDC | 429 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3820 | 3820 |  | DS2 | 3822 | [16 empty] | 4-33-02 | 4-33-03 | 3-5F | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3822_DS | 3822 DS | LINE345 | E05/345/3820/DS2 |  |  |  | CDC | 430 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | PHA | [17 empty] | 1-04-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1510_PHA | 嘉義山線(1510) 相間RY | LINE161 | E05/161/1510/PHA |  |  |  | CDC | 431 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | GDA | [17 empty] | 1-04-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1510_GDA | 嘉義山線(1510) 接地RY | LINE161 | E05/161/1510/GDA |  |  |  | CDC | 432 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | 79UL | [17 empty] | 2-30-12 |  | 2-0A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1510_79UL | 嘉義山線(1510) 79RY U/L | LINE161 | E05/161/1510/79UL |  |  |  | CDC | 433 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | ABS1 | 1511 | [16 empty] | 1-34-08 | 1-34-09 | 1-44 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1511_ABS | 1511(嘉義山線) ABS | LINE161 | E05/161/1510/ABS1 |  |  |  | CDC | 434 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | ABS2 | 1512 | [16 empty] | 1-34-10 | 1-34-11 | 1-45 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1512_ABS | 1512(嘉義山線) ABS | LINE161 | E05/161/1510/ABS2 |  |  |  | CDC | 435 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | ABS3 | 1513 | [16 empty] | 1-34-12 | 1-34-13 | 1-46 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1513_ABS | 1513(嘉義山線) ABS | LINE161 | E05/161/1510/ABS3 |  |  |  | CDC | 436 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | E3 | 1513E | [16 empty] | 1-34-14 | 1-34-15 | 1-47 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1513E_ES | 1513E(嘉義山線) ES | LINE161 | E05/161/1510/ES3 |  |  |  | CDC | 437 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1520_PHA | 嘉義海線(1520) 相間RY | LINE161 | E05/161/1520/PHA |  |  |  | CDC | 438 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1520_GDA | 嘉義海線(1520) 接地RY | LINE161 | E05/161/1520/GDA |  |  |  | CDC | 439 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | 79UL | [17 empty] | 2-30-10 |  | 2-08 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1520_79UL | 嘉義海線(1520) 79RY U/L | LINE161 | E05/161/1520/79UL |  |  |  | CDC | 440 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | ABS1 | 1521 | [16 empty] | 1-34-00 | 1-34-01 | 1-40 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1521_ABS | 1521(嘉義海線) ABS | LINE161 | E05/161/1520/ABS1 |  |  |  | CDC | 441 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | ABS2 | 1522 | [16 empty] | 1-34-02 | 1-34-03 | 1-41 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1522_ABS | 1522(嘉義海線) ABS | LINE161 | E05/161/1520/ABS2 |  |  |  | CDC | 442 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | ABS3 | 1523 | [16 empty] | 1-34-04 | 1-34-05 | 1-42 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1523_ABS | 1523(嘉義海線) ABS | LINE161 | E05/161/1520/ABS3 |  |  |  | CDC | 443 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | E3 | 1523E | [16 empty] | 1-34-06 | 1-34-07 | 1-43 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1523E_ES | 1523E(嘉義海線) ES | LINE161 | E05/161/1520/ES3 |  |  |  | CDC | 444 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | PHA | [17 empty] | 1-06-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1530_PHA | 柳營山線(1530) 相間RY | LINE161 | E05/161/1530/PHA |  |  |  | CDC | 445 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | GDA | [17 empty] | 1-06-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1530_GDA | 柳營山線(1530) 接地RY | LINE161 | E05/161/1530/GDA |  |  |  | CDC | 446 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | 87A | [17 empty] | 1-05-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1530_87A | 柳營山線(1530) 87RY | LINE161 | E05/161/1530/87A |  |  |  | CDC | 447 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | 87UL | [17 empty] | 2-31-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_87UL | 柳營山線(1530) 87RY U/L | LINE161 | E05/161/1530/1_87UL2 |  |  |  | CDC | 448 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | 79UL | [17 empty] | 2-31-04 |  | 2-12 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_79UL | 柳營山線(1530) 79RY U/L | LINE161 | E05/161/1530/79UL |  |  |  | CDC | 449 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | ABS1 | 1531 | [16 empty] | 1-36-08 | 1-36-09 | 1-54 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1531_ABS | 1531(柳營山線) ABS | LINE161 | E05/161/1530/ABS1 |  |  |  | CDC | 450 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | ABS2 | 1532 | [16 empty] | 1-36-10 | 1-36-11 | 1-55 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1532_ABS | 1532(柳營山線) ABS | LINE161 | E05/161/1530/ABS2 |  |  |  | CDC | 451 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | ABS3 | 1533 | [16 empty] | 1-36-12 | 1-36-13 | 1-56 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1533_ABS | 1533(柳營山線) ABS | LINE161 | E05/161/1530/ABS3 |  |  |  | CDC | 452 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | E3 | 1533E | [16 empty] | 1-36-14 | 1-36-15 | 1-57 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1533E_ES | 1533E(柳營山線) ES | LINE161 | E05/161/1530/ES3 |  |  |  | CDC | 453 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | PHA | [17 empty] | 1-05-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1540_PHA | 柳營海線(1540) 相間RY | LINE161 | E05/161/1540/PHA |  |  |  | CDC | 454 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | GDA | [17 empty] | 1-05-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1540_GDA | 柳營海線(1540) 接地RY | LINE161 | E05/161/1540/GDA |  |  |  | CDC | 455 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | 87A | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1540_87A | 柳營海線(1540) 87RY | LINE161 | E05/161/1540/87A |  |  |  | CDC | 456 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | 87UL | [17 empty] | 2-31-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_87UL | 柳營海線(1540) 87RY U/L | LINE161 | E05/161/1540/1_87UL2 |  |  |  | CDC | 457 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | 79UL | [17 empty] | 2-31-02 |  | 2-10 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_79UL | 柳營海線(1540) 79RY U/L | LINE161 | E05/161/1540/79UL |  |  |  | CDC | 458 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | ABS1 | 1541 | [16 empty] | 1-36-00 | 1-36-01 | 1-50 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1541_ABS | 1541(柳營海線) ABS | LINE161 | E05/161/1540/ABS1 |  |  |  | CDC | 459 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | ABS2 | 1542 | [16 empty] | 1-36-02 | 1-36-03 | 1-51 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1542_ABS | 1542(柳營海線) ABS | LINE161 | E05/161/1540/ABS2 |  |  |  | CDC | 460 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | ABS3 | 1543 | [16 empty] | 1-36-04 | 1-36-05 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1543_ABS | 1543(柳營海線) ABS | LINE161 | E05/161/1540/ABS3 |  |  |  | CDC | 461 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | E3 | 1543E | [16 empty] | 1-36-06 | 1-36-07 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1543E_ES | 1543E(柳營海線) ES | LINE161 | E05/161/1540/ES3 |  |  |  | CDC | 462 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | PHA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1550_PHA | 雲林山線(1550) 相間RY | LINE161 | E05/161/1550/PHA |  |  |  | CDC | 463 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | GDA | [17 empty] | 1-01-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1550_GDA | 雲林山線(1550) 接地RY | LINE161 | E05/161/1550/GDA |  |  |  | CDC | 464 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | 79UL | [17 empty] | 2-30-02 |  | 2-00 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1550_79UL | 雲林山線(1550) 79RY U/L | LINE161 | E05/161/1550/79UL |  |  |  | CDC | 465 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | ABS1 | 1551 | [16 empty] | 1-31-08 | 1-31-09 | 1-28 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1551_ABS | 1551(雲林山線) ABS | LINE161 | E05/161/1550/ABS1 |  |  |  | CDC | 466 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | ABS2 | 1552 | [16 empty] | 1-31-10 | 1-31-11 | 1-29 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1552_ABS | 1552(雲林山線) ABS | LINE161 | E05/161/1550/ABS2 |  |  |  | CDC | 467 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | ABS3 | 1553 | [16 empty] | 1-31-12 | 1-31-13 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1553_ABS | 1553(雲林山線) ABS | LINE161 | E05/161/1550/ABS3 |  |  |  | CDC | 468 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | E3 | 1553E | [16 empty] | 1-31-14 | 1-31-15 | 1-2B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1553E_ES | 1553E(雲林山線) ES | LINE161 | E05/161/1550/ES3 |  |  |  | CDC | 469 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | PHA | [17 empty] | 1-01-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1560_PHA | 雲林海線(1560) 相間RY | LINE161 | E05/161/1560/PHA |  |  |  | CDC | 470 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | GDA | [17 empty] | 1-01-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1560_GDA | 雲林海線(1560) 接地RY | LINE161 | E05/161/1560/GDA |  |  |  | CDC | 471 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | 79UL | [17 empty] | 2-30-04 |  | 2-02 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1560_79UL | 雲林海線(1560) 79RY U/L | LINE161 | E05/161/1560/79UL |  |  |  | CDC | 472 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | ABS1 | 1561 | [16 empty] | 1-32-00 | 1-32-01 | 1-2C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1561_ABS | 1561(雲林海線) ABS | LINE161 | E05/161/1560/ABS1 |  |  |  | CDC | 473 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | ABS2 | 1562 | [16 empty] | 1-32-02 | 1-32-03 | 1-2D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1562_ABS | 1562(雲林海線) ABS | LINE161 | E05/161/1560/ABS2 |  |  |  | CDC | 474 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | ABS3 | 1563 | [16 empty] | 1-32-04 | 1-32-05 | 1-2E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1563_ABS | 1563(雲林海線) ABS | LINE161 | E05/161/1560/ABS3 |  |  |  | CDC | 475 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | E3 | 1563E | [16 empty] | 1-32-06 | 1-32-07 | 1-2F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1563E_ES | 1563E(雲林海線) ES | LINE161 | E05/161/1560/ES3 |  |  |  | CDC | 476 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | PHA | [17 empty] | 1-07-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1580_PHA | 嘉民雲林線(1580) 相間RY | LINE161 | E05/161/1580/PHA |  |  |  | CDC | 477 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | GDA | [17 empty] | 1-07-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1580_GDA | 嘉民雲林線(1580) 接地RY | LINE161 | E05/161/1580/GDA |  |  |  | CDC | 478 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | 79UL | [17 empty] | 2-31-08 |  | 2-16 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1580_79UL | 嘉民雲林線(1580) 79RY U/L | LINE161 | E05/161/1580/79UL |  |  |  | CDC | 479 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | ABS1 | 1581 | [16 empty] | 1-37-08 | 1-37-09 | 1-5C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1581_ABS | 1581(嘉民雲林線) ABS | LINE161 | E05/161/1580/ABS1 |  |  |  | CDC | 480 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | ABS2 | 1582 | [16 empty] | 1-37-10 | 1-37-11 | 1-5D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1582_ABS | 1582(嘉民雲林線) ABS | LINE161 | E05/161/1580/ABS2 |  |  |  | CDC | 481 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | ABS3 | 1583 | [16 empty] | 1-37-12 | 1-37-13 | 1-5E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1583_ABS | 1583(嘉民雲林線) ABS | LINE161 | E05/161/1580/ABS3 |  |  |  | CDC | 482 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | E3 | 1583E | [16 empty] | 1-37-14 | 1-37-15 | 1-5F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1583E_ES | 1583E(嘉民雲林線) ES | LINE161 | E05/161/1580/ES3 |  |  |  | CDC | 483 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | PHA | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1590_PHA | 斗工紅線(1590) 相間RY | LINE161 | E05/161/1590/PHA |  |  |  | CDC | 484 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | GDA | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1590_GDA | 斗工紅線(1590) 接地RY | LINE161 | E05/161/1590/GDA |  |  |  | CDC | 485 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | 79UL | [17 empty] | 2-31-06 |  | 2-14 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1590_79UL | 斗工紅線(1590) 79RY U/L | LINE161 | E05/161/1590/79UL |  |  |  | CDC | 486 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | ABS1 | 1591 | [16 empty] | 1-37-00 | 1-37-01 | 1-58 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1591_ABS | 1591(斗工紅線) ABS | LINE161 | E05/161/1590/ABS1 |  |  |  | CDC | 487 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | ABS2 | 1592 | [16 empty] | 1-37-02 | 1-37-03 | 1-59 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1592_ABS | 1592(斗工紅線) ABS | LINE161 | E05/161/1590/ABS2 |  |  |  | CDC | 488 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | ABS3 | 1593 | [16 empty] | 1-37-04 | 1-37-05 | 1-5A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1593_ABS | 1593(斗工紅線) ABS | LINE161 | E05/161/1590/ABS3 |  |  |  | CDC | 489 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | E3 | 1593E | [16 empty] | 1-37-06 | 1-37-07 | 1-5B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1593E_ES | 1593E(斗工紅線) ES | LINE161 | E05/161/1590/ES3 |  |  |  | CDC | 490 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | PHA | [17 empty] | 1-04-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1610_PHA | 嘉義南線(1610) 相間RY | LINE161 | E05/161/1610/PHA |  |  |  | CDC | 491 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | GDA | [17 empty] | 1-04-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1610_GDA | 嘉義南線(1610) 接地RY | LINE161 | E05/161/1610/GDA |  |  |  | CDC | 492 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | 79UL | [17 empty] | 2-30-14 |  | 2-0C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1610_79UL | 嘉義南線(1610) 79RY U/L | LINE161 | E05/161/1610/79UL |  |  |  | CDC | 493 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | ABS1 | 1611 | [16 empty] | 1-35-00 | 1-35-01 | 1-48 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1611_ABS | 1611(嘉義南線) ABS | LINE161 | E05/161/1610/ABS1 |  |  |  | CDC | 494 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | ABS2 | 1612 | [16 empty] | 1-35-02 | 1-35-03 | 1-49 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1612_ABS | 1612(嘉義南線) ABS | LINE161 | E05/161/1610/ABS2 |  |  |  | CDC | 495 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | ABS3 | 1613 | [16 empty] | 1-35-04 | 1-35-05 | 1-4A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1613_ABS | 1613(嘉義南線) ABS | LINE161 | E05/161/1610/ABS3 |  |  |  | CDC | 496 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | E3 | 1613E | [16 empty] | 1-35-06 | 1-35-07 | 1-4B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1613E_ES | 1613E(嘉義南線) ES | LINE161 | E05/161/1610/ES3 |  |  |  | CDC | 497 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | PHA | [17 empty] | 1-05-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1620_PHA | 嘉義北線(1620) 相間RY | LINE161 | E05/161/1620/PHA |  |  |  | CDC | 498 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | GDA | [17 empty] | 1-05-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1620_GDA | 嘉義北線(1620) 接地RY | LINE161 | E05/161/1620/GDA |  |  |  | CDC | 499 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | 79UL | [17 empty] | 2-31-00 |  | 2-0E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1620_79UL | 嘉義北線(1620) 79RY U/L | LINE161 | E05/161/1620/79UL |  |  |  | CDC | 500 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | ABS1 | 1621 | [16 empty] | 1-35-08 | 1-35-09 | 1-4C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1621_ABS | 1621(嘉義北線) ABS | LINE161 | E05/161/1620/ABS1 |  |  |  | CDC | 501 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | ABS2 | 1622 | [16 empty] | 1-35-10 | 1-35-11 | 1-4D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1622_ABS | 1622(嘉義北線) ABS | LINE161 | E05/161/1620/ABS2 |  |  |  | CDC | 502 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | ABS3 | 1623 | [16 empty] | 1-35-12 | 1-35-13 | 1-4E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1623_ABS | 1623(嘉義北線) ABS | LINE161 | E05/161/1620/ABS3 |  |  |  | CDC | 503 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | E3 | 1623E | [16 empty] | 1-35-14 | 1-35-15 | 1-4F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1623E_ES | 1623E(嘉義北線) ES | LINE161 | E05/161/1620/ES3 |  |  |  | CDC | 504 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | PHA | [17 empty] | 1-03-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1630_PHA | 北港南線(1630) 相間RY | LINE161 | E05/161/1630/PHA |  |  |  | CDC | 505 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | GDA | [17 empty] | 1-03-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1630_GDA | 北港南線(1630) 接地RY | LINE161 | E05/161/1630/GDA |  |  |  | CDC | 506 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | 79UL | [17 empty] | 2-30-08 |  | 2-06 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1630_79UL | 北港南線(1630) 79RY U/L | LINE161 | E05/161/1630/79UL |  |  |  | CDC | 507 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | ABS1 | 1631 | [16 empty] | 1-33-08 | 1-33-09 | 1-3C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1631_ABS | 1631(北港南線) ABS | LINE161 | E05/161/1630/ABS1 |  |  |  | CDC | 508 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | ABS2 | 1632 | [16 empty] | 1-33-10 | 1-33-11 | 1-3D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1632_ABS | 1632(北港南線) ABS | LINE161 | E05/161/1630/ABS2 |  |  |  | CDC | 509 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | ABS3 | 1633 | [16 empty] | 1-33-12 | 1-33-13 | 1-3E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1633_ABS | 1633(北港南線) ABS | LINE161 | E05/161/1630/ABS3 |  |  |  | CDC | 510 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | E3 | 1633E | [16 empty] | 1-33-14 | 1-33-15 | 1-3F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1633E_ES | 1633E(北港南線) ES | LINE161 | E05/161/1630/ES3 |  |  |  | CDC | 511 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | PHA | [17 empty] | 1-02-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1640_PHA | 北港北線(1640) 相間RY | LINE161 | E05/161/1640/PHA |  |  |  | CDC | 512 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | GDA | [17 empty] | 1-02-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1640_GDA | 北港北線(1640) 接地RY | LINE161 | E05/161/1640/GDA |  |  |  | CDC | 513 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | 79UL | [17 empty] | 2-30-06 |  | 2-04 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1640_79UL | 北港北線(1640) 79RY U/L | LINE161 | E05/161/1640/79UL |  |  |  | CDC | 514 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | ABS1 | 1641 | [16 empty] | 1-33-00 | 1-33-01 | 1-38 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1641_ABS | 1641(北港北線) ABS | LINE161 | E05/161/1640/ABS1 |  |  |  | CDC | 515 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | ABS2 | 1642 | [16 empty] | 1-33-02 | 1-33-03 | 1-39 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1642_ABS | 1642(北港北線) ABS | LINE161 | E05/161/1640/ABS2 |  |  |  | CDC | 516 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | ABS3 | 1643 | [16 empty] | 1-33-04 | 1-33-05 | 1-3A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1643_ABS | 1643(北港北線) ABS | LINE161 | E05/161/1640/ABS3 |  |  |  | CDC | 517 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | E3 | 1643E | [16 empty] | 1-33-06 | 1-33-07 | 1-3B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1643E_ES | 1643E(北港北線) ES | LINE161 | E05/161/1640/ES3 |  |  |  | CDC | 518 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | PHA | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1710_PHA | 台嘉一路(1710) 相間RY | LINE161 | E05/161/1710/PHA |  |  |  | CDC | 519 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | GDA | [17 empty] | 1-02-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1710_GDA | 台嘉一路(1710) 接地RY | LINE161 | E05/161/1710/GDA |  |  |  | CDC | 520 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | 85MA | [17 empty] | 1-0A-01 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1710_85MA | 台嘉一路(1710) 85RY(M) | LINE161 | E05/161/1710/85A |  |  |  | CDC | 521 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | 85BA | [17 empty] | 1-0A-00 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1710_85BA | 台嘉一路(1710) 85RY(B) | LINE161 | E05/161/1710/87A |  |  |  | CDC | 522 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | 85U1 | [17 empty] | 2-34-01 |  | 2-1B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1710_85U1 | 台嘉一路(1710) 85RY(M) U/L | LINE161 | E05/161/1710/85UL |  |  |  | CDC | 523 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | 85U2 | [17 empty] | 2-34-02 |  | 2-1C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1710_85U2 | 台嘉一路(1710) 85RY(B) U/L | LINE161 | E05/161/1710/1_87UL2 |  |  |  | CDC | 524 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | ABS1 | 1711 | [16 empty] | 1-32-08 | 1-32-09 | 1-30 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1711_ABS | 1711(台嘉一路) ABS | LINE161 | E05/161/1710/ABS1 |  |  |  | CDC | 525 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | ABS2 | 1712 | [16 empty] | 1-32-10 | 1-32-11 | 1-31 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1712_ABS | 1712(台嘉一路) ABS | LINE161 | E05/161/1710/ABS2 |  |  |  | CDC | 526 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | ABS3 | 1713 | [16 empty] | 1-32-12 | 1-32-13 | 1-32 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1713_ABS | 1713(台嘉一路) ABS | LINE161 | E05/161/1710/ABS3 |  |  |  | CDC | 527 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | E3 | 1713E | [16 empty] | 1-32-14 | 1-32-15 | 1-33 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1713E_ES | 1713E(台嘉一路) ES | LINE161 | E05/161/1710/ES3 |  |  |  | CDC | 528 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | PHA | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1720_PHA | 台嘉二路(1720) 相間RY | LINE161 | E05/161/1720/PHA |  |  |  | CDC | 529 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | GDA | [17 empty] | 1-09-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1720_GDA | 台嘉二路(1720) 接地RY | LINE161 | E05/161/1720/GDA |  |  |  | CDC | 530 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | 85MA | [17 empty] | 1-09-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1720_85MA | 台嘉二路(1720) 85RY(M) | LINE161 | E05/161/1720/85A |  |  |  | CDC | 531 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | 85BA | [17 empty] | 1-09-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1720_85BA | 台嘉二路(1720) 85RY(B) | LINE161 | E05/161/1720/87A |  |  |  | CDC | 532 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | 85U1 | [17 empty] | 2-34-03 |  | 2-1D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1720_85U1 | 台嘉二路(1720) 85RY(M) U/L | LINE161 | E05/161/1720/85UL |  |  |  | CDC | 533 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | 85U2 | [17 empty] | 2-34-04 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1720_85U2 | 台嘉二路(1720) 85RY(B) U/L | LINE161 | E05/161/1720/1_87UL2 |  |  |  | CDC | 534 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | ABS1 | 1721 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-34 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1721_ABS | 1721(台嘉二路) ABS | LINE161 | E05/161/1720/ABS1 |  |  |  | CDC | 535 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | ABS2 | 1722 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-35 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1722_ABS | 1722(台嘉二路) ABS | LINE161 | E05/161/1720/ABS2 |  |  |  | CDC | 536 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | ABS3 | 1723 | [16 empty] | 1-3B-04 | 1-3B-05 | 1-36 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1723_ABS | 1723(台嘉二路) ABS | LINE161 | E05/161/1720/ABS3 |  |  |  | CDC | 537 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | E3 | 1723E | [16 empty] | 1-3B-06 | 1-3B-07 | 1-37 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1723E_ES | 1723E(台嘉二路) ES | LINE161 | E05/161/1720/ES3 |  |  |  | CDC | 538 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | 87A | [17 empty] | 1-0D-02 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1730_87A | 嘉惠一路(1730) 87RY | LINE161 | E05/161/1730/87A |  |  |  | CDC | 539 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | 21A | [17 empty] | 1-0D-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1730_21A | 嘉惠一路(1730) 21RY | LINE161 | E05/161/1730/21A |  |  |  | CDC | 540 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | 79UL | [17 empty] | 2-30-00 |  | 2-28 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1730_79UL | 嘉惠一路(1730) 79RY U/L | LINE161 | E05/161/1730/79UL |  |  |  | CDC | 541 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | DS1 | 1731 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1731_DS | 1731(嘉惠一路) DS | LINE161 | E05/161/1730/DS1 |  |  |  | CDC | 542 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | DS2 | 1732 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1732_DS | 1732(嘉惠一路) DS | LINE161 | E05/161/1730/DS2 |  |  |  | CDC | 543 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | DS3 | 1733 | [16 empty] | 1-3C-04 | 1-3C-05 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1733_DS | 1733(嘉惠一路) DS | LINE161 | E05/161/1730/DS3 |  |  |  | CDC | 544 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | E3 | 1733E | [16 empty] | 1-3C-06 | 1-3C-07 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1733E_ES | 1733E(嘉惠一路) ES | LINE161 | E05/161/1730/ES3 |  |  |  | CDC | 545 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | 87A | [17 empty] | 1-0D-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1740_87A | 嘉惠二路(1740) 87RY | LINE161 | E05/161/1740/87A |  |  |  | CDC | 546 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | 21A | [17 empty] | 1-0D-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1740_21A | 嘉惠二路(1740) 21RY | LINE161 | E05/161/1740/21A |  |  |  | CDC | 547 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | 79UL | [17 empty] | 2-30-01 |  | 2-29 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1740_79UL | 嘉惠二路(1740) 79RY U/L | LINE161 | E05/161/1740/79UL |  |  |  | CDC | 548 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | DS1 | 1741 | [16 empty] | 1-3C-08 | 1-3C-09 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1741_DS | 1741(嘉惠二路) DS | LINE161 | E05/161/1740/DS1 |  |  |  | CDC | 549 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | DS2 | 1742 | [16 empty] | 1-3C-10 | 1-3C-11 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1742_DS | 1742(嘉惠二路) DS | LINE161 | E05/161/1740/DS2 |  |  |  | CDC | 550 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | DS3 | 1743 | [16 empty] | 1-3C-12 | 1-3C-13 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1743_DS | 1743(嘉惠二路) DS | LINE161 | E05/161/1740/DS3 |  |  |  | CDC | 551 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | E3 | 1743E | [16 empty] | 1-3C-14 | 1-3C-15 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1743E_ES | 1743E(嘉惠二路) ES | LINE161 | E05/161/1740/ES3 |  |  |  | CDC | 552 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1500_50A | 161KV TIE(1500) 50RY | TIE | E05/161/1500/50A |  |  |  | CDC | 553 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-38-00 | 1-38-01 | 1-60 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1501_DS | 1501(TIE) DS | TIE | E05/161/1500/DS1 |  |  |  | CDC | 554 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-38-06 | 1-38-07 | 1-61 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1502_DS | 1502(TIE) DS | TIE | E05/161/1500/DS2 |  |  |  | CDC | 555 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 1600 | TIE(1600) |  | 50A | [17 empty] | 1-07-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1600_50A | 161KV TIE(1600) 50RY | TIE | E05/161/1600/50A |  |  |  | CDC | 556 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS1 | 1601 | [16 empty] | 1-39-00 | 1-39-01 | 1-64 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1601_DS | 1601(TIE) DS | TIE | E05/161/1600/DS1 |  |  |  | CDC | 557 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS2 | 1602 | [16 empty] | 1-39-06 | 1-39-07 | 1-65 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1602_DS | 1602(TIE) DS | TIE | E05/161/1600/DS2 |  |  |  | CDC | 558 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-68 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1701_DS | 1701(TIE) DS | TIE | E05/161/1700/DS1 |  |  |  | CDC | 559 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | DS3 | 1703 | [16 empty] | 1-3A-04 | 1-3A-05 | 1-69 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1703_DS | 1703(TIE) DS | TIE | E05/161/1700/DS2 |  |  |  | CDC | 560 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1802 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-6A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1802_DS | 1802(TIE) DS | TIE | E05/161/1800/DS1 |  |  |  | CDC | 561 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | DS4 | 1804 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-6B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1804_DS | 1804(TIE) DS | TIE | E05/161/1800/DS2 |  |  |  | CDC | 562 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 87A1 | [17 empty] | 3-03-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#1ATR_87A1 | #1ATR 第一組 87RY | ATR | E05//1ATR/87A1 |  |  |  | CDC | 563 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 87A2 | [17 empty] | 3-03-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#1ATR_87A2 | #1ATR 第二組 87RY | ATR | E05//1ATR/87A2 |  |  |  | CDC | 564 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 96PA | [17 empty] | 3-04-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#1ATR_96PA | #1ATR 機械保護動作 | ATR | E05//1ATR/96PA |  |  |  | CDC | 565 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 51ZA | [17 empty] | 3-04-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#1ATR_51ZA | #1ATR 51Z(21+50,59-2,51Z) | ATR | E05//1ATR/51ZA |  |  |  | CDC | 566 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 59A | [17 empty] | 3-04-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#1ATR_59A | #1ATR 59RY | ATR | E05//1ATR/59A |  |  |  | CDC | 567 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 1_87UL1 | [17 empty] | 3-30-02 |  | 4-40 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_87UL1 | #1ATR 第一組 87RY U/L | OTHER | E05//1ATR/1_87UL1 |  |  |  | CDC | 568 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 1_87UL2 | [17 empty] | 3-30-03 |  | 4-41 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_87UL2 | #1ATR 第二組 87RY U/L | OTHER | E05//1ATR/1_87UL2 |  |  |  | CDC | 569 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 96D | [17 empty] | 3-30-08 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_96D | #1ATR 96D RY | ATR | E05//1ATR/96D |  |  |  | CDC | 570 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 96P | [17 empty] | 3-30-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_96P | #1ATR 96P RY | ATR | E05//1ATR/96P |  |  |  | CDC | 571 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 63Q | [17 empty] | 3-30-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_63Q | #1ATR 63Q RY | ATR | E05//1ATR/63Q |  |  |  | CDC | 572 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 96B1 | [17 empty] | 3-30-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_96B1 | #1ATR 96B1 RY | ATR | E05//1ATR/96B1 |  |  |  | CDC | 573 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 96B2 | [17 empty] | 3-30-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_96B2 | #1ATR 96B2 RY | ATR | E05//1ATR/96B2 |  |  |  | CDC | 574 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | TRA | [17 empty] | 3-30-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_TRA | #1ATR 重故障 | ATR | E05//1ATR/TRA |  |  |  | CDC | 575 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | TRF | [17 empty] | 3-30-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_TRF | #1ATR 輕故障 | ATR | E05//1ATR/TRF |  |  |  | CDC | 576 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SupLocal | [17 empty] | 3-30-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_S/L | #1ATR OLTC S/L | ATR | E05//1ATR/SupLocal |  |  |  | CDC | 577 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | A_M | [17 empty] | 3-30-05 |  | 3-74 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_A/M | #1ATR OLTC A/M | ATR | E05/345/3590/Tap Chan |  |  |  | CDC | 578 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | M/F/I | [17 empty] | 4-35-12 | 4-35-13 | 3-75 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#1ATR_M/F/I | #1ATR M/F/I | ATR | E05//1ATR/M_F_I |  |  |  | CDC | 579 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | DS1 | 3591 | [16 empty] | 3-3E-10 | 3-3E-11 | 3-3D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3591_DS | 3591(#1ATR) DS | ATR | E05/345/3590/DS1 |  |  |  | CDC | 580 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | DS2 | 3592 | [16 empty] | 3-3E-12 | 3-3E-13 | 3-3E | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3592_DS | 3592(#1ATR) DS | ATR | E05/345/3590/DS2 |  |  |  | CDC | 581 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 87A1 | [17 empty] | 3-04-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#2ATR_87A1 | #2ATR 第一組 87RY | ATR | E05//2ATR/87A1 |  |  |  | CDC | 582 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 87A2 | [17 empty] | 3-04-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#2ATR_87A2 | #2ATR 第二組 87RY | ATR | E05//2ATR/87A2 |  |  |  | CDC | 583 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 96PA | [17 empty] | 3-04-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#2ATR_96PA | #2ATR 機械保護動作 | ATR | E05//2ATR/96PA |  |  |  | CDC | 584 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 51ZA | [17 empty] | 3-04-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#2ATR_51ZA | #2ATR 51Z(21+50,59-2,51Z) | ATR | E05//2ATR/51ZA |  |  |  | CDC | 585 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 59A | [17 empty] | 3-04-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#2ATR_59A | #2ATR 59RY | ATR | E05//2ATR/59A |  |  |  | CDC | 586 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 1_87UL1 | [17 empty] | 3-31-02 |  | 4-44 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_87UL1 | #2ATR 第一組 87RY U/L | OTHER | E05//2ATR/1_87UL1 |  |  |  | CDC | 587 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 1_87UL2 | [17 empty] | 3-31-03 |  | 4-45 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_87UL2 | #2ATR 第二組 87RY U/L | OTHER | E05//2ATR/1_87UL2 |  |  |  | CDC | 588 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 96D | [17 empty] | 3-31-08 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_96D | #2ATR 96D RY | ATR | E05//2ATR/96D |  |  |  | CDC | 589 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 96P | [17 empty] | 3-31-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_96P | #2ATR 96P RY | ATR | E05//2ATR/96P |  |  |  | CDC | 590 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 63Q | [17 empty] | 3-31-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_63Q | #2ATR 63Q RY | ATR | E05//2ATR/63Q |  |  |  | CDC | 591 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 96B1 | [17 empty] | 3-31-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_96B1 | #2ATR 96B1 RY | ATR | E05//2ATR/96B1 |  |  |  | CDC | 592 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 96B2 | [17 empty] | 3-31-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_96B2 | #2ATR 96B2 RY | ATR | E05//2ATR/96B2 |  |  |  | CDC | 593 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | TRA | [17 empty] | 3-31-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_TRA | #2ATR 重故障 | ATR | E05//2ATR/TRA |  |  |  | CDC | 594 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | TRF | [17 empty] | 3-31-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_TRF | #2ATR 輕故障 | ATR | E05//2ATR/TRF |  |  |  | CDC | 595 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SupLocal | [17 empty] | 3-31-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_S/L | #2ATR OLTC S/L | ATR | E05//2ATR/SupLocal |  |  |  | CDC | 596 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | A_M | [17 empty] | 3-31-05 |  | 3-78 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_A/M | #2ATR OLTC A/M | ATR | E05/345/3630/Tap Chan |  |  |  | CDC | 597 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | M/F/I | [17 empty] | 4-35-14 | 4-35-15 | 3-79 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#2ATR_M/F/I | #2ATR M/F/I | ATR | E05//2ATR/M_F_I |  |  |  | CDC | 598 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | DS1 | 3631 | [16 empty] | 3-3F-08 | 3-3F-09 | 3-44 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3631_DS | 3631(#2ATR) DS | ATR | E05/345/3630/DS1 |  |  |  | CDC | 599 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | DS2 | 3632 | [16 empty] | 3-3F-10 | 3-3F-11 | 3-45 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3632_DS | 3632(#2ATR) DS | ATR | E05/345/3630/DS2 |  |  |  | CDC | 600 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 87A1 | [17 empty] | 3-05-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#3ATR_87A1 | #3ATR 第一組 87RY | ATR | E05//3ATR/87A1 |  |  |  | CDC | 601 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 87A2 | [17 empty] | 3-05-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#3ATR_87A2 | #3ATR 第二組 87RY | ATR | E05//3ATR/87A2 |  |  |  | CDC | 602 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 96PA | [17 empty] | 3-05-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#3ATR_96PA | #3ATR 機械保護動作 | ATR | E05//3ATR/96PA |  |  |  | CDC | 603 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 51ZA | [17 empty] | 3-05-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#3ATR_51ZA | #3ATR 51Z(21+50,59-2,51Z) | ATR | E05//3ATR/51ZA |  |  |  | CDC | 604 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 59A | [17 empty] | 3-05-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#3ATR_59A | #3ATR 59RY | ATR | E05//3ATR/59A |  |  |  | CDC | 605 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 1_87UL1 | [17 empty] | 3-32-02 |  | 4-3B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_87UL1 | #3ATR 第一組 87RY U/L | OTHER | E05//3ATR/1_87UL1 |  |  |  | CDC | 606 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 1_87UL2 | [17 empty] | 3-32-03 |  | 4-3E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_87UL2 | #3ATR 第二組 87RY U/L | OTHER | E05//3ATR/1_87UL2 |  |  |  | CDC | 607 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 96D | [17 empty] | 3-32-08 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_96D | #3ATR 96D RY | ATR | E05//3ATR/96D |  |  |  | CDC | 608 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 96P | [17 empty] | 3-32-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_96P | #3ATR 96P RY | ATR | E05//3ATR/96P |  |  |  | CDC | 609 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 63Q | [17 empty] | 3-32-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_63Q | #3ATR 63Q RY | ATR | E05//3ATR/63Q |  |  |  | CDC | 610 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 96B1 | [17 empty] | 3-32-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_96B1 | #3ATR 96B1 RY | ATR | E05//3ATR/96B1 |  |  |  | CDC | 611 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 96B2 | [17 empty] | 3-32-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_96B2 | #3ATR 96B2 RY | ATR | E05//3ATR/96B2 |  |  |  | CDC | 612 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | TRA | [17 empty] | 3-32-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_TRA | #3ATR 重故障 | ATR | E05//3ATR/TRA |  |  |  | CDC | 613 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | TRF | [17 empty] | 3-32-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_TRF | #3ATR 輕故障 | ATR | E05//3ATR/TRF |  |  |  | CDC | 614 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | SupLocal | [17 empty] | 3-32-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_S/L | #3ATR OLTC S/L | ATR | E05//3ATR/SupLocal |  |  |  | CDC | 615 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | A_M | [17 empty] | 3-32-05 |  | 3-7C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_A/M | #3ATR OLTC A/M | ATR | E05/345/3660/Tap Chan |  |  |  | CDC | 616 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | M/F/I | [17 empty] | 4-36-00 | 4-36-01 | 3-7D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#3ATR_M/F/I | #3ATR M/F/I | ATR | E05//3ATR/M_F_I |  |  |  | CDC | 617 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | DS1 | 3661 | [16 empty] | 4-30-10 | 4-30-11 | 3-4B | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3661_DS | 3661(#3ATR) DS | ATR | E05/345/3660/DS1 |  |  |  | CDC | 618 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | DS2 | 3662 | [16 empty] | 4-30-12 | 4-30-13 | 3-4C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3662_DS | 3662(#3ATR) DS | ATR | E05/345/3660/DS2 |  |  |  | CDC | 619 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 87A1 | [17 empty] | 3-05-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#4ATR_87A1 | #4ATR 第一組 87RY | ATR | E05//4ATR/87A1 |  |  |  | CDC | 620 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 87A2 | [17 empty] | 3-05-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#4ATR_87A2 | #4ATR 第二組 87RY | ATR | E05//4ATR/87A2 |  |  |  | CDC | 621 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 96PA | [17 empty] | 3-05-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#4ATR_96PA | #4ATR 機械保護動作 | ATR | E05//4ATR/96PA |  |  |  | CDC | 622 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 51ZA | [17 empty] | 3-06-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#4ATR_51ZA | #4ATR 51Z(21+50,59-2,51Z) | ATR | E05//4ATR/51ZA |  |  |  | CDC | 623 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 59A | [17 empty] | 3-06-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#4ATR_59A | #4ATR 59RY | ATR | E05//4ATR/59A |  |  |  | CDC | 624 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 1_87UL1 | [17 empty] | 3-32-13 |  | 4-48 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_87UL1 | #4ATR 第一組 87RY U/L | OTHER | E05//4ATR/1_87UL1 |  |  |  | CDC | 625 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 1_87UL2 | [17 empty] | 3-32-14 |  | 4-49 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_87UL2 | #4ATR 第二組 87RY U/L | OTHER | E05//4ATR/1_87UL2 |  |  |  | CDC | 626 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 96D | [17 empty] | 3-33-03 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_96D | #4ATR 96D RY | ATR | E05//4ATR/96D |  |  |  | CDC | 627 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 96P | [17 empty] | 3-33-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_96P | #4ATR 96P RY | ATR | E05//4ATR/96P |  |  |  | CDC | 628 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 63Q | [17 empty] | 3-33-05 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_63Q | #4ATR 63Q RY | ATR | E05//4ATR/63Q |  |  |  | CDC | 629 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 96B1 | [17 empty] | 3-33-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_96B1 | #4ATR 96B1 RY | ATR | E05//4ATR/96B1 |  |  |  | CDC | 630 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 96B2 | [17 empty] | 3-33-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_96B2 | #4ATR 96B2 RY | ATR | E05//4ATR/96B2 |  |  |  | CDC | 631 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | TRA | [17 empty] | 3-33-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_TRA | #4ATR 重故障 | ATR | E05//4ATR/TRA |  |  |  | CDC | 632 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | TRF | [17 empty] | 3-33-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_TRF | #4ATR 輕故障 | ATR | E05//4ATR/TRF |  |  |  | CDC | 633 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | SupLocal | [17 empty] | 3-32-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_S/L | #4ATR OLTC S/L | ATR | E05//4ATR/SupLocal |  |  |  | CDC | 634 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | A_M | [17 empty] | 3-33-00 |  | 4-00 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_A/M | #4ATR OLTC A/M | ATR | E05/345/3730/Tap Chan |  |  |  | CDC | 635 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | M/F/I | [17 empty] | 4-36-02 | 4-36-03 | 4-01 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#4ATR_M/F/I | #4ATR M/F/I | ATR | E05//4ATR/M_F_I |  |  |  | CDC | 636 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | DS1 | 3731 | [16 empty] | 4-31-08 | 4-31-09 | 3-52 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3731_DS | 3731(#4ATR) DS | ATR | E05/345/3730/DS1 |  |  |  | CDC | 637 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | DS2 | 3732 | [16 empty] | 4-31-10 | 4-31-11 | 3-53 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3732_DS | 3732(#4ATR) DS | ATR | E05/345/3730/DS2 |  |  |  | CDC | 638 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 87A1 | [17 empty] | 3-06-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#5ATR_87A1 | #5ATR 第一組 87RY | ATR | E05//5ATR/87A1 |  |  |  | CDC | 639 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 87A2 | [17 empty] | 3-06-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#5ATR_87A2 | #5ATR 第二組 87RY | ATR | E05//5ATR/87A2 |  |  |  | CDC | 640 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 96PA | [17 empty] | 3-06-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#5ATR_96PA | #5ATR 機械保護動作 | ATR | E05//5ATR/96PA |  |  |  | CDC | 641 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 51ZA | [17 empty] | 3-06-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#5ATR_51ZA | #5ATR 51Z(21+50,59-2,51Z) | ATR | E05//5ATR/51ZA |  |  |  | CDC | 642 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 59A | [17 empty] | 3-06-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#5ATR_59A | #5ATR 59RY | ATR | E05//5ATR/59A |  |  |  | CDC | 643 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 1_87UL1 | [17 empty] | 3-33-08 |  | 4-4B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_87UL1 | #5ATR 第一組 87RY U/L | OTHER | E05//5ATR/1_87UL1 |  |  |  | CDC | 644 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 1_87UL2 | [17 empty] | 3-33-09 |  | 4-4C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_87UL2 | #5ATR 第二組 87RY U/L | OTHER | E05//5ATR/1_87UL2 |  |  |  | CDC | 645 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 96D | [17 empty] | 3-33-14 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_96D | #5ATR 96D RY | ATR | E05//5ATR/96D |  |  |  | CDC | 646 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 96P | [17 empty] | 3-33-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_96P | #5ATR 96P RY | ATR | E05//5ATR/96P |  |  |  | CDC | 647 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 63Q | [17 empty] | 3-34-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_63Q | #5ATR 63Q RY | ATR | E05//5ATR/63Q |  |  |  | CDC | 648 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 96B1 | [17 empty] | 3-33-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_96B1 | #5ATR 96B1 RY | ATR | E05//5ATR/96B1 |  |  |  | CDC | 649 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 96B2 | [17 empty] | 3-33-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_96B2 | #5ATR 96B2 RY | ATR | E05//5ATR/96B2 |  |  |  | CDC | 650 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | TRA | [17 empty] | 3-34-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_TRA | #5ATR 重故障 | ATR | E05//5ATR/TRA |  |  |  | CDC | 651 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | TRF | [17 empty] | 3-34-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_TRF | #5ATR 輕故障 | ATR | E05//5ATR/TRF |  |  |  | CDC | 652 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SupLocal | [17 empty] | 3-33-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_S/L | #5ATR OLTC S/L | ATR | E05//5ATR/SupLocal |  |  |  | CDC | 653 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | A_M | [17 empty] | 3-33-11 |  | 4-04 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_A/M | #5ATR OLTC A/M | ATR | E05/345/3790/Tap Chan |  |  |  | CDC | 654 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | M/F/I | [17 empty] | 4-36-04 | 4-36-05 | 4-05 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#5ATR_M/F/I | #5ATR M/F/I | ATR | E05//5ATR/M_F_I |  |  |  | CDC | 655 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | DS1 | 3791 | [16 empty] | 4-32-06 | 4-32-07 | 3-59 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3791_DS | 3791(#5ATR) DS | ATR | E05/345/3790/DS1 |  |  |  | CDC | 656 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | DS2 | 3792 | [16 empty] | 4-32-08 | 4-32-09 | 3-5A | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3792_DS | 3792(#5ATR) DS | ATR | E05/345/3790/DS2 |  |  |  | CDC | 657 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 87A1 | [17 empty] | 3-06-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#6ATR_87A1 | #6ATR 第一組 87RY | ATR | E05//6ATR/87A1 |  |  |  | CDC | 658 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 87A2 | [17 empty] | 3-07-00 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#6ATR_87A2 | #6ATR 第二組 87RY | ATR | E05//6ATR/87A2 |  |  |  | CDC | 659 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 96PA | [17 empty] | 3-07-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#6ATR_96PA | #6ATR 機械保護動作 | ATR | E05//6ATR/96PA |  |  |  | CDC | 660 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 51ZA | [17 empty] | 3-07-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#6ATR_51ZA | #6ATR 51Z(21+50,59-2,51Z) | ATR | E05//6ATR/51ZA |  |  |  | CDC | 661 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 59A | [17 empty] | 3-07-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#6ATR_59A | #6ATR 59RY | ATR | E05//6ATR/59A |  |  |  | CDC | 662 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 1_87UL1 | [17 empty] | 3-34-08 |  | 4-4F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_87UL1 | #6ATR 第一組 87RY U/L | OTHER | E05//6ATR/1_87UL1 |  |  |  | CDC | 663 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 1_87UL2 | [17 empty] | 3-34-09 |  | 4-50 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_87UL2 | #6ATR 第二組 87RY U/L | OTHER | E05//6ATR/1_87UL2 |  |  |  | CDC | 664 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 96D | [17 empty] | 3-34-14 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_96D | #6ATR 96D RY | ATR | E05//6ATR/96D |  |  |  | CDC | 665 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 96P | [17 empty] | 3-34-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_96P | #6ATR 96P RY | ATR | E05//6ATR/96P |  |  |  | CDC | 666 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 63Q | [17 empty] | 3-35-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_63Q | #6ATR 63Q RY | ATR | E05//6ATR/63Q |  |  |  | CDC | 667 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 96B1 | [17 empty] | 3-34-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_96B1 | #6ATR 96B1 RY | ATR | E05//6ATR/96B1 |  |  |  | CDC | 668 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 96B2 | [17 empty] | 3-34-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_96B2 | #6ATR 96B2 RY | ATR | E05//6ATR/96B2 |  |  |  | CDC | 669 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | TRA | [17 empty] | 3-35-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_TRA | #6ATR 重故障 | ATR | E05//6ATR/TRA |  |  |  | CDC | 670 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | TRF | [17 empty] | 3-35-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_TRF | #6ATR 輕故障 | ATR | E05//6ATR/TRF |  |  |  | CDC | 671 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SupLocal | [17 empty] | 3-34-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_S/L | #6ATR OLTC S/L | ATR | E05//6ATR/SupLocal |  |  |  | CDC | 672 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | A_M | [17 empty] | 3-34-11 |  | 4-08 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_A/M | #6ATR OLTC A/M | ATR | E05/345/3830/Tap Chan |  |  |  | CDC | 673 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | M/F/I | [17 empty] | 4-36-06 | 4-36-07 | 4-09 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#6ATR_M/F/I | #6ATR M/F/I | ATR | E05//6ATR/M_F_I |  |  |  | CDC | 674 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | DS1 | 3831 | [16 empty] | 4-33-04 | 4-33-05 | 3-60 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3831_DS | 3831(#6ATR) DS | ATR | E05/345/3830/DS1 |  |  |  | CDC | 675 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | DS2 | 3832 | [16 empty] | 4-33-06 | 4-33-07 | 3-61 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3832_DS | 3832(#6ATR) DS | ATR | E05/345/3830/DS2 |  |  |  | CDC | 676 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 1SSTR | #1SSTR |  | 51A | [17 empty] | 3-16-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1SSTR_51A | #1SSTR 51RY | OTHER | E05/33/310/PHA |  |  |  | CDC | 677 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2SSTR | #2SSTR |  | 51A | [17 empty] | 3-17-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2SSTR_51A | #2SSTR 51RY | OTHER | E05/33/320/PHA |  |  |  | CDC | 678 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 2-31-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | E05/161/1BUS/BUS_VUA |  |  |  | CDC | 679 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-08-02 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.161#1BUS_87A | 161KV #1BUS 87RY | BUS | E05/161/1BUS/87A |  |  |  | CDC | 680 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 2-32-00 |  | 2-18 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | E05/161/1BUS/87UL |  |  |  | CDC | 681 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 2-31-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | E05/161/2BUS/BUS_VUA |  |  |  | CDC | 682 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-08-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.161#2BUS_87A | 161KV #2BUS 87RY | BUS | E05/161/2BUS/87A |  |  |  | CDC | 683 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 2-32-01 |  | 2-19 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | E05/161/2BUS/87UL |  |  |  | CDC | 684 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1613BUS | #3BUS |  | VUA | [17 empty] | 2-31-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161#3BUS_VUA | 161KV #3BUS 衡相RY | BUS | E05/161/3BUS/BUS_VUA |  |  |  | CDC | 685 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1613BUS | #3BUS |  | 87A | [17 empty] | 1-08-04 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.161#3BUS_87A | 161KV #3BUS 87RY | BUS | E05/161/3BUS/87A |  |  |  | CDC | 686 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1613BUS | #3BUS |  | 87UL | [17 empty] | 2-32-02 |  | 2-1A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.161#3BUS_87UL | 161KV #3BUS 87RY U/L | OTHER | E05/161/3BUS/87UL |  |  |  | CDC | 687 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 161 | 161kV | 1614BUS | #4BUS |  | VUA | [17 empty] | 2-31-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161#4BUS_VUA | 161KV #4BUS 衡相RY | BUS | E05/161/4BUS/BUS_VUA |  |  |  | CDC | 688 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1614BUS | #4BUS |  | 87A | [17 empty] | 1-08-05 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.161#4BUS_87A | 161KV #4BUS 87RY | BUS | E05/161/4BUS/87A |  |  |  | CDC | 689 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1614BUS | #4BUS |  | 87UL | [17 empty] | 2-32-03 |  | 2-1F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.161#4BUS_87UL | 161KV #4BUS 87RY U/L | OTHER | E05/161/4BUS/87UL |  |  |  | CDC | 690 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3451B | #1BUS |  | 87A1 | [17 empty] | 3-07-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.345#1B_87A1 | 345KV #1BUS 第一組 87RY | BUS | E05/345/1BUS/87A1 |  |  |  | CDC | 691 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3451B | #1BUS |  | 87A2 | [17 empty] | 3-07-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.345#1B_87A2 | 345KV #1BUS 第二組 87RY | BUS | E05/345/1BUS/87A2 |  |  |  | CDC | 692 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3451B | #1BUS |  | 1_87UL1 | [17 empty] | 3-35-08 |  | 4-33 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.345#1B_87UL1 | 345KV #1BUS 第一組 87RY U/L | OTHER | E05/345/1BUS/1_87UL1 |  |  |  | CDC | 693 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3451B | #1BUS |  | 1_87UL2 | [17 empty] | 3-35-09 |  | 4-35 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.345#1B_87UL2 | 345KV #1BUS 第二組 87RY U/L | OTHER | E05/345/1BUS/1_87UL2 |  |  |  | CDC | 694 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3452B | #2BUS |  | 87A1 | [17 empty] | 3-07-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.345#2B_87A1 | 345KV #2BUS 第一組 87RY | BUS | E05/345/2BUS/87A1 |  |  |  | CDC | 695 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3452B | #2BUS |  | 87A2 | [17 empty] | 3-07-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.345#2B_87A2 | 345KV #2BUS 第二組 87RY | BUS | E05/345/2BUS/87A2 |  |  |  | CDC | 696 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3452B | #2BUS |  | 1_87UL1 | [17 empty] | 3-35-10 |  | 4-34 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.345#2B_87UL1 | 345KV #2BUS 第一組 87RY U/L | OTHER | E05/345/2BUS/1_87UL1 |  |  |  | CDC | 697 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV | 3452B | #2BUS |  | 1_87UL2 | [17 empty] | 3-35-11 |  | 4-36 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.345#2B_87UL2 | 345KV #2BUS 第二組 87RY U/L | OTHER | E05/345/2BUS/1_87UL2 |  |  |  | CDC | 698 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 345 | 345kV |  |  |  | BFA | [17 empty] | 3-08-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_BFA | 345KV斷路器失靈(BF)警報 | OTHER | E05/345/ComPoint/BFA |  |  |  | CDC | 699 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV |  |  |  | OSCA | [17 empty] | 3-08-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_OSCA | 345KV 示波器啟動警報 | OTHER | E05/345/ComPoint/OSCA |  |  |  | CDC | 700 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 復閉 | 復閉 |  | RCA | [17 empty] | 3-08-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_RCA | 345KV 79RY(復閉) 動作 | OTHER | E05/345/ComPoint/RCA |  |  |  | CDC | 701 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 斷路器失靈RY | 斷路器失靈RY |  | BFS | [17 empty] | 3-35-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.345KV_BFS | 345KV 斷路器失靈RY U/L | OTHER | E05/345/ComPoint/BFS |  |  |  | CDC | 702 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E05 | 嘉民ES | 345 | 345kV |  |  |  | CBA | [17 empty] | 3-35-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_CBA | 345KV 斷路器重故障 | OTHER | E05/345/ComPoint/CBA |  |  |  | CDC | 703 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV |  |  |  | CBF | [17 empty] | 3-35-14 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_CBF | 345KV 斷路器輕故障 | OTHER | E05/345/ComPoint/CBF |  |  |  | CDC | 704 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV |  |  |  | COMT | [17 empty] | 3-35-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_COMT | 345KV 空壓機運轉超時警報 | OTHER | E05/345/ComPoint/COMT |  |  |  | CDC | 705 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 25RY | 25RY |  | 25TA | [17 empty] | 3-16-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_25TA | 345KV 25RY 超時動作警報 | OTHER | E05/345/ComPoint/25TA |  |  |  | CDC | 706 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 25RY | 25RY |  | 25PFA | [17 empty] | 3-16-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_25PFA | 345KV 25RY 電源故障警報 | OTHER | E05/345/ComPoint/25PFA |  |  |  | CDC | 707 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 510 | 510 |  | CB | [17 empty] | 3-14-00 |  | 3-0B | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.510_CB | 510 CB | OTHER | E05/33/510/CB |  |  |  | CDC | 708 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 510 | 510 |  | 87A | [17 empty] | 3-14-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.510_87A | 510 87RY | OTHER | E05/33/510/87A |  |  |  | CDC | 709 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 510 | 510 |  | PHA | [17 empty] | 3-14-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.510_PHA | 510 相間RY | OTHER | E05/33/510/PHA |  |  |  | CDC | 710 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 520 | 520 |  | CB | [17 empty] | 3-14-03 |  | 3-10 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.520_CB | 520 CB | OTHER | E05/33/520/CB |  |  |  | CDC | 711 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 520 | 520 |  | 87A | [17 empty] | 3-14-05 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.520_87A | 520 87RY | OTHER | E05/33/520/87A |  |  |  | CDC | 712 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 520 | 520 |  | PHA | [17 empty] | 3-14-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.520_PHA | 520 相間RY | OTHER | E05/33/520/PHA |  |  |  | CDC | 713 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 550 | 550 |  | CB | [17 empty] | 3-15-02 |  | 3-1F | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.550_CB | 550 CB | OTHER | E05/33/550/CB |  |  |  | CDC | 714 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 550 | 550 |  | 87A | [17 empty] | 3-15-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.550_87A | 550 87RY | OTHER | E05/33/550/87A |  |  |  | CDC | 715 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 560 | 560 |  | CB | [17 empty] | 3-15-05 |  | 3-24 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.560_CB | 560 CB | OTHER | E05/33/560/CB |  |  |  | CDC | 716 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 560 | 560 |  | 87A | [17 empty] | 3-15-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.560_87A | 560 87RY | OTHER | E05/33/560/87A |  |  |  | CDC | 717 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | _ABS | ABS |  | ABS_89A | [17 empty] | 2-34-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | E05/161/ComPoint/ABS_89A |  |  |  | CDC | 718 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV |  |  |  | BFA | [17 empty] | 1-08-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_BFA | 161KV斷路器失靈(BF)RY | OTHER | E05/161/ComPoint/BFA |  |  |  | CDC | 719 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-34-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_CBA | 161KV斷路器重故障 | OTHER | E05/161/ComPoint/CBA |  |  |  | CDC | 720 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-34-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_CBF | 161KV斷路器輕故障 | OTHER | E05/161/ComPoint/CBF |  |  |  | CDC | 721 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-09-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_OSCA | 161KV示波器啟動警報 | OTHER | E05/161/ComPoint/OSCA |  |  |  | CDC | 722 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-08-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | E05/161/ComPoint/RCA |  |  |  | CDC | 723 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV |  |  |  | COMT | [17 empty] | 2-34-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | E05/161/ComPoint/COMT |  |  |  | CDC | 724 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 25PFA | [17 empty] | 1-10-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | E05/0/StaDev/25PFA |  |  |  | CDC | 725 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 25TA | [17 empty] | 1-10-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | E05/0/StaDev/25TA |  |  |  | CDC | 726 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | ACB1 | [17 empty] | 4-39-12 |  | 4-38 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACB1 | 所內電源ACB1 | OTHER | E05/0/StaDev/ACB1 |  |  |  | CDC | 727 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | ACB2 | [17 empty] | 4-39-14 |  | 4-3A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACB2 | 所內電源ACB2 | OTHER | E05/0/StaDev/ACB2 |  |  |  | CDC | 728 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | CHG1 | [17 empty] | 3-3A-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.直流充電機故障 | 變電所#1直流充電機故障 | OTHER | E05/0/StaDev/CHG1 |  |  |  | CDC | 729 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | OilLeak | [17 empty] | 3-39-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.洩油池水位警報 | 洩油池水位警報 | OTHER | E05/0/StaDev/OilLeak |  |  |  | CDC | 730 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | CHG2 | [17 empty] | 3-3A-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | E05/0/StaDev/CHG2 |  |  |  | CDC | 731 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | Door1 | [17 empty] | 3-39-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.無人化門禁(1) | 無人化門禁(1) | OTHER | E05/0/StaDev/Door1 |  |  |  | CDC | 732 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | OPEN/CLOSE | CLOSE
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SR96B1 | [17 empty] | 4-39-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SR96B1 | #1ATR 161KV 電抗器96B1 RY | OTHER | E05/161/1SR/96B1 |  |  |  | CDC | 733 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SR96B2 | [17 empty] | 4-39-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SR96B2 | #1ATR 161KV 電抗器96B2 RY | OTHER | E05/161/1SR/96B2 |  |  |  | CDC | 734 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SR96D | [17 empty] | 4-39-02 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SR96D | #1ATR 161KV 電抗器96D RY | OTHER | E05/161/1SR/96D |  |  |  | CDC | 735 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SR96P | [17 empty] | 4-39-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SR96P | #1ATR 161KV 電抗器96P RY | OTHER | E05/161/1SR/96P |  |  |  | CDC | 736 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SR96B1 | [17 empty] | 4-39-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SR96B1 | #2ATR 161KV 電抗器96B1 RY | OTHER | E05/161/2SR/96B1 |  |  |  | CDC | 737 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SR96B2 | [17 empty] | 4-39-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SR96B2 | #2ATR 161KV 電抗器96B2 RY | OTHER | E05/161/2SR/96B2 |  |  |  | CDC | 738 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SR96D | [17 empty] | 4-39-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SR96D | #2ATR 161KV 電抗器96D RY | OTHER | E05/161/2SR/96D |  |  |  | CDC | 739 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SR96P | [17 empty] | 4-39-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SR96P | #2ATR 161KV 電抗器96P RY | OTHER | E05/161/2SR/96P |  |  |  | CDC | 740 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | #2充電機故障 | [17 empty] | 3-3B-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#2充電機故障 | 變電所#2直流充電機故障 | OTHER | E05/0/StaDev/CHG1_1 |  |  |  | CDC | 741 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | #3充電機故障 | [17 empty] | 3-3B-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#3充電機故障 | 變電所#3直流充電機故障 | OTHER | E05/0/StaDev/CHG1_2 |  |  |  | CDC | 742 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SR96B1 | [17 empty] | 4-3C-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SR96B1 | #5ATR 161KV 電抗器96B1 RY | OTHER | E05/161/5SR/96B1 |  |  |  | CDC | 743 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SR96B2 | [17 empty] | 4-3C-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SR96B2 | #5ATR 161KV 電抗器96B2 RY | OTHER | E05/161/5SR/96B2 |  |  |  | CDC | 744 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SR96D | [17 empty] | 4-3C-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SR96D | #5ATR 161KV 電抗器96D RY | OTHER | E05/161/5SR/96D |  |  |  | CDC | 745 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SR96P | [17 empty] | 4-3C-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SR96P | #5ATR 161KV 電抗器96P RY | OTHER | E05/161/5SR/96P |  |  |  | CDC | 746 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SR96B1 | [17 empty] | 4-3C-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SR96B1 | #6ATR 161KV 電抗器96B1 RY | OTHER | E05/161/6SR/96B1 |  |  |  | CDC | 747 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SR96B2 | [17 empty] | 4-3C-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SR96B2 | #6ATR 161KV 電抗器96B2 RY | OTHER | E05/161/6SR/96B2 |  |  |  | CDC | 748 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SR96D | [17 empty] | 4-3C-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SR96D | #6ATR 161KV 電抗器96D RY | OTHER | E05/161/6SR/96D |  |  |  | CDC | 749 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SR96P | [17 empty] | 4-3C-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SR96P | #6ATR 161KV 電抗器96P RY | OTHER | E05/161/6SR/96P |  |  |  | CDC | 750 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 2-35-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | E05/161/1500/50SA |  |  |  | CDC | 751 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501BE | [16 empty] | 1-38-02 | 1-38-03 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1501BE_DS | 1501BE DS | OTHER | E05/161/1500/BE1 |  |  |  | CDC | 752 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501E | [16 empty] | 1-38-04 | 1-38-05 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1501E_DS | 1501E DS | OTHER | E05/161/1500/E1 |  |  |  | CDC | 753 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502BE | [16 empty] | 1-38-08 | 1-38-09 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1502BE_DS | 1502BE DS | OTHER | E05/161/1500/BE2 |  |  |  | CDC | 754 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502E | [16 empty] | 1-38-10 | 1-38-11 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1502E_DS | 1502E DS | OTHER | E05/161/1500/E2 |  |  |  | CDC | 755 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1500 | TIE(1500) |  | ABS3 | 1503 | [16 empty] | 1-38-12 | 1-38-13 | 1-62 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1503_ABS | 1503 ABS | OTHER | E05/161/1500/ABS1 |  |  |  | CDC | 756 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 1510 | 嘉義山線(1510) |  | RYFA | [17 empty] | 2-32-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1510_RYFA | 嘉民嘉義山線(1510)數位電驛故障 | OTHER | E05/161/1510/RYFA |  |  |  | CDC | 757 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1520 | 嘉義海線(1520) |  | RYFA | [17 empty] | 2-32-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1520_RYFA | 嘉民嘉義海線(1520)數位電驛故障 | OTHER | E05/161/1520/RYFA |  |  |  | CDC | 758 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1530 | 柳營山線(1530) |  | 87CFA | [17 empty] | 2-32-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_87CFA | 嘉民柳營山線(1530)87RY通訊故障 | OTHER | E05/161/1530/87CFA |  |  |  | CDC | 759 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1530 | 柳營山線(1530) |  | DTTA | [17 empty] | 1-0B-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_DTTA | 嘉民柳營山線(1530)遠方遙跳 | OTHER | E05/161/1530/DTTA |  |  |  | CDC | 760 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1530 | 柳營山線(1530) |  | RYFA | [17 empty] | 2-32-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1530_RYFA | 嘉民柳營山線(1530)數位電驛故障 | OTHER | E05/161/1530/RYFA |  |  |  | CDC | 761 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1540 | 柳營海線(1540) |  | 87CFA | [17 empty] | 2-32-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_87CFA | 嘉民柳營海線(1540)87RY通訊故障 | OTHER | E05/161/1540/87CFA |  |  |  | CDC | 762 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1540 | 柳營海線(1540) |  | DTTA | [17 empty] | 1-0B-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_DTTA | 嘉民柳營海線(1540)遠方遙跳 | OTHER | E05/161/1540/DTTA |  |  |  | CDC | 763 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1540 | 柳營海線(1540) |  | RYFA | [17 empty] | 2-32-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1540_RYFA | 嘉民柳營海線(1540)數位電驛故障 | OTHER | E05/161/1540/RYFA |  |  |  | CDC | 764 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1550 | 雲林山線(1550) |  | RYFA | [17 empty] | 2-32-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1550_RYFA | 嘉民雲林山線(1550)數位電驛故障 | OTHER | E05/161/1550/RYFA |  |  |  | CDC | 765 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1560 | 雲林海線(1560) |  | RYFA | [17 empty] | 2-32-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1560_RYFA | 嘉民雲林海線(1560)數位電驛故障 | OTHER | E05/161/1560/RYFA |  |  |  | CDC | 766 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1580 | 嘉民雲林線(1580) |  | RYFA | [17 empty] | 2-33-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1580_RYFA | 嘉民雲林線(1580)數位電驛故障 | OTHER | E05/161/1580/RYFA |  |  |  | CDC | 767 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1590 | 斗工紅線(1590) |  | RYFA | [17 empty] | 2-33-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1590_RYFA | 嘉民斗工紅線(1590)數位電驛故障 | OTHER | E05/161/1590/RYFA |  |  |  | CDC | 768 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1600TIE | 1600 |  | 50SA | [17 empty] | 2-35-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1600TIE_50SA | 161KV TIE(1600) 50RY 測試/正常 | OTHER | E05/161/1600/50SA |  |  |  | CDC | 769 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS1 | 1601BE | [16 empty] | 1-39-02 | 1-39-03 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1601BE_DS | 1601BE DS | OTHER | E05/161/1600/BE1 |  |  |  | CDC | 770 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS1 | 1601E | [16 empty] | 1-39-04 | 1-39-05 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1601E_DS | 1601E DS | OTHER | E05/161/1600/E1 |  |  |  | CDC | 771 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | DS2 | 1602E | [16 empty] | 1-39-10 | 1-39-11 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1602E_DS | 1602E DS | OTHER | E05/161/1600/E2 |  |  |  | CDC | 772 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1600 | TIE(1600) |  | ABS3 | 1603 | [16 empty] | 1-39-12 | 1-39-13 | 1-66 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1603_ABS | 1603 ABS | OTHER | E05/161/1600/ABS1 |  |  |  | CDC | 773 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 1610 | 嘉義南線(1610) |  | RYFA | [17 empty] | 2-33-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1610_RYFA | 嘉民嘉義南線(1610)數位電驛故障 | OTHER | E05/161/1610/RYFA |  |  |  | CDC | 774 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 161B3E | [17 empty] | 1-3D-00 | 1-3D-01 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.161B3E | 161B3E | OTHER | E05/161/161B3E/BE1 |  |  |  | CDC | 775 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 161B4E | [17 empty] | 1-3D-02 | 1-3D-03 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.161B4E | 161B4E | OTHER | E05/161/161B4E/BE2 |  |  |  | CDC | 776 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 斷路器失靈RY | 斷路器失靈RY |  | BFS | [17 empty] | 2-34-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_BFS | 161KV 斷路器失靈RY U/L | OTHER | E05/161/ComPoint/BFS |  |  |  | CDC | 777 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E05 | 嘉民ES | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | E05/161/ComPoint/OSCF |  |  |  | CDC | 778 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | _RTU | RTU |  | SupLocal | [17 empty] | 1-3B-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_RTU_S/L | 161KV RTU S/L | OTHER | E05/161/ComPoint/RTU_R_L |  |  |  | CDC | 779 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E05 | 嘉民ES | 161 | 161kV | _TEST | TEST |  | CB | [17 empty] | 1-3B-08 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_TEST_CB | 161KV TEST CB | OTHER | E05/161/ComPoint/Test_CB |  |  |  | CDC | 780 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  | 1620 | 嘉義北線(1620) |  | RYFA | [17 empty] | 2-33-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1620_RYFA | 嘉民嘉義北線(1620)數位電驛故障 | OTHER | E05/161/1620/RYFA |  |  |  | CDC | 781 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1630 | 北港南線(1630) |  | RYFA | [17 empty] | 2-33-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1630_RYFA | 嘉民北港南線(1630)數位電驛故障 | OTHER | E05/161/1630/RYFA |  |  |  | CDC | 782 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1640 | 北港北線(1640) |  | RYFA | [17 empty] | 2-33-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1640_RYFA | 嘉民北港北線(1640)數位電驛故障 | OTHER | E05/161/1640/RYFA |  |  |  | CDC | 783 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | DS1 | 1701E | [16 empty] | 1-3A-02 | 1-3A-03 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1701E_DS | 1701E DS | OTHER | E05/161/1700/E1 |  |  |  | CDC | 784 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1700 | TIE(1700) |  | DS3 | 1703E | [16 empty] | 1-3A-06 | 1-3A-07 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1703E_DS | 1703E DS | OTHER | E05/161/1700/E3 |  |  |  | CDC | 785 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 1710 | 台嘉一路(1710) |  | 85CFA | [17 empty] | 2-33-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1710_85CFA | 嘉民台嘉一路(1710)85RY通訊故障 | OTHER | E05/161/1710/85CFA |  |  |  | CDC | 786 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1710 | 台嘉一路(1710) |  | RYFA | [17 empty] | 2-33-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1710_RYFA | 嘉民台嘉一線(1710)數位電驛故障 | OTHER | E05/161/1710/RYFA |  |  |  | CDC | 787 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1720 | 台嘉二路(1720) |  | 85CFA | [17 empty] | 2-33-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1720_85CFA | 嘉民台嘉二路(1720)85RY通訊故障 | OTHER | E05/161/1720/85CFA |  |  |  | CDC | 788 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1720 | 台嘉二路(1720) |  | RYFA | [17 empty] | 2-33-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1720_RYFA | 嘉民台嘉二線(1720)數位電驛故障 | OTHER | E05/161/1720/RYFA |  |  |  | CDC | 789 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1730 | 嘉惠一路(1730) |  | RAOA | [17 empty] | 1-3B-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1730_RAOA | 嘉民嘉惠一路(1730)TONE故障 | OTHER | E05/161/1730/87CFA |  |  |  | CDC | 790 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1730 | 嘉惠一路(1730) |  | RY1A | [17 empty] | 1-3B-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1730_RY1A | 嘉民嘉惠一路(1730)第一套RY故障 | OTHER | E05/161/1730/RYFA |  |  |  | CDC | 791 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1730 | 嘉惠一路(1730) |  | RY2A | [17 empty] | 1-3B-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1730_RY2A | 嘉民嘉惠一路(1730)第二套RY故障 | OTHER | E05/161/1730/RYFA2 |  |  |  | CDC | 792 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1740 | 嘉惠二路(1740) |  | RAOA | [17 empty] | 1-3B-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1740_RAOA | 嘉民嘉惠二路(1740)TONE故障 | OTHER | E05/161/1740/87CFA |  |  |  | CDC | 793 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1740 | 嘉惠二路(1740) |  | RY1A | [17 empty] | 1-3B-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1740_RY1A | 嘉民嘉惠二路(1740)第一套RY故障 | OTHER | E05/161/1740/RYFA |  |  |  | CDC | 794 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1740 | 嘉惠二路(1740) |  | RY2A | [17 empty] | 1-3B-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1740_RY2A | 嘉民嘉惠二路(1740)第二套RY故障 | OTHER | E05/161/1740/RYFA2 |  |  |  | CDC | 795 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | DS2 | 1802E | [16 empty] | 1-3A-10 | 1-3A-11 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1802E_DS | 1802E DS | OTHER | E05/161/1800/E2 |  |  |  | CDC | 796 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1800 | TIE(1800) |  | DS4 | 1804E | [16 empty] | 1-3A-14 | 1-3A-15 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.1804E_DS | 1804E DS | OTHER | E05/161/1800/E4 |  |  |  | CDC | 797 | GENERICDIPoint | ES005_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 33 | 33kV | CB | CB |  | CBA | [17 empty] | 3-36-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.33KV_CBA | 33KV CB 重故障 | OTHER | E05/33/ComPoint/SHRA |  |  |  | CDC | 798 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV | CB | CB |  | CBF | [17 empty] | 3-36-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.33KV_CBF | 33KV CB 輕故障 | OTHER | E05/33/ComPoint/CBF |  |  |  | CDC | 799 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 33 | 33kV |  |  |  | COMT | [17 empty] | 3-36-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.33KV_COMT | 33KV 空壓機警報 | OTHER | E05/33/ComPoint/COMT |  |  |  | CDC | 800 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV |  |  |  | OSCF | [17 empty] | 3-3A-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_OSCF | 345KV 示波器故障/缺紙 | OTHER | E05/345/ComPoint/OSCF |  |  |  | CDC | 801 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | _RTU | RTU |  | SupLocal | [17 empty] | 3-30-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_RTU_S/L | 345KV RTU S/L | OTHER | E05/345/ComPoint/RTU_R_L |  |  |  | CDC | 802 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
E05 | 嘉民ES | 345 | 345kV | _TEST | TEST |  | CB | [17 empty] | 3-30-00 |  | 3-00 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_TEST_CB | 345KV TEST CB | OTHER | E05/345/ComPoint/Test_CB |  |  |  | CDC | 803 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  | 3510 | 麥寮二路(3510) |  | 85CFA(1) | [17 empty] | 3-36-08 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_85CFA(1) | 麥寮二路(3510)#2 87RY通訊故障 | OTHER | E05/345/3510/85CFA1 |  |  |  | CDC | 804 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3510 | 麥寮二路(3510) |  | 87CFA(1) | [17 empty] | 3-36-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3510_87CFA(1) | 麥寮二路(3510)#1 87RY通訊故障 | OTHER | E05/345/3510/87CFA1 |  |  |  | CDC | 805 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | E1 | 3511E | [16 empty] | 4-36-08 | 4-36-09 | [6 empty] | CDCS_N | [8 empty] | 嘉民ES.3511E_ES | 麥寮二路 3511E ES | OTHER | E05/345/3510/ES1 |  |  |  | CDC | 806 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | E2 | 3532E | [16 empty] | 4-36-14 | 4-36-15 | [6 empty] | CDCS_N | [8 empty] | 嘉民ES.3532E_ES | #8ATR 3532E ES | OTHER | E05/345/3530/ES2 |  |  |  | CDC | 807 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 3540 | 麥寮一路(3540) |  | 85CFA(1) | [17 empty] | 3-37-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_85CFA(1) | 麥寮一路(3540)#2 87RY通訊故障 | OTHER | E05/345/3540/85CFA1 |  |  |  | CDC | 808 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3540 | 麥寮一路(3540) |  | 85CFA(2) | [17 empty] | 3-37-07 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_85CFA(2) | 麥寮一路(3560)#2 87RY通訊故障 | OTHER | E05/345/3540/85CFA2 |  |  |  | CDC | 809 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3540 | 麥寮一路(3540) |  | 87CFA(1) | [17 empty] | 3-37-00 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_87CFA(1) | 麥寮一路(3540)#1 87RY通訊故障 | OTHER | E05/345/3540/87CFA1 |  |  |  | CDC | 810 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3540 | 麥寮一路(3540) |  | 87CFA(2) | [17 empty] | 3-37-05 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3540_87CFA(2) | 麥寮一路(3560)#1 87RY通訊故障 | OTHER | E05/345/3540/87CFA2 |  |  |  | CDC | 811 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3570 | 中寮二路(3570) |  | 85CFA | [17 empty] | 3-37-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_85CFA | 中寮二路(3570) 85RY通訊故障 | OTHER | E05/345/3570/85CFA |  |  |  | CDC | 812 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3570 | 中寮二路(3570) |  | 87CFA | [17 empty] | 3-37-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3570_87CFA | 中寮二路(3570) 87RY通訊故障 | OTHER | E05/345/3570/87CFA |  |  |  | CDC | 813 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | E1 | 3591E | [16 empty] | 4-37-04 | 4-37-05 | 4-28 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3591E_ES | #1ATR 3591E ES | OTHER | E05/345/3590/ES1 |  |  |  | CDC | 814 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 3610 | 中寮一路(3610) |  | 85CFA | [17 empty] | 3-38-01 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_85CFA | 中寮一路(3610) 85RY通訊故障 | OTHER | E05/345/3610/85CFA |  |  |  | CDC | 815 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3610 | 中寮一路(3610) |  | 87CFA | [17 empty] | 3-37-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3610_87CFA | 中寮一路(3610) 87RY通訊故障 | OTHER | E05/345/3610/87CFA |  |  |  | CDC | 816 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | E1 | 3611E | [16 empty] | 4-36-10 | 4-36-11 | [6 empty] | CDCS_N | [8 empty] | 嘉民ES.3611E_ES | 中寮一路 3611E ES | OTHER | E05/345/3610/ES1 |  |  |  | CDC | 817 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | E1 | 3631E | [16 empty] | 4-37-06 | 4-37-07 | 4-29 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3631E_ES | #2ATR 3631E ES | OTHER | E05/345/3630/ES1 |  |  |  | CDC | 818 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | E2 | 3632E | [16 empty] | 4-37-00 | 4-37-01 | [6 empty] | CDCS_N | [8 empty] | 嘉民ES.3632E_ES | #2ATR 3632E ES | OTHER | E05/345/3630/ES2 |  |  |  | CDC | 819 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 3640 | 中寮三路(3640) |  | 85CFA | [17 empty] | 3-38-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_85CFA | 中寮三路(3640) 85RY通訊故障 | OTHER | E05/345/3640/85CFA |  |  |  | CDC | 820 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3640 | 中寮三路(3640) |  | 87CFA | [17 empty] | 3-38-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3640_87CFA | 中寮三路(3640) 87RY通訊故障 | OTHER | E05/345/3640/87CFA |  |  |  | CDC | 821 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | E1 | 3661E | [16 empty] | 4-37-08 | 4-37-09 | 4-2A | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3661E_ES | #3ATR 3661E ES | OTHER | E05/345/3660/ES1 |  |  |  | CDC | 822 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 3710 | 龍崎紅線(3710) |  | 85CFA | [17 empty] | 3-38-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_85CFA | 龍崎紅線(3710) 85RY通訊故障 | OTHER | E05/345/3710/85CFA |  |  |  | CDC | 823 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3710 | 龍崎紅線(3710) |  | 87CFA | [17 empty] | 3-38-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.3710_87CFA | 龍崎紅線(3710) 87RY通訊故障 | OTHER | E05/345/3710/87CFA |  |  |  | CDC | 824 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | E1 | 3731E | [16 empty] | 4-37-10 | 4-37-11 | 4-2B | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3731E_ES | #4ATR 3731E ES | OTHER | E05/345/3730/ES1 |  |  |  | CDC | 825 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 3770 | 新南科一路(3770) |  | 85CFA | [17 empty] | 3-39-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.3770_85CFA | 新南科一路(3770) 85RY通訊故障 | OTHER | E05/345/3770/85CFA |  |  |  | CDC | 826 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3770 | 新南科一路(3770) |  | 87CFA | [17 empty] | 3-38-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.3770_87CFA | 新南科一路(3770) 87RY通訊故障 | OTHER | E05/345/3770/87CFA |  |  |  | CDC | 827 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | E1 | 3771E | [16 empty] | 4-36-12 | 4-36-13 | [6 empty] | ADCS_N | [8 empty] | 嘉民ES.3771E_ES | 新南科一路 3771E ES | OTHER | E05/345/3770/ES1 |  |  |  | CDC | 828 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | E1 | 3791E | [16 empty] | 4-37-12 | 4-37-13 | 4-2C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3791E_ES | #5ATR 3791E ES | OTHER | E05/345/3790/ES1 |  |  |  | CDC | 829 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | E2 | 3792E | [16 empty] | 4-37-02 | 4-37-03 | [6 empty] | CDCS_N | [8 empty] | 嘉民ES.3792E_ES | #5ATR 3792E ES | OTHER | E05/345/3790/ES2 |  |  |  | CDC | 830 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 3810 | 新南科二路(3810) |  | 85CFA | [17 empty] | 3-39-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.3810_85CFA | 新南科二路(3810) 85RY通訊故障 | OTHER | E05/345/3810/85CFA |  |  |  | CDC | 831 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3810 | 新南科二路(3810) |  | 87CFA | [17 empty] | 3-39-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.3810_87CFA | 新南科二路(3810) 87RY通訊故障 | OTHER | E05/345/3810/87CFA |  |  |  | CDC | 832 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | E1 | 3831E | [16 empty] | 4-37-14 | 4-37-15 | 4-2D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3831E_ES | #6ATR 3831E ES | OTHER | E05/345/3830/ES1 |  |  |  | CDC | 833 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | COF | [17 empty] | 3-3A-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.COF | 消防警報 | OTHER | E05/0/StaDev/Fire |  |  |  | CDC | 834 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 外燈(1) | [17 empty] | 3-3B-03 |  | 4-1E | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.外燈(1) | 3570側開關場長夜燈 | OTHER | E05/0/StaDev/Lights1 |  |  |  | CDC | 835 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | 外燈(2) | [17 empty] | 3-3B-04 |  | 4-1F | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.外燈(2) | 3720側開關場長夜燈 | OTHER | E05/0/StaDev/Lights2 |  |  |  | CDC | 836 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | 外燈(3) | [17 empty] | 3-3B-05 |  | 4-20 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.外燈(3) | 3820側開關場長夜燈 | OTHER | E05/0/StaDev/Lights3 |  |  |  | CDC | 837 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | 外燈(4) | [17 empty] | 3-3B-06 |  | 4-21 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.外燈(4) | 1711側開關場長夜燈 | OTHER | E05/0/StaDev/Lights4 |  |  |  | CDC | 838 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | 外燈(5) | [17 empty] | 3-3B-07 |  | 4-22 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.外燈(5) | 1700側開關場長夜燈 | OTHER | E05/0/StaDev/Lights5 |  |  |  | CDC | 839 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | 外燈(6) | [17 empty] | 3-3B-08 |  | 4-23 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.外燈(6) | 1542側開關場長夜燈 | OTHER | E05/0/StaDev/Lights6 |  |  |  | CDC | 840 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | DCA | [17 empty] | 3-3A-03 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.直流電源DCA | 345KV直流電源故障警報 | OTHER | E05/0/StaDev/DCA |  |  |  | CDC | 841 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | DCE | [17 empty] | 3-3A-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.直流電源DCE | 345KV直流接地故障警報 | OTHER | E05/0/StaDev/DCE |  |  |  | CDC | 842 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 空調機故障 | [17 empty] | 3-39-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.空調機故障 | 空調機故障或電源跳脫 | OTHER | E05/0/StaDev/AIRCON |  |  |  | CDC | 843 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 信號燈(1) | [17 empty] | 3-3B-00 |  | 4-1B | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.信號燈(1) | 通訊塔防情信號燈 | OTHER | E05/0/StaDev/Lights |  |  |  | CDC | 844 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | 信號燈(2) | [17 empty] | 3-3B-01 |  | 4-1C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.信號燈(2) | 161KV防情信號燈 | OTHER | E05/161/StaDev/Lights |  |  |  | CDC | 845 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | 信號燈(3) | [17 empty] | 3-3B-02 |  | 4-1D | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.信號燈(3) | 345KV防情信號燈 | OTHER | E05/345/StaDev/Lights |  |  |  | CDC | 846 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | 通訊室溫度 | [17 empty] | 3-3A-14 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.通訊室溫度 | 通訊室溫度警報 | OTHER | E05/0/StaDev/R_Temp |  |  |  | CDC | 847 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 電驛室溫度 | [17 empty] | 3-3A-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.電驛室溫度 | 電驛室溫度警報 | OTHER | E05/0/StaDev/R_Temp1 |  |  |  | CDC | 848 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 510 | 510 |  | ABS1 | 511 | [16 empty] | 4-33-12 | 4-33-13 | 3-64 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.511_ABS | 511 ABS | OTHER | E05/33/510/ABS1 |  |  |  | CDC | 849 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 520 | 520 |  | ABS1 | 521 | [16 empty] | 4-34-02 | 4-34-03 | 3-67 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.521_ABS | 521 ABS | OTHER | E05/33/520/ABS1 |  |  |  | CDC | 850 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 550 | 550 |  | ABS1 | 551 | [16 empty] | 4-35-04 | 4-35-05 | 3-70 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.551_ABS | 551 ABS | OTHER | E05/33/550/ABS1 |  |  |  | CDC | 851 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 560 | 560 |  | ABS1 | 561 | [16 empty] | 4-35-10 | 4-35-11 | 3-73 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.561_ABS | 561 ABS | OTHER | E05/33/560/ABS1 |  |  |  | CDC | 852 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | ABS1 | 1651 | [16 empty] | 4-33-08 | 4-33-09 | 3-62 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1651_ABS | 1651(#1ATR) ABS | ATR | E05/161/1650/ABS1 |  |  |  | CDC | 853 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1650 | #1ATR(1650) |  | ABS2 | 1652 | [16 empty] | 4-33-10 | 4-33-11 | 3-63 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1652_ABS | 1652(#1ATR) ABS | ATR | E05/161/1650/ABS2 |  |  |  | CDC | 854 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | ABS1 | 1661 | [16 empty] | 4-33-14 | 4-33-15 | 3-65 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1661_ABS | 1661(#2ATR) ABS | ATR | E05/161/1660/ABS1 |  |  |  | CDC | 855 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | ABS1 | 1671 | [16 empty] | 4-34-04 | 4-34-05 | 3-68 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1671_ABS | 1671(#3ATR) ABS | ATR | E05/161/1670/ABS1 |  |  |  | CDC | 856 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1670 | #3ATR(1670) |  | ABS2 | 1672 | [16 empty] | 4-34-06 | 4-34-07 | 3-69 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1672_ABS | 1672(#3ATR) ABS | ATR | E05/161/1670/ABS2 |  |  |  | CDC | 857 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1660 | #2ATR(1660) |  | ABS2 | 1662 | [16 empty] | 4-34-00 | 4-34-01 | 3-66 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1662_ABS | 1662(#2ATR) ABS | ATR | E05/161/1660/ABS2 |  |  |  | CDC | 858 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | ABS1 | 1681 | [16 empty] | 4-34-10 | 4-34-11 | 3-6B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1681_ABS | 1681(#4ATR) ABS | ATR | E05/161/1680/ABS1 |  |  |  | CDC | 859 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | ABS1 | 1691 | [16 empty] | 4-35-00 | 4-35-01 | 3-6E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1691_ABS | 1691(#5ATR) ABS | ATR | E05/161/1690/ABS1 |  |  |  | CDC | 860 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1690 | #5ATR(1690) |  | ABS2 | 1692 | [16 empty] | 4-35-02 | 4-35-03 | 3-6F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1692_ABS | 1692(#5ATR) ABS | ATR | E05/161/1690/ABS2 |  |  |  | CDC | 861 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1680 | #4ATR(1680) |  | ABS2 | 1682 | [16 empty] | 4-34-12 | 4-34-13 | 3-6C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1682_ABS | 1682(#4ATR) ABS | ATR | E05/161/1680/ABS2 |  |  |  | CDC | 862 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | ABS1 | 1861 | [16 empty] | 4-35-06 | 4-35-07 | 3-71 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1861_ABS | 1861(#6ATR) ABS | ATR | E05/161/1860/ABS1 |  |  |  | CDC | 863 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1860 | #6ATR(1860) |  | ABS2 | 1862 | [16 empty] | 4-35-08 | 4-35-09 | 3-72 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1862_ABS | 1862(#6ATR) ABS | ATR | E05/161/1860/ABS2 |  |  |  | CDC | 864 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA31 | [17 empty] | 3-0C-01 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA31 | 麥寮二路(3510) #3差流(87L)RY | LINE345 | E05/345/4510/1SSA1 |  |  |  | CDC | 865 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA32 | [17 empty] | 3-0C-02 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA32 | 麥寮二路(3510) #3測距(21)RY | LINE345 | E05/345/4510/1SSA2 |  |  |  | CDC | 866 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | SSA4 | [17 empty] | 3-0C-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3510_SSA4 | 麥寮二路(3510) #4測距(21)RY | LINE345 | E05/345/4510/2SSA |  |  |  | CDC | 867 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA31 | [17 empty] | 3-0C-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA31 | 麥寮一路(3540) #3差流(87L)RY | LINE345 | E05/345/4520/1SSA1 |  |  |  | CDC | 868 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA32 | [17 empty] | 3-0C-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA32 | 麥寮一路(3540) #3測距(21)RY | LINE345 | E05/345/4520/1SSA2 |  |  |  | CDC | 869 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | SSA4 | [17 empty] | 3-0C-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.3540_SSA4 | 麥寮一路(3540) #4測距(21)RY | LINE345 | E05/345/4520/2SSA |  |  |  | CDC | 870 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | PMA | [17 empty] | 3-3B-11 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.PMA | 電力量測表計警報 | OTHER | E05/0/StaDev/PMA |  |  |  | CDC | 871 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 3-39-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.水位警報(1) | 地下室水位0.5M警報 | OTHER | E05/0/StaDev/Water1 |  |  |  | CDC | 872 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 3-39-14 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.水位警報(2) | 地下室水位1M警報 | OTHER | E05/0/StaDev/Water2 |  |  |  | CDC | 873 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 直流電源DCA(2) | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.直流電源DCA(2) | 161KV直流電源跳脫警報 | OTHER | E05/161/StaDev/DCA2 |  |  |  | CDC | 874 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | CommACF | [17 empty] | 3-3A-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.通訊設備AC故障 | 通訊設備AC故障 | OTHER | E05/0/StaDev/CommACF |  |  |  | CDC | 875 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | 87A | [17 empty] | 1-04-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1610_87A | 嘉義南線(1610) 87RY | LINE161 | E05/161/1610/87A |  |  |  | CDC | 876 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | 87UL | [17 empty] | 2-30-15 |  | 2-0D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1610_87UL | 嘉義南線(1610) 87RY U/L | LINE161 | E05/161/1610/1_87UL2 |  |  |  | CDC | 877 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1610 | 嘉義南線(1610) |  | 87CFA | [17 empty] | 2-33-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1610_87CFA | 嘉民嘉義南線(1610)87RY通訊故障 | OTHER | E05/161/1610/87CFA |  |  |  | CDC | 878 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | 87A | [17 empty] | 1-02-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1630_87A | 北港南線(1630) 87RY | LINE161 | E05/161/1630/87A |  |  |  | CDC | 879 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | 87UL | [17 empty] | 2-30-09 |  | 2-07 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1630_87UL | 北港南線(1630) 87RY U/L | LINE161 | E05/161/1630/1_87UL2 |  |  |  | CDC | 880 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1630 | 北港南線(1630) |  | 87CFA | [17 empty] | 2-33-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1630_87CFA | 嘉民北港南線(1630)87RY通訊故障 | OTHER | E05/161/1630/87CFA |  |  |  | CDC | 881 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | 87A | [17 empty] | 1-02-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1640_87A | 北港北線(1640) 87RY | LINE161 | E05/161/1640/87A |  |  |  | CDC | 882 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | 87UL | [17 empty] | 2-30-07 |  | 2-05 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1640_87UL | 北港北線(1640) 87RY U/L | LINE161 | E05/161/1640/1_87UL2 |  |  |  | CDC | 883 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1640 | 北港北線(1640) |  | 87CFA | [17 empty] | 2-33-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1640_87CFA | 嘉民北港北線(1640)87RY通訊故障 | OTHER | E05/161/1640/87CFA |  |  |  | CDC | 884 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | 87A | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1550_87A | 雲林山線(1550) 87RY | LINE161 | E05/161/1550/87A |  |  |  | CDC | 885 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | 87UL | [17 empty] | 2-30-03 |  | 2-01 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1550_87UL | 雲林山線(1550) 87RY U/L | LINE161 | E05/161/1550/1_87UL2 |  |  |  | CDC | 886 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1550 | 雲林山線(1550) |  | 87CFA | [17 empty] | 2-32-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1550_87CFA | 嘉民雲林山線(1550)87RY通訊故障 | OTHER | E05/161/1550/87CFA |  |  |  | CDC | 887 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | 87A | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1560_87A | 雲林海線(1560) 87RY | LINE161 | E05/161/1560/87A |  |  |  | CDC | 888 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | 87UL | [17 empty] | 2-30-05 |  | 2-03 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1560_87UL | 雲林海線(1560) 87RY U/L | LINE161 | E05/161/1560/1_87UL2 |  |  |  | CDC | 889 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1560 | 雲林海線(1560) |  | 87CFA | [17 empty] | 2-32-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1560_87CFA | 嘉民雲林海線(1560)87RY通訊故障 | OTHER | E05/161/1560/87CFA |  |  |  | CDC | 890 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | 3520 | 3520 |  | CB | [17 empty] | 3-00-01 |  | 3-02 | [5 empty] | 345KV_N | [8 empty] | 嘉民ES.3520_CB | 3520 CB | LINE345 | E05/345/3520/CB |  |  |  | CDC | 891 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3520 | 3520 |  | DS1 | 3521 | [16 empty] | 3-3C-06 | 3-3C-07 | 3-2B | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3521_DS | 3521 DS | LINE345 | E05/345/3520/DS1 |  |  |  | CDC | 892 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | 3520 | 3520 |  | DS2 | 3522 | [16 empty] | 3-3C-08 | 3-3C-09 | 3-2C | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.3522_DS | 3522 DS | LINE345 | E05/345/3520/DS2 |  |  |  | CDC | 893 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | 87A | [17 empty] | 1-04-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1620_87A | 嘉義北線(1620) 87RY | LINE161 | E05/161/1620/87A |  |  |  | CDC | 894 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | 87UL | [17 empty] | 2-31-01 |  | 2-0F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1620_87UL | 嘉義北線(1620) 87RY U/L | LINE161 | E05/161/1620/1_87UL2 |  |  |  | CDC | 895 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1620 | 嘉義北線(1620) |  | 87CFA | [17 empty] | 2-33-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1620_87CFA | 嘉民嘉義北線(1620)87RY通訊故障 | OTHER | E05/161/1620/87CFA |  |  |  | CDC | 896 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | 87A | [17 empty] | 1-03-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1510_87A | 嘉義山線(1510) 87RY | LINE161 | E05/161/1510/87A |  |  |  | CDC | 897 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | 87UL | [17 empty] | 2-30-13 |  | 2-0B | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1510_87UL | 嘉義山線(1510) 87RY U/L | LINE161 | E05/161/1510/1_87UL2 |  |  |  | CDC | 898 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1510 | 嘉義山線(1510) |  | 87CFA | [17 empty] | 2-32-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1510_87CFA | 嘉民嘉義山線(1510)87RY通訊故障 | OTHER | E05/161/1510/87CFA |  |  |  | CDC | 899 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | 87A | [17 empty] | 1-03-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1520_87A | 嘉義海線(1520) 87RY | LINE161 | E05/161/1520/85A |  |  |  | CDC | 900 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | 87UL | [17 empty] | 2-30-11 |  | 2-09 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1520_87UL | 嘉義海線(1520) 87RY U/L | LINE161 | E05/161/1520/85UL |  |  |  | CDC | 901 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1520 | 嘉義海線(1520) |  | 87CFA | [17 empty] | 2-32-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1520_87CFA | 嘉民嘉義海線(1520)87RY通訊故障 | OTHER | E05/161/1520/85CFA |  |  |  | CDC | 902 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | 87A | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1590_87A | 斗工紅線(1590) 87RY | LINE161 | E05/161/1590/87A |  |  |  | CDC | 903 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | 87UL | [17 empty] | 2-31-07 |  | 2-15 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1590_87UL | 斗工紅線(1590) 87RY U/L | LINE161 | E05/161/1590/1_87UL2 |  |  |  | CDC | 904 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1590 | 斗工紅線(1590) |  | 87CFA | [17 empty] | 2-33-02 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1590_87CFA | 嘉民斗工紅線(1590)87RY通訊故障 | OTHER | E05/161/1590/87CFA |  |  |  | CDC | 905 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | 87A | [17 empty] | 1-06-07 | [7 empty] | 161KV_N | [8 empty] | 嘉民ES.1580_87A | 嘉民雲林線(1580) 87RY | LINE161 | E05/161/1580/87A |  |  |  | CDC | 906 | GENERICDIPoint | ES005_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | 87UL | [17 empty] | 2-31-09 |  | 2-17 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1580_87UL | 嘉民雲林線(1580) 87RY U/L | LINE161 | E05/161/1580/1_87UL2 |  |  |  | CDC | 907 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1580 | 嘉民雲林線(1580) |  | 87CFA | [17 empty] | 2-33-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.1580_87CFA | 嘉民雲林線(1580)87RY通訊故障 | OTHER | E05/161/1580/87CFA |  |  |  | CDC | 908 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 161_SBUS | #3,4BUS |  | 87CTFA | [17 empty] | 2-34-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161_SBUS_CTFA | 161KV#3,4BUS 87RYCT迴路故障 | OTHER | E05/161/ComPoint/34B_CTFA |  |  |  | CDC | 909 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 161_SBUS | #3,4BUS |  | RYFA | [17 empty] | 2-34-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161_SBUS_RYFA | 161KV#3,4BUS 87RY數位電驛故障 | OTHER | E05/161/ComPoint/34B_RYFA |  |  |  | CDC | 910 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 161_NBUS | #1,2BUS |  | 87CTFA | [17 empty] | 2-34-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161_NBUS_CTFA | 161KV#1,2BUS 87RYCT迴路故障 | OTHER | E05/161/ComPoint/12B_CTFA |  |  |  | CDC | 911 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 161_NBUS | #1,2BUS |  | RYFA | [17 empty] | 2-34-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161_NBUS_RYFA | 161KV#1,2BUS 87RY數位電驛故障 | OTHER | E05/161/ComPoint/12B_RYFA |  |  |  | CDC | 912 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | CB | [17 empty] | 3-0D-02 |  | 3-25 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1880_CB | 1880(#8ATR) CB | ATR | E05/161/1880/CB |  |  |  | CDC | 913 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 87A1 | [17 empty] | 3-0D-03 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#8ATR_87A1 | #8ATR 第一組 87RY | ATR | E05//8ATR/87A1 |  |  |  | CDC | 914 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 87A2 | [17 empty] | 3-0D-04 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#8ATR_87A2 | #8ATR 第二組 87RY | ATR | E05//8ATR/87A2 |  |  |  | CDC | 915 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 96PA | [17 empty] | 3-0D-05 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#8ATR_96PA | #8ATR 機械保護動作 | ATR | E05//8ATR/96PA |  |  |  | CDC | 916 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 51ZA | [17 empty] | 3-0D-06 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#8ATR_51ZA | #8ATR 51Z(21+50,59-2,51Z) | ATR | E05//8ATR/51ZA |  |  |  | CDC | 917 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 59A | [17 empty] | 3-0D-07 | [7 empty] | 345KV_N | [8 empty] | 嘉民ES.#8ATR_59A | #8ATR 59RY | ATR | E05//8ATR/59A |  |  |  | CDC | 918 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 1_87UL1 | [17 empty] | 4-38-00 |  | 4-53 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_87UL1 | #8ATR 第一組 87RY U/L | OTHER | E05//8ATR/1_87UL1 |  |  |  | CDC | 919 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 1_87UL2 | [17 empty] | 4-38-01 |  | 4-54 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_87UL2 | #8ATR 第二組 87RY U/L | OTHER | E05//8ATR/1_87UL2 |  |  |  | CDC | 920 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 96D | [17 empty] | 4-38-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_96D | #8ATR 96D RY | ATR | E05//8ATR/96D |  |  |  | CDC | 921 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 96P | [17 empty] | 3-0E-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_96P | #8ATR 96P RY | OTHER | E05//8ATR/96P |  |  |  | CDC | 922 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 63Q | [17 empty] | 4-38-08 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_63Q | #8ATR 63Q RY | ATR | E05//8ATR/63Q |  |  |  | CDC | 923 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 96B1 | [17 empty] | 4-38-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_96B1 | #8ATR 96B1 RY | ATR | E05//8ATR/96B1 |  |  |  | CDC | 924 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 96B2 | [17 empty] | 4-38-05 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_96B2 | #8ATR 96B2 RY | ATR | E05//8ATR/96B2 |  |  |  | CDC | 925 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | TRA | [17 empty] | 4-38-10 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_TRA | #8ATR 重故障 | ATR | E05//8ATR/TRA |  |  |  | CDC | 926 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | TRF | [17 empty] | 4-38-09 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_TRF | #8ATR 輕故障 | ATR | E05//8ATR/TRF |  |  |  | CDC | 927 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | SupLocal | [17 empty] | 4-38-02 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_S/L | #8ATR OLTC S/L | ATR | E05//8ATR/SupLocal |  |  |  | CDC | 928 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | A_M | [17 empty] | 4-38-03 |  | 4-24 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_A/M | #8ATR OLTC A/M | ATR | E05/345/3530/Tap Chan |  |  |  | CDC | 929 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | M/F/I | [17 empty] | 4-3A-06 | 4-3A-07 | 4-25 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.#8ATR_M/F/I | #8ATR M/F/I | ATR | E05//8ATR/M_F_I |  |  |  | CDC | 930 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | ABS1 | 1881 | [16 empty] | 4-3A-00 | 4-3A-01 | 4-30 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1881_ABS | 1881(#8ATR) ABS | ATR | E05/161/1880/ABS1 |  |  |  | CDC | 931 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 161 | 161kV | 1880 | #8ATR(1880) |  | ABS2 | 1882 | [16 empty] | 4-3A-02 | 4-3A-03 | 4-31 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1882_ABS | 1882(#8ATR) ABS | ATR | E05/161/1880/ABS2 |  |  |  | CDC | 932 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 580 | 580 |  | CB | [17 empty] | 3-16-02 |  | 3-26 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.580_CB | 580 CB | OTHER | E05/33/580/CB |  |  |  | CDC | 933 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 580 | 580 |  | 87A | [17 empty] | 3-16-04 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.580_87A | 580 87RY | OTHER | E05/33/580/87A |  |  |  | CDC | 934 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 580 | 580 |  | DS1 | 581 | [16 empty] | 4-3A-04 | 4-3A-05 | 4-32 | [5 empty] | CDCS_N | [8 empty] | 嘉民ES.581_DS | 581 DS | OTHER | E05/33/580/DS1 |  |  |  | CDC | 935 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 345 | 345kV | BUS | #1,2BUS |  | CTFA1 | [17 empty] | 3-3B-13 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KVBUS_CTFA1 | 345KV #1,2BUS 第一套CT回路故障 | OTHER | E05/345/ComPoint/87CTFA1 |  |  |  | CDC | 936 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | BUS | #1,2BUS |  | CTFA2 | [17 empty] | 3-3B-15 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KVBUS_CTFA2 | 345KV #1,2BUS 第二套CT回路故障 | OTHER | E05/345/ComPoint/87CTFA2 |  |  |  | CDC | 937 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | BUS | #1,2BUS |  | RYFA1 | [17 empty] | 3-3B-12 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KVBUS_RYFA1 | 345KV #1,2BUS 第一套數位RY故障 | OTHER | E05/345/ComPoint/12B_RYFA1 |  |  |  | CDC | 938 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV | BUS | #1,2BUS |  | RYFA2 | [17 empty] | 3-3B-14 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KVBUS_RYFA2 | 345KV #1,2BUS 第二套數位RY故障 | OTHER | E05/345/ComPoint/12B_RYFA2 |  |  |  | CDC | 939 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 330 | #3SSTR(330) |  | CB | [17 empty] | 3-14-06 |  | 3-15 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.330_CB | 330(#3SSTR) CB | OTHER | E05/33/330/CB |  |  |  | CDC | 940 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 340 | #4SSTR(340) |  | CB | [17 empty] | 3-15-00 |  | 3-1A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.340_CB | 340(#4SSTR) CB | OTHER | E05/33/340/CB |  |  |  | CDC | 941 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 330 | #3SSTR(330) |  | ABS1 | 331 | [16 empty] | 4-34-08 | 4-34-09 | 3-6A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.331_ABS | 331 ABS | OTHER | E05/33/330/ABS1 |  |  |  | CDC | 942 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 340 | #4SSTR(340) |  | ABS1 | 341 | [16 empty] | 4-34-14 | 4-34-15 | 3-6D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.341_ABS | 341 ABS | OTHER | E05/33/340/ABS1 |  |  |  | CDC | 943 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | BVS | #34BUS |  | RY | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.BVS_RY | 161KV #34BUS GRZ100 RY U/L | OTHER | E05/161/StaDev/GRZ100 |  |  |  | CDC | 944 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | EQA | [17 empty] | 3-0E-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_EQA | #8ATR 地震檢知 RY 動作 | OTHER | E05/0/8ATR/2A7Other |  |  |  | CDC | 945 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 345 | 345kV |  |  |  | BFRYFA | [17 empty] | 3-36-03 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.345KV_BFRYFA | 345KV斷路器失靈電驛故障 | OTHER | E05/345/ComPoint/RYFA |  |  |  | CDC | 946 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV |  |  |  | BFRYFA | [17 empty] | 2-35-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.161KV_BFRYFA | 161KV斷路器失靈電驛故障 | OTHER | E05/161/ComPoint/RYFA |  |  |  | CDC | 947 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | CB | [17 empty] | 3-0E-05 |  | 3-27 | [5 empty] | 161KV_N | [8 empty] | 嘉民ES.1830_CB | 1830(#3ATR) CB | ATR | E05/161/1830/CB |  |  |  | CDC | 948 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS1 | 1831 | [16 empty] | 4-3A-08 | 4-3A-09 | 4-2E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1831_DS | 1831(#3ATR) DS | ATR | E05/161/1830/DS1 |  |  |  | CDC | 949 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 161 | 161kV | 1830 | #3ATR(1830) |  | DS2 | 1832 | [16 empty] | 4-3A-10 | 4-3A-11 | 4-2F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.1832_DS | 1832(#3ATR) DS | ATR | E05/161/1830/DS2 |  |  |  | CDC | 950 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
E05 | 嘉民ES | 0 |  | 310 | #1SSTR(310) |  | CB | [17 empty] | 3-16-05 |  | 4-16 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.310_CB | 310(#1SSTR) CB | OTHER | E05/33/310/CB |  |  |  | CDC | 951 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 320 | #2SSTR(320) |  | CB | [17 empty] | 3-16-07 |  | 4-37 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.320_CB | 320(#2SSTR) CB | OTHER | E05/33/320/CB |  |  |  | CDC | 952 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 51A | [17 empty] | 3-0E-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_51A | #3ATR 51RY | OTHER | E05//3ATR/51A |  |  |  | CDC | 953 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | ATR_86A | [17 empty] | 3-0E-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_86A | #3ATR 86RY | OTHER | E05//3ATR/ATR_86A |  |  |  | CDC | 954 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | RYFA | [17 empty] | 4-3D-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_RYFA | (#3ATR)數位電驛故障 | OTHER | E05//3ATR/RYFA |  |  |  | CDC | 955 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 310 | #1SSTR(310) |  | RYFA | [17 empty] | 4-3C-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.310_RYFA | (310)數位電驛故障 | OTHER | E05/33/310/RYFA |  |  |  | CDC | 956 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 310 | #1SSTR(310) |  | DS1 | 311 | [16 empty] | 4-3A-12 | 4-3A-13 | 4-17 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.311_DS | 311 DS | OTHER | E05/33/310/DS1 |  |  |  | CDC | 957 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 320 | #2SSTR(320) |  | RYFA | [17 empty] | 4-3C-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.320_RYFA | (320)數位電驛故障 | OTHER | E05/33/320/RYFA |  |  |  | CDC | 958 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 330 | #3SSTR(330) |  | 151A | [17 empty] | 3-17-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.330_151A | #3ATR 330#1 51RY | OTHER | E05/33/330/PHA1 |  |  |  | CDC | 959 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 330 | #3SSTR(330) |  | 251A | [17 empty] | 3-17-02 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.330_251A | #3ATR 330#2 51RY | OTHER | E05/33/330/PHA2 |  |  |  | CDC | 960 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SHR96B1 | [17 empty] | 3-30-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SHR96B1 | #1ATR 33KV 電抗器96B1 RY | OTHER | E05/33/1SHR/96B1 |  |  |  | CDC | 961 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SHR96B2 | [17 empty] | 3-30-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SHR96B2 | #1ATR 33KV 電抗器96B2 RY | OTHER | E05/33/1SHR/96B2 |  |  |  | CDC | 962 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SHR96D | [17 empty] | 3-30-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SHR96D | #1ATR 33KV 電抗器96D RY | OTHER | E05/33/1SHR/96D |  |  |  | CDC | 963 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SHR96P | [17 empty] | 3-31-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SHR96P | #1ATR 33KV 電抗器96P RY | OTHER | E05/33/1SHR/96P |  |  |  | CDC | 964 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | SHRTRA | [17 empty] | 3-31-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_SHRTRA | #1ATR 33KV 電抗器 重故障 | OTHER | E05/33/1SHR/SHRA |  |  |  | CDC | 965 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SHR96B1 | [17 empty] | 3-31-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SHR96B1 | #2ATR 33KV 電抗器96B1 RY | OTHER | E05/33/2SHR/96B1 |  |  |  | CDC | 966 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SHR96B2 | [17 empty] | 3-31-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SHR96B2 | #2ATR 33KV 電抗器96B2 RY | OTHER | E05/33/2SHR/96B2 |  |  |  | CDC | 967 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SHR96D | [17 empty] | 3-31-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SHR96D | #2ATR 33KV 電抗器96D RY | OTHER | E05/33/2SHR/96D |  |  |  | CDC | 968 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SHR96P | [17 empty] | 3-32-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SHR96P | #2ATR 33KV 電抗器96P RY | OTHER | E05/33/2SHR/96P |  |  |  | CDC | 969 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | SHRTRA | [17 empty] | 3-32-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_SHRTRA | #2ATR 33KV 電抗器 重故障 | OTHER | E05/33/2SHR/SHRA |  |  |  | CDC | 970 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SHR96B1 | [17 empty] | 3-34-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SHR96B1 | #5ATR 33KV 電抗器96B1 RY | OTHER | E05/33/5SHR/96B1 |  |  |  | CDC | 971 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SHR96B2 | [17 empty] | 3-34-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SHR96B2 | #5ATR 33KV 電抗器96B2 RY | OTHER | E05/33/5SHR/96B2 |  |  |  | CDC | 972 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SHR96D | [17 empty] | 3-34-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SHR96D | #5ATR 33KV 電抗器96D RY | OTHER | E05/33/5SHR/96D |  |  |  | CDC | 973 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SHR96P | [17 empty] | 3-34-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SHR96P | #5ATR 33KV 電抗器96P RY | OTHER | E05/33/5SHR/96P |  |  |  | CDC | 974 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | SHRTRA | [17 empty] | 3-34-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_SHRTRA | #5ATR 33KV 電抗器 重故障 | OTHER | E05/33/5SHR/SHRA |  |  |  | CDC | 975 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SHR96B1 | [17 empty] | 3-35-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SHR96B1 | #6ATR 33KV 電抗器96B1 RY | OTHER | E05/33/6SHR/96B1 |  |  |  | CDC | 976 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SHR96B2 | [17 empty] | 3-35-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SHR96B2 | #6ATR 33KV 電抗器96B2 RY | OTHER | E05/33/6SHR/96B2 |  |  |  | CDC | 977 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SHR96D | [17 empty] | 3-35-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SHR96D | #6ATR 33KV 電抗器96D RY | OTHER | E05/33/6SHR/96D |  |  |  | CDC | 978 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SHR96P | [17 empty] | 3-35-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SHR96P | #6ATR 33KV 電抗器96P RY | OTHER | E05/33/6SHR/96P |  |  |  | CDC | 979 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | SHRTRA | [17 empty] | 3-35-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_SHRTRA | #6ATR 33KV 電抗器 重故障 | OTHER | E05/33/6SHR/SHRA |  |  |  | CDC | 980 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | SHR96B1 | [17 empty] | 4-38-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_SHR96B1 | #8ATR 33KV 電抗器96B1 RY | OTHER | E05/33/8SHR/96B1 |  |  |  | CDC | 981 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | SHR96B2 | [17 empty] | 4-38-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_SHR96B2 | #8ATR 33KV 電抗器96B2 RY | OTHER | E05/33/8SHR/96B2 |  |  |  | CDC | 982 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | SHR96D | [17 empty] | 4-38-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_SHR96D | #8ATR 33KV 電抗器96D RY | OTHER | E05/33/8SHR/96D |  |  |  | CDC | 983 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | SHR96P | [17 empty] | 4-38-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_SHR96P | #8ATR 33KV 電抗器96P RY | OTHER | E05/33/8SHR/96P |  |  |  | CDC | 984 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | SR96B1 | [17 empty] | 4-39-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_SR96B1 | #3ATR 161KV 電抗器96B1 RY | OTHER | E05/161/3SR/96B1 |  |  |  | CDC | 985 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | SR96B2 | [17 empty] | 4-39-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_SR96B2 | #3ATR 161KV 電抗器96B2 RY | OTHER | E05/161/3SR/96B2 |  |  |  | CDC | 986 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | SR96D | [17 empty] | 4-39-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_SR96D | #3ATR 161KV 電抗器96D RY | OTHER | E05/161/3SR/96D |  |  |  | CDC | 987 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | SR96B1 | [17 empty] | 4-3C-00 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_SR96B1 | #4ATR 161KV 電抗器96B1 RY | OTHER | E05/161/4SR/96B1 |  |  |  | CDC | 988 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | SR96B2 | [17 empty] | 4-3C-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_SR96B2 | #4ATR 161KV 電抗器96B2 RY | OTHER | E05/161/4SR/96B2 |  |  |  | CDC | 989 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | SR96D | [17 empty] | 4-3C-02 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_SR96D | #4ATR 161KV 電抗器96D RY | OTHER | E05/161/4SR/96D |  |  |  | CDC | 990 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | 51Z_UL | [17 empty] | 4-39-15 |  | 4-3C | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_51ZUL | #3ATR 51ZRY U/L | OTHER | E05//3ATR/51Z_UL |  |  |  | CDC | 991 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | SR96P | [17 empty] | 4-3C-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_SR96P | #4ATR 161KV 電抗器96P RY | OTHER | E05/161/4SR/96P |  |  |  | CDC | 992 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 320 | #2SSTR(320) |  | DS1 | 321 | [16 empty] | 4-3B-00 | 4-3B-01 | 4-3F | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.321_DS | 321 DS | OTHER | E05/33/320/DS1 |  |  |  | CDC | 993 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
E05 | 嘉民ES | 0 |  | 3ATR | #3ATR |  | SR96P | [17 empty] | 4-39-11 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#3ATR_SR96P | #3ATR 161KV 電抗器96P RY | OTHER | E05/161/3SR/96P |  |  |  | CDC | 994 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | ACB3 | [17 empty] | 3-39-07 |  | 4-18 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACB3 | 所內電源ACB3 | OTHER | E05/0/StaDev/ACB3 |  |  |  | CDC | 995 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | ACB4 | [17 empty] | 3-39-09 |  | 4-1A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACB4 | 所內電源ACB4 | OTHER | E05/0/StaDev/ACB4 |  |  |  | CDC | 996 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
E05 | 嘉民ES | 0 |  |  |  |  | 所內電源ACB(1) | [17 empty] | 4-3C-13 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACB(1) | ACB1,ACB2,ACBT1所內電源故障 | OTHER | E05/0/StaDev/ACBA1 |  |  |  | CDC | 997 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 所內電源ACB(2) | [17 empty] | 3-3A-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACB(2) | ACB3,ACB4,ACBT2所內電源故障 | OTHER | E05/0/StaDev/ACBA2 |  |  |  | CDC | 998 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 所內電源ACBT1 | [17 empty] | 4-39-13 |  | 4-39 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACBT1 | 所內電源ACBT1 | OTHER | E05/0/StaDev/ACBT1 |  |  |  | CDC | 999 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | ACBT2 | [17 empty] | 3-39-08 |  | 4-19 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源ACBT2 | 所內電源ACBT2 | OTHER | E05/0/StaDev/ACBT2 |  |  |  | CDC | 1000 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
E05 | 嘉民ES | 0 |  |  |  |  | 所內電源欠壓1 | [17 empty] | 4-3C-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源欠壓1 | ACB1,ACB2,ACBT1所內電源欠壓 | OTHER | E05/0/StaDev/STUV1 |  |  |  | CDC | 1001 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  |  |  |  | 所內電源欠壓2 | [17 empty] | 3-39-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.所內電源欠壓2 | ACB3,ACB4,ACBT2所內電源欠壓 | OTHER | E05/0/StaDev/STUV2 |  |  |  | CDC | 1002 | GENERICDIPoint | ES005_L3 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR_510 | #1ATR |  | 87UL | [17 empty] | 4-3D-07 |  | 4-43 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_510_87UL | #1ATR 電抗器(510) 87RY U/L | OTHER | E05/33/510/87UL |  |  |  | CDC | 1003 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | 51Z_UL | [17 empty] | 4-3D-05 |  | 4-42 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_51ZUL | #1ATR 51ZRY U/L | OTHER | E05//1ATR/51Z_UL |  |  |  | CDC | 1004 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | ATR_86A | [17 empty] | 4-3D-04 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_86A | #1ATR 86(51Z/87/96)RY | OTHER | E05//1ATR/ATR_86A |  |  |  | CDC | 1005 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 1ATR | #1ATR |  | RYFA | [17 empty] | 4-3D-06 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#1ATR_RYFA | (#1ATR)數位電驛故障 | OTHER | E05//1ATR/RYFA |  |  |  | CDC | 1006 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | 51Z_UL | [17 empty] | 4-3D-09 |  | 4-46 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_51ZUL | #2ATR 51ZRY U/L | OTHER | E05//2ATR/51Z_UL |  |  |  | CDC | 1007 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 2ATR_520 | #2ATR |  | 87UL | [17 empty] | 4-3D-11 |  | 4-47 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_520_87UL | #2ATR 電抗器(520) 87RY U/L | OTHER | E05/33/520/87UL |  |  |  | CDC | 1008 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | ATR_86A | [17 empty] | 4-3D-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_86A | #2ATR 86(51Z/87/96)RY | OTHER | E05//2ATR/ATR_86A |  |  |  | CDC | 1009 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 2ATR | #2ATR |  | RYFA | [17 empty] | 4-3D-10 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#2ATR_RYFA | (#2ATR)數位電驛故障 | OTHER | E05//2ATR/RYFA |  |  |  | CDC | 1010 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | 51Z_UL | [17 empty] | 4-3D-13 |  | 4-4A | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_51ZUL | #4ATR 51ZRY U/L | OTHER | E05//4ATR/51Z_UL |  |  |  | CDC | 1011 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | ATR_86A | [17 empty] | 4-3D-12 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_86A | #4ATR 86(51Z/87/96)RY | OTHER | E05//4ATR/ATR_86A |  |  |  | CDC | 1012 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 4ATR | #4ATR |  | RYFA | [17 empty] | 4-3D-14 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#4ATR_RYFA | (#4ATR)數位電驛故障 | OTHER | E05//4ATR/RYFA |  |  |  | CDC | 1013 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | 51Z_UL | [17 empty] | 4-3E-00 |  | 4-4D | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_51ZUL | #5ATR 51ZRY U/L | OTHER | E05//5ATR/51Z_UL |  |  |  | CDC | 1014 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 5ATR_550 | #5ATR |  | 87UL | [17 empty] | 4-3E-02 |  | 4-4E | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_550_87UL | #5ATR 電抗器(550) 87RY U/L | OTHER | E05/33/550/87UL |  |  |  | CDC | 1015 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | ATR_86A | [17 empty] | 4-3D-15 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_86A | #5ATR 86(51Z/87/96)RY | OTHER | E05//5ATR/ATR_86A |  |  |  | CDC | 1016 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 5ATR | #5ATR |  | RYFA | [17 empty] | 4-3E-01 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#5ATR_RYFA | (#5ATR)數位電驛故障 | OTHER | E05//5ATR/RYFA |  |  |  | CDC | 1017 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | 51Z_UL | [17 empty] | 4-3E-04 |  | 4-51 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_51ZUL | #6ATR 51ZRY U/L | OTHER | E05//6ATR/51Z_UL |  |  |  | CDC | 1018 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 6ATR_560 | #6ATR |  | 87UL | [17 empty] | 4-3E-06 |  | 4-52 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_560_87UL | #6ATR 電抗器(560) 87RY U/L | OTHER | E05/33/560/87UL |  |  |  | CDC | 1019 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | ATR_86A | [17 empty] | 4-3E-03 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_86A | #6ATR 86(51Z/87/96)RY | OTHER | E05//6ATR/ATR_86A |  |  |  | CDC | 1020 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 6ATR | #6ATR |  | RYFA | [17 empty] | 4-3E-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#6ATR_RYFA | (#6ATR)數位電驛故障 | OTHER | E05//6ATR/RYFA |  |  |  | CDC | 1021 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | 51Z_UL | [17 empty] | 4-3E-08 |  | 4-55 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_51ZUL | #8ATR 51ZRY U/L | OTHER | E05//8ATR/51Z_UL |  |  |  | CDC | 1022 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 8ATR_580 | #8ATR |  | 87UL | [17 empty] | 4-3E-10 |  | 4-56 | [5 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_580_87UL | #8ATR 電抗器(580) 87RY U/L | OTHER | E05/33/580/87UL |  |  |  | CDC | 1023 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | ATR_86A | [17 empty] | 4-3E-07 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_86A | #8ATR 86(51Z/87/96)RY | OTHER | E05//8ATR/ATR_86A |  |  |  | CDC | 1024 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 8ATR | #8ATR |  | RYFA | [17 empty] | 4-3E-09 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.#8ATR_RYFA | (#8ATR)數位電驛故障 | OTHER | E05//8ATR/RYFA |  |  |  | CDC | 1025 | GENERICDIPoint | ES005_L4 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 550 | 550 |  | 51A | [17 empty] | 3-15-03 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.550_51A | 550 51A | OTHER | E05/33/550/PHA |  |  |  | CDC | 1026 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 560 | 560 |  | 51A | [17 empty] | 3-15-06 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.560_51A | 560 51A | OTHER | E05/33/560/PHA |  |  |  | CDC | 1027 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 580 | 580 |  | 51A | [17 empty] | 3-16-03 | [7 empty] | CDCS_N | [8 empty] | 嘉民ES.580_51A | 580 51A | OTHER | E05/33/580/PHA |  |  |  | CDC | 1028 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 340 | #4SSTR(340) |  | 151A | [17 empty] | 3-17-05 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.340_151A | #4ATR 340 151A | OTHER |  |  |  |  | CDC | 1029 | GENERICDIPoint | ES005_L3 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | 有感地震警報 | 有感地震警報 |  | EQA | [17 empty] | 2-35-08 | [7 empty] | ADCS_N | [8 empty] | 嘉民ES.EQA | 有感地震警報 EQA | OTHER | E05/0/StaDev/EQA |  |  |  | CDC | 1030 | GENERICDIPoint | ES005_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
E05 | 嘉民ES | 0 |  | NA | NA |  | 01 | [25 empty] | CDCS | [8 empty] | 嘉民ES.NA_01 | 嘉民ES裝置容量 | [6 empty] | 1031 | NotelAIPoint | [21 empty] | MW | 10000.000000 | 10000.000000 | 10000.000000 | 10000.000000 | 0.100000 | -10000.000000 | -10000.000000 | -10000.000000 | -10000.000000
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | LE0 | 3510LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3510LE | 3510LE (非取樣點) | LINE345 | E05/345/3510/LE0 |  |  |  |  | 1032 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3510 | 麥寮二路(3510) |  | BE0 | 3510BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3510BE | 3510BE (非取樣點) | LINE345 | E05/345/3510/BE0 |  |  |  |  | 1033 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | BE0 | 3530BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3530BE | 3530BE (非取樣點) | ATR | E05/345/3530/BE0 |  |  |  |  | 1034 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | LE0 | 3540LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3540LE | 3540LE (非取樣點) | LINE345 | E05/345/3540/LE0 |  |  |  |  | 1035 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3540 | 麥寮一路(3540) |  | BE0 | 3540BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3540BE | 3540BE (非取樣點) | LINE345 | E05/345/3540/BE0 |  |  |  |  | 1036 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | LE0 | 3560LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3560LE | 3560LE (非取樣點) | LINE345 | E05/345/3560/LE0 |  |  |  |  | 1037 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3560 | 3560 |  | BE0 | 3560BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3560BE | 3560BE (非取樣點) | LINE345 | E05/345/3560/BE0 |  |  |  |  | 1038 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | LE0 | 3570LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3570LE | 3570LE (非取樣點) | LINE345 | E05/345/3570/LE0 |  |  |  |  | 1039 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3570 | 中寮二路(3570) |  | BE0 | 3570BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3570BE | 3570BE (非取樣點) | LINE345 | E05/345/3570/BE0 |  |  |  |  | 1040 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | LE0 | 3610LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3610LE | 3610LE (非取樣點) | LINE345 | E05/345/3610/LE0 |  |  |  |  | 1041 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3610 | 中寮一路(3610) |  | BE0 | 3610BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3610BE | 3610BE (非取樣點) | LINE345 | E05/345/3610/BE0 |  |  |  |  | 1042 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | LE0 | 3640LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3640LE | 3640LE (非取樣點) | LINE345 | E05/345/3640/LE0 |  |  |  |  | 1043 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3640 | 中寮三路(3640) |  | BE0 | 3640BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3640BE | 3640BE (非取樣點) | LINE345 | E05/345/3640/BE0 |  |  |  |  | 1044 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | LE0 | 3710LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3710LE | 3710LE (非取樣點) | LINE345 | E05/345/3710/LE0 |  |  |  |  | 1045 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3710 | 龍崎紅線(3710) |  | BE0 | 3710BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3710BE | 3710BE (非取樣點) | LINE345 | E05/345/3710/BE0 |  |  |  |  | 1046 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | LE0 | 3770LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3770LE | 3770LE (非取樣點) | LINE345 | E05/345/3770/LE0 |  |  |  |  | 1047 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3770 | 新南科一路(3770) |  | BE0 | 3770BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3770BE | 3770BE (非取樣點) | LINE345 | E05/345/3770/BE0 |  |  |  |  | 1048 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | LE0 | 3810LE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3810LE | 3810LE (非取樣點) | LINE345 | E05/345/3810/LE0 |  |  |  |  | 1049 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3810 | 新南科二路(3810) |  | BE0 | 3810BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3810BE | 3810BE (非取樣點) | LINE345 | E05/345/3810/BE0 |  |  |  |  | 1050 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3580 | 3580 |  | E1 | 3581E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3581E | 3581E (非取樣點) | LINE345 | E05/345/3580/E1 |  |  |  |  | 1051 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3580 | 3580 |  | E2 | 3582E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3582E | 3582E (非取樣點) | LINE345 | E05/345/3580/E2 |  |  |  |  | 1052 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3620 | 3620 |  | E1 | 3621E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3621E | 3621E (非取樣點) | LINE345 | E05/345/3620/E1 |  |  |  |  | 1053 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3620 | 3620 |  | E2 | 3622E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3622E | 3622E (非取樣點) | LINE345 | E05/345/3620/E2 |  |  |  |  | 1054 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3650 | 3650 |  | E1 | 3651E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3651E | 3651E (非取樣點) | LINE345 | E05/345/3650/E1 |  |  |  |  | 1055 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3650 | 3650 |  | E2 | 3652E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3652E | 3652E (非取樣點) | LINE345 | E05/345/3650/E2 |  |  |  |  | 1056 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3720 | 3720 |  | E1 | 3721E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3721E | 3721E (非取樣點) | LINE345 | E05/345/3720/E1 |  |  |  |  | 1057 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3720 | 3720 |  | E2 | 3722E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3722E | 3722E (非取樣點) | LINE345 | E05/345/3720/E2 |  |  |  |  | 1058 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3780 | 3780 |  | E1 | 3781E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3781E | 3781E (非取樣點) | LINE345 | E05/345/3780/E1 |  |  |  |  | 1059 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3780 | 3780 |  | E2 | 3782E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3782E | 3782E (非取樣點) | LINE345 | E05/345/3780/E2 |  |  |  |  | 1060 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3820 | 3820 |  | E1 | 3821E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3821E | 3821E (非取樣點) | LINE345 | E05/345/3820/E1 |  |  |  |  | 1061 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3820 | 3820 |  | E2 | 3822E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3822E | 3822E (非取樣點) | LINE345 | E05/345/3820/E2 |  |  |  |  | 1062 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1510LE | 1510LE (非取樣點) | LINE161 | E05/161/1510/LE0 |  |  |  |  | 1063 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1510 | 嘉義山線(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1510BE | 1510BE (非取樣點) | LINE161 | E05/161/1510/BE0 |  |  |  |  | 1064 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1520LE | 1520LE (非取樣點) | LINE161 | E05/161/1520/LE0 |  |  |  |  | 1065 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1520 | 嘉義海線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1520BE | 1520BE (非取樣點) | LINE161 | E05/161/1520/BE0 |  |  |  |  | 1066 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1530LE | 1530LE (非取樣點) | LINE161 | E05/161/1530/LE0 |  |  |  |  | 1067 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1530 | 柳營山線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1530BE | 1530BE (非取樣點) | LINE161 | E05/161/1530/BE0 |  |  |  |  | 1068 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1540LE | 1540LE (非取樣點) | LINE161 | E05/161/1540/LE0 |  |  |  |  | 1069 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1540 | 柳營海線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1540BE | 1540BE (非取樣點) | LINE161 | E05/161/1540/BE0 |  |  |  |  | 1070 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1550LE | 1550LE (非取樣點) | LINE161 | E05/161/1550/LE0 |  |  |  |  | 1071 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1550 | 雲林山線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1550BE | 1550BE (非取樣點) | LINE161 | E05/161/1550/BE0 |  |  |  |  | 1072 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1560LE | 1560LE (非取樣點) | LINE161 | E05/161/1560/LE0 |  |  |  |  | 1073 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1560 | 雲林海線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1560BE | 1560BE (非取樣點) | LINE161 | E05/161/1560/BE0 |  |  |  |  | 1074 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1580LE | 1580LE (非取樣點) | LINE161 | E05/161/1580/LE0 |  |  |  |  | 1075 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1580 | 嘉民雲林線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1580BE | 1580BE (非取樣點) | LINE161 | E05/161/1580/BE0 |  |  |  |  | 1076 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | LE0 | 1590LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1590LE | 1590LE (非取樣點) | LINE161 | E05/161/1590/LE0 |  |  |  |  | 1077 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1590 | 斗工紅線(1590) |  | BE0 | 1590BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1590BE | 1590BE (非取樣點) | LINE161 | E05/161/1590/BE0 |  |  |  |  | 1078 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | LE0 | 1610LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1610LE | 1610LE (非取樣點) | LINE161 | E05/161/1610/LE0 |  |  |  |  | 1079 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1610 | 嘉義南線(1610) |  | BE0 | 1610BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1610BE | 1610BE (非取樣點) | LINE161 | E05/161/1610/BE0 |  |  |  |  | 1080 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | LE0 | 1620LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1620LE | 1620LE (非取樣點) | LINE161 | E05/161/1620/LE0 |  |  |  |  | 1081 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1620 | 嘉義北線(1620) |  | BE0 | 1620BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1620BE | 1620BE (非取樣點) | LINE161 | E05/161/1620/BE0 |  |  |  |  | 1082 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | LE0 | 1630LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1630LE | 1630LE (非取樣點) | LINE161 | E05/161/1630/LE0 |  |  |  |  | 1083 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1630 | 北港南線(1630) |  | BE0 | 1630BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1630BE | 1630BE (非取樣點) | LINE161 | E05/161/1630/BE0 |  |  |  |  | 1084 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | LE0 | 1640LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1640LE | 1640LE (非取樣點) | LINE161 | E05/161/1640/LE0 |  |  |  |  | 1085 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1640 | 北港北線(1640) |  | BE0 | 1640BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1640BE | 1640BE (非取樣點) | LINE161 | E05/161/1640/BE0 |  |  |  |  | 1086 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | LE0 | 1710LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1710LE | 1710LE (非取樣點) | LINE161 | E05/161/1710/LE0 |  |  |  |  | 1087 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1710 | 台嘉一路(1710) |  | BE0 | 1710BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1710BE | 1710BE (非取樣點) | LINE161 | E05/161/1710/BE0 |  |  |  |  | 1088 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | LE0 | 1720LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1720LE | 1720LE (非取樣點) | LINE161 | E05/161/1720/LE0 |  |  |  |  | 1089 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1720 | 台嘉二路(1720) |  | BE0 | 1720BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1720BE | 1720BE (非取樣點) | LINE161 | E05/161/1720/BE0 |  |  |  |  | 1090 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | LE0 | 1730LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1730LE | 1730LE (非取樣點) | LINE161 | E05/161/1730/LE0 |  |  |  |  | 1091 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1730 | 嘉惠一路(1730) |  | BE0 | 1730BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1730BE | 1730BE (非取樣點) | LINE161 | E05/161/1730/BE0 |  |  |  |  | 1092 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | LE0 | 1740LE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1740LE | 1740LE (非取樣點) | LINE161 | E05/161/1740/LE0 |  |  |  |  | 1093 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 161 | 161kV | 1740 | 嘉惠二路(1740) |  | BE0 | 1740BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1740BE | 1740BE (非取樣點) | LINE161 | E05/161/1740/BE0 |  |  |  |  | 1094 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | TE0 | 3590TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3590TE | 3590TE (非取樣點) | ATR | E05/345/3590/TE0 |  |  |  |  | 1095 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3590 | #1ATR(3590) |  | BE0 | 3590BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3590BE | 3590BE (非取樣點) | ATR | E05/345/3590/BE0 |  |  |  |  | 1096 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | TE0 | 3630TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3630TE | 3630TE (非取樣點) | ATR | E05/345/3630/TE0 |  |  |  |  | 1097 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3630 | #2ATR(3630) |  | BE0 | 3630BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3630BE | 3630BE (非取樣點) | ATR | E05/345/3630/BE0 |  |  |  |  | 1098 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | TE0 | 3660TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3660TE | 3660TE (非取樣點) | ATR | E05/345/3660/TE0 |  |  |  |  | 1099 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3660 | #3ATR(3660) |  | BE0 | 3660BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3660BE | 3660BE (非取樣點) | ATR | E05/345/3660/BE0 |  |  |  |  | 1100 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | TE0 | 3730TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3730TE | 3730TE (非取樣點) | ATR | E05/345/3730/TE0 |  |  |  |  | 1101 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3730 | #4ATR(3730) |  | BE0 | 3730BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3730BE | 3730BE (非取樣點) | ATR | E05/345/3730/BE0 |  |  |  |  | 1102 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | TE0 | 3790TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3790TE | 3790TE (非取樣點) | ATR | E05/345/3790/TE0 |  |  |  |  | 1103 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3790 | #5ATR(3790) |  | BE0 | 3790BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3790BE | 3790BE (非取樣點) | ATR | E05/345/3790/BE0 |  |  |  |  | 1104 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | TE0 | 3830TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3830TE | 3830TE (非取樣點) | ATR | E05/345/3830/TE0 |  |  |  |  | 1105 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3830 | #6ATR(3830) |  | BE0 | 3830BE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3830BE | 3830BE (非取樣點) | ATR | E05/345/3830/BE0 |  |  |  |  | 1106 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.161B1E | 161B1E (非取樣點) | BUS | E05/161/161B1E/BE1 |  |  |  |  | 1107 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.161B2E | 161B2E (非取樣點) | BUS | E05/161/161B2E/BE2 |  |  |  |  | 1108 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 1109 | NotelDIPoint | [38 empty] | START/STOP | STOP
E05 | 嘉民ES | 0 |  |  |  |  | 1650BE | 1650BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1650BE | 1650BE(#1ATR)(非取樣點) | OTHER | E05/161/1650/BE0 |  |  |  |  | 1110 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1650TE | 1650TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1650TE | 1650TE(#1ATR)(非取樣點) | OTHER | E05/161/1650/TE0 |  |  |  |  | 1111 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1660BE | 1660BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1660BE | 1660BE(#2ATR)(非取樣點) | OTHER | E05/161/1660/BE0 |  |  |  |  | 1112 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1660TE | 1660TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1660TE | 1660TE(#2ATR)(非取樣點) | OTHER | E05/161/1660/TE0 |  |  |  |  | 1113 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1670BE | 1670BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1670BE | 1670BE(#3ATR)(非取樣點) | OTHER | E05/161/1670/BE0 |  |  |  |  | 1114 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1670TE | 1670TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1670TE | 1670TE(#3ATR)(非取樣點) | OTHER | E05/161/1670/TE0 |  |  |  |  | 1115 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1680BE | 1680BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1680BE | 1680BE(#4ATR)(非取樣點) | OTHER | E05/161/1680/BE0 |  |  |  |  | 1116 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1680TE | 1680TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1680TE | 1680TE(#4ATR)(非取樣點) | OTHER | E05/161/1680/TE0 |  |  |  |  | 1117 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1690BE | 1690BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1690BE | 1690BE(#5ATR)(非取樣點) | OTHER | E05/161/1690/BE0 |  |  |  |  | 1118 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1690TE | 1690TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1690TE | 1690TE(#5ATR)(非取樣點) | OTHER | E05/161/1690/TE0 |  |  |  |  | 1119 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1860BE | 1860BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1860BE | 1860BE(#6ATR)(非取樣點) | OTHER | E05/161/1860/BE0 |  |  |  |  | 1120 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1860TE | 1860TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1860TE | 1860TE(#6ATR)(非取樣點) | OTHER | E05/161/1860/TE0 |  |  |  |  | 1121 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3520 | 3520 |  | E1 | 3521E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3521E | 3521E (非取樣點) | LINE345 | E05/345/3520/E1 |  |  |  |  | 1122 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3520 | 3520 |  | E2 | 3522E | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3522E | 3522E (非取樣點) | LINE345 | E05/345/3520/E2 |  |  |  |  | 1123 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 345 | 345kV | 3530 | #8ATR(3530) |  | TE0 | 3530TE | [24 empty] | CDCS_N | [8 empty] | 嘉民ES.3530TE | 3530TE (非取樣點) | ATR | E05/345/3530/TE0 |  |  |  |  | 1124 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1880BE | 1880BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1880BE | 1880BE(#8ATR)(非取樣點) | OTHER | E05/161/1880/BE0 |  |  |  |  | 1125 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1880TE | 1880TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1880TE | 1880TE(#8ATR)(非取樣點) | OTHER | E05/161/1880/TE0 |  |  |  |  | 1126 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1830BE | 1830BE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1830BE | 1830BE(#3ATR)(非取樣點) | OTHER | E05/161/1830/BE0 |  |  |  |  | 1127 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1830TE | 1830TE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1830TE | 1830TE(#3ATR)(非取樣點) | OTHER | E05/161/1830/TE0 |  |  |  |  | 1128 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1650SRE | 1650SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1650SRE | 1650SRE(#1ATR)(非取樣點) | OTHER | E05/161/1650/RE0 |  |  |  |  | 1129 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1660SRE | 1660SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1660SRE | 1660SRE(#2ATR)(非取樣點) | OTHER | E05/161/1660/RE0 |  |  |  |  | 1130 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1670SRE | 1670SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1670SRE | 1670SRE(#3ATR)(非取樣點) | OTHER | E05/161/1670/RE0 |  |  |  |  | 1131 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1680SRE | 1680SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1680SRE | 1680SRE(#4ATR)(非取樣點) | OTHER | E05/161/1680/RE0 |  |  |  |  | 1132 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1690SRE | 1690SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1690SRE | 1690SRE(#5ATR)(非取樣點) | OTHER | E05/161/1690/RE0 |  |  |  |  | 1133 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1860SRE | 1860SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1860SRE | 1860SRE(#6ATR)(非取樣點) | OTHER | E05/161/1860/RE0 |  |  |  |  | 1134 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
E05 | 嘉民ES | 0 |  |  |  |  | 1830SRE | 1830SRE | [24 empty] | ADCS_N | [8 empty] | 嘉民ES.1830SRE | 1830SRE(#3ATR)(非取樣點) | OTHER | E05/161/1830/RE0 |  |  |  |  | 1135 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 嘉民台嘉一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 台嘉CS.1510_AMP | 嘉民台嘉一路 AMP | LINE161 | C21/161/1510/I |  | AMP_CAL |  |  | 1136 | CalcAIPoint | [21 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
C21 | 台嘉CS | 161 | 161kV | 1520 | 嘉民台嘉二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 台嘉CS.1520_AMP | 嘉民台嘉二路 AMP | LINE161 | C21/161/1520/I |  | AMP_CAL |  |  | 1137 | CalcAIPoint | [21 empty] | C20R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
C21 | 台嘉CS | 161 | 161kV | 1510 | 1510BE |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1510BE_ES | 1510BE(嘉民台嘉一路)(非取樣點) | OTHER | [5 empty] | 1138 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 1510LE |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1510LE_ES | 1510LE(嘉民台嘉一路)(非取樣點) | OTHER | [5 empty] | 1139 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 1510 |  | CB | 1510_CB | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1510_CB | 1510(嘉民台嘉一路)(非取樣點) | OTHER | C21/161/1510/CB |  |  |  |  | 1140 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1510 | 1510 |  | E2 | 1512E | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1512E_ES | 1512E(嘉民台嘉一路)(非取樣點) | OTHER | C21/161/1510/E2 |  |  |  |  | 1141 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1510 | 1510 |  | DS2 | 1512 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1512_DS | 1512(嘉民台嘉一路)(非取樣點) | OTHER | C21/161/1510/DS2 |  |  |  |  | 1142 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1520 | 1520BE |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1520BE_ES | 1520BE(嘉民台嘉二路)(非取樣點) | OTHER | [5 empty] | 1143 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1520 | 1520LE |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1520LE_ES | 1520LE(嘉民台嘉二路)(非取樣點) | OTHER | [5 empty] | 1144 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1520 | 1520 |  | CB | 1520_CB | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1520_CB | 1520(嘉民台嘉二路)(非取樣點) | OTHER | C21/161/1520/CB |  |  |  |  | 1145 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1520 | 1520 |  | E2 | 1522E | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1522E_ES | 1522E(嘉民台嘉二路)(非取樣點) | OTHER | C21/161/1520/E2 |  |  |  |  | 1146 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1520 | 1520 |  | DS2 | 1522 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1522_DS | 1522(嘉民台嘉二路)(非取樣點) | OTHER | C21/161/1520/DS2 |  |  |  |  | 1147 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1501_DS | 1501(TIE) DS(非取樣點) | OTHER | C21/161/1500/DS1 |  |  |  |  | 1148 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | 1650BE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1650BE_ES | 1650BE(#1MTR) ES(非取樣點) | OTHER | [5 empty] | 1149 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | 1650TE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1650TE_ES | 1650TE(#1MTR) ES(非取樣點) | OTHER | [5 empty] | 1150 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB | 1650_CB | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1650_CB | 1650(#1MTR) CB(非取樣點) | OTHER | C21/161/1650/CB |  |  |  |  | 1151 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1651_DS | 1651(#1MTR) DS(非取樣點) | OTHER | C21/161/1650/DS1 |  |  |  |  | 1152 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1660BE_ES | 1660BE(#2MTR) ES(非取樣點) | OTHER | [5 empty] | 1153 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1660TE_ES | 1660TE(#2MTR) ES(非取樣點) | OTHER | [5 empty] | 1154 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | 1660_CB | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1660_CB | 1660(#2MTR) CB(非取樣點) | OTHER | C21/161/1660/CB |  |  |  |  | 1155 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1661_DS | 1661(#2MTR) DS(非取樣點) | OTHER | C21/161/1660/DS1 |  |  |  |  | 1156 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | BE0 | 1680BE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1680BE_ES | 1680BE(#4GTR) ES(非取樣點) | OTHER | [5 empty] | 1157 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | TE0 | 1680TE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1680TE_ES | 1680TE(#4GTR) ES(非取樣點) | OTHER | [5 empty] | 1158 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | CB | 1680_CB | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1680_CB | 1680(#4GTR) CB(非取樣點) | OTHER | C21/161/1680/CB |  |  |  |  | 1159 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | DS1 | 1681 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1681_DS | 1681(#4GTR) DS(非取樣點) | OTHER | C21/161/1680/DS1 |  |  |  |  | 1160 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | E2 | 1682E | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1682E_ES | 1682E(#4GTR) ES(非取樣點) | OTHER | C21/161/1680/E2 |  |  |  |  | 1161 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1680 | #4GTR(1680) |  | DS2 | 1682 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1682_DS | 1682(#4GTR) DS(非取樣點) | OTHER | C21/161/1680/DS2 |  |  |  |  | 1162 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1501E_ES | 1501E(TIE) ES(非取樣點) | OTHER | C21/161/1500/E1 |  |  |  |  | 1163 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | BE0 | 1670BE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1670BE_ES | 1670BE(#2MTR) ES(非取樣點) | OTHER | [5 empty] | 1164 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | TE0 | 1670TE | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1670TE_ES | 1670TE(#2MTR) ES(非取樣點) | OTHER | [5 empty] | 1165 | NotelDIPoint |  |  |  |  | D_E_TEXT | [33 empty] | CLOSE/OPEN | OPEN
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | CB | 1670_CB | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1670_CB | 1670(#2MTR) CB(非取樣點) | OTHER | C21/161/1670/CB |  |  |  |  | 1166 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
C21 | 台嘉CS | 161 | 161kV | 1670 | #2MTR(1670) |  | DS1 | 1671 | [24 empty] | ADCS_N | [8 empty] | 台嘉CS.1671_DS | 1671(#2MTR) DS(非取樣點) | OTHER | C21/161/1670/DS1 |  |  |  |  | 1167 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo