## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1540LE | 1540LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1540BE | 1540BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1650TE | 1650TE (非取樣點) | MTR | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1650NE | #1MTR(1650) |  | NE0 | 1651N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/1MTR | [13 empty] | no rule | B2/P01_A1 | [8 empty] | 新營PS.1651N | 1651N (非取樣點) | MTR | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1650BE | 1650BE (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.750TE | 750TE (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.750BE | 750BE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1660TE | 1660TE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1660NE | #2MTR(1660) |  | NE0 | 1661N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/2MTR | [13 empty] | no rule | B2/P01_A1 | [8 empty] | 新營PS.1661N | 1661N (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1660BE | 1660BE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.760TE | 760TE (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.760BE | 760BE (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1670TE | 1670TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1670NE | #3MTR(1670) |  | NE0 | 1671N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/3MTR | [13 empty] | no rule | B2/P01_A1 | [8 empty] | 新營PS.1671N | 1671N (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1670BE | 1670BE (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.770TE | 770TE (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.770BE | 770BE (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.330_DS | 330_DS (非取樣點) | MTR | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.330_ES | 330_ES (非取樣點) | MTR | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.340_DS | 340_DS (非取樣點) | MTR | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.340_ES | 340_ES (非取樣點) | MTR | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.360_DS | 360_DS (非取樣點) | MTR | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.360_ES | 360_ES (非取樣點) | MTR | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.350_DS | 350_DS (非取樣點) | MTR | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.350_ES | 350_ES (非取樣點) | MTR | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.601E | 601E (非取樣點) | TIE | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.602E | 602E (非取樣點) | TIE | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1680TE | 1680TE (非取樣點) | MTR | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1680NE | #4MTR(1680) |  | NE0 | 1681N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/4MTR | [13 empty] | no rule | B2/P01_A1 | [8 empty] | 新營PS.1681N | 1681N (非取樣點) | MTR | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.1680BE | 1680BE (非取樣點) | MTR | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.780TE | 780TE (非取樣點) | MTR | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.780BE | 780BE (非取樣點) | MTR | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.650LE | 650LE (非取樣點) | LINE69 | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.650BE | 650BE (非取樣點) | LINE69 | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.660LE | 660LE (非取樣點) | LINE69 | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.660BE | 660BE (非取樣點) | LINE69 | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.670BE | 670BE (非取樣點) | LINE69 | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.680LE | 680LE (非取樣點) | LINE69 | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.680BE | 680BE (非取樣點) | LINE69 | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.710LE | 710LE (非取樣點) | LINE69 | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.710BE | 710BE (非取樣點) | LINE69 | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.720LE | 720LE (非取樣點) | LINE69 | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.720BE | 720BE (非取樣點) | LINE69 | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.730LE | 730LE (非取樣點) | LINE69 | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.730BE | 730BE (非取樣點) | LINE69 | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.910LE | 910LE (非取樣點) | LINE69 | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.910BE | 910BE (非取樣點) | LINE69 | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.810BE | 810BE (非取樣點) | SC | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.810CE | 810CE (非取樣點) | SC | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.820BE | 820BE (非取樣點) | SC | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.820CE | 820CE (非取樣點) | SC | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.830BE | 830BE (非取樣點) | SC | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_A1 | [8 empty] | 新營PS.830CE | 830CE (非取樣點) | SC | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC31_DS | VC31_DS (非取樣點) | FEEDER | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC31_ES | VC31_ES (非取樣點) | FEEDER | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC32_DS | VC32_DS (非取樣點) | FEEDER | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC32_ES | VC32_ES (非取樣點) | FEEDER | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC33_DS | VC33_DS (非取樣點) | FEEDER | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC33_ES | VC33_ES (非取樣點) | FEEDER | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC34_DS | VC34_DS (非取樣點) | FEEDER | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC34_ES | VC34_ES (非取樣點) | FEEDER | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC35_DS | VC35_DS (非取樣點) | FEEDER | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC35_ES | VC35_ES (非取樣點) | FEEDER | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC36_DS | VC36_DS (非取樣點) | FEEDER | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC36_ES | VC36_ES (非取樣點) | FEEDER | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.100_DS | 100_DS (非取樣點) | TIE | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC37_DS | VC37_DS (非取樣點) | FEEDER | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC37_ES | VC37_ES (非取樣點) | FEEDER | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC38_DS | VC38_DS (非取樣點) | FEEDER | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC38_ES | VC38_ES (非取樣點) | FEEDER | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC39_DS | VC39_DS (非取樣點) | FEEDER | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC39_ES | VC39_ES (非取樣點) | FEEDER | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC40_DS | VC40_DS (非取樣點) | FEEDER | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC40_ES | VC40_ES (非取樣點) | FEEDER | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC61_DS | VC61_DS (非取樣點) | FEEDER | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC61_ES | VC61_ES (非取樣點) | FEEDER | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC62_DS | VC62_DS (非取樣點) | FEEDER | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC62_ES | VC62_ES (非取樣點) | FEEDER | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC63_DS | VC63_DS (非取樣點) | FEEDER | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC63_ES | VC63_ES (非取樣點) | FEEDER | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC64_DS | VC64_DS (非取樣點) | FEEDER | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC64_ES | VC64_ES (非取樣點) | FEEDER | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.200_DS | 200_DS (非取樣點) | TIE | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC65_DS | VC65_DS (非取樣點) | FEEDER | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC65_ES | VC65_ES (非取樣點) | FEEDER | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC66_DS | VC66_DS (非取樣點) | FEEDER | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC66_ES | VC66_ES (非取樣點) | FEEDER | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC67_DS | VC67_DS (非取樣點) | FEEDER | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC67_ES | VC67_ES (非取樣點) | FEEDER | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC68_DS | VC68_DS (非取樣點) | FEEDER | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC68_ES | VC68_ES (非取樣點) | FEEDER | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC69_DS | VC69_DS (非取樣點) | FEEDER | [5 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC69_ES | VC69_ES (非取樣點) | FEEDER | [5 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC70_DS | VC70_DS (非取樣點) | FEEDER | [5 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P01_D1 | [8 empty] | 新營PS.VC70_ES | VC70_ES (非取樣點) | FEEDER | [5 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P01_A1 | [8 empty] | 新營PS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aabz | B2/P01_A1 | [8 empty] | 新營PS.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aabz | B2/P01_A1 | [8 empty] | 新營PS.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE1 | (非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaqz | B2/P01_A1 | [8 empty] | 新營PS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE2 | (非取樣點) | B2,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aaqz | B2/P01_A1 | [8 empty] | 新營PS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 140 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 141 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1540 | MW | 新營柳營海線 1540 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1540_MW | 新營柳營海線 MW | LINE161 | [5 empty] | 142 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1540 | MVAR | 新營柳營海線 1540 乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1540_MVAR | 新營柳營海線 MVAR | LINE161 | [5 empty] | 143 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1560 | MW | 嘉義新營山上白線1560 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1560_MW | 嘉義山上白線 MW | LINE161 | [5 empty] | 144 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1560 | MVAR | 嘉義新營山上白線1560 乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1560_MVAR | 嘉義山上白線 MVAR | LINE161 | [5 empty] | 145 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1570 | MW | 新營下營一路 1570 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1570_MW | 新營下營一路 MW | LINE161 | [5 empty] | 146 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1570 | MVAR | 新營下營一路 1570 乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1570_MVAR | 新營下營一路 MVAR | LINE161 | [5 empty] | 147 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1580 | MW | 新營下營二路 1580 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1580_MW | 新營下營二路 MW | LINE161 | [5 empty] | 148 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1580 | MVAR | 新營下營二路 1580 乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1580_MVAR | 新營下營二路 MVAR | LINE161 | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8E |  |  | 1530 | MW | 新營柳營山線 1530 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1530_MW | 新營柳營山線 MW | LINE161 | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8F |  |  | 1530 | MVAR | 新營柳營山線 1530乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1530_MVAR | 新營柳營山線 MVAR | LINE161 | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-90 |  |  | 1550 | MW | 嘉義新營山上紅線1550 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1550_MW | 嘉義山上紅線 MW | LINE161 | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0017 |  |  | 1-91 |  |  | 1550 | MVAR | 嘉義新營山上紅線1550 乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1550_MVAR | 嘉義山上紅線 MVAR | LINE161 | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-92 |  |  | 1520 | MW | 新營華卡線 1520 瓦 | MW_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1520_MW | 華卡線 MW | LINE161 | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-93 |  |  | 1520 | MVAR | 新營華卡線 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1520_MVAR | 華卡線 MVAR | LINE161 | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0020 |  |  | 1-94 |  |  | 1500 | A | 1500 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0021 |  |  | 1-95 |  |  | #1BUS | KV | 161KV #1BUS ST相電壓 | kV_-210_210(-2000_2000) | aaa | B2/P01_A1 | [8 empty] | 新營PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0022 |  |  | 1-96 |  |  | #2BUS | KV | 161KV #2BUS ST相電壓 | kV_-210_210(-2000_2000) | aab | B2/P01_A1 | [8 empty] | 新營PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P01 | 新營PS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | #1MTR | 升/降 | #1MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | #1MTR | ℃ | #1MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_OIL | #1MTR 油溫 | MTR | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-99 |  |  | #1MTR | ℃ | #1MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_COIL | #1MTR 線溫 | MTR | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | #2MTR | 升/降 | #2MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | #2MTR | ℃ | #2MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_OIL | #2MTR 油溫 | MTR | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | #2MTR | ℃ | #2MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_COIL | #2MTR 線溫 | MTR | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | #3MTR | 升/降 | #3MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | #3MTR | ℃ | #3MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_OIL | #3MTR 油溫 | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | #3MTR | ℃ | #3MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_COIL | #3MTR 線溫 | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | #2ADTR | 升/降 | #2ADTR TAP | TAP_-8.5_8.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | #2BDTR | 升/降 | #2BDTR TAP | TAP_-8.5_8.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS |  |  | 2DTR | #2DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | #2DTR | ℃ | #2DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | #2ADTR | ℃ | #2ADTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | #2BDTR | ℃ | #2BDTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | #3ADTR | 升/降 | #3ADTR TAP | TAP_-8.5_8.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | #3BDTR | 升/降 | #3BDTR TAP | TAP_-8.5_8.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS |  |  | 3DTR | #3DTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | #3DTR | ℃ | #3DTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | #3ADTR | ℃ | #3ADTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | #3BDTR | ℃ | #3BDTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 730 | MW | 新營新西線 730 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.730_MW | 新西線 MW | LINE69 | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 730 | MAVR | 新營新西線 730 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.730_MVAR | 新西線 MVAR | LINE69 | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0050 |  |  | 1-B2 |  |  | 750 | MW | #1MTR 二次側 750 瓦 | MW_-360_360(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#1MTR_MW | #1MTR二次側 MW | MTR | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-B3 |  |  | 750 | MAVR | #1MTR 二次側 750 乏 | MVAR_-240_240(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-B4 |  |  | 770 | MW | #3MTR 二次側 770 瓦 | MW_-360_360(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#3MTR_MW | #3MTR二次側 MW | MTR | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 770 | MAVR | #3MTR 二次側 770 乏 | MVAR_-240_240(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 670 | MW | 新營大寮二路 670 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.670_MW | 大寮二路 MW | LINE69 | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-B7 |  |  | 670 | MAVR | 新營大寮二路 670 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.670_MVAR | 大寮二路 MVAR | LINE69 | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 610 | MW | 新營官田一路 610 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.610_MW | 備用線 MW | LINE69 | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 610 | MAVR | 新營官田一路 610 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.610_MVAR | 備用線 MVAR | LINE69 | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-BA |  |  | 760 | MW | #2MTR 二次側 760 瓦 | MW_-360_360(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#2MTR_MW | #2MTR二次側 MW | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 760 | MAVR | #2MTR 二次側 760 瓦 | MVAR_-240_240(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 620 | MW | 新營新東線 620 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.620_MW | 新營新東線 MW | LINE69 | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-BD |  |  | 620 | MAVR | 新營新東線 620 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.620_MVAR | 新營新東線 MVAR | LINE69 | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0062 |  |  | 1-BE |  |  | 680 | MW | 新營大寮一路 680 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.680_MW | 大寮一路 MW | LINE69 | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-BF |  |  | 680 | MAVR | 新營大寮一路 680 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.680_MVAR | 大寮一路 MVAR | LINE69 | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-C2 |  |  | 660 | MW | 新營官田二路 660 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.660_MW | 官田二路 MW | LINE69 | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0067 |  |  | 1-C3 |  |  | 660 | MVAR | 新營官田二路 660 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.660_MVAR | 官田二路 MVAR | LINE69 | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-C4 |  |  | 630 | MW | 新營白河水上線 630 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.630_MW | 新營白河水上線 MW | LINE69 | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-C5 |  |  | 630 | MVAR | 新營白河水上線 630 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.630_MVAR | 新營白河水上線 MVAR | LINE69 | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0070 |  |  | 1-C6 |  |  | 710 | MW | 新營東盟榮剛榮重線 710 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.710_MW | 東盟榮剛榮重線 MW | LINE69 | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | MVAR |  | B3 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-C7 |  |  | 710 | MVAR | 新營東盟榮剛榮重線 710 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.710_MVAR | 東盟榮剛榮重線 MVAR | LINE69 | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-C8 |  |  | 650 | MW | 新營隆田線 650 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.650_MW | 隆田線 MW | LINE69 | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-C9 |  |  | 650 | MVAR | 新營隆田線 650 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.650_MVAR | 隆田線 MVAR | LINE69 | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-CA |  |  | 640 | MW | 新營營糖線 640 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.640_MW | 營糖線 MW | LINE69 | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-CB |  |  | 640 | MVAR | 新營營糖線 640 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.640_MVAR | 營糖線 MVAR | LINE69 | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 720 | MW | 新營學甲二路 720 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.720_MW | 新營學甲二路 MW | LINE69 | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 720 | MVAR | 新營學甲二路 720 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.720_MVAR | 新營學甲二路 MVAR | LINE69 | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 910 | MW | 新營學甲一路 910 瓦 | MW_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.910_MW | 新營學甲一路 MW | LINE69 | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 910 | MVAR | 新營學甲一路 910 乏 | MVAR_-144_144(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.910_MVAR | 新營學甲一路 MVAR | LINE69 | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 600 | A | 600 TIE R相電流 | A_-2000_2000(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C20R1500 | 1425 | 1500 | 1650 | 1845 | 2.27 | -1425 | -1500 | -1650 | -1845 | 1 | 0.01 | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0081 |  |  | 1-D1 |  |  | #1BUS | KV | 69KV #1BUS ST相電壓 | kV_-90_90(-2000_2000) | aaa | B2/P01_A1 | [8 empty] | 新營PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P01 | 新營PS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0082 |  |  | 1-D2 |  |  | #2BUS | KV | 69KV #2BUS ST相電壓 | kV_-90_90(-2000_2000) | aab | B2/P01_A1 | [8 empty] | 新營PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P01 | 新營PS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | #4MTR | ℃ | #4MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_OIL | #4MTR 油溫 | MTR | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | #4MTR | ℃ | #4MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_COIL | #4MTR 線溫 | MTR | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | #4MTR | 升/降 | #4MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_TAP | #4MTR OLTC TAP | MTR | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 780 | MW | #4MTR 二次側 780 瓦 | MW_-360_360(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#4MTR_MW | #4MTR二次側 MW | MTR | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 780 | MVAR | #4MTR 二次側 780 乏 | MVAR_-240_240(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.#4MTR_MVAR | #4MTR二次側 MVAR | MTR | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 新11線 | A | 新11線F1 VC31 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新31線A0 | 11KV新31線 N相AMP | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 新12線 | A | 新12線F2 VC32 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新32線A0 | 11KV新32線 N相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 新13線 | A | 新13線F3 VC33 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新33線A0 | 11KV新33線 N相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 新14線 | A | 新14線F4 VC34 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新34線A0 | 11KV新34線 N相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 新15線 | A | 新15線F5 VC35 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新35線A0 | 11KV新35線 N相AMP | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 新16線 | A | 新16線F6 VC36 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新36線A0 | 11KV新36線 N相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 新17線 | A | 新17線F7 VC37 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新37線A0 | 11KV新37線 N相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 新18線 | A | 新18線F8 VC38 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新38線A0 | 11KV新38線 N相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 新19線 | A | 新19線F9 VC39 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新39線A0 | 11KV新39線 N相AMP | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 新20線 | A | 新20線F10 VC40 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新40線A0 | 11KV新40線 N相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 新61線 | A | 新61線F11 VC61 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新61線A0 | 23KV新61線 N相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 新62線 | A | 新62線F12 VC62 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新62線A0 | 23KV新62線 N相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 新63線 | A | 新63線F13 VC63 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新63線A0 | 23KV新63線 N相AMP | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 新64線 | A | 新64線F14 VC64 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新64線A0 | 23KV新64線 N相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 新65線 | A | 新65線F15 VC65 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新65線A0 | 23KV新65線 N相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 新66線 | A | 新66線F16 VC66 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新66線A0 | 23KV新66線 N相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 新67線 | A | 新67線F17 VC67 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新67線A0 | 23KV新67線 N相AMP | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 新68線 | A | 新68線F18 VC68 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新68線A0 | 23KV新68線 N相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 新69線 | A | 新69線F19 VC69 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新69線A0 | 23KV新69線 N相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 新70線 | A | 新70線F20 VC70 A (N) | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新70線A0 | 23KV新70線 N相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 1540 | KV | 新營柳營海線 1540LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1540LPD_KV | 新營柳營海線(1540) LPD KV | LINE161 | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 1530 | KV | 新營柳營山線 1530LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1530LPD_KV | 新營柳營山線(1530) LPD KV | LINE161 | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 1560 | KV | 嘉義新營山上分岐白線 1560 LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1560LPD_KV | 嘉義山上白線(1560) LPD KV | LINE161 | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 1550 | KV | 嘉義新營山上紅線1550 LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1550LPD_KV | 嘉義山上紅線(1550) LPD KV | LINE161 | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 1570 | KV | 新營下營一路 1570 LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1570LPD_KV | 新營下營一路(1570) LPD KV | LINE161 | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 1580 | KV | 新營下營二路 1580 LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1580LPD_KV | 新營下營二路(1580) LPD KV | LINE161 | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 1520 | KV | 新營華卡線 1520 LPD | kV_-210_210(-2000_2000) |  | B2/P01_A1 | [8 empty] | 新營PS.1520LPD_KV | 華卡線(1520) LPD KV | LINE161 | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 330 | MVAR | 2DTR M2A 乏 | MVAR_-36_36(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 330 | MW | 2DTR M2A 瓦 | MW_-36_36(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 330 | A1 | 2DTR M2A R相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 330 | A2 | 2DTR M2A S相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 330 | A3 | 2DTR M2A T相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | VC31 | MVAR | 新11線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新31線KVAR | 11KV新31線 KVAR | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | VC31 | A1 | 新11線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新31線A1 | 11KV新31線 R相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | VC31 | A2 | 新11線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新31線A2 | 11KV新31線 S相AMP | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | VC31 | A3 | 新11線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新31線A3 | 11KV新31線 T相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | VC32 | MVAR | 新12線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新32線KVAR | 11KV新32線 KVAR | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | VC32 | A1 | 新12線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新32線A1 | 11KV新32線 R相AMP | FEEDER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | VC32 | A2 | 新12線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新32線A2 | 11KV新32線 S相AMP | FEEDER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | VC32 | A3 | 新12線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新32線A3 | 11KV新32線 T相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | VC33 | MVAR | 新13線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新33線KVAR | 11KV新33線 KVAR | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | VC33 | A1 | 新13線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新33線A1 | 11KV新33線 R相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | VC33 | A2 | 新13線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新33線A2 | 11KV新33線 S相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | VC33 | A3 | 新13線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新33線A3 | 11KV新33線 T相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | VC34 | MVAR | 新14線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新34線KVAR | 11KV新34線 KVAR | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | VC34 | A1 | 新14線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新34線A1 | 11KV新34線 R相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | VC34 | A2 | 新14線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新34線A2 | 11KV新34線 S相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | VC34 | A3 | 新14線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新34線A3 | 11KV新34線 T相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | VC35 | MVAR | 新15線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新35線KVAR | 11KV新35線 KVAR | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | VC35 | A1 | 新15線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新35線A1 | 11KV新35線 R相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | VC35 | A2 | 新15線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新35線A2 | 11KV新35線 S相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | VC35 | A3 | 新15線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新35線A3 | 11KV新35線 T相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | VC36 | MVAR | 新16線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新36線KVAR | 11KV新36線 KVAR | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | VC36 | A1 | 新16線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新36線A1 | 11KV新36線 R相AMP | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | VC36 | A2 | 新16線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新36線A2 | 11KV新36線 S相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | VC36 | A3 | 新16線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新36線A3 | 11KV新36線 T相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0159 |  |  | 2-9F |  |  | #2A BUS | KV | 23KV #2A BUS PT RN相電流 | kV_-9_9(-2000_2000) | aaa | B3/P01_A1 | [8 empty] | 新營PS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 100 | A1 | 11KV #1TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 100 | A2 | 11KV #1TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 100 | A3 | 11KV #1TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 350 | KVAR | 3DTR M3A 乏 | MVAR_-54_54(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | 350 | MW | 3DTR M3A 瓦 | MW_-36_36(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | 350 | A1 | 3DTR M3A R相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | 350 | A2 | 3DTR M3A S相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | 350 | A3 | 3DTR M3A T相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | VC37 | KVAR | F7 新17線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新37線KVAR | 11KV新37線 KVAR | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | VC37 | A1 | F7 新17線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新37線A1 | 11KV新37線 R相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | VC37 | A2 | F7 新17線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新37線A2 | 11KV新37線 S相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | VC37 | A3 | F7 新17線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新37線A3 | 11KV新37線 T相AMP | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | VC38 | KVAR | F7 新18線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新38線KVAR | 11KV新38線 KVAR | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | VC38 | A1 | F8 新18線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新38線A1 | 11KV新38線 R相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | VC38 | A2 | F8 新18線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新38線A2 | 11KV新38線 S相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | VC38 | A3 | F8 新18線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新38線A3 | 11KV新38線 T相AMP | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | VC39 | KVAR | F9 新19線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新39線KVAR | 11KV新39線 KVAR | FEEDER | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | VC39 | A1 | F9 新19線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新39線A1 | 11KV新39線 R相AMP | FEEDER | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | VC39 | A2 | F9 新19線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新39線A2 | 11KV新39線 S相AMP | FEEDER | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | VC39 | A3 | F9 新19線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新39線A3 | 11KV新39線 T相AMP | FEEDER | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | VC40 | KVAR | F10 新20線 乏 | KVAR_-10800_10800(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新40線KVAR | 11KV新40線 KVAR | FEEDER | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | VC40 | A1 | F10 新20線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新40線A1 | 11KV新40線 R相AMP | FEEDER | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | VC40 | A2 | F10 新20線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新40線A2 | 11KV新40線 S相AMP | FEEDER | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | VC40 | A3 | F10 新20線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新40線A3 | 11KV新40線 T相AMP | FEEDER | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 2BBUS | #2BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0184 |  |  | 2-B8 |  |  | #2B BUS | KV | 23KV #2B BUS PT RN相電壓 | kV_-18_18(-2000_2000) | baa | B3/P01_A1 | [8 empty] | 新營PS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 340 | KVAR | 2DTR M2B 乏 | MVAR_-72_72(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 340 | MW | 2DTR M2B 瓦 | MW_-72_72(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 340 | A1 | 2DTR M2B R相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 340 | A2 | 2DTR M2B S相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | 340 | A3 | 2DTR M2B T相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | VC61 | KVAR | F11 新61線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新61線KVAR | 23KV新61線 KVAR | FEEDER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | VC61 | A1 | F11 新61線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新61線A1 | 23KV新61線 R相AMP | FEEDER | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.3 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | VC61 | A2 | F11 新61線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新61線A2 | 23KV新61線 S相AMP | FEEDER | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | VC61 | A3 | F11 新61線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新61線A3 | 23KV新61線 T相AMP | FEEDER | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | VC62 | KVAR | F12 新62線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新62線KVAR | 23KV新62線 KVAR | FEEDER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | VC62 | A1 | F12 新62線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新62線A1 | 23KV新62線 R相AMP | FEEDER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | VC62 | A2 | F12 新62線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新62線A2 | 23KV新62線 S相AMP | FEEDER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | VC62 | A3 | F12 新62線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新62線A3 | 23KV新62線 T相AMP | FEEDER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | VC63 | KVAR | F13 新63線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新63線KVAR | 23KV新63線 KVAR | FEEDER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | VC63 | A1 | F13 新63線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新63線A1 | 23KV新63線 R相AMP | FEEDER | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | VC63 | A2 | F13 新63線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新63線A2 | 23KV新63線 S相AMP | FEEDER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | VC63 | A3 | F13 新63線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新63線A3 | 23KV新63線 T相AMP | FEEDER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0204 |  |  | 2-CC |  |  | VC64 | KVAR | F14 新64線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新64線KVAR | 23KV新64線 KVAR | FEEDER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0205 |  |  | 2-CD |  |  | VC64 | A1 | F14 新64線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新64線A1 | 23KV新64線 R相AMP | FEEDER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | VC64 | A2 | F14 新64線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新64線A2 | 23KV新64線 S相AMP | FEEDER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | VC64 | A3 | F14 新64線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新64線A3 | 23KV新64線 T相AMP | FEEDER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0208 |  |  | 2-D0 |  |  | #3A BUS | KV | 11KV #3A BUS PT RN相電壓 | kV_-9_9(-2000_2000) | aba | B3/P01_A1 | [8 empty] | 新營PS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | 200 | A1 | 23KV #2TIE R相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.23KV_200_A1 | 23KV 200 R相AMP | TIE | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | 200 | A2 | 23KV #2TIE S相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.23KV_200_A2 | 23KV 200 S相AMP | TIE | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | 200 | A3 | 23KV #2TIE T相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.23KV_200_A3 | 23KV 200 T相AMP | TIE | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | 360 | KVAR | 3DTR M3B 乏 | MVAR_-72_72(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0213 |  |  | 2-D5 |  |  | 360 | MW | 3DTR M3B 瓦 | MW_-72_72(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | 360 | A1 | 3DTR M3B R相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 360 | A2 | 3DTR M3B S相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 360 | A3 | 3DTR M3B T相電流 | A_-2000_2000(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | VC65 | KVAR | F15 新65線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新65線KVAR | 23KV新65線 KVAR | FEEDER | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | VC65 | A1 | F15 新65線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新65線A1 | 23KV新65線 R相AMP | FEEDER | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | VC65 | A2 | F15 新65線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新65線A2 | 23KV新65線 S相AMP | FEEDER | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | VC65 | A3 | F15 新65線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新65線A3 | 23KV新65線 T相AMP | FEEDER | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | VC66 | KVAR | F16 新66線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新66線KVAR | 23KV新66線 KVAR | FEEDER | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | VC66 | A1 | F16 新66線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新66線A1 | 23KV新66線 R相AMP | FEEDER | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | VC66 | A2 | F16 新66線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新66線A2 | 23KV新66線 S相AMP | FEEDER | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | VC66 | A3 | F16 新66線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新66線A3 | 23KV新66線 T相AMP | FEEDER | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | VC67 | KVAR | F17 新67線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新67線KVAR | 23KV新67線 KVAR | FEEDER | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | VC67 | A1 | F17 新67線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新67線A1 | 23KV新67線 R相AMP | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | VC67 | A2 | F17 新67線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新67線A2 | 23KV新67線 S相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | VC67 | A3 | F17 新67線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新67線A3 | 23KV新67線 T相AMP | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | VC68 | KVAR | F18 新68線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新68線KVAR | 23KV新68線 KVAR | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | VC68 | A1 | F18 新68線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新68線A1 | 23KV新68線 R相AMP | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | VC68 | A2 | F18 新68線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新68線A2 | 23KV新68線 S相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | VC68 | A3 | F18 新68線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新68線A3 | 23KV新68線 T相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | VC69 | KVAR | F19 新69線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新69線KVAR | 23KV新69線 KVAR | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | VC69 | A1 | F19 新69線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新69線A1 | 23KV新69線 R相AMP | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | VC69 | A2 | F19 新69線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新69線A2 | 23KV新69線 S相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | VC69 | A3 | F19 新69線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新69線A3 | 23KV新69線 T相AMP | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | VC70 | KVAR | F20 新70線 乏 | KVAR_-21600_21600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新70線KVAR | 23KV新70線 KVAR | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | VC70 | A1 | F20 新70線 R相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新70線A1 | 23KV新70線 R相AMP | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | VC70 | A2 | F20 新70線 S相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新70線A2 | 23KV新70線 S相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | VC70 | A3 | F20 新70線 T相電流 | A_-600_600(-2000_2000) |  | B2/P01_D1 | [8 empty] | 新營PS.新70線A3 | 23KV新70線 T相AMP | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0241 |  |  | 2-F1 |  |  | #3 BUS | KV | 23KV #3B BUS PT RN相電壓 | kV_-18_18(-2000_2000) | bba | B3/P01_A1 | [8 empty] | 新營PS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | DCV | 65.5 | DC-P 電壓 | kV_-150_150(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | DCV | -65.5 | DC-N 電壓 | kV_-150_150(-2000_2000) |  | B3/P01_A1 | [8 empty] | 新營PS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D06O/T1 |  | 0005 |  |  | 1-00-05 |  |  | 1540 | ON/OFF | 新營柳營海線 |  | aada | B2/P01_A1 | [8 empty] | 新營PS.1540_CB | 1540(新營柳營海線) CB | LINE161 | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 1550 | 87A | 嘉義新營山上紅線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1550_87A | 嘉義山上紅線(1550) 87RY | LINE161 | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 1550 | PHA | 嘉義新營山上分歧紅線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1550_PHA | 嘉義山上紅線(1550) 相間RY | LINE161 | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 1550 | GDA | 嘉義新營山上紅線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1550_GDA | 嘉義山上紅線(1550) 接地RY | LINE161 | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D06M/T1 |  | 0009 |  |  | 1-01-01 |  |  | 1530 | ON/OFF | 新營柳營山線 |  | aaga | B2/P01_A1 | [8 empty] | 新營PS.1530_CB | 1530(新營柳營山線) CB | LINE161 | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 1560 | 87A | 嘉義新營山上分歧白線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_87A | 嘉義山上白線(1560) 87RY | LINE161 | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 1560 | PHA | 嘉義新營山上分歧白線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_PHA | 嘉義山上白線(1560) 相間RY | LINE161 | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0012 |  |  | 1-01-04 |  |  | 1560 | GDA | 嘉義新營山上分歧白線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_GDA | 嘉義山上白線(1560) 接地RY | LINE161 | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01TN09R/T2 |  | 0013 |  |  | 1-01-05 |  |  | 1550 | ON/OFF | 嘉義新營山上分歧紅線 |  | aaja | B2/P01_A1 | [8 empty] | 新營PS.1550_CB | 1550(嘉義山上紅線) CB | LINE161 | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 1540 | 87A | 新營柳營海線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1540_87A | 新營柳營海線(1540) 87RY | LINE161 | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0015 |  |  | 1-01-07 |  |  | 1540 | PHA | 新營柳營海線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1540_PHA | 新營柳營海線(1540) 相間RY | LINE161 | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 1540 | GDA | 新營柳營海線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1540_GDA | 新營柳營海線(1540) 接地RY | LINE161 | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | #3DTR | 86A | #3DTR_86A |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_86A | #3DTR 86RY | OTHER | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0018 |  |  | 1-02-02 |  |  | #2DTR | 86A | #2DTR_86A |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_86A | #2DTR 86RY | OTHER | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01TN10W/T2 |  | 0019 |  |  | 1-02-03 |  |  | 1560 | ON/OFF | 嘉義新營山上分歧白線 |  | aama | B2/P01_A1 | [8 empty] | 新營PS.1560_CB | 1560(嘉義山上白線) CB | LINE161 | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 1530 | 87A | 新營柳營山線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1530_87A | 新營柳營山線(1530) 87RY | LINE161 | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0021 |  |  | 1-02-05 |  |  | 1530 | PHA | 新營柳營山線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1530_PHA | 新營柳營山線(1530) 相間RY | LINE161 | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 1530 | GDA | 新營柳營山線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1530_GDA | 新營柳營山線(1530) 接地RY | LINE161 | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0025 |  |  | 1-03-01 |  |  | 1500 | ON/OFF | 1500 TIE |  | aanz | B2/P01_A1 | [8 empty] | 新營PS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 1500 | 50A | 1500 TIE |  |  | B2/P01_A1 | [8 empty] | 新營PS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0027 |  |  | 1-03-03 |  |  | 161KV BUS | 87B1A | 161KV #1BUS 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.161#1BUS_87A | 161KV #1BUS 87A | BUS | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 161KV BUS | 87B2A | 161KV #2BUS 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.161#2BUS_87A | 161KV #2BUS 87A | BUS | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | #2MTR | GDA | #2MTR_GDA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_GDA | #2MTR GDA | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0030 |  |  | 1-03-06 |  |  | #2MTR | 86A | #2MTR_86A |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_86A | #2MTR 86RY | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | #1MTR | GDA | #1MTR_GDA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_GDA | #1MTR GDA | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0032 |  |  | 1-04-00 |  |  | 1650 | ON/OFF | 一號主變一次側 |  | aafb | B2/P01_A1 | [8 empty] | 新營PS.1650_CB | 1650(#1MTR) CB | MTR | [5 empty] | 386 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0033 |  |  | 1-04-01 |  |  | 750 | ON/OFF | 一號主變二次側 |  | aafa | B2/P01_A1 | [8 empty] | 新營PS.750_CB | 750(#1MTR) CB | MTR | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS |  |  | 1MTR | #1MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | #1MTR | PHA | #1MTR_PHA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_PHA | #1MTR PHA | OTHER | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | #1MTR | 87A | 一號主變差動電驛 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_87A | #1MTR 87RY | MTR | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | #1MTR | 96PA | 一號主變 機械保護動作(96PA) |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | #1MTR | 51ZA | 一號主變 51Z RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0039 |  |  | 1-04-07 |  |  | #1MTR | 86A | #1MTR_86A |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_86A | #1MTR 86RY | OTHER | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0040 |  |  | 1-05-00 |  |  | 1660 | ON/OFF | 二號主變一次側 |  | aaib | B2/P01_A1 | [8 empty] | 新營PS.1660_CB | 1660(#2MTR) CB | MTR | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0041 |  |  | 1-05-01 |  |  | 760 | ON/OFF | 二號主變二次側 |  | aaja | B2/P01_A1 | [8 empty] | 新營PS.760_CB | 760(#2MTR) CB | MTR | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS |  |  | 2MTR | #2MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | #2MTR | PHA | #2MTR_PHA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_PHA | #2MTR PHA | OTHER | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | #2MTR | 87A | 二號主變差動電驛 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_87A | #2MTR 87RY | MTR | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | #2MTR | 96PA | 二號主變 機械保護動作(96PA) |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | #2MTR | 51ZA | 二號主變 51Z RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | #3MTR | GDA | #3MTR_GDA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_GDA | #3MTR GDA | OTHER | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0048 |  |  | 1-06-00 |  |  | 1670 | ON/OFF | 三號主變一次側 |  | aalb | B2/P01_A1 | [8 empty] | 新營PS.1670_CB | 1670(#3MTR) CB | MTR | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0049 |  |  | 1-06-01 |  |  | 770 | ON/OFF | 三號主變二次側 |  | aana | B2/P01_A1 | [8 empty] | 新營PS.770_CB | 770(#3MTR) CB | MTR | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS |  |  | 3MTR | #3MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | #3MTR | PHA | #3MTR_PHA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_PHA | #3MTR PHA | OTHER | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #3MTR | 87A | 三號主變差動電驛 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_87A | #3MTR 87RY | MTR | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #3MTR | 96PA | 三號主變 機械保護動作(96PA) |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #3MTR | 51ZA | 三號主變 51Z RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #3MTR | 86A | #3MTR_86A |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_86A | #3MTR 86RY | OTHER | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0064 |  |  | 1-08-00 |  |  | 1760 | ON/OFF | 二號配變一次側 |  | aahb | ELEM/P01_A1 | [8 empty] | 新營PS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | T/2DTR(A) |  |  | 0065 |  |  | 1-08-01 |  |  | 330 M2A | ON/OFF | 二號配變二次側 330 M2A |  | aaaa | ELEM/P01_A1 | [8 empty] | 新營PS.330_CB | 330(#2DTR) CB | MTR | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | T/2DTR(B) |  |  | 0066 |  |  | 1-08-02 |  |  | 340 M2B | ON/OFF | 二號配變二次側 340 M2B |  | baca | ELEM/P01_A1 | [8 empty] | 新營PS.340_CB | 340(#2DTR) CB | MTR | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #2DTr | 87A | 二號配變差動電驛 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #2DTr | 96PA | 二號配變 機械保護動作(96PA) |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | #2DTr | 51ZA | 二號配變 51Z RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 1760 | PHA | 二號配變一次側 |  |  | B2/P01_A1 | [8 empty] | 新營PS.#2DTR_51A | #2DTR 51RY | MTR | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 1760 | GDA | 二號配變一次側 |  |  | B2/P01_A1 | [8 empty] | 新營PS.#2DTR_51NA | #2DTR 51N RY | MTR | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | 330 M2A | PHA | 二號配變二次側 330 M2A |  |  | B3/P01_A1 | [8 empty] | 新營PS.330_51A | #2DTR二次側(330) 51RY | MTR | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 340 M2B | PHA | 二號配變二次側 340 M2B |  |  | B3/P01_A1 | [8 empty] | 新營PS.340_51A | #2DTR二次側(340) 51RY | MTR | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0074 |  |  | 1-09-02 |  |  | 1770 | ON/OFF | 三號配變一次側 |  | aakb | ELEM/P01_A1 | [8 empty] | 新營PS.1770_CB | 1770(#3DTR) CB | MTR | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | T/3DTR(B) |  |  | 0075 |  |  | 1-09-03 |  |  | 360 M3B | ON/OFF | 三號配變二次側 360 M3B |  | bbja | ELEM/P01_A1 | [8 empty] | 新營PS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3ABus | T/3DTR(A) |  |  | 0076 |  |  | 1-09-04 |  |  | 350 M3A | ON/OFF | 三號配變二次側 350 M3A |  | abfa | ELEM/P01_A1 | [8 empty] | 新營PS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | #3DTr | 87A | 三號配變差動電驛 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_87A | #3DTR 87RY | MTR | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | #3DTr | 96PA | 三號配變 機械保護動作(96PA) |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | #3DTr | 51ZA | 三號配變 51Z RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_51ZA | #3DTR 51Z RY | MTR | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-0A-00 |  |  | 1770 | PHA | 三號配變一次側 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_51A | #3DTR 51RY | MTR | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 1770 | GDA | 三號配變一次側 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_51NA | #3DTR 51N RY | MTR | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 360 M3B | PHA | 三號配變二次側 360 M3B |  |  | B3/P01_A1 | [8 empty] | 新營PS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-0A-03 |  |  | 350 M3A | PHA | 三號配變二次側 350 M3A |  |  | B3/P01_A1 | [8 empty] | 新營PS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0084 |  |  | 1-0A-04 |  |  | 600 | ON/OFF | 600 TIE CB |  | aacz | B2/P01_A1 | [8 empty] | 新營PS.600_CB | 600(TIE) CB | TIE | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | 600 | #1 PHA | 600 TIE #1 PHA |  |  | B2/P01_A1 | [8 empty] | 新營PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  |  | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | 600 | #1 GDA | 600 TIE #1 GDA |  |  | B2/P01_A1 | [8 empty] | 新營PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-0A-07 |  |  | 69KV BUS | 87B1A | 69KV #1BUS 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.69#1BUS_87A | 69KV #1BUS 87A | BUS | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0088 |  |  | 1-0B-00 |  |  | 69KV BUS | 87B2A | 69KV #2BUS 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.69#2BUS_87A | 69KV #2BUS 87A | BUS | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 161KV | RCA | 線路復閉電驛動作警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | OSCA | A/N | 69KV示波器啟動警報OSCA |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_OSCA | 69KV示波器啟動警報 | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | #2DTR 330 | 81A | 二號配變 330 81 RY 動作 |  |  | ELEM/P01_A1 | [16 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0094 |  |  | 1-0B-06 |  |  | 69KV | RCA | 線路復閉電驛動作警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_RCA | 69KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D011/T1 |  | 0096 |  |  | 1-0C-00 |  |  | 1570 | ON/OFF | 新營下營一路 1570 ON/OFF |  | aaoa | B2/P01_A1 | [8 empty] | 新營PS.1570_CB | 1570(新營下營一路) CB | LINE161 | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-0C-01 |  |  | 1570 | 87A | 新營下營一路 1570 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_87A | 新營下營一路(1570) 87RY | LINE161 | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0098 |  |  | 1-0C-02 |  |  | 1570 | PHA | 新營下營一路 1570 PHA |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_PHA | 新營下營一路(1570) 相間RY | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 1570 | GDA | 新營下營一路 1570 GDA |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_GDA | 新營下營一路(1570) 接地RY | LINE161 | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01D012/T1 |  | 0102 |  |  | 1-0C-06 |  |  | 1580 | ON/OFF | 新營下營二路 1580 ON/OFF |  | aapa | B2/P01_A1 | [8 empty] | 新營PS.1580_CB | 1580(新營下營二路) CB | LINE161 | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | 1580 | 87A | 新營下營二路 1580 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_87A | 新營下營二路(1580) 87RY | LINE161 | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0104 |  |  | 1-0D-00 |  |  | 1580 | PHA | 新營下營二路 1580 PHA |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_PHA | 新營下營二路(1580) 相間RY | LINE161 | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0105 |  |  | 1-0D-01 |  |  | 1580 | GDA | 新營下營二路 1580 GDA |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_GDA | 新營下營二路(1580) 接地RY | LINE161 | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0106 |  |  | 1-0D-02 |  |  | #4MTR | GDA | #4MTR_GDA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_GDA | #4MTR GDA | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0107 |  |  | 1-0D-03 |  |  | #4MTR | 86A | #4MTR_86A |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_86A | #4MTR 86RY | OTHER | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01C62/T1 |  | 0108 |  |  | 1-0D-04 |  |  | 1520 | ON/OFF | 新營華卡線 |  | aaaa | B2/P01_A1 | [8 empty] | 新營PS.1520_CB | 1520(華卡線) CB | LINE161 | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0110 |  |  | 1-0D-06 |  |  | 1520 | PHA | 新營華卡線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1520_PHA | 華卡線(1520) 相間RY | LINE161 | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0111 |  |  | 1-0D-07 |  |  | 1520 | GDA | 新營華卡線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1520_GDA | 華卡線(1520) 接地RY | LINE161 | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4MTR |  | 0120 |  |  | 1-0F-00 |  |  | 1680 | ON/OFF | 四號主變一次側 |  | aaeb | B2/P01_A1 | [8 empty] | 新營PS.1680_CB | 1680(#4MTR) CB | MTR | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4MTR |  | 0121 |  |  | 1-0F-01 |  |  | 780 | ON/OFF | 四號主變二次側 |  | aaaa | B2/P01_A1 | [8 empty] | 新營PS.780_CB | 780(#4MTR) CB | MTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS |  |  | 4MTR | #4MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0123 |  |  | 1-0F-03 |  |  | #4MTR | PHA | #4MTR_PHA |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_PHA | #4MTR PHA | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | #4MTR | 87A | 四號主變差動電驛 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_87A | #4MTR 87RY | MTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #4MTR | 96PA | 四號主變 96D,63A RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_96PA | #4MTR 機械保護動作 | MTR | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #4MTR | 51ZA | 四號主變 51Z RY |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_51ZA | #4MTR 51Z RY | MTR | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | 161RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/P01_A1 | [16 empty] | 456 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0192 |  |  | 1-18-00 |  |  | 610 | ON/OFF | 新營官田一路 |  | aabb | B2/P01_A1 | [8 empty] | 新營PS.610_CB | 610(備用線) CB | LINE69 | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 610 | 85A | 新營官田一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.610_85A | 備用線(610) 85RY | LINE69 | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | 610 | PHA | 新營官田一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.610_PHA | 備用線(610) 相間RY | LINE69 | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 610 | GDA | 新營官田一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.610_GDA | 備用線(610) 接地RY | LINE69 | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S45/T1 |  | 0196 |  |  | 1-18-04 |  |  | 620 | ON/OFF | 新營新東線 |  | aadb | B2/P01_A1 | [8 empty] | 新營PS.620_CB | 620(新營新東線) CB | LINE69 | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 620 | 87A | 新營新東線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.620_87A | 新營新東線(620) 87RY | LINE69 | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 620 | PHA | 新營新東線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.620_PHA | 新營新東線(620) 相間RY | LINE69 | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 620 | GDA | 新營新東線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.620_GDA | 新營新東線(620) 接地RY | LINE69 | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01TN04/T2 |  | 0200 |  |  | 1-19-00 |  |  | 630 | ON/OFF | 新營白河水上線 |  | aaeb | B2/P01_A1 | [8 empty] | 新營PS.630_CB | 630(新營白河水上線) CB | LINE69 | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | 630 | 87A | 新營白河水上線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.630_87A | 新營白河水上線(630) 87RY | LINE69 | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 630 | PHA | 新營白河水上線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.630_PHA | 新營白河水上線(630) 相間RY | LINE69 | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 630 | GDA | 新營白河水上線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.630_GDA | 新營白河水上線(630) 接地RY | LINE69 | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01TN15/T2 |  | 0204 |  |  | 1-19-04 |  |  | 640 | ON/OFF | 新營營糖線 |  | aagb | B2/P01_A1 | [8 empty] | 新營PS.640_CB | 640(營糖線) CB | LINE69 | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0205 |  |  | 1-19-05 |  |  | 640 | 85A | 新營營糖線 (沒設備) |  |  | B2/P01_A1 | [8 empty] | 新營PS.640_85A | 營糖線(640) 85RY | LINE69 | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0206 |  |  | 1-19-06 |  |  | 640 | PHA | 新營營糖線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.640_PHA | 營糖線(640) 相間RY | LINE69 | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0207 |  |  | 1-19-07 |  |  | 640 | GDA | 新營營糖線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.640_GDA | 營糖線(640) 接地RY | LINE69 | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S41/T1 |  | 0208 |  |  | 1-1A-00 |  |  | 650 | ON/OFF | 新營隆田線 |  | aahb | B2/P01_A1 | [8 empty] | 新營PS.650_CB | 650(隆田線) CB | LINE69 | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0209 |  |  | 1-1A-01 |  |  | 650 | 87A | 新營隆田線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.650_87A | 隆田線(650) 87RY | LINE69 | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | 650 | PHA | 新營隆田線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.650_PHA | 隆田線(650) 相間RY | LINE69 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | 650 | GDA | 新營隆田線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.650_GDA | 隆田線(650) 接地RY | LINE69 | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S402/T1 |  | 0212 |  |  | 1-1A-04 |  |  | 660 | ON/OFF | 新營官田二路 |  | aaib | B2/P01_A1 | [8 empty] | 新營PS.660_CB | 660(官田二路) CB | LINE69 | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 660 | 87A | 新營官田二路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.660_87A | 官田二路(660) 87RY | LINE69 | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0214 |  |  | 1-1A-06 |  |  | 660 | PHA | 新營官田二路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.660_PHA | 官田二路(660) 相間RY | LINE69 | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 660 | GDA | 新營官田二路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.660_GDA | 官田二路(660) 接地RY | LINE69 | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S212/T1 |  | 0216 |  |  | 1-1B-00 |  |  | 670 | ON/OFF | 新營大寮二路 |  | aakb | B2/P01_A1 | [8 empty] | 新營PS.670_CB | 670(大寮二路) CB | LINE69 | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0217 |  |  | 1-1B-01 |  |  | 670 | 87A | 新營大寮二路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.670_87A | 大寮二路(670) 87RY | LINE69 | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0218 |  |  | 1-1B-02 |  |  | 670 | PHA | 新營大寮二路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.670_PHA | 大寮二路(670) 相間RY | LINE69 | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 670 | GDA | 新營大寮二路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.670_GDA | 大寮二路(670) 接地RY | LINE69 | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S211/T1 |  | 0220 |  |  | 1-1B-04 |  |  | 680 | ON/OFF | 新營大寮一路 |  | aalb | B2/P01_A1 | [8 empty] | 新營PS.680_CB | 680(大寮一路) CB | LINE69 | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0221 |  |  | 1-1B-05 |  |  | 680 | 87A | 新營大寮一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.680_87A | 大寮一路(680) 87RY | LINE69 | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 680 | PHA | 新營大寮一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.680_PHA | 大寮一路(680) 相間RY | LINE69 | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | 680 | GDA | 新營大寮一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.680_GDA | 大寮一路(680) 接地RY | LINE69 | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01TN16/T2 |  | 0224 |  |  | 1-1C-00 |  |  | 710 | ON/OFF | 新營東盟榮剛榮重線 |  | aamb | B2/P01_A1 | [8 empty] | 新營PS.710_CB | 710(東盟榮剛榮重線) CB | LINE69 | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 710 | 85A | 新營東盟榮剛榮重線 (沒設備) |  |  | B2/P01_A1 | [8 empty] | 新營PS.710_85A | 東盟榮剛榮重線(710) 85RY | LINE69 | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 1-1C-02 |  |  | 710 | PHA | 新營東盟榮剛榮重線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.710_PHA | 東盟榮剛榮重線(710) 相間RY | LINE69 | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0227 |  |  | 1-1C-03 |  |  | 710 | GDA | 新營東盟榮剛榮重線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.710_GDA | 東盟榮剛榮重線(710) 接地RY | LINE69 | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S432/T1 |  | 0228 |  |  | 1-1C-04 |  |  | 720 | ON/OFF | 新營學甲二路 CB |  | aaob | B2/P01_A1 | [8 empty] | 新營PS.720_CB | 720(新營學甲二路) CB | LINE69 | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 720 | 87A | 新營學甲二路 87A |  |  | B2/P01_A1 | [8 empty] | 新營PS.720_87A | 新營學甲二路(720) 87RY | LINE69 | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0230 |  |  | 1-1C-06 |  |  | 720 | PHA | 新營學甲二路 PHA |  |  | B2/P01_A1 | [8 empty] | 新營PS.720_PHA | 新營學甲二路(720) 相間RY | LINE69 | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 720 | GDA | 新營學甲二路 GDA |  |  | B2/P01_A1 | [8 empty] | 新營PS.720_GDA | 新營學甲二路(720) 接地RY | LINE69 | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S44/T1 |  | 0232 |  |  | 1-1D-00 |  |  | 730 | ON/OFF | 新營新西線 |  | aapb | B2/P01_A1 | [8 empty] | 新營PS.730_CB | 730(新西線) CB | LINE69 | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0233 |  |  | 1-1D-01 |  |  | 730 | 87A | 新營新西線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.730_87A | 新西線(730) 87RY | LINE69 | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | 730 | PHA | 新營新西線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.730_PHA | 新西線(730) 相間RY | LINE69 | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 730 | GDA | 新營新西線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.730_GDA | 新西線(730) 接地RY | LINE69 | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P01S431/T1 |  | 0236 |  |  | 1-1D-04 |  |  | 910 | ON/OFF | 新營學甲一路 |  | aaub | B2/P01_A1 | [8 empty] | 新營PS.910_CB | 910(新營學甲一路) CB | LINE69 | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 910 | 87A | 新營學甲一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.910_87A | 新營學甲一路(910) 87RY | LINE69 | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 910 | PHA | 新營學甲一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.910_PHA | 新營學甲一路(910) 相間RY | LINE69 | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0239 |  |  | 1-1D-07 |  |  | 910 | GDA | 新營學甲一路 |  |  | B2/P01_A1 | [8 empty] | 新營PS.910_GDA | 新營學甲一路(910) 接地RY | LINE69 | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/1SC |  | 0240 |  |  | 1-1E-00 |  |  | 810 | ON/OFF | 69KV #1SC |  | aarb | B2/P01_A1 | [8 empty] | 新營PS.810_CB | 810(69KV #1SC) CB | SC | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 810 | SCA | 69KV #1SC |  |  | B2/P01_A1 | [8 empty] | 新營PS.810_SCA | 69KV #1SC 51,51N RY | SC | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0242 |  |  | 1-1E-02 |  |  | 810 | UVA | 69KV #1SC |  |  | B2/P01_A1 | [8 empty] | 新營PS.810_OUVA | 69KV #1SC 27,59RY | SC | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/2SC |  | 0243 |  |  | 1-1E-03 |  |  | 820 | ON/OFF | 69KV #2SC |  | aasb | B2/P01_A1 | [8 empty] | 新營PS.820_CB | 820(69KV #2SC) CB | SC | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 820 | SCA | 69KV #2SC |  |  | B2/P01_A1 | [8 empty] | 新營PS.820_SCA | 69KV #2SC 51,51N RY | SC | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0245 |  |  | 1-1E-05 |  |  | 820 | UVA | 69KV #2SC |  |  | B2/P01_A1 | [8 empty] | 新營PS.820_OUVA | 69KV #2SC 27,59RY | SC | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/3SC |  | 0246 |  |  | 1-1E-06 |  |  | 830 | ON/OFF | 69KV #3SC |  | aatb | B2/P01_A1 | [8 empty] | 新營PS.830_CB | 830(69KV #3SC) CB | SC | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0247 |  |  | 1-1E-07 |  |  | 830 | SCA | 69KV #3SC |  |  | B2/P01_A1 | [8 empty] | 新營PS.830_SCA | 69KV #3SC 51,51N RY | SC | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0248 |  |  | 1-1F-00 |  |  | 830 | UVA | 69KV #3SC |  |  | B2/P01_A1 | [8 empty] | 新營PS.830_OUVA | 69KV #3SC 27,59RY | SC | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0249 |  |  | 1-1F-01 |  |  | 640 | 81A | 新營營糖線 |  |  | B2/P01_A1 | [8 empty] | 新營PS.640_81A/S | (640) 81RY A/S | LINE69 | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | 600 | #2PHA | 600 TIE #2 PHA |  |  | B2/P01_A1 | [8 empty] | 新營PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  |  | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0251 |  |  | 1-1F-03 |  |  | 600 | #2GDA | 600 TIE #2 GDA |  |  | B2/P01_A1 | [8 empty] | 新營PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/VC31/T1 |  |  | 0256 |  |  | 2-00-00 |  |  | VC31 | ON/OFF | F1 新11線 |  | aacb | B2/P01_D1 | [8 empty] | 新營PS.VC31_CB | VC31(新31線) CB | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | VC31 | PHA | F1 新11線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC31_PHA | 新31線(VC31) 相間RY | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | VC31 | GDA | F1 新11線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC31_GDA | 新31線(VC31) 接地RY | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/VC32/T1 |  |  | 0259 |  |  | 2-00-03 |  |  | VC32 | ON/OFF | F2 新12線 |  | aadb | B2/P01_D1 | [8 empty] | 新營PS.VC32_CB | VC32(新32線) CB | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | VC32 | PHA | F2 新12線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC32_PHA | 新32線(VC32) 相間RY | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0261 |  |  | 2-00-05 |  |  | VC32 | GDA | F2 新12線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC32_GDA | 新32線(VC32) 接地RY | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/VC33/T1 |  |  | 0262 |  |  | 2-00-06 |  |  | VC33 | ON/OFF | F3 新13線 |  | aafb | B2/P01_D1 | [8 empty] | 新營PS.VC33_CB | VC33(新33線) CB | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | VC33 | PHA | F3 新13線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC33_PHA | 新33線(VC33) 相間RY | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | VC33 | GDA | F3 新13線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC33_GDA | 新33線(VC33) 接地RY | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/VC34/T1 |  |  | 0265 |  |  | 2-01-01 |  |  | VC34 | ON/OFF | F4 新14線 |  | aagb | B2/P01_D1 | [8 empty] | 新營PS.VC34_CB | VC34(新34線) CB | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0266 |  |  | 2-01-02 |  |  | VC34 | PHA | F4 新14線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC34_PHA | 新34線(VC34) 相間RY | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | VC34 | GDA | F4 新14線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC34_GDA | 新34線(VC34) 接地RY | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/VC35/T1 |  |  | 0268 |  |  | 2-01-04 |  |  | VC35 | ON/OFF | F5 新15線 |  | aahb | B2/P01_D1 | [8 empty] | 新營PS.VC35_CB | VC35(新35線) CB | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | VC35 | PHA | F5 新15線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC35_PHA | 新35線(VC35) 相間RY | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | VC35 | GDA | F5 新15線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC35_GDA | 新35線(VC35) 接地RY | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/VC36/T1 |  |  | 0271 |  |  | 2-01-07 |  |  | VC36 | ON/OFF | F6 新16線 |  | aaib | B2/P01_D1 | [8 empty] | 新營PS.VC36_CB | VC36(新36線) CB | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | VC36 | PHA | F6 新16線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC36_PHA | 新36線(VC36) 相間RY | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 |  |  | 2-02-01 |  |  | VC36 | GDA | F6 新16線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC36_GDA | 新36線(VC36) 接地RY | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrH | B/2ABus | C/1SC |  |  | 0274 |  |  | 2-02-02 |  |  | 210 | ON/OFF | #1 SC 210 |  | aabb | B3/P01_A1 | [8 empty] | 新營PS.210_CB | 210(11KV #1SC) CB | SC | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | 210 | SCA | #1 SC 210 |  |  | B3/P01_A1 | [8 empty] | 新營PS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0276 |  |  | 2-02-04 |  |  | 210 | UVA | #1 SC 210 |  |  | B3/P01_A1 | [8 empty] | 新營PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrH | B/2ABus | C/2SC |  |  | 0277 |  |  | 2-02-05 |  |  | 220 | ON/OFF | #2 SC 220 |  | aajb | B3/P01_A1 | [8 empty] | 新營PS.220_CB | 220(11KV #2SC) CB | SC | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | 220 | SCA | #2 SC 220 |  |  | B3/P01_A1 | [8 empty] | 新營PS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0279 |  |  | 2-02-07 |  |  | 220 | UVA | #2 SC 220 |  |  | B3/P01_A1 | [8 empty] | 新營PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/2ABus | B/3ABus |  |  | 0280 |  |  | 2-03-00 |  |  | 100 | ON/OFF | #1TIE |  | aakb | B3/P01_A1 | [8 empty] | 新營PS.100_CB | 100(TIE) CB | TIE | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0281 |  |  | 2-03-01 |  |  | 100 | PHA | #1TIE |  |  | B3/P01_A1 | [8 empty] | 新營PS.100_51A | 11KV TIE(100) 51RY | TIE | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 100 | TIE(100) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | 100 | GDA | #1TIE |  |  | B3/P01_A1 | [8 empty] | 新營PS.100_51NA | 11KV TIE(100) 51N RY | TIE | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3ABus | L/VC37/T1 |  |  | 0283 |  |  | 2-03-03 |  |  | VC37 | ON/OFF | F7 新17線 |  | abab | B2/P01_D1 | [8 empty] | 新營PS.VC37_CB | VC37(新37線) CB | FEEDER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | VC37 | PHA | F7 新17線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC37_PHA | 新37線(VC37) 相間RY | FEEDER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | VC37 | GDA | F7 新17線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC37_GDA | 新37線(VC37) 接地RY | FEEDER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3ABus | L/VC38/T1 |  |  | 0286 |  |  | 2-03-06 |  |  | VC38 | ON/OFF | F8 新18線 |  | abbb | B2/P01_D1 | [8 empty] | 新營PS.VC38_CB | VC38(新38線) CB | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0287 |  |  | 2-03-07 |  |  | VC38 | PHA | F8 新18線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC38_PHA | 新38線(VC38) 相間RY | FEEDER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0288 |  |  | 2-04-00 |  |  | VC38 | GDA | F8 新18線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC38_GDA | 新38線(VC38) 接地RY | FEEDER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3ABus | L/VC39/T1 |  |  | 0289 |  |  | 2-04-01 |  |  | VC39 | ON/OFF | F9 新19線 |  | abcb | B2/P01_D1 | [8 empty] | 新營PS.VC39_CB | VC39(新39線) CB | FEEDER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0290 |  |  | 2-04-02 |  |  | VC39 | PHA | F9 新19線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC39_PHA | 新39線(VC39) 相間RY | FEEDER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0291 |  |  | 2-04-03 |  |  | VC39 | GDA | F9 新19線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC39_GDA | 新39線(VC39) 接地RY | FEEDER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3ABus | L/VC40/T1 |  |  | 0292 |  |  | 2-04-04 |  |  | VC40 | ON/OFF | F10 新20線 |  | abdb | B2/P01_D1 | [8 empty] | 新營PS.VC40_CB | VC40(新40線) CB | FEEDER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0293 |  |  | 2-04-05 |  |  | VC40 | PHA | F10 新20線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC40_PHA | 新40線(VC40) 相間RY | FEEDER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0294 |  |  | 2-04-06 |  |  | VC40 | GDA | F10 新20線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC40_GDA | 新40線(VC40) 接地RY | FEEDER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrH | B/3ABus | C/4SC |  |  | 0295 |  |  | 2-04-07 |  |  | 240 | ON/OFF | #4 SC 240 |  | abeb | B3/P01_A1 | [8 empty] | 新營PS.240_CB | 240(11KV #4SC) CB | SC | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0296 |  |  | 2-05-00 |  |  | 240 | SCA | #4 SC 240 |  |  | B3/P01_A1 | [8 empty] | 新營PS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0297 |  |  | 2-05-01 |  |  | 240 | UVA | #4 SC 240 |  |  | B3/P01_A1 | [8 empty] | 新營PS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/VC61/T1 |  |  | 0298 |  |  | 2-05-02 |  |  | VC61 | ON/OFF | F11 新61線 |  | baeb | B2/P01_D1 | [8 empty] | 新營PS.VC61_CB | VC61(新61線) CB | FEEDER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0299 |  |  | 2-05-03 |  |  | VC61 | PHA | F11 新61線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC61_PHA | 新61線(VC61) 相間RY | FEEDER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0300 |  |  | 2-05-04 |  |  | VC61 | GDA | F11 新61線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC61_GDA | 新61線(VC61) 接地RY | FEEDER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/VC62/T1 |  |  | 0301 |  |  | 2-05-05 |  |  | VC62 | ON/OFF | F12 新62線 |  | bafb | B2/P01_D1 | [8 empty] | 新營PS.VC62_CB | VC62(新62線) CB | FEEDER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0302 |  |  | 2-05-06 |  |  | VC62 | PHA | F12 新62線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC62_PHA | 新62線(VC62) 相間RY | FEEDER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0303 |  |  | 2-05-07 |  |  | VC62 | GDA | F12 新62線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC62_GDA | 新62線(VC62) 接地RY | FEEDER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/VC63/T1 |  |  | 0304 |  |  | 2-06-00 |  |  | VC63 | ON/OFF | F13 新63線 |  | bagb | B2/P01_D1 | [8 empty] | 新營PS.VC63_CB | VC63(新63線) CB | FEEDER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0305 |  |  | 2-06-01 |  |  | VC63 | PHA | F13 新63線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC63_PHA | 新63線(VC63) 相間RY | FEEDER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0306 |  |  | 2-06-02 |  |  | VC63 | GDA | F13 新63線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC63_GDA | 新63線(VC63) 接地RY | FEEDER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/VC64/T1 |  |  | 0307 |  |  | 2-06-03 |  |  | VC64 | ON/OFF | F14 新64線 |  | bahb | B2/P01_D1 | [8 empty] | 新營PS.VC64_CB | VC64(新64線) CB | FEEDER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0308 |  |  | 2-06-04 |  |  | VC64 | PHA | F14 新64線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC64_PHA | 新64線(VC64) 相間RY | FEEDER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0309 |  |  | 2-06-05 |  |  | VC64 | GDA | F14 新64線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC64_GDA | 新64線(VC64) 接地RY | FEEDER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrH | B/2BBus | C/3SC |  |  | 0310 |  |  | 2-06-06 |  |  | 230 | ON/OFF | #3 SC 230 |  | badb | B3/P01_A1 | [8 empty] | 新營PS.230_CB | 230(23KV #3SC) CB | SC | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0311 |  |  | 2-06-07 |  |  | 230 | SCA | #3 SC 230 |  |  | B3/P01_A1 | [8 empty] | 新營PS.230_SCA | 23KV #3SC 51,51N RY | SC | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0312 |  |  | 2-07-00 |  |  | 230 | UVA | #3 SC 230 |  |  | B3/P01_A1 | [8 empty] | 新營PS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/2BBus | B/3BBus |  |  | 0313 |  |  | 2-07-01 |  |  | 200 | ON/OFF | #2TIE |  | baib | B3/P01_A1 | [8 empty] | 新營PS.200_CB | 200(TIE) CB | TIE | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0314 |  |  | 2-07-02 |  |  | 200 | PHA | #2TIE |  |  | B3/P01_A1 | [8 empty] | 新營PS.200_51A | 23KV TIE(200) 51RY | TIE | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 200 | TIE(200) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0315 |  |  | 2-07-03 |  |  | 200 | GDA | #2TIE |  |  | B3/P01_A1 | [8 empty] | 新營PS.200_51NA | 23KV TIE(200) 51N RY | TIE | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | L/VC65/T1 |  |  | 0316 |  |  | 2-07-04 |  |  | VC65 | ON/OFF | F15 新65線 |  | bbbb | B2/P01_D1 | [8 empty] | 新營PS.VC65_CB | VC65(新65線) CB | FEEDER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0317 |  |  | 2-07-05 |  |  | VC65 | PHA | F15 新65線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC65_PHA | 新65線(VC65) 相間RY | FEEDER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0318 |  |  | 2-07-06 |  |  | VC65 | GDA | F15 新65線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC65_GDA | 新65線(VC65) 接地RY | FEEDER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | L/VC66/T1 |  |  | 0319 |  |  | 2-07-07 |  |  | VC66 | ON/OFF | F16 新66線 |  | bbcb | B2/P01_D1 | [8 empty] | 新營PS.VC66_CB | VC66(新66線) CB | FEEDER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0320 |  |  | 2-08-00 |  |  | VC66 | PHA | F16 新66線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC66_PHA | 新66線(VC66) 相間RY | FEEDER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0321 |  |  | 2-08-01 |  |  | VC66 | GDA | F16 新66線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC66_GDA | 新66線(VC66) 接地RY | FEEDER | [5 empty] | 582 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | L/VC67/T1 |  |  | 0322 |  |  | 2-08-02 |  |  | VC67 | ON/OFF | F17 新67線 |  | bbdb | B2/P01_D1 | [8 empty] | 新營PS.VC67_CB | VC67(新67線) CB | FEEDER | [5 empty] | 583 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0323 |  |  | 2-08-03 |  |  | VC67 | PHA | F17 新67線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC67_PHA | 新67線(VC67) 相間RY | FEEDER | [5 empty] | 584 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0324 |  |  | 2-08-04 |  |  | VC67 | GDA | F17 新67線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC67_GDA | 新67線(VC67) 接地RY | FEEDER | [5 empty] | 585 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | L/VC68/T1 |  |  | 0325 |  |  | 2-08-05 |  |  | VC68 | ON/OFF | F18 新68線 |  | bbeb | B2/P01_D1 | [8 empty] | 新營PS.VC68_CB | VC68(新68線) CB | FEEDER | [5 empty] | 586 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0326 |  |  | 2-08-06 |  |  | VC68 | PHA | F18 新68線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC68_PHA | 新68線(VC68) 相間RY | FEEDER | [5 empty] | 587 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0327 |  |  | 2-08-07 |  |  | VC68 | GDA | F18 新68線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC68_GDA | 新68線(VC68) 接地RY | FEEDER | [5 empty] | 588 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | L/VC69/T1 |  |  | 0328 |  |  | 2-09-00 |  |  | VC69 | ON/OFF | F19 新69線 |  | bbgb | B2/P01_D1 | [8 empty] | 新營PS.VC69_CB | VC69(新69線) CB | FEEDER | [5 empty] | 589 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0329 |  |  | 2-09-01 |  |  | VC69 | PHA | F19 新69線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC69_PHA | 新69線(VC69) 相間RY | FEEDER | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0330 |  |  | 2-09-02 |  |  | VC69 | GDA | F19 新69線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC69_GDA | 新69線(VC69) 接地RY | FEEDER | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/3BBus | L/VC70/T1 |  |  | 0331 |  |  | 2-09-03 |  |  | VC70 | ON/OFF | F20 新70線 |  | bbhb | B2/P01_D1 | [8 empty] | 新營PS.VC70_CB | VC70(新70線) CB | FEEDER | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0332 |  |  | 2-09-04 |  |  | VC70 | PHA | F20 新70線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC70_PHA | 新70線(VC70) 相間RY | FEEDER | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0333 |  |  | 2-09-05 |  |  | VC70 | GDA | F20 新70線 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC70_GDA | 新70線(VC70) 接地RY | FEEDER | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrH | B/3BBus | C/5SC |  |  | 0334 |  |  | 2-09-06 |  |  | 250 | ON/OFF | #5 SC 250 |  | bbab | B3/P01_A1 | [8 empty] | 新營PS.250_CB | 250(23KV #5SC) CB | SC | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0335 |  |  | 2-09-07 |  |  | 250 | SCA | #5 SC 250 |  |  | B3/P01_A1 | [8 empty] | 新營PS.250_SCA | 23KV #5SC 51,51N RY | SC | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0336 |  |  | 2-0A-00 |  |  | 250 | UVA | #5 SC 250 |  |  | B3/P01_A1 | [8 empty] | 新營PS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrH | B/3BBus | C/6SC |  |  | 0337 |  |  | 2-0A-01 |  |  | 260 | ON/OFF | #6 SC 260 |  | bbib | B3/P01_A1 | [8 empty] | 新營PS.260_CB | 260(23KV #6SC) CB | SC | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0338 |  |  | 2-0A-02 |  |  | 260 | SCA | #6 SC 260 |  |  | B3/P01_A1 | [8 empty] | 新營PS.260_SCA | 23KV #6SC 51,51N RY | SC | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0339 |  |  | 2-0A-03 |  |  | 260 | UVA | #6 SC 260 |  |  | B3/P01_A1 | [8 empty] | 新營PS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  |  | 1-30-00 |  |  | TEST CB |  | ON/OFF |  |  | ELEM/ALL | [8 empty] | 新營PS.TEST_CB | TEST CB | OTHER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | RTU | L/S | LOCAL/REMOTE(SUPY) |  |  | ELEM/P01_A1 | [8 empty] | 新營PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
P01 | 新營PS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 1-30-02 |  |  | #1MTR | 遙控/現場 | #1MTR S/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 1MTR | #1MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0771 |  |  | 1-30-03 |  |  | #1MTR | A/M | #1MTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0772 |  |  | 1-30-04 |  |  | #1MTR | TRA | #1MTR 重故障 |  | a | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_TRA | #1MTR 重故障 | MTR | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0773 |  |  | 1-30-05 |  |  | #1MTR | TRF | #1MTR 輕故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_TRF | #1MTR 輕故障 | MTR | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 1-30-06 |  |  | #2MTR | 遙控/現場 | #2MTR S/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 2MTR | #2MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0775 |  |  | 1-30-07 |  |  | #2MTR | A/M | #2MTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0776 |  |  | 1-30-08 |  |  | #2MTR | TRA | #2MTR 重故障 |  | a | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_TRA | #2MTR 重故障 | MTR | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0777 |  |  | 1-30-09 |  |  | #2MTR | TRF | #2MTR 輕故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_TRF | #2MTR 輕故障 | MTR | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0778 |  |  | 1-30-10 |  |  | #3MTR | 遙控/現場 | #3MTR S/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 3MTR | #3MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0779 |  |  | 1-30-11 |  |  | #3MTR | A/M | #3MTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0780 |  |  | 1-30-12 |  |  | #3MTR | TRA | #3MTR 重故障 |  | a | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_TRA | #3MTR 重故障 | MTR | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0781 |  |  | 1-30-13 |  |  | #3MTR | TRF | #3MTR 輕故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_TRF | #3MTR 輕故障 | MTR | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0786 |  |  | 1-31-02 |  |  | #2ADTR | 遙控/現場 | #2ADTR S/L |  | c | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0787 |  |  | 1-31-03 |  |  | #2ADTR | A/M | #2ADTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0788 |  |  | 1-31-04 |  |  | #2BDTR | 遙控/現場 | #2BDTR S/L |  | b | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0789 |  |  | 1-31-05 |  |  | #2BDTR | A/M | #2BDTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0790 |  |  | 1-31-06 |  |  | #2DTR | TRA | #2DTR 重故障 |  | a | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0791 |  |  | 1-31-07 |  |  | #2DTR | TRF | #2DTR 輕故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0792 |  |  | 1-31-08 |  |  | #3ADTR | 遙控/現場 | #3ADTR S/L |  | c | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0793 |  |  | 1-31-09 |  |  | #3ADTR | A/M | #3ADTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0794 |  |  | 1-31-10 |  |  | #3BDTR | 遙控/現場 | #3BDTR S/L |  | b | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0795 |  |  | 1-31-11 |  |  | #3BDTR | A/M | #3BDTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0796 |  |  | 1-31-12 |  |  | #3DTR | TRA | #3DTR 重故障 |  | a | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0797 |  |  | 1-31-13 |  |  | #3DTR | TRF | #3DTR 輕故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0798 |  |  | 1-31-14 |  |  | #1 BUS | ON/OFF | 161KV #1 BUS╴87UL |  |  | B2/P01_A1 | [8 empty] | 新營PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0799 |  |  | 1-31-15 |  |  | #2 BUS | ON/OFF | 161KV #2 BUS╴87UL |  |  | B2/P01_A1 | [8 empty] | 新營PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0800 |  |  | 1-32-00 |  |  | #1MTR | USE/LOCK | 1MTR #1 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0801 |  |  | 1-32-01 |  |  | #2MTR | USE/LOCK | 2MTR #1 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | [5 empty] | 630 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0802 |  |  | 1-32-02 |  |  | #3MTR | USE/LOCK | 3MTR #1 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | [5 empty] | 631 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0804 |  |  | 1-32-04 |  |  | #2DTR | USE/LOCK | 2DTR #1 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | [5 empty] | 632 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0805 |  |  | 1-32-05 |  |  | #3DTR | USE/LOCK | 3DTR #1 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | [5 empty] | 633 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | OilLeak | 集油池抽水泵警報 | Element | Status | 洩油池水位警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0806 |  |  | 1-32-06 |  |  | DTR OWF | ON/OFF | DTR MTR OWF 集油抽水泵閉鎖 |  |  | B3/P01_A1 | [8 empty] | 新營PS.集油池警報 | DTR,MTR集油池警報 | OTHER | [5 empty] | 634 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0808 |  |  | 1-32-08 |  |  | 161KV | ON/OFF | 161KV COMT 空壓機超時 |  |  | B3/P01_A1 | [8 empty] | 新營PS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0809 |  |  | 1-32-09 |  |  | 161KV | CBA | 161KV CB 重故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0810 |  |  | 1-32-10 |  |  | 161KV | CBF | 161KV CB 輕故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 637 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0812 |  |  | 1-32-12 |  |  | 161KV | VUA | 161KV #1BUS 電壓電驛 |  |  | B2/P01_A1 | [8 empty] | 新營PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 638 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0813 |  |  | 1-32-13 |  |  | 161KV | VUA | 161KV #2BUS 電壓電驛 |  |  | B2/P01_A1 | [8 empty] | 新營PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 639 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0814 |  |  | 1-32-14 |  |  | 1540 | ON/OFF | 1540新營柳營海線RAOA(87L通訊故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1540_87CFA | 新營柳營海線(1540)87RY通訊故障 | OTHER | [5 empty] | 640 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0815 |  |  | 1-32-15 |  |  | 1530 | ON/OFF | 1530新營柳營山線RAOA(87L通訊故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1530_87CFA | 新營柳營山線(1530)87RY通訊故障 | OTHER | [5 empty] | 641 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 1-33-00 |  |  | 1560 | ON/OFF | 1560嘉義新營山上分歧白線87CFA (87L通訊故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_87CFA | 嘉義山上白線(1560)87RY通訊故障 | OTHER | [5 empty] | 642 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 1-33-01 |  |  | 1550 | ON/OFF | 1550嘉義新營山上分歧紅線87CFA (87L通訊故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1550_87CFA | 嘉義山上紅線(1550)87RY通訊故障 | OTHER | [5 empty] | 643 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 1-33-02 |  |  | 1530 | ON/OFF | 1530新營柳營山線87LA |  |  | B2/P01_A1 | [8 empty] | 新營PS.1530_RYFA | 新營柳營山線(1530)數位電驛故障 | OTHER | [5 empty] | 644 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0819 |  |  | 1-33-03 |  |  | 1540 | ON/OFF | 1540新營柳營海線87LA |  |  | B2/P01_A1 | [8 empty] | 新營PS.1540_RYFA | 新營柳營海線(1540)數位電驛故障 | OTHER | [5 empty] | 645 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0820 |  |  | 1-33-04 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_OSCF | 161KV示波器缺紙或故障警報 | OTHER | [5 empty] | 646 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 1-33-05 |  |  | 161KV | OPA | OPA 充油式電纜警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 647 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 1-33-06 |  |  | CHG2 | ON/OFF | 通訊充電機故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 1-33-07 |  |  | ACFA | ON/OFF | ACFA 通訊設備AC故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 1-33-11 |  |  | STUV | ON/OFF | 所內電源欠壓警報 |  |  | ELEM/P01_A1 | [8 empty] | 新營PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0828 |  |  | 1-33-12 |  |  | 1550 | ON/OFF | 1550嘉義新營山上分歧紅線RYFA(電驛故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1550_RYFA | 嘉義山上紅線(1550)數位電驛故障 | OTHER | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | UPSA |  |  | Status | UPS故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0829 |  |  | 1-33-13 |  |  | AD大樓 | A/N | AD大樓UPS警報 UPSA |  |  | B3/P01_A1 | [8 empty] | 新營PS.UPSA | ADCC大樓UPS警報 | OTHER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0830 |  |  | 1-33-14 |  |  | 1560 | ON/OFF | 1560嘉義新營山上白線RYFA(電驛故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_RYFA | 嘉義山上白線(1560)數位電驛故障 | OTHER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0831 |  |  | 1-33-15 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/P01_A1 | [8 empty] | 新營PS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場照明(A) |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0832 |  |  | 1-34-00 |  |  | FLA1 | ON/OFF | FLA1 無人化開關照明 |  |  | B3/P01_A1 | [8 empty] | 新營PS.開關場照明(A) | 開關場照明(A) | OTHER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場照明(B) |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0833 |  |  | 1-34-01 |  |  | FLA2 | ON/OFF | FLA2 無人化開關照明 |  |  | B3/P01_A1 | [8 empty] | 新營PS.開關場照明(B) | 開關場照明(B) | OTHER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Lights3 | 開關場照明(C) |  | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0834 |  |  | 1-34-02 |  |  | FLB1 | ON/OFF | FLB1 無人化開關照明 |  |  | B3/P01_A1 | [8 empty] | 新營PS.開關場照明(C) | 開關場照明(C) | OTHER | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Lights4 | 開關場照明(D) |  | Status | 照明4 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0835 |  |  | 1-34-03 |  |  | FLB2 | ON/OFF | FLB2 無人化開關照明 |  |  | B3/P01_A1 | [8 empty] | 新營PS.開關場照明(D) | 開關場照明(D) | OTHER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Lights5 | 開關場照明(E) | Element | Status | 照明5 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0836 |  |  | 1-34-04 |  |  | FLC1 | ON/OFF | FLC1 無人化開關照明 |  |  | B3/P01_A1 | [8 empty] | 新營PS.開關場照明(E) | 開關場照明(E) | OTHER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Lights6 | 開關場照明(F) | Element | [12 empty] | 0837 |  |  | 1-34-05 |  |  | FLC2 | ON/OFF | FLC2 無人化開關照明 |  |  | B3/P01_A1 | [8 empty] | 新營PS.開關場照明(F) | 開關場照明(F) | OTHER | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [19 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Fire2 | ADCC大樓 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0838 |  |  | 1-34-06 |  |  | 火災警報(2) | ON/OFF | 火災警報(2)建物-ADCC大樓 |  |  | B3/P01_A1 | [8 empty] | 新營PS.火災警報(2) | 火災警報(2)建物-ADCC大樓 | OTHER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Fire4 | 主(配)變壓器 |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0839 |  |  | 1-34-07 |  |  | 火災警報(4) | ON/OFF | 火災警報(4)-主(配)變壓器 |  |  | B3/P01_A1 | [8 empty] | 新營PS.火災警報(4) | 火災警報(4)-主(配)變壓器 | OTHER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0841 |  |  | 1-34-09 |  |  | #2MTR | RYFA | 2MTR 數位電驛故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0842 |  |  | 1-34-10 |  |  | #2MTR | USE/LOCK | 2MTR #2 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0843 |  |  | 1-34-11 |  |  | #2MTR | USE/LOCK | 2MTR 51Z RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 1MTR | #1MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0844 |  |  | 1-34-12 |  |  | #1MTR | RYFA | 1MTR 數位電驛故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 1-34-13 |  |  | #1MTR | USE/LOCK | 1MTR #2 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0846 |  |  | 1-34-14 |  |  | #1MTR | USE/LOCK | 1MTR 51Z RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0847 |  |  | 1-34-15 |  |  | SC 60RY | ON/OFF | 11KV SC 60A |  |  | B3/P01_A1 | [8 empty] | 新營PS.11KV_SC_60A | 11KV電容器組 60RY | OTHER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0848 |  |  | 1-35-00 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0849 |  |  | 1-35-01 |  |  | #1MTR | ON/OFF | #1MTR 96P |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_96P | #1MTR 96P RY | MTR | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0850 |  |  | 1-35-02 |  |  | #1MTR | ON/OFF | #1MTR 96D |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_96D | #1MTR 96D RY | MTR | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0851 |  |  | 1-35-03 |  |  | #1MTR | ON/OFF | #1MTR 96B1 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0852 |  |  | 1-35-04 |  |  | #1MTR | ON/OFF | #1MTR 96B2 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_96B2 | #1MTR 96B2 RY | MTR | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 1MTR | #1MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0853 |  |  | 1-35-05 |  |  | #1MTR | ON/OFF | #1MTR 63Q |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_63Q | #1MTR 63Q RY | MTR | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0854 |  |  | 1-35-06 |  |  | #2MTR | ON/OFF | #2MTR 96P |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_96P | #2MTR 96P RY | MTR | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0855 |  |  | 1-35-07 |  |  | #2MTR | ON/OFF | #2MTR 96D |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_96D | #2MTR 96D RY | MTR | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 1-35-08 |  |  | #2MTR | ON/OFF | #2MTR 96B1 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0857 |  |  | 1-35-09 |  |  | #2MTR | ON/OFF | #2MTR 96B2 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2MTR | #2MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0858 |  |  | 1-35-10 |  |  | #2MTR | ON/OFF | #2MTR 63Q |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_63Q | #2MTR 63Q RY | MTR | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0859 |  |  | 0-35-11 |  |  | #3MTR | ON/OFF | #3MTR 96P |  |  | B1/P01_A1 | [16 empty] | 681 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0860 |  |  | 1-35-12 |  |  | #3MTR | ON/OFF | #3MTR 96D |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_96D | #3MTR 96D RY | MTR | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0861 |  |  | 1-35-13 |  |  | #3MTR | ON/OFF | #3MTR 96B1 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0862 |  |  | 1-35-14 |  |  | #3MTR | ON/OFF | #3MTR 96B2 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_96B2 | #3MTR 96B2 RY | MTR | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0863 |  |  | 1-35-15 |  |  | #3MTR | ON/OFF | #3MTR 63Q |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_63Q | #3MTR 63Q RY | MTR | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0869 |  |  | 1-36-05 |  |  | #2DTR | ON/OFF | #2DTR 96P |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0870 |  |  | 1-36-06 |  |  | #2DTR | ON/OFF | #2DTR 96D |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 1-36-07 |  |  | #2DTR | ON/OFF | #2DTR 96B1 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0872 |  |  | 1-36-08 |  |  | #2DTR | ON/OFF | #2DTR 96B2 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0873 |  |  | 1-36-09 |  |  | #2DTR | ON/OFF | #2DTR 63Q |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0874 |  |  | 1-36-10 |  |  | #3DTR | ON/OFF | #3DTR 96P |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0875 |  |  | 1-36-11 |  |  | #3DTR | ON/OFF | #3DTR 96D |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0876 |  |  | 1-36-12 |  |  | #3DTR | ON/OFF | #3DTR 96B1 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0877 |  |  | 1-36-13 |  |  | #3DTR | ON/OFF | #3DTR 96B2 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0878 |  |  | 1-36-14 |  |  | #3DTR | ON/OFF | #3DTR 63Q |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0879 |  |  | 1-36-15 |  |  | 地下室 | A/N | 地下室水位第一段警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0880 |  |  | 1-37-00 |  |  | 地下室 | A/N | 地下室水位第二段警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0881 |  |  | 1-37-01 |  |  | 720 | USE/LOCK | 新營學甲二路 720 87 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.720_87UL | 新營學甲二路(720) 87RY U/L | LINE69 | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 1-37-02 |  |  | 720 | 87CFA | 新營學甲二路 720 87 Ry通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.720_87CFA | 新營學甲二路(720)87RY通訊故障 | OTHER | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 1-37-03 |  |  | 720 | RYFA | 新營學甲二路 720 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.720_RYFA | 新營學甲二路(720)數位電驛故障 | OTHER | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 1-37-04 |  |  | 600 | RYFA | 69KV TIE 600數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0885 |  |  | 1-37-05 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | ComPoint |  |  | 12B_CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0886 |  |  | 1-37-06 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0887 |  |  | 1-37-07 |  |  | BUS | A/N | 69KV BUS數位電驛故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | 12B_CTFA |  | Element | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0888 |  |  | 1-37-08 |  |  | BUS | A/N | 69KV BUS 87RY CT 迴路故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 1-37-09 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 1-37-10 |  |  | #4MTR | 遙控/現場 | #4MTR S/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_S/L | #4MTR OLTC S/L | MTR | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS |  |  | 4MTR | #4MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0891 |  |  | 1-37-11 |  |  | #4MTR | A/M | #4MTR OLTC A/M |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_A/M | #4MTR OLTC A/M | MTR | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P01 | 新營PS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0892 |  |  | 1-37-12 |  |  | #4MTR | TRA | #4MTR 重故障 |  | a | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_TRA | #4MTR 重故障 | MTR | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0893 |  |  | 1-37-13 |  |  | #4MTR | TRF | #4MTR 輕故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_TRF | #4MTR 輕故障 | MTR | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0894 | 895 |  | 1-37-14 | 1-37-15 |  | #4MTR | M/I | #4MTR M/I |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_M/F/I | #4MTR M/F/I | MTR | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS |  |  | 1MTR | #1MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0896 | 897 |  | 1-38-00 | 1-38-01 |  | #1MTR | M/I | #1MTR M/I |  |  | B1/P01_A1 | [8 empty] | 新營PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS |  |  | 2MTR | #2MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0898 | 899 |  | 1-38-02 | 1-38-03 |  | #2MTR | M/I | #2MTR M/I |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS |  |  | 3MTR | #3MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0900 | 901 |  | 1-38-04 | 1-38-05 |  | #3MTR | M/I | #3MTR M/I |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | DS1 | 1541 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0910 | 911 |  | 1-38-14 | 1-38-15 |  | 1541 | ON | 新營柳營海線 1541ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1541_DS | 1541(新營柳營海線) DS | LINE161 | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | DS2 | 1542 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0912 | 913 |  | 1-39-00 | 1-39-01 |  | 1542 | ON | 新營柳營海線 1542ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1542_DS | 1542(新營柳營海線) DS | LINE161 | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | DS3 | 1543 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0914 | 915 |  | 1-39-02 | 1-39-03 |  | 1543 | ON | 新營柳營海線 1543ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1543_DS | 1543(新營柳營海線) DS | LINE161 | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | ES3 | 1543E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0916 | 917 |  | 1-39-04 | 1-39-05 |  | 1543E | ON | 新營柳營海線 1543EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1543E_ES | 1543E(新營柳營海線) ES | LINE161 | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | DS1 | 1531 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0918 | 919 |  | 1-39-06 | 1-39-07 |  | 1531 | ON | 新營柳營山線1531ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1531_DS | 1531(新營柳營山線) DS | LINE161 | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | DS2 | 1532 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0920 | 921 |  | 1-39-08 | 1-39-09 |  | 1532 | ON | 新營柳營山線1532ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1532_DS | 1532(新營柳營山線) DS | LINE161 | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | DS3 | 1533 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0922 | 923 |  | 1-39-10 | 1-39-11 |  | 1533 | ON | 新營柳營山線1533ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1533_DS | 1533(新營柳營山線) DS | LINE161 | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0924 | 925 |  | 1-39-12 | 1-39-13 |  | 1533E | ON | 新營柳營山線1533EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1533E_ES | 1533E(新營柳營山線) ES | LINE161 | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0926 | 927 |  | 1-39-14 | 1-39-15 |  | 1551 | ON | 嘉義新營山上分歧紅線1551ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1551_DS | 1551(嘉義山上紅線) DS | LINE161 | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0928 | 929 |  | 1-3A-00 | 1-3A-01 |  | 1552 | ON | 嘉義新營山上分歧紅線1552ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1552_DS | 1552(嘉義山上紅線) DS | LINE161 | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0930 | 931 |  | 1-3A-02 | 1-3A-03 |  | 1553 | ON | 嘉義新營山上分歧紅線1553ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1553_DS | 1553(嘉義山上紅線) DS | LINE161 | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0932 | 933 |  | 1-3A-04 | 1-3A-05 |  | 1553E | ON | 嘉義新營山上分歧紅線1553EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1553E_ES | 1553E(嘉義山上紅線) ES | LINE161 | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | DS1 | 1561 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0934 | 935 |  | 1-3A-06 | 1-3A-07 |  | 1561 | ON | 嘉義新營山上白線1561 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1561_DS | 1561(嘉義山上白線) DS | LINE161 | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | DS2 | 1562 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0936 | 937 |  | 1-3A-08 | 1-3A-09 |  | 1562 | ON | 嘉義新營山上白線1562 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1562_DS | 1562(嘉義山上白線) DS | LINE161 | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | DS3 | 1563 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0938 | 939 |  | 1-3A-10 | 1-3A-11 |  | 1563 | ON | 嘉義新營山上白線1563 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1563_DS | 1563(嘉義山上白線) DS | LINE161 | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0940 | 941 |  | 1-3A-12 | 1-3A-13 |  | 1563E | ON | 嘉義新營山上白線1563E ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1563E_ES | 1563E(嘉義山上白線) ES | LINE161 | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | DS1 | 1571 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0942 | 943 |  | 1-3A-14 | 1-3A-15 |  | 1571 | ON | 新營下營一路1571 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1571_DS | 1571(新營下營一路) DS | LINE161 | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | DS2 | 1572 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0944 | 945 |  | 1-3B-00 | 1-3B-01 |  | 1572 | ON | 新營下營一路1572 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1572_DS | 1572(新營下營一路) DS | LINE161 | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | DS3 | 1573 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0946 | 947 |  | 1-3B-02 | 1-3B-03 |  | 1573 | ON | 新營下營一路1573 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1573_DS | 1573(新營下營一路) DS | LINE161 | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0948 | 949 |  | 1-3B-04 | 1-3B-05 |  | 1573E | ON | 新營下營一路1573E ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1573E_ES | 1573E(新營下營一路) ES | LINE161 | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | DS1 | 1581 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0950 | 951 |  | 1-3B-06 | 1-3B-07 |  | 1581 | ON | 新營下營二路1581 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1581_DS | 1581(新營下營二路) DS | LINE161 | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | DS2 | 1582 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0952 | 953 |  | 1-3B-08 | 1-3B-09 |  | 1582 | ON | 新營下營二路1582 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1582_DS | 1582(新營下營二路) DS | LINE161 | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | DS3 | 1583 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0954 | 955 |  | 1-3B-10 | 1-3B-11 |  | 1583 | ON | 新營下營二路1583 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1583_DS | 1583(新營下營二路) DS | LINE161 | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0956 | 957 |  | 1-3B-12 | 1-3B-13 |  | 1583E | ON | 新營下營二路1583E ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1583E_ES | 1583E(新營下營二路) ES | LINE161 | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | DS1 | 1521 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0958 | 959 |  | 1-3B-14 | 1-3B-15 |  | 1521 | ON | 新營華卡線1521 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1521_DS | 1521(華卡線) DS | LINE161 | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | DS2 | 1522 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 961 |  | 1-3C-00 | 1-3C-01 |  | 1522 | ON | 新營華卡線1522 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1522_DS | 1522(華卡線) DS | LINE161 | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | DS3 | 1523 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 963 |  | 1-3C-02 | 1-3C-03 |  | 1523 | ON | 新營華卡線1523 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1523_DS | 1523(華卡線) DS | LINE161 | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0964 | 965 |  | 1-3C-04 | 1-3C-05 |  | 1523E | ON | 新營華卡線1523E ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1523E_ES | 1523E(華卡線) ES | LINE161 | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0974 | 975 |  | 1-3C-14 | 1-3C-15 |  | 1501 | ON | 161KV TIE 1501 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 977 |  | 1-3D-00 | 1-3D-01 |  | 1502 | ON | 161KV TIE 1502ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 979 |  | 1-3D-02 | 1-3D-03 |  | 1651 | ON | #1MTR 1651 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1651_DS | 1651(#1MTR) DS | MTR | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 981 |  | 1-3D-04 | 1-3D-05 |  | 1652 | ON | #1MTR 1652 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1652_DS | 1652(#1MTR) DS | MTR | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 983 |  | 1-3D-06 | 1-3D-07 |  | 1661 | ON | #2MTR 1661 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1661_DS | 1661(#2MTR) DS | MTR | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0984 | 985 |  | 1-3D-08 | 1-3D-09 |  | 1662 | ON | #2MTR 1662 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1662_DS | 1662(#2MTR) DS | MTR | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | DS1 | 1671 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0986 | 987 |  | 1-3D-10 | 1-3D-11 |  | 1671 | ON | #3MTR 1671 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1671_DS | 1671(#3MTR) DS | MTR | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | DS2 | 1672 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0988 | 989 |  | 1-3D-12 | 1-3D-13 |  | 1672 | ON | #3MTR 1672 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1672_DS | 1672(#3MTR) DS | MTR | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | DS1 | 1681 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0990 | 991 |  | 1-3D-14 | 1-3D-15 |  | 1681 | ON | #4MTR 1681 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1681_DS | 1681(#4MTR) DS | MTR | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | DS2 | 1682 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 993 |  | 1-3E-00 | 1-3E-01 |  | 1682 | ON | #4MTR 1682 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1682_DS | 1682(#4MTR) DS | MTR | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 995 |  | 1-3E-02 | 1-3E-03 |  | 1761 | ON | #2DTR 1761 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0996 | 997 |  | 1-3E-04 | 1-3E-05 |  | 1762 | ON | #2DTR 1762 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0998 | 999 |  | 1-3E-06 | 1-3E-07 |  | 1771 | ON | #3DTR 1771 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 |  | 1-3E-08 | 1-3E-09 |  | 1772 | ON | #3DTR 1772 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1002 | 1003 |  | 1-3E-10 | 1-3E-11 |  | 751 | ON | #1MTR 751 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.751_DS | 751(#1MTR) DS | MTR | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 |  | 1-3E-12 | 1-3E-13 |  | 752 | ON | #1MTR 752 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.752_DS | 752(#1MTR) DS | MTR | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1006 | 1007 |  | 1-3E-14 | 1-3E-15 |  | 761 | ON | #2MTR 761 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.761_DS | 761(#2MTR) DS | MTR | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1008 | 1009 |  | 1-3F-00 | 1-3F-01 |  | 762 | ON | #2MTR 762 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.762_DS | 762(#2MTR) DS | MTR | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1010 | 1011 |  | 1-3F-02 | 1-3F-03 |  | 771 | ON | #3MTR 771 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.771_DS | 771(#3MTR) DS | MTR | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1012 | 1013 |  | 1-3F-04 | 1-3F-05 |  | 772 | ON | #3MTR 772 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.772_DS | 772(#3MTR) DS | MTR | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1014 |  |  | 1-3F-06 |  |  | 1570 | A/N | 新營下營一路 1570 87CFA(87L通訊故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_87CFA | 新營下營一路(1570)87RY通訊故障 | OTHER | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1015 |  |  | 1-3F-07 |  |  | 1570 | A/N | 新營下營一路 1570 RYFA(電驛故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_RYFA | 新營下營一路(1570)數位電驛故障 | OTHER | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1016 |  |  | 1-3F-08 |  |  | 1580 | A/N | 新營下營二路 1580 87CFA(87L通訊故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_87CFA | 新營下營二路(1580)87RY通訊故障 | OTHER | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1017 |  |  | 1-3F-09 |  |  | 1580 | A/N | 新營下營二路 1580 RYFA(電驛故障) |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_RYFA | 新營下營二路(1580)數位電驛故障 | OTHER | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1018 |  |  | 1-3F-10 |  |  | 620 | 87CFA | 新營新東線(620) 87Ry通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.620_87CFA | 新營新東線(620)87RY通訊故障 | OTHER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1019 |  |  | 1-3F-11 |  |  | 620 | RYFA | 新營新東線(620) 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.620_RYFA | 新營新東線(620)數位電驛故障 | OTHER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1020 |  |  | 1-3F-12 |  |  | 730 | 87CFA | 新營新西線(730) 87Ry通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.730_87CFA | 新營新西線(730)87RY通訊故障 | OTHER | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1021 |  |  | 1-3F-13 |  |  | 730 | RYFA | 新營新西線(730) 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.730_RYFA | 新營新西線(730)數位電驛故障 | OTHER | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1022 |  |  | 1-3F-14 |  |  | 1520 | RYFA | 新營華卡線(1520) 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.1520_RYFA | 華卡線(1520)數位電驛故障 | OTHER | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | DS1 | 611 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1024 | 1025 |  | 2-30-00 | 2-30-01 |  | 611 | ON | 新營官田一路 611 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.611_DS | 611(備用線) DS | LINE69 | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | DS2 | 612 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1026 | 1027 |  | 2-30-02 | 2-30-03 |  | 612 | ON | 新營官田一路 612 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.612_DS | 612(備用線) DS | LINE69 | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | DS3 | 613 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1028 | 1029 |  | 2-30-04 | 2-30-05 |  | 613 | ON | 新營官田一路 613 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.613_DS | 613(備用線) DS | LINE69 | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | ES3 | 613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1030 | 1031 |  | 2-30-06 | 2-30-07 |  | 613E | ON | 新營官田一路 613 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.613E_ES | 613E(備用線) ES | LINE69 | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | DS1 | 621 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1032 | 1033 |  | 2-30-08 | 2-30-09 |  | 621 | ON | 新營新東線 621 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.621_DS | 621(新營新東線) DS | LINE69 | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | DS2 | 622 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1034 | 1035 |  | 2-30-10 | 2-30-11 |  | 622 | ON | 新營新東線 622 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.622_DS | 622(新營新東線) DS | LINE69 | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | DS3 | 623 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1036 | 1037 |  | 2-30-12 | 2-30-13 |  | 623 | ON | 新營新東線 623 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.623_DS | 623(新營新東線) DS | LINE69 | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | ES3 | 623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1038 | 1039 |  | 2-30-14 | 2-30-15 |  | 623E | ON | 新營新東線 623 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.623E_ES | 623E(新營新東線) ES | LINE69 | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | DS1 | 631 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1040 | 1041 |  | 2-31-00 | 2-31-01 |  | 631 | ON | 新營白河水上線 631 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.631_DS | 631(新營白河水上線) DS | LINE69 | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | DS2 | 632 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1042 | 1043 |  | 2-31-02 | 2-31-03 |  | 632 | ON | 新營白河水上線 632 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.632_DS | 632(新營白河水上線) DS | LINE69 | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | DS3 | 633 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1044 | 1045 |  | 2-31-04 | 2-31-05 |  | 633 | ON | 新營白河水上線 633 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.633_DS | 633(新營白河水上線) DS | LINE69 | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | ES3 | 633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1046 | 1047 |  | 2-31-06 | 2-31-07 |  | 633E | ON | 新營白河水上線 633 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.633E_ES | 633E(新營白河水上線) ES | LINE69 | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | DS1 | 641 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1048 | 1049 |  | 2-31-08 | 2-31-09 |  | 641 | ON | 新營營糖線 641 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.641_DS | 641(營糖線) DS | LINE69 | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | DS2 | 642 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1050 | 1051 |  | 2-31-10 | 2-31-11 |  | 642 | ON | 新營營糖線 642 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.642_DS | 642(營糖線) DS | LINE69 | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | DS3 | 643 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1052 | 1053 |  | 2-31-12 | 2-31-13 |  | 643 | ON | 新營營糖線 643 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.643_DS | 643(營糖線) DS | LINE69 | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | ES3 | 643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1054 | 1055 |  | 2-31-14 | 2-31-15 |  | 643E | ON | 新營營糖線 643 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.643E_ES | 643E(營糖線) ES | LINE69 | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | DS1 | 651 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1056 | 1057 |  | 2-32-00 | 2-32-01 |  | 651 | ON | 新營隆田線 651 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.651_DS | 651(隆田線) DS | LINE69 | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | DS2 | 652 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1058 | 1059 |  | 2-32-02 | 2-32-03 |  | 652 | ON | 新營隆田線 652 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.652_DS | 652(隆田線) DS | LINE69 | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | DS3 | 653 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1060 | 1061 |  | 2-32-04 | 2-32-05 |  | 653 | ON | 新營隆田線 653 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.653_DS | 653(隆田線) DS | LINE69 | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | ES3 | 653E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1062 | 1063 |  | 2-32-06 | 2-32-07 |  | 653E | ON | 新營隆田線 653 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.653E_ES | 653E(隆田線) ES | LINE69 | [5 empty] | 791 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | DS1 | 661 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1064 | 1065 |  | 2-32-08 | 2-32-09 |  | 661 | ON | 新營官田二路 661 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.661_DS | 661(官田二路) DS | LINE69 | [5 empty] | 792 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | DS2 | 662 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1066 | 1067 |  | 2-32-10 | 2-32-11 |  | 662 | ON | 新營官田二路 662 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.662_DS | 662(官田二路) DS | LINE69 | [5 empty] | 793 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | DS3 | 663 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1068 | 1069 |  | 2-32-12 | 2-32-13 |  | 663 | ON | 新營官田二路 663 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.663_DS | 663(官田二路) DS | LINE69 | [5 empty] | 794 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | ES3 | 663E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1070 | 1071 |  | 2-32-14 | 2-32-15 |  | 663E | ON | 新營官田二路 663 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.663E_ES | 663E(官田二路) ES | LINE69 | [5 empty] | 795 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | DS1 | 671 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1072 | 1073 |  | 2-33-00 | 2-33-01 |  | 671 | ON | 新營大寮二路 671 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.671_DS | 671(大寮二路) DS | LINE69 | [5 empty] | 796 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | DS2 | 672 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1074 | 1075 |  | 2-33-02 | 2-33-03 |  | 672 | ON | 新營大寮二路 672 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.672_DS | 672(大寮二路) DS | LINE69 | [5 empty] | 797 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | DS3 | 673 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1076 | 1077 |  | 2-33-04 | 2-33-05 |  | 673 | ON | 新營大寮二路 673 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.673_DS | 673(大寮二路) DS | LINE69 | [5 empty] | 798 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | ES3 | 673E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1078 | 1079 |  | 2-33-06 | 2-33-07 |  | 673E | ON | 新營大寮二路 673 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.673E_ES | 673E(大寮二路) ES | LINE69 | [5 empty] | 799 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | DS1 | 681 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1080 | 1081 |  | 2-33-08 | 2-33-09 |  | 681 | ON | 新營大寮一路 681 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.681_DS | 681(大寮一路) DS | LINE69 | [5 empty] | 800 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | DS2 | 682 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1082 | 1083 |  | 2-33-10 | 2-33-11 |  | 682 | ON | 新營大寮一路 682 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.682_DS | 682(大寮一路) DS | LINE69 | [5 empty] | 801 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | DS3 | 683 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1084 | 1085 |  | 2-33-12 | 2-33-13 |  | 683 | ON | 新營大寮一路 683 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.683_DS | 683(大寮一路) DS | LINE69 | [5 empty] | 802 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | ES3 | 683E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1086 | 1087 |  | 2-33-14 | 2-33-15 |  | 683E | ON | 新營大寮一路 683 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.683E_ES | 683E(大寮一路) ES | LINE69 | [5 empty] | 803 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | DS1 | 711 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1088 | 1089 |  | 2-34-00 | 2-34-01 |  | 711 | ON | 新營東盟榮剛榮重線 711 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.711_DS | 711(東盟榮剛榮重線) DS | LINE69 | [5 empty] | 804 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | DS2 | 712 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1090 | 1091 |  | 2-34-02 | 2-34-03 |  | 712 | ON | 新營東盟榮剛榮重線 712 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.712_DS | 712(東盟榮剛榮重線) DS | LINE69 | [5 empty] | 805 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | DS3 | 713 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1092 | 1093 |  | 2-34-04 | 2-34-05 |  | 713 | ON | 新營東盟榮剛榮重線 713 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.713_DS | 713(東盟榮剛榮重線) DS | LINE69 | [5 empty] | 806 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | ES3 | 713E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1094 | 1095 |  | 2-34-06 | 2-34-07 |  | 713E | ON | 新營東盟榮剛榮重線 713 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.713E_ES | 713E(東盟榮剛榮重線) ES | LINE69 | [5 empty] | 807 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | DS1 | 721 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1096 | 1097 |  | 2-34-08 | 2-34-09 |  | 721 | ON | 新營學甲二路 721 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.721_DS | 721(新營學甲二路) DS | LINE69 | [5 empty] | 808 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | DS2 | 722 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1098 | 1099 |  | 2-34-10 | 2-34-11 |  | 722 | ON | 新營學甲二路 722 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.722_DS | 722(新營學甲二路) DS | LINE69 | [5 empty] | 809 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | DS3 | 723 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1100 | 1101 |  | 2-34-12 | 2-34-13 |  | 723 | ON | 新營學甲二路 723 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.723_DS | 723(新營學甲二路) DS | LINE69 | [5 empty] | 810 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | ES3 | 723E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1102 | 1103 |  | 2-34-14 | 2-34-15 |  | 723E | ON | 新營學甲二路 723 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.723E_ES | 723E(新營學甲二路) ES | LINE69 | [5 empty] | 811 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | DS1 | 731 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1104 | 1105 |  | 2-35-00 | 2-35-01 |  | 731 | ON | 新營新西線 731 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.731_DS | 731(新西線) DS | LINE69 | [5 empty] | 812 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | DS2 | 732 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1106 | 1107 |  | 2-35-02 | 2-35-03 |  | 732 | ON | 新營新西線 732 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.732_DS | 732(新西線) DS | LINE69 | [5 empty] | 813 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | DS3 | 733 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1108 | 1109 |  | 2-35-04 | 2-35-05 |  | 733 | ON | 新營新西線 733 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.733_DS | 733(新西線) DS | LINE69 | [5 empty] | 814 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | ES3 | 733E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1110 | 1111 |  | 2-35-06 | 2-35-07 |  | 733E | ON | 新營新西線 733 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.733E_ES | 733E(新西線) ES | LINE69 | [5 empty] | 815 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | DS1 | 911 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1112 | 1113 |  | 2-35-08 | 2-35-09 |  | 911 | ON | 新營學甲一路 911 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.911_DS | 911(新營學甲一路) DS | LINE69 | [5 empty] | 816 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | DS2 | 912 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1114 | 1115 |  | 2-35-10 | 2-35-11 |  | 912 | ON | 新營學甲一路 912 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.912_DS | 912(新營學甲一路) DS | LINE69 | [5 empty] | 817 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | DS3 | 913 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1116 | 1117 |  | 2-35-12 | 2-35-13 |  | 913 | ON | 新營學甲一路 913 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.913_DS | 913(新營學甲一路) DS | LINE69 | [5 empty] | 818 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | ES3 | 913E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1118 | 1119 |  | 2-35-14 | 2-35-15 |  | 913E | ON | 新營學甲一路 913 EABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.913E_ES | 913E(新營學甲一路) ES | LINE69 | [5 empty] | 819 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1120 | 1121 |  | 2-36-00 | 2-36-01 |  | 601 | ON | 69KV TIE 601 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.601_DS | 601(TIE) DS | TIE | [5 empty] | 820 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1122 | 1123 |  | 2-36-02 | 2-36-03 |  | 602 | ON | 69KV TIE 602 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.602_DS | 602(TIE) DS | TIE | [5 empty] | 821 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1124 | 1125 |  | 2-36-04 | 2-36-05 |  | 811 | ON | 69KV #1SC 811 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.811_DS | 811(69KV #1SC) DS | SC | [5 empty] | 822 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1126 | 1127 |  | 2-36-06 | 2-36-07 |  | 812 | ON | 69KV #1SC 812 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.812_DS | 812(69KV #1SC) DS | SC | [5 empty] | 823 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | DS1 | 821 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1128 | 1129 |  | 2-36-08 | 2-36-09 |  | 821 | ON | 69KV #2SC 821 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.821_DS | 821(69KV #2SC) DS | SC | [5 empty] | 824 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | DS2 | 822 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1130 | 1131 |  | 2-36-10 | 2-36-11 |  | 822 | ON | 69KV #2SC 822 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.822_DS | 822(69KV #2SC) DS | SC | [5 empty] | 825 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | DS1 | 831 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1132 | 1133 |  | 2-36-12 | 2-36-13 |  | 831 | ON | 69KV #3SC 831 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.831_DS | 831(69KV #3SC) DS | SC | [5 empty] | 826 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | DS2 | 832 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1134 | 1135 |  | 2-36-14 | 2-36-15 |  | 832 | ON | 69KV #3SC 832 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.832_DS | 832(69KV #3SC) DS | SC | [5 empty] | 827 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | DS1 | 781 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1136 | 1137 |  | 2-37-00 | 2-37-01 |  | 781 | ON | #4MTR 781 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.781_DS | 781(#4MTR) DS | MTR | [5 empty] | 828 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | DS2 | 782 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1138 | 1139 |  | 2-37-02 | 2-37-03 |  | 782 | ON | #4MTR 782 ABS |  |  | B2/P01_A1 | [8 empty] | 新營PS.782_DS | 782(#4MTR) DS | MTR | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1152 |  |  | 2-38-00 |  |  | 670 | 87CFA | 新營大寮二路 670 87Ry 通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.670_87CFA | 新營大寮二路(670)87RY通訊故障 | OTHER | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1153 |  |  | 2-38-01 |  |  | 670 | RYFA | 新營大寮二路 670 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.670_RYFA | 新營大寮二路(670)數位電驛故障 | OTHER | [5 empty] | 831 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1154 |  |  | 2-38-02 |  |  | 670 | USE/LOCK | 新營大寮二路 670 87 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.670_87UL | 大寮二路(670) 87RY U/L | LINE69 | [5 empty] | 832 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1155 |  |  | 2-38-03 |  |  | 680 | 87CFA | 新營大寮一路 680 87Ry 通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.680_87CFA | 新營大寮ㄧ路(680)87RY通訊故障 | OTHER | [5 empty] | 833 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1156 |  |  | 2-38-04 |  |  | 680 | RYFA | 新營大寮一路 680 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.680_RYFA | 新營大寮ㄧ路(680)數位電驛故障 | OTHER | [5 empty] | 834 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1157 |  |  | 2-38-05 |  |  | 680 | USE/LOCK | 新營大寮一路 680 87 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.680_87UL | 大寮一路(680) 87RY U/L | LINE69 | [5 empty] | 835 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1158 |  |  | 2-38-06 |  |  | 630 | 87CFA | 新營白河水上線 630 87Ry 通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.630_87CFA | 新營白河水上線 87RY通訊故障 | OTHER | [5 empty] | 836 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1159 |  |  | 2-38-07 |  |  | 630 | RYFA | 新營白河水上線 630 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.630_RYFA | 新營白河水上線 數位電驛故障 | OTHER | [5 empty] | 837 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1160 |  |  | 2-38-08 |  |  | 630 | USE/LOCK | 新營白河水上線 630 87 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.630_87UL | 新營白河水上線(630) 87RY U/L | LINE69 | [5 empty] | 838 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1161 |  |  | 2-38-09 |  |  | 650 | 87CFA | 新營隆田線 650 87Ry 通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.650_87CFA | 新營隆田線(650)87RY通訊故障 | OTHER | [5 empty] | 839 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1162 |  |  | 2-38-10 |  |  | 650 | RYFA | 新營隆田線 650 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.650_RYFA | 新營隆田線(650)數位電驛故障 | OTHER | [5 empty] | 840 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1163 |  |  | 2-38-11 |  |  | 660 | 87CFA | 新營官田二路 660 87Ry 通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.660_87CFA | 新營官田二路(660)87RY通訊故障 | OTHER | [5 empty] | 841 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1164 |  |  | 2-38-12 |  |  | 660 | RYFA | 新營官田二路 660 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.660_RYFA | 新營官田二路(660)數位電驛故障 | OTHER | [5 empty] | 842 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1165 |  |  | 2-38-13 |  |  | #4MTR | RYFA | 4MTR 數位電驛故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_RYFA | #4MTR數位電驛故障 | OTHER | [5 empty] | 843 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1166 |  |  | 2-38-14 |  |  | #3MTR | RYFA | 3MTR 數位電驛故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER | [5 empty] | 844 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1167 |  |  | 2-38-15 |  |  | #3MTR | USE/LOCK | 3MTR #2 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER | [5 empty] | 845 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1168 |  |  | 2-39-00 |  |  | #2DTR | USE/LOCK | 2DTR #2 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | [5 empty] | 846 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1169 |  |  | 2-39-01 |  |  | 1520 | USE/LOCK | 新營華卡線 1520 79 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1520_79UL | 華卡線(1520) 79RY U/L | LINE161 | [5 empty] | 847 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1170 |  |  | 2-39-02 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/P01_A1 | [8 empty] | 新營PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 848 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
P01 | 新營PS |  |  | 3MTR | #3MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1171 |  |  | 2-39-03 |  |  | #3MTR | USE/LOCK | 3MTR 51Z RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER | [5 empty] | 849 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1172 |  |  | 2-39-04 |  |  | #4MTR | USE/LOCK | 4MTR #2 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_87UL2 | #4MTR #2 87RY U/L | OTHER | [5 empty] | 850 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1173 |  |  | 2-39-05 |  |  | #4MTR | USE/LOCK | 4MTR 51Z RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_51ZUL | #4MTR 51ZRY U/L | OTHER | [5 empty] | 851 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1174 |  |  | 2-39-06 |  |  | #2DTR | USE/LOCK | 2DTR 51Z RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | [5 empty] | 852 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1175 |  |  | 2-39-07 |  |  | 730 | USE/LOCK | 新營新西線 730 87 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.730_87UL | 新西線(730) 87RY U/L | LINE69 | [5 empty] | 853 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1177 |  |  | 2-39-09 |  |  | 910 | USE/LOCK | 新營學甲一路 910 87 RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.910_87UL | 新營學甲一路(910) 87RY U/L | LINE69 | [5 empty] | 854 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1178 |  |  | 2-39-10 |  |  | 910 | 87CFA | 新營學甲一路 910 87 Ry通訊故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.910_87CFA | 新營學甲一路(910)87RY通訊故障 | OTHER | [5 empty] | 855 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1179 |  |  | 2-39-11 |  |  | 910 | RYFA | 新營學甲一路 910 數位電驛故障 |  |  | B2/P01_A1 | [8 empty] | 新營PS.910_RYFA | 新營學甲一路(910)數位電驛故障 | OTHER | [5 empty] | 856 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1180 |  |  | 2-39-12 |  |  | 1570 | USE/LOCK | 新營下營一路 1570 87RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_87UL | 新營下營一路(1570) 87RY U/L | LINE161 | [5 empty] | 857 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1181 |  |  | 2-39-13 |  |  | 1570 | USE/LOCK | 新營下營一路 1570 79RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1570_79UL | 新營下營一路(1570) 79RY U/L | LINE161 | [5 empty] | 858 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1182 |  |  | 2-39-14 |  |  | 1580 | USE/LOCK | 新營下營二路 1580 87RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_87UL | 新營下營二路(1580) 87RY U/L | LINE161 | [5 empty] | 859 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1183 |  |  | 2-39-15 |  |  | 1580 | USE/LOCK | 新營下營二路 1580 79RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1580_79UL | 新營下營二路(1580) 79RY U/L | LINE161 | [5 empty] | 860 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 0 |  | ComPoint |  |  | RYFA | 低頻電驛故障 |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1184 |  |  | 2-3A-00 |  |  | RYFA | A/N | 低頻電驛故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.81RYFA | 低頻電驛故障 | OTHER | [5 empty] | 861 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1185 |  |  | 2-3A-01 |  |  | 1550 | USE/LOCK | 嘉義新營山上紅線79RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1550_79UL | 嘉義山上紅線(1550) 79RY U/L | LINE161 | [5 empty] | 862 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1186 |  |  | 2-3A-02 |  |  | 1560 | USE/LOCK | 嘉義新營山上白線1560 87RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_87UL | 嘉義山上白線(1560) 87RY U/L | LINE161 | [5 empty] | 863 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1187 |  |  | 2-3A-03 |  |  | 1560 | USE/LOCK | 嘉義新營山上白線1560 79RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1560_79UL | 嘉義山上白線(1560) 79RY U/L | LINE161 | [5 empty] | 864 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1188 |  |  | 2-3A-04 |  |  | #2DTR | RYFA | 2DTR 數位電驛故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 865 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1189 |  |  | 2-3A-05 |  |  | 1540 | USE/LOCK | 新營柳營海線79RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1540_79UL | 新營柳營海線(1540) 79RY U/L | LINE161 | [5 empty] | 866 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1190 |  |  | 2-3A-06 |  |  | #3DTR | USE/LOCK | 3DTR #2 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | [5 empty] | 867 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1191 |  |  | 2-3A-07 |  |  | 1530 | USE/LOCK | 新營柳營山線79RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.1530_79UL | 新營柳營山線(1530) 79RY U/L | LINE161 | [5 empty] | 868 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1192 |  |  | 2-3A-08 |  |  | 610 | USE/LOCK | 新營官田一路 610 85RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.610_85UL | 備用線(610) 85RY U/L | LINE69 | [5 empty] | 869 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1193 |  |  | 2-3A-09 |  |  | 620 | USE/LOCK | 新營新東線 620 87RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.620_87UL | 新營新東線(620) 87RY U/L | LINE69 | [5 empty] | 870 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1194 |  |  | 2-3A-10 |  |  | 650 | USE/LOCK | 新營隆田線 650 87RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.650_87UL | 隆田線(650) 87RY U/L | LINE69 | [5 empty] | 871 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1195 |  |  | 2-3A-11 |  |  | #3DTR | USE/LOCK | 3DTR 51Z RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | [5 empty] | 872 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | 74A |  |  | Status | 74RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1196 |  |  | 2-3A-12 |  |  | 610 | 74RY | 新營官田一路 74A |  |  | B2/P01_A1 | [8 empty] | 新營PS.610_74A | 備用線(610) 74RY | LINE69 | [5 empty] | 873 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1198 |  |  | 2-3A-14 |  |  | 660 | USE/LOCK | 新營官田二路 660 87RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.660_87UL | 官田二路(660) 87RY U/L | LINE69 | [5 empty] | 874 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1199 |  |  | 2-3A-15 |  |  | #3DTR | RYFA | 3DTR 數位電驛故障 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | [5 empty] | 875 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | 81UL |  |  | Status | 81RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1200 |  |  | 2-3B-00 |  |  | 640 | USE/LOCK | 新營營糖線 640 81RY U/L |  |  | B2/P01_A1 | [8 empty] | 新營PS.640_81UL | (640) 81RY U/L | LINE69 | [5 empty] | 876 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1202 |  |  | 2-3B-02 |  |  | 25RY | ON/OFF | 同步電源故障 25PFA |  |  | B3/P01_A1 | [8 empty] | 新營PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 877 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1203 |  |  | 2-3B-03 |  |  | 25RY | ON/OFF | 同步超時警報 25TA |  |  | B3/P01_A1 | [8 empty] | 新營PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 878 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1204 |  |  | 2-3B-04 |  |  | #1 BUS | ON/OFF | 69KV #1 BUS╴87UL |  |  | B2/P01_A1 | [8 empty] | 新營PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | [5 empty] | 879 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1205 |  |  | 2-3B-05 |  |  | #2 BUS | ON/OFF | 69KV #2 BUS╴87UL |  |  | B2/P01_A1 | [8 empty] | 新營PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | [5 empty] | 880 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1206 |  |  | 2-3B-06 |  |  | 23KV | CBA | 23 KV CB 重故障 |  |  | ELEM/P01_A1 | [8 empty] | 新營PS.11KV_CBA | 11KV斷路器重故障 | OTHER | [5 empty] | 881 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1207 |  |  | 2-3B-07 |  |  | 23KV | CBF | 23 KV CB 輕故障 |  |  | ELEM/P01_A1 | [8 empty] | 新營PS.11KV_CBF | 11KV斷路器輕故障 | OTHER | [5 empty] | 882 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1208 |  |  | 2-3B-08 |  |  | VC31 | USE/LOCK | F1 新11線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC31_79UL | 新31線(VC31) 79RY U/L | FEEDER | [5 empty] | 883 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1209 |  |  | 2-3B-09 |  |  | VC32 | USE/LOCK | F2 新12線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC32_79UL | 新32線(VC32) 79RY U/L | FEEDER | [5 empty] | 884 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1210 |  |  | 2-3B-10 |  |  | VC33 | USE/LOCK | F3 新13線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC33_79UL | 新33線(VC33) 79RY U/L | FEEDER | [5 empty] | 885 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1211 |  |  | 2-3B-11 |  |  | VC34 | USE/LOCK | F4 新14線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC34_79UL | 新34線(VC34) 79RY U/L | FEEDER | [5 empty] | 886 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1212 |  |  | 2-3B-12 |  |  | VC35 | USE/LOCK | F5 新15線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC35_79UL | 新35線(VC35) 79RY U/L | FEEDER | [5 empty] | 887 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1213 |  |  | 2-3B-13 |  |  | VC36 | USE/LOCK | F6 新16線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC36_79UL | 新36線(VC36) 79RY U/L | FEEDER | [5 empty] | 888 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  | B2,B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1214 |  |  | 2-3B-14 |  |  | 210 | A/M | 23KV #1 SC Q-CTL A/M |  |  | B3/P01_A1 | [8 empty] | 新營PS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 889 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  | B2,B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1215 |  |  | 2-3B-15 |  |  | 220 | A/M | 23KV #2 SC Q-CTL A/M |  |  | B3/P01_A1 | [8 empty] | 新營PS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 890 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1216 |  |  | 2-3C-00 |  |  | VC37 | USE/LOCK | F7 新17線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC37_79UL | 新37線(VC37) 79RY U/L | FEEDER | [5 empty] | 891 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1217 |  |  | 2-3C-01 |  |  | VC38 | USE/LOCK | F8 新18線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC38_79UL | 新38線(VC38) 79RY U/L | FEEDER | [5 empty] | 892 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1218 |  |  | 2-3C-02 |  |  | VC39 | USE/LOCK | F9 新19線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC39_79UL | 新39線(VC39) 79RY U/L | FEEDER | [5 empty] | 893 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1219 |  |  | 2-3C-03 |  |  | VC40 | USE/LOCK | F10 新20線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC40_79UL | 新40線(VC40) 79RY U/L | FEEDER | [5 empty] | 894 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  | B2,B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1220 |  |  | 2-3C-04 |  |  | 240 | A/M | 23KV #4 SC Q-CTL A/M |  |  | B3/P01_A1 | [8 empty] | 新營PS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 895 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1221 |  |  | 2-3C-05 |  |  | VC61 | USE/LOCK | F11 新61線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC61_79UL | 新61線(VC61) 79RY U/L | FEEDER | [5 empty] | 896 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1222 |  |  | 2-3C-06 |  |  | VC62 | USE/LOCK | F12 新62線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC62_79UL | 新62線(VC62) 79RY U/L | FEEDER | [5 empty] | 897 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1223 |  |  | 2-3C-07 |  |  | VC63 | USE/LOCK | F13 新63線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC63_79UL | 新63線(VC63) 79RY U/L | FEEDER | [5 empty] | 898 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1224 |  |  | 2-3C-08 |  |  | VC64 | USE/LOCK | F14 新64線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC64_79UL | 新64線(VC64) 79RY U/L | FEEDER | [5 empty] | 899 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1225 |  |  | 2-3C-09 |  |  | 230 | A/M | 23KV #3 SC Q-CTL A/M |  |  | B3/P01_A1 | [8 empty] | 新營PS.230_A/M | 23KV #3SC 乏控器 A/M | SC | [5 empty] | 900 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1226 |  |  | 2-3C-10 |  |  | VC65 | USE/LOCK | F15 新65線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC65_79UL | 新65線(VC65) 79RY U/L | FEEDER | [5 empty] | 901 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1227 |  |  | 2-3C-11 |  |  | VC66 | USE/LOCK | F16 新66線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC66_79UL | 新66線(VC66) 79RY U/L | FEEDER | [5 empty] | 902 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1228 |  |  | 2-3C-12 |  |  | VC67 | USE/LOCK | F17 新67線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC67_79UL | 新67線(VC67) 79RY U/L | FEEDER | [5 empty] | 903 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1229 |  |  | 2-3C-13 |  |  | VC68 | USE/LOCK | F18 新68線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC68_79UL | 新68線(VC68) 79RY U/L | FEEDER | [5 empty] | 904 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1230 |  |  | 2-3C-14 |  |  | VC69 | USE/LOCK | F19 新69線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC69_79UL | 新69線(VC69) 79RY U/L | FEEDER | [5 empty] | 905 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1231 |  |  | 2-3C-15 |  |  | VC70 | USE/LOCK | F20 新70線 79RY U/L |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC70_79UL | 新70線(VC70) 79RY U/L | FEEDER | [5 empty] | 906 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1232 |  |  | 2-3D-00 |  |  | 250 | A/M | 23KV #5 SC Q-CTL A/M |  |  | B3/P01_A1 | [8 empty] | 新營PS.250_A/M | 23KV #5SC 乏控器 A/M | SC | [5 empty] | 907 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M |  | B3 | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1233 |  |  | 2-3D-01 |  |  | 260 | A/M | 23KV #6 SC Q-CTL A/M |  |  | B3/P01_A1 | [8 empty] | 新營PS.260_A/M | 23KV #6SC 乏控器 A/M | SC | [5 empty] | 908 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1234 |  |  | 2-3D-02 |  |  | 空壓機 | COMT | 69KV CB COMT 空壓機超時 |  |  | B3/P01_A1 | [8 empty] | 新營PS.69空壓機COMT | 69KV空壓機運轉超時警報 | OTHER | [5 empty] | 909 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1235 |  |  | 2-3D-03 |  |  | 69KV | CBA | 69KV CB 重故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_CBA | 69KV斷路器重故障 | OTHER | [5 empty] | 910 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1236 |  |  | 2-3D-04 |  |  | 69KV | CBF | 69KV CB 輕故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | [5 empty] | 911 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1237 |  |  | 2-3D-05 |  |  | 69KV | VUA | 69KV#1BUS VUA1 電驛 |  |  | B2/P01_A1 | [8 empty] | 新營PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | [5 empty] | 912 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1238 |  |  | 2-3D-06 |  |  | 69KV | VUA | 69KV#2BUS VUA2 電驛 |  |  | B2/P01_A1 | [8 empty] | 新營PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 913 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1239 |  |  | 2-3D-07 |  |  | OSCF | A/N | 69KV示波器缺紙或故障警報OSCF |  |  | B3/P01_A1 | [8 empty] | 新營PS.69KV_OSCF | 69KV示波器缺紙或故障警報 | OTHER | [5 empty] | 914 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1240 |  |  | 2-3D-08 |  |  | CHG1 |  | CHG1 變電充電機故障 |  |  | B3/P01_A1 | [8 empty] | 新營PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 915 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1241 |  |  | 2-3D-09 |  |  | DCV | DCA | DCA 直流電源故障 |  |  | ELEM/P01_A1 | [8 empty] | 新營PS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 916 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1242 |  |  | 2-3D-10 |  |  | DCV | DCE | DCE 直流接地故障 |  |  | ELEM/P01_A1 | [8 empty] | 新營PS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 917 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1243 |  |  | 2-3D-11 |  |  | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 918 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACBT1 |  |  | Status | 所內電源ACB TIE1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1244 |  |  | 2-3D-12 |  |  | ACB TIE1 | ON/OFF | 所內電源 ACB TIE1 |  |  | B3/P01_A1 | [8 empty] | 新營PS.ACB_TIE1 | 所內電源ACB TIE1 | OTHER | [5 empty] | 919 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1245 |  |  | 2-3D-13 |  |  | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 920 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACBA1 | #1ACBA | Element | Status | 第一套所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1246 |  |  | 2-3D-14 |  |  | ACB1 | ON/OFF | ACB1 跳脫警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內#1ACBA | 開關場所內電源#1ACBA | OTHER | [5 empty] | 921 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACBT |  | Element | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 1247 |  |  | 2-3D-15 |  |  | ACB TIE1 | ON/OFF | ACB TIE1 跳脫警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內#TIE1_ACBA | 開關場所內電源#TIE1 ACBA | OTHER | [5 empty] | 922 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACBA2 | #2ACBA | Element | Status | 第二套所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1248 |  |  | 2-3E-00 |  |  | ACB2 | ON/OFF | ACB2 跳脫警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內#2ACBA | 開關場所內電源#2ACBA | OTHER | [5 empty] | 923 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACB3 |  |  | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1249 |  |  | 2-3E-01 |  |  | ADCS | ON/OFF | 所內電源 ACB3 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內電源ACB3 | 調度中心電源 ACB3(#3SSTR) | OTHER | [5 empty] | 924 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACBT2 |  |  | Status | 所內電源ACB TIE2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1250 |  |  | 2-3E-02 |  |  | ADCS | ON/OFF | 所內電源 ACB TIE2 |  |  | B3/P01_A1 | [8 empty] | 新營PS.ACB_TIE2 | 調度中心電源 ACB TIE2 | OTHER | [5 empty] | 925 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACB4 |  |  | Status | 所內電源ACB4 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1251 |  |  | 2-3E-03 |  |  | ADCS | ON/OFF | 所內電源 ACB4 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內電源ACB4 | 調度中心電源 ACB4(#4SSTR) | OTHER | [5 empty] | 926 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | ACB5 | 發電機 |  | Status | 所內電源ACB5 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1252 |  |  | 2-3E-04 |  |  | ADCS | ON/OFF | 發電機 ACB5 |  |  | B3/P01_A1 | [8 empty] | 新營PS.所內電源ACB5 | 調度中心電源 ACB5(發電機) | OTHER | [5 empty] | 927 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P01 | 新營PS | 0 |  | StaDev | 所內設施 |  | R_Temp | 控制室 |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1253 |  |  | 2-3E-05 |  |  | 控制室 | ON/OFF | 控制室溫度警報 |  |  | B3/P01_A1 | [8 empty] | 新營PS.控制室溫度警報 | 1F控制室溫度警報 | OTHER | [5 empty] | 928 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1254 |  |  | 2-3E-06 |  |  | #4MTR | USE/LOCK | 4MTR #1 87RY U/L |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_87UL1 | #4MTR #1 87RY U/L | OTHER | [5 empty] | 929 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1255 |  |  | 2-3E-07 |  |  | #4MTR | N/A | #4MTR 96P |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_96P | #4MTR 96P RY | MTR | [5 empty] | 930 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1256 |  |  | 2-3E-08 |  |  | VC31 | ON/OFF | F1 新11線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC31_ADJ | 新31線(VC31) LCO分流器 U/L | FEEDER | [5 empty] | 931 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1257 |  |  | 2-3E-09 |  |  | VC32 | ON/OFF | F2 新12線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC32_ADJ | 新32線(VC32) LCO分流器 U/L | FEEDER | [5 empty] | 932 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1258 |  |  | 2-3E-10 |  |  | VC33 | ON/OFF | F3 新13線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC33_ADJ | 新33線(VC33) LCO分流器 U/L | FEEDER | [5 empty] | 933 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1259 |  |  | 2-3E-11 |  |  | VC34 | ON/OFF | F4 新14線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC34_ADJ | 新34線(VC34) LCO分流器 U/L | FEEDER | [5 empty] | 934 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1260 |  |  | 2-3E-12 |  |  | VC35 | ON/OFF | F5 新15線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC35_ADJ | 新35線(VC35) LCO分流器 U/L | FEEDER | [5 empty] | 935 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1261 |  |  | 2-3E-13 |  |  | VC36 | ON/OFF | F6 新16線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC36_ADJ | 新36線(VC36) LCO分流器 U/L | FEEDER | [5 empty] | 936 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1262 |  |  | 2-3E-14 |  |  | VC37 | ON/OFF | F7 新17線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC37_ADJ | 新37線(VC37) LCO分流器 U/L | FEEDER | [5 empty] | 937 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1263 |  |  | 2-3E-15 |  |  | VC38 | ON/OFF | F8 新18線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC38_ADJ | 新38線(VC38) LCO分流器 U/L | FEEDER | [5 empty] | 938 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1264 |  |  | 2-3F-00 |  |  | VC39 | ON/OFF | F9 新19線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC39_ADJ | 新39線(VC39) LCO分流器 U/L | FEEDER | [5 empty] | 939 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1265 |  |  | 2-3F-01 |  |  | VC40 | ON/OFF | F10 新20線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC40_ADJ | 新40線(VC40) LCO分流器 U/L | FEEDER | [5 empty] | 940 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1266 |  |  | 2-3F-02 |  |  | VC61 | ON/OFF | F11 新61線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC61_ADJ | 新61線(VC61) LCO分流器 U/L | FEEDER | [5 empty] | 941 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1267 |  |  | 2-3F-03 |  |  | VC62 | ON/OFF | F12 新62線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC62_ADJ | 新62線(VC62) LCO分流器 U/L | FEEDER | [5 empty] | 942 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1268 |  |  | 2-3F-04 |  |  | VC63 | ON/OFF | F13 新63線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC63_ADJ | 新63線(VC63) LCO分流器 U/L | FEEDER | [5 empty] | 943 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1269 |  |  | 2-3F-05 |  |  | VC64 | ON/OFF | F14 新64線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC64_ADJ | 新64線(VC64) LCO分流器 U/L | FEEDER | [5 empty] | 944 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1270 |  |  | 2-3F-06 |  |  | VC65 | ON/OFF | F15 新65線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC65_ADJ | 新65線(VC65) LCO分流器 U/L | FEEDER | [5 empty] | 945 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1271 |  |  | 2-3F-07 |  |  | VC66 | ON/OFF | F16 新66線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC66_ADJ | 新66線(VC66) LCO分流器 U/L | FEEDER | [5 empty] | 946 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1272 |  |  | 2-3F-08 |  |  | VC67 | ON/OFF | F17 新67線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC67_ADJ | 新67線(VC67) LCO分流器 U/L | FEEDER | [5 empty] | 947 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1273 |  |  | 2-3F-09 |  |  | VC68 | ON/OFF | F18 新68線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC68_ADJ | 新68線(VC68) LCO分流器 U/L | FEEDER | [5 empty] | 948 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1274 |  |  | 2-3F-10 |  |  | VC69 | ON/OFF | F19 新69線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC69_ADJ | 新69線(VC69) LCO分流器 U/L | FEEDER | [5 empty] | 949 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1275 |  |  | 2-3F-11 |  |  | VC70 | ON/OFF | F20 新70線 LCO分流器 |  |  | B2/P01_D1 | [8 empty] | 新營PS.VC70_ADJ | 新70線(VC70) LCO分流器 U/L | FEEDER | [5 empty] | 950 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1276 |  |  | 2-3F-12 |  |  | #4MTR | N/A | #4MTR 96D |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_96D | #4MTR 96D RY | MTR | [5 empty] | 951 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1277 |  |  | 2-3F-13 |  |  | #4MTR | N/A | #4MTR 96B1 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_96B1 | #4MTR 96B1 RY | MTR | [5 empty] | 952 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1278 |  |  | 2-3F-14 |  |  | #4MTR | N/A | #4MTR 96B2 |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_96B2 | #4MTR 96B2 RY | MTR | [5 empty] | 953 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS |  |  | 4MTR | #4MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1279 |  |  | 2-3F-15 |  |  | #4MTR | N/A | #4MTR 63Q |  |  | B1/P01_A1 | [8 empty] | 新營PS.#4MTR_63Q | #4MTR 63Q RY | MTR | [5 empty] | 954 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 | [10 empty] | B3/P01_A1 | [16 empty] | 955 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P01 | 新營PS | 22 | 22kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0024 | [10 empty] | B3/P01_A1 | [16 empty] | 956 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P01 | 新營PS | 11 | 11kV | 350 | #3DTR(A)(350) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 | [10 empty] | B3/P01_A1 | [16 empty] | 957 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P01 | 新營PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 | [10 empty] | B3/P01_A1 | [16 empty] | 958 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
P01 | 新營PS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: P01/161/1BUS/V; OPRD2: P01/161/2BUS/V
P01 | 新營PS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: P01/69/1BUS/V; OPRD2: P01/69/2BUS/V
P01 | 新營PS |  |  | 2DTR | 2DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#2DTR_MVAR | #2DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: P01/11/330/MVAR; OPRD2: P01/22/340/MVAR
P01 | 新營PS |  |  | 2DTR | 2DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#2DTR_MW | #2DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: P01/11/330/MW; OPRD2: P01/22/340/MW
P01 | 新營PS |  |  | 3DTR | 3DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#3DTR_MVAR | #3DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: P01/11/350/MVAR; OPRD2: P01/22/360/MVAR
P01 | 新營PS |  |  | 3DTR | 3DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#3DTR_MW | #3DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: P01/11/350/MW; OPRD2: P01/22/360/MW
P01 | 新營PS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/P01_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: P01/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: P01/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
P01 | 新營PS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/P01_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_23 | OPRD1: P01/161/1520/MW; OPRD2: P01/161/1530/MW; OPRD3: P01/161/1540/MW; OPRD4: P01/161/1550/MW; OPRD5: P01/161/1560/MW; OPRD6: P01/161/1570/MW; OPRD7: P01/161/1580/MW; OPRD8: P01/69/610/MW; OPRD9: P01/69/620/MW; OPRD10: P01/69/630/MW; OPRD11: P01/69/640/MW; OPRD12: P01/69/650/MW; OPRD13: P01/69/660/MW; OPRD14: P01/69/670/MW; OPRD15: P01/69/680/MW; OPRD16: P01/69/710/MW; OPRD17: P01/69/720/MW; OPRD18: P01/69/730/MW; OPRD19: P01/69/750/MW; OPRD20: P01/69/760/MW; OPRD21: P01/69/770/MW; OPRD22: P01/69/780/MW; OPRD23: P01/69/910/MW
P01 | 新營PS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/P01_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: P01/0/CalcPoint/OPRN2_MW
P01 | 新營PS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/P01_A1 | [17 empty] | none
P01 | 新營PS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/P01_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: P01/0/CalcPoint/OPRN1; OPRD2: P01/0/CalcPoint/OPRN2; OPRD3: P01/0/CalcPoint/PRFL_UL
P01 | 新營PS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P01/11/330/I_R; OPRD2: P01/22/340/I_R
P01 | 新營PS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P01/11/330/I_S; OPRD2: P01/22/340/I_S
P01 | 新營PS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P01/11/330/I_T; OPRD2: P01/22/340/I_T
P01 | 新營PS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P01/11/350/I_R; OPRD2: P01/22/360/I_R
P01 | 新營PS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P01/11/350/I_S; OPRD2: P01/22/360/I_S
P01 | 新營PS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P01_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P01/11/350/I_T; OPRD2: P01/22/360/I_T
P01 | 新營PS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P01/69/750/MW; OPRD2: P01/69/750/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P01/69/760/MW; OPRD2: P01/69/760/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P01/69/770/MW; OPRD2: P01/69/770/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P01_A1 | [12 empty] | 新營PS.#4MTR_AMP | #4MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P01/69/780/MW; OPRD2: P01/69/780/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC31/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC32/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC33/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC34/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC35/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC36/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC37/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC38/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC39/MVAR; OPRD3: NULL
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/11/VC40/MVAR; OPRD3: NULL
P01 | 新營PS | 161 | 161kV | 1520 | 新營～華卡線(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1520_AMP | 華卡線 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P01/161/1520/MW; OPRD2: P01/161/1520/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 161 | 161kV | 1530 | 新營～柳營山線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1530_AMP | 新營柳營山線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P01/161/1530/MW; OPRD2: P01/161/1530/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 161 | 161kV | 1540 | 新營～柳營海線(1540) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1540_AMP | 新營柳營海線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P01/161/1540/MW; OPRD2: P01/161/1540/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義～新營、山上紅線(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1550_AMP | 嘉義山上紅線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P01/161/1550/MW; OPRD2: P01/161/1550/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義～新營、山上白線(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1560_AMP | 嘉義山上白線 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P01/161/1560/MW; OPRD2: P01/161/1560/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 161 | 161kV | 1570 | 新營～下營一路(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1570_AMP | 新營下營一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P01/161/1570/MW; OPRD2: P01/161/1570/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 161 | 161kV | 1580 | 新營～下營二路(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.1580_AMP | 新營下營二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P01/161/1580/MW; OPRD2: P01/161/1580/MVAR; OPRD3: P01/0/CalcPoint/Vbs4
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC61/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC62/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC63/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC64/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC65/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC66/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC67/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC68/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC69/MVAR; OPRD3: NULL
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P01/22/VC70/MVAR; OPRD3: NULL
P01 | 新營PS | 69 | 69kV | 610 | 新營官田一路(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.610_AMP | 備用線 AMP | LINE69 | AMP_CAL | C12R0896 | amp_cal | OPRD1: P01/69/610/MW; OPRD2: P01/69/610/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 620 | 新營～新東線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.620_AMP | 新營新東線 AMP | LINE69 | AMP_CAL | C12R0952 | amp_cal | OPRD1: P01/69/620/MW; OPRD2: P01/69/620/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 630 | 新營～水上～白河線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.630_AMP | 新營白河水上線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: P01/69/630/MW; OPRD2: P01/69/630/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 640 | 新營～營糖、營紙、史谷脫線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.640_AMP | 營糖線 AMP | LINE69 | AMP_CAL | C12R0640 | amp_cal | OPRD1: P01/69/640/MW; OPRD2: P01/69/640/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 650 | 新營～隆田線(650) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.650_AMP | 隆田線 AMP | LINE69 | AMP_CAL | C12R0905 | amp_cal | OPRD1: P01/69/650/MW; OPRD2: P01/69/650/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 660 | 新營～官田二路(660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.660_AMP | 官田二路 AMP | LINE69 | AMP_CAL | C12R0905 | amp_cal | OPRD1: P01/69/660/MW; OPRD2: P01/69/660/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 670 | 新營～大寮二路(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.670_AMP | 大寮二路 AMP | LINE69 | AMP_CAL | C12R0952 | amp_cal | OPRD1: P01/69/670/MW; OPRD2: P01/69/670/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 680 | 新營～大寮一路(680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.680_AMP | 大寮一路 AMP | LINE69 | AMP_CAL | C12R0952 | amp_cal | OPRD1: P01/69/680/MW; OPRD2: P01/69/680/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 710 | 新營～東盟、榮剛、榮重線(710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.710_AMP | 東盟榮剛榮重線 AMP | LINE69 | AMP_CAL | C12R0641 | amp_cal | OPRD1: P01/69/710/MW; OPRD2: P01/69/710/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 720 | 新營～學甲二路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.720_AMP | 新營學甲二路 AMP | LINE69 | AMP_CAL | C12R0896 | amp_cal | OPRD1: P01/69/720/MW; OPRD2: P01/69/720/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 730 | 新營～新西線(730) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.730_AMP | 新西線 AMP | LINE69 | AMP_CAL | C12R0899 | amp_cal | OPRD1: P01/69/730/MW; OPRD2: P01/69/730/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 69 | 69kV | 910 | 新營～學甲一路(910) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.910_AMP | 新營學甲一路 AMP | LINE69 | AMP_CAL | C12R0899 | amp_cal | OPRD1: P01/69/910/MW; OPRD2: P01/69/910/MVAR; OPRD3: P01/0/CalcPoint/Vbs2
P01 | 新營PS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P01/11/2ABUS/V
P01 | 新營PS | 11 | 11kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P01/11/3ABUS/V
P01 | 新營PS | 22 | 22kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P01/22/2BBUS/V
P01 | 新營PS | 22 | 22kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P01_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P01/22/3BBUS/V
P01 | 新營PS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 新營PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P01/69/750/MW; OPRD2: P01/69/750/MVAR
P01 | 新營PS |  |  | 2DTR | 2DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 新營PS.#2DTR_MVA | #2DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: P01//2DTR/MW; OPRD2: P01//2DTR/MVAR
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 新營PS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P01/11/330/MW; OPRD2: P01/11/330/MVAR
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 新營PS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P01/22/340/MW; OPRD2: P01/22/340/MVAR
P01 | 新營PS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 新營PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P01/69/760/MW; OPRD2: P01/69/760/MVAR
P01 | 新營PS |  |  | 3DTR | 3DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 新營PS.#3DTR_MVA | #3DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: P01//3DTR/MW; OPRD2: P01//3DTR/MVAR
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 新營PS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P01/11/350/MW; OPRD2: P01/11/350/MVAR
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 新營PS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P01/22/360/MW; OPRD2: P01/22/360/MVAR
P01 | 新營PS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 新營PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P01/69/770/MW; OPRD2: P01/69/770/MVAR
P01 | 新營PS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P01_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 新營PS.#4MTR_MVA | #4MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P01/69/780/MW; OPRD2: P01/69/780/MVAR
P01 | 新營PS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#1MTR_LOAD | #1MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P01//1MTR/MVA; OPRD2: 0
P01 | 新營PS |  |  | 2DTR | 2DTR |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR_LOAD | #2DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: P01//2DTR/MVA; OPRD2: 0
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P01//2DTR(A)/MVA; OPRD2: 0
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P01//2DTR(B)/MVA; OPRD2: 0
P01 | 新營PS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2MTR_LOAD | #2MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P01//2MTR/MVA; OPRD2: 0
P01 | 新營PS |  |  | 3DTR | 3DTR |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR_LOAD | #3DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: P01//3DTR/MVA; OPRD2: 0
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P01//3DTR(A)/MVA; OPRD2: 0
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P01//3DTR(B)/MVA; OPRD2: 0
P01 | 新營PS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3MTR_LOAD | #3MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P01//3MTR/MVA; OPRD2: 0
P01 | 新營PS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#4MTR_LOAD | #4MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P01//4MTR/MVA; OPRD2: 0
P01 | 新營PS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#1MTR_PF | #1MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/69/750/MW; OPRD2: P01/69/750/MVAR
P01 | 新營PS |  |  | 2DTR | 2DTR |  | PF | [9 empty] | B1/P01_A1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: P01//2DTR/MW; OPRD2: P01//2DTR/MVAR
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/11/330/MW; OPRD2: P01/11/330/MVAR
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/22/340/MW; OPRD2: P01/22/340/MVAR
P01 | 新營PS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2MTR_PF | #2MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/69/760/MW; OPRD2: P01/69/760/MVAR
P01 | 新營PS |  |  | 3DTR | 3DTR |  | PF | [9 empty] | B1/P01_A1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: P01//3DTR/MW; OPRD2: P01//3DTR/MVAR
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/11/350/MW; OPRD2: P01/11/350/MVAR
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/22/360/MW; OPRD2: P01/22/360/MVAR
P01 | 新營PS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3MTR_PF | #3MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/69/770/MW; OPRD2: P01/69/770/MVAR
P01 | 新營PS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#4MTR_PF | #4MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P01/69/780/MW; OPRD2: P01/69/780/MVAR
P01 | 新營PS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P01//2DTR(A)/SupLocal; OPRD2: P01//2DTR(A)/Tap Chan
P01 | 新營PS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P01//2DTR(B)/SupLocal; OPRD2: P01//2DTR(B)/Tap Chan
P01 | 新營PS |  |  | 3DTR(A) | #3DTR(A) |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P01//3DTR(A)/SupLocal; OPRD2: P01//3DTR(A)/Tap Chan
P01 | 新營PS |  |  | 3DTR(B) | #3DTR(B) |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P01//3DTR(B)/SupLocal; OPRD2: P01//3DTR(B)/Tap Chan
P01 | 新營PS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P01//1MTR/SupLocal; OPRD2: P01//1MTR/Tap Chan; OPRD3: P01//1MTR/M_F_I
P01 | 新營PS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P01//2MTR/SupLocal; OPRD2: P01//2MTR/Tap Chan; OPRD3: P01//2MTR/M_F_I
P01 | 新營PS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P01//3MTR/SupLocal; OPRD2: P01//3MTR/Tap Chan; OPRD3: P01//3MTR/M_F_I
P01 | 新營PS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/P01_A1 | [12 empty] | 新營PS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P01//4MTR/SupLocal; OPRD2: P01//4MTR/Tap Chan; OPRD3: P01//4MTR/M_F_I
P01 | 新營PS | 11 | 11kV | 1BUS | #1BUS |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B3/P01_A1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: NULL; OPRD3: P01/11/1BUS/I_S; OPRD4: P01/11/1BUS/I_T
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/2ABUS/V; OPRD2: P01/11/VC31/I_R; OPRD3: P01/11/VC31/I_S; OPRD4: P01/11/VC31/I_T
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/2ABUS/V; OPRD2: P01/11/VC32/I_R; OPRD3: P01/11/VC32/I_S; OPRD4: P01/11/VC32/I_T
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/2ABUS/V; OPRD2: P01/11/VC33/I_R; OPRD3: P01/11/VC33/I_S; OPRD4: P01/11/VC33/I_T
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/2ABUS/V; OPRD2: P01/11/VC34/I_R; OPRD3: P01/11/VC34/I_S; OPRD4: P01/11/VC34/I_T
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/2ABUS/V; OPRD2: P01/11/VC35/I_R; OPRD3: P01/11/VC35/I_S; OPRD4: P01/11/VC35/I_T
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/2ABUS/V; OPRD2: P01/11/VC36/I_R; OPRD3: P01/11/VC36/I_S; OPRD4: P01/11/VC36/I_T
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/3ABUS/V; OPRD2: P01/11/VC37/I_R; OPRD3: P01/11/VC37/I_S; OPRD4: P01/11/VC37/I_T
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/3ABUS/V; OPRD2: P01/11/VC38/I_R; OPRD3: P01/11/VC38/I_S; OPRD4: P01/11/VC38/I_T
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/3ABUS/V; OPRD2: P01/11/VC39/I_R; OPRD3: P01/11/VC39/I_S; OPRD4: P01/11/VC39/I_T
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/11/3ABUS/V; OPRD2: P01/11/VC40/I_R; OPRD3: P01/11/VC40/I_S; OPRD4: P01/11/VC40/I_T
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/2BBUS/V; OPRD2: P01/22/VC61/I_R; OPRD3: P01/22/VC61/I_S; OPRD4: P01/22/VC61/I_T
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/2BBUS/V; OPRD2: P01/22/VC62/I_R; OPRD3: P01/22/VC62/I_S; OPRD4: P01/22/VC62/I_T
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/2BBUS/V; OPRD2: P01/22/VC63/I_R; OPRD3: P01/22/VC63/I_S; OPRD4: P01/22/VC63/I_T
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/2BBUS/V; OPRD2: P01/22/VC64/I_R; OPRD3: P01/22/VC64/I_S; OPRD4: P01/22/VC64/I_T
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/3BBUS/V; OPRD2: P01/22/VC65/I_R; OPRD3: P01/22/VC65/I_S; OPRD4: P01/22/VC65/I_T
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/3BBUS/V; OPRD2: P01/22/VC66/I_R; OPRD3: P01/22/VC66/I_S; OPRD4: P01/22/VC66/I_T
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/3BBUS/V; OPRD2: P01/22/VC67/I_R; OPRD3: P01/22/VC67/I_S; OPRD4: P01/22/VC67/I_T
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/3BBUS/V; OPRD2: P01/22/VC68/I_R; OPRD3: P01/22/VC68/I_S; OPRD4: P01/22/VC68/I_T
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/3BBUS/V; OPRD2: P01/22/VC69/I_R; OPRD3: P01/22/VC69/I_S; OPRD4: P01/22/VC69/I_T
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P01/22/3BBUS/V; OPRD2: P01/22/VC70/I_R; OPRD3: P01/22/VC70/I_S; OPRD4: P01/22/VC70/I_T
P01 | 新營PS | 11 | 11kV | 1BUS | #1BUS |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B3/P01_A1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/1BUS/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC31 | 新11線(VC31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC31/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC32 | 新12線(VC32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC32/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC33 | 新13線(VC33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC33/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC34 | 新14線(VC34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC34/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC35 | 新15線(VC35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC35/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC36 | 新16線(VC36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC36/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC37 | 新17線(VC37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC37/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC38 | 新18線(VC38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC38/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC39 | 新19線(VC39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC39/kVA; OPRD2: NULL
P01 | 新營PS | 11 | 11kV | VC40 | 新20線(VC40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/11/VC40/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC61 | 新61線(VC61) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC61/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC62 | 新62線(VC62) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC62/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC63 | 新63線(VC63) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC63/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC64 | 新64線(VC64) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC64/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC65 | 新65線(VC65) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC65/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC66 | 新66線(VC66) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC66/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC67 | 新67線(VC67) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC67/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC68 | 新68線(VC68) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC68/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC69 | 新69線(VC69) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC69/kVA; OPRD2: NULL
P01 | 新營PS | 22 | 22kV | VC70 | 新70線(VC70) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P01_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P01/22/VC70/kVA; OPRD2: NULL
P01 | 新營PS | 0 |  | CalcPoint |  |  | DTR_MW | [9 empty] | B1/P01_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_6 | OPRD1: P01//2DTR/MW; OPRD2: P01//3DTR/MW; OPRD3: P01/69/750/MW; OPRD4: P01/69/760/MW; OPRD5: P01/69/770/MW; OPRD6: P01/69/780/MW
P01 | 新營PS | 0 |  | CalcPoint |  |  | DTR_MVAR | [9 empty] | B1/P01_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_6 | OPRD1: P01//2DTR/MVAR; OPRD2: P01//3DTR/MVAR; OPRD3: P01/69/750/MVAR; OPRD4: P01/69/760/MVAR; OPRD5: P01/69/770/MVAR; OPRD6: P01/69/780/MVAR
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P01_A1 | [12 empty] | 新營PS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P01/11/210/CB; OPRD2: 6.9; OPRD3: 0
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P01_A1 | [12 empty] | 新營PS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P01/11/220/CB; OPRD2: 6.9; OPRD3: 0
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P01_A1 | [12 empty] | 新營PS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P01/11/240/CB; OPRD2: 6.9; OPRD3: 0
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P01_A1 | [12 empty] | 新營PS.230_SC_MVAR | 23KV#3SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P01/22/230/CB; OPRD2: 13.8; OPRD3: 0
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P01_A1 | [12 empty] | 新營PS.250_SC_MVAR | 23KV#5SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P01/22/250/CB; OPRD2: 13.8; OPRD3: 0
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P01_A1 | [12 empty] | 新營PS.260_SC_MVAR | 23KV#6SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P01/22/260/CB; OPRD2: 13.8; OPRD3: 0
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P01/69/810/CB; OPRD2: 69; OPRD3: 0
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.820_SC_MVAR | 69KV#2SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P01/69/820/CB; OPRD2: 69; OPRD3: 0
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P01_A1 | [12 empty] | 新營PS.830_SC_MVAR | 69KV#3SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P01/69/830/CB; OPRD2: 69; OPRD3: 0
P01 | 新營PS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/P01_A1 | [12 empty] | 新營PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_28 |  | com_alarm_72 | P01//1MTR/96B2 | P01//1MTR/63Q | P01//1MTR/51ZA | P01//1MTR/TRA | P01//1MTR/96D | P01//1MTR/96B1 | P01//1MTR/96PA | P01//1MTR/GDA | P01//1MTR/PHA | P01//1MTR/87A | P01//2DTR/51ZA | P01//2DTR/96PA | P01//2DTR/TRA | P01//2DTR/96B2 | P01//2DTR/63Q | P01//2DTR/96D | P01//2DTR/96B1 | P01//2DTR/87A | P01//2MTR/51ZA | P01//2MTR/63Q | P01//2MTR/96PA | P01//2MTR/PHA | P01//2MTR/87A | P01//2MTR/TRA | P01//2MTR/96D | P01//2MTR/GDA | P01//2MTR/96B2 | P01//2MTR/96B1 | P01//3DTR/96D | P01//3DTR/TRA | P01//3DTR/96B1 | P01//3DTR/96PA | P01//3DTR/87A | P01//3DTR/63Q | P01//3DTR/51ZA | P01//3DTR/GDA | P01//3DTR/96B2 | P01//3DTR/PHA | P01//3MTR/96PA | P01//3MTR/51ZA | P01//3MTR/87A | P01//3MTR/GDA | P01//3MTR/PHA | P01//3MTR/TRA | P01//3MTR/96B2 | P01//3MTR/63Q | P01//3MTR/96D | P01//3MTR/96B1 | P01//4MTR/63Q | P01//4MTR/96B2
P01 | 新營PS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/P01_A1 | [12 empty] | 新營PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_6 |  | com_alarm_6 | OPRD1: P01//1MTR/TRF; OPRD2: P01//2DTR/TRF; OPRD3: P01//2MTR/TRF; OPRD4: P01//3DTR/TRF; OPRD5: P01//3MTR/TRF; OPRD6: P01//4MTR/TRF
P01 | 新營PS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/161/1760/CB
P01 | 新營PS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/11/330/CB
P01 | 新營PS | 22 | 22kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/22/340/CB
P01 | 新營PS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/161/1770/CB
P01 | 新營PS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/22/360/CB
P01 | 新營PS | 11 | 11kV | 350_D1 | #2DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/11/350/CB
P01 | 新營PS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/11/330/81A
P01 | 新營PS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/0/RTU/RTU_R_L
P01 | 新營PS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/0/StaDev/STUV
P01 | 新營PS | 22 | 22kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/22/ComPoint/CBA
P01 | 新營PS | 22 | 22kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/22/ComPoint/CBF
P01 | 新營PS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/0/StaDev/DCA
P01 | 新營PS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P01_D1 | [17 empty] | lamp2CC | OPRD1: P01/0/StaDev/DCE

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P01 | 新營PS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 新營PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | P01/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
P01 | 新營PS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 新營PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | P01/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1530_AMP | 新營柳營山線 AMP | LINE161 | P01/161/1530/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1540_AMP | 新營柳營海線 AMP | LINE161 | P01/161/1540/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1580_AMP | 新營下營二路 AMP | LINE161 | P01/161/1580/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.610_AMP | 備用線 AMP | LINE69 | P01/69/610/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C12R0896 | 806.400024 | 806.400024 | 896.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.620_AMP | 新營新東線 AMP | LINE69 | P01/69/620/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C12R0952 | 856.000000 | 856.000000 | 952.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.630_AMP | 新營白河水上線 AMP | LINE69 | P01/69/630/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.640_AMP | 營糖線 AMP | LINE69 | P01/69/640/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C12R0640 | 576.000000 | 576.000000 | 640.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.650_AMP | 隆田線 AMP | LINE69 | P01/69/650/I |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C12R0905 | 814.500000 | 814.500000 | 905.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.660_AMP | 官田二路 AMP | LINE69 | P01/69/660/I |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C12R0905 | 814.500000 | 814.500000 | 905.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.670_AMP | 大寮二路 AMP | LINE69 | P01/69/670/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C12R0952 | 856.000000 | 856.000000 | 952.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.680_AMP | 大寮一路 AMP | LINE69 | P01/69/680/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C12R0952 | 856.000000 | 856.000000 | 952.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.710_AMP | 東盟榮剛榮重線 AMP | LINE69 | P01/69/710/I |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C12R0641 | 576.900024 | 576.900024 | 641.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.720_AMP | 新營學甲二路 AMP | LINE69 | P01/69/720/I |  | AMP_CAL |  |  | 16 | CalcAIPoint | [21 empty] | C12R0896 | 806.400024 | 806.400024 | 896.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.730_AMP | 新西線 AMP | LINE69 | P01/69/730/I |  | AMP_CAL |  |  | 17 | CalcAIPoint | [21 empty] | C12R0899 | 806.400024 | 806.400024 | 899.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | P01//1MTR/MVA |  | MVA_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_LOAD | #1MTR 負載率 | MTR | P01//1MTR/Loading |  | TR_LOAD_200 |  |  | 19 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_PF | #1MTR 功率因素 | MTR | P01//1MTR/PF |  | RPDC_PF_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | P01//1MTR/I |  | AMP_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P01 | 新營PS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | P01//2MTR/MVA |  | MVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_LOAD | #2MTR 負載率 | MTR | P01//2MTR/Loading |  | TR_LOAD_200 |  |  | 23 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_PF | #2MTR 功率因素 | MTR | P01//2MTR/PF |  | RPDC_PF_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | P01//2MTR/I |  | AMP_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P01 | 新營PS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | P01//3MTR/MVA |  | MVA_CAL |  |  | 26 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_LOAD | #3MTR 負載率 | MTR | P01//3MTR/Loading |  | TR_LOAD_200 |  |  | 27 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_PF | #3MTR 功率因素 | MTR | P01//3MTR/PF |  | RPDC_PF_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | P01//3MTR/I |  | AMP_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P01 | 新營PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MW) |  | MW | [25 empty] | ADCS_N | [8 empty] | 新營PS.RPDC_MTR_MW | SUM(161/69KV MTR MW) | MTR |  |  | RPDC_4MTR_MW_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MVAR) |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.RPDC_MTR_MVAR | SUM(161/69KV MTR MVAR) | MTR |  |  | RPDC_4MTR_MVAR_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | RPDC_MTR | RPDC |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.RPDC_MTR_PF | RPDC MTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR | P01//2DTR(A)/MVA |  | MVA_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR | P01//2DTR(A)/Loading |  | TR_LOAD_30 |  |  | 34 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR | P01//2DTR(A)/PF |  | RPDC_PF_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR | P01//2DTR(B)/MVA |  | MVA_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR | P01//2DTR(B)/Loading |  | TR_LOAD_30 |  |  | 37 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR | P01//2DTR(B)/PF |  | RPDC_PF_CAL |  |  | 38 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR | P01//3DTR(A)/MVA |  | MVA_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR | P01//3DTR(A)/Loading |  | TR_LOAD_30 |  |  | 40 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR | P01//3DTR(A)/PF |  | RPDC_PF_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR | P01//3DTR(B)/MVA |  | MVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR | P01//3DTR(B)/Loading |  | TR_LOAD_30 |  |  | 43 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR | P01//3DTR(B)/PF |  | RPDC_PF_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_MW | #2DTR MW | MTR | P01//2DTR/MW |  | MTR_PQ_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_MVAR | #2DTR MVAR | MTR | P01//2DTR/MVAR |  | MTR_PQ_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_MVA | #2DTR二次側 MVA | MTR | P01//2DTR/MVA |  | MVA_CAL |  |  | 47 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_LOAD | #2DTR 負載率 | MTR | P01//2DTR/Loading |  | TR_LOAD_60 |  |  | 48 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_MW | #3DTR MW | MTR | P01//3DTR/MW |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_MVAR | #3DTR MVAR | MTR | P01//3DTR/MVAR |  | MTR_PQ_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_MVA | #3DTR二次側 MVA | MTR | P01//3DTR/MVA |  | MVA_CAL |  |  | 51 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_LOAD | #3DTR 負載率 | MTR | P01//3DTR/Loading |  | TR_LOAD_60 |  |  | 52 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.210_SC_MVAR | 11KV#1SC MVAR | SC | P01/11/210/MVAR |  | SC_CAL_11 |  |  | 53 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.220_SC_MVAR | 11KV#2SC MVAR | SC | P01/11/220/MVAR |  | SC_CAL_11 |  |  | 54 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 22 | 22kV | 230_SC | #3SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.230_SC_MVAR | 23KV#3SC MVAR | SC | P01/22/230/MVAR |  | SC_CAL_23 |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.240_SC_MVAR | 11KV#4SC MVAR | SC | P01/11/240/MVAR |  | SC_CAL_11 |  |  | 56 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 22 | 22kV | 250_SC | #5SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.250_SC_MVAR | 23KV#5SC MVAR | SC | P01/22/250/MVAR |  | SC_CAL_23 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 22 | 22kV | 260_SC | #6SC | 9 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.260_SC_MVAR | 23KV#6SC MVAR | SC | P01/22/260/MVAR |  | SC_CAL_23 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 810_SC | #1SC | 43.200001 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.810_SC_MVAR | 69KV#1SC MVAR | SC | P01/69/810/MVAR |  | SC_CAL_69 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.820_SC_MVAR | 69KV#2SC MVAR | SC | P01/69/820/MVAR |  | SC_CAL_69 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | MVAR | [25 empty] | ADCS_N | [8 empty] | 新營PS.830_SC_MVAR | 69KV#3SC MVAR | SC | P01/69/830/MVAR |  | SC_CAL_69 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | TRTOT | 新營主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 新營PS.TRTOT_MW | 新營主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_6 |  |  | 62 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | TRTOT | 新營主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 新營PS.TRTOT_MVAR | 新營主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_6 |  |  | 63 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_MVA | #4MTR二次側 MVA | MTR | P01//4MTR/MVA |  | MVA_CAL |  |  | 64 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_LOAD | #4MTR 負載率 | MTR | P01//4MTR/Loading |  | TR_LOAD_200 |  |  | 65 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_PF | #4MTR 功率因素 | MTR | P01//4MTR/PF |  | RPDC_PF_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_AMP | #4MTR 二次側 AMP | MTR | P01//4MTR/I |  | AMP_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1550_AMP | 嘉義山上紅線 AMP | LINE161 | P01/161/1550/I |  | AMP_CAL |  |  | 68 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1560_AMP | 嘉義山上白線 AMP | LINE161 | P01/161/1560/I |  | AMP_CAL |  |  | 69 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 0 |  | MTR_TOT | 新營MTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 新營PS.MTR_TOT_MW | 新營MTR瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_4 |  |  | 70 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | DTR_TOT | 新營DTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 新營PS.DTR_TOT_MW | 新營DTR瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1570_AMP | 新營下營一路 AMP | LINE161 | P01/161/1570/I |  | AMP_CAL |  |  | 72 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 0 |  |  |  |  | 新61線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新61線KVA | 23KV新61線KVA | FEEDER |  |  | KVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新61線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新61線KW | 23KV新61線KW | FEEDER |  |  | KW_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新62線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新62線KVA | 23KV新62線KVA | FEEDER |  |  | KVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新62線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新62線KW | 23KV新62線KW | FEEDER |  |  | KW_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新63線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新63線KVA | 23KV新63線KVA | FEEDER |  |  | KVA_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新63線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新63線KW | 23KV新63線KW | FEEDER |  |  | KW_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新64線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新64線KVA | 23KV新64線KVA | FEEDER |  |  | KVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新64線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新64線KW | 23KV新64線KW | FEEDER |  |  | KW_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新65線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新65線KVA | 23KV新65線KVA | FEEDER |  |  | KVA_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新65線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新65線KW | 23KV新65線KW | FEEDER |  |  | KW_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新66線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新66線KVA | 23KV新66線KVA | FEEDER |  |  | KVA_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新66線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新66線KW | 23KV新66線KW | FEEDER |  |  | KW_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新67線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新67線KVA | 23KV新67線KVA | FEEDER |  |  | KVA_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新67線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新67線KW | 23KV新67線KW | FEEDER |  |  | KW_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新68線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新68線KVA | 23KV新68線KVA | FEEDER |  |  | KVA_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新68線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新68線KW | 23KV新68線KW | FEEDER |  |  | KW_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新69線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新69線KVA | 23KV新69線KVA | FEEDER |  |  | KVA_CAL |  |  | 89 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新69線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新69線KW | 23KV新69線KW | FEEDER |  |  | KW_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新70線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新70線KVA | 23KV新70線KVA | FEEDER |  |  | KVA_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新70線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新70線KW | 23KV新70線KW | FEEDER |  |  | KW_CAL |  |  | 92 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | TEN_DAYS15 | (1520+1580 MW) |  | MW | [25 empty] | CDCS | [8 empty] | 新營PS.TEN_DAYS15_MW | (1520+1580 MW) |  |  |  | MTR_PQ_CAL |  |  | 93 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.910_AMP | 新營學甲一路 AMP | LINE69 | P01/69/910/I |  | AMP_CAL |  |  | 94 | CalcAIPoint | [21 empty] | C12R0899 | 806.400024 | 806.400024 | 899.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 新營PS.1520_AMP | 華卡線 AMP | LINE161 | P01/161/1520/I |  | AMP_CAL |  |  | 95 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P01 | 新營PS | 0 |  |  |  |  | 新31線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新31線KVA | 11KV新31線KVA | FEEDER |  |  | KVA_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新31線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新31線KW | 11KV新31線KW | FEEDER |  |  | KW_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新32線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新32線KVA | 11KV新32線KVA | FEEDER |  |  | KVA_CAL |  |  | 98 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新32線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新32線KW | 11KV新32線KW | FEEDER |  |  | KW_CAL |  |  | 99 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新33線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新33線KVA | 11KV新33線KVA | FEEDER |  |  | KVA_CAL |  |  | 100 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新33線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新33線KW | 11KV新33線KW | FEEDER |  |  | KW_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新34線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新34線KVA | 11KV新34線KVA | FEEDER |  |  | KVA_CAL |  |  | 102 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新34線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新34線KW | 11KV新34線KW | FEEDER |  |  | KW_CAL |  |  | 103 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新35線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新35線KVA | 11KV新35線KVA | FEEDER |  |  | KVA_CAL |  |  | 104 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新35線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新35線KW | 11KV新35線KW | FEEDER |  |  | KW_CAL |  |  | 105 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新36線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新36線KVA | 11KV新36線KVA | FEEDER |  |  | KVA_CAL |  |  | 106 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新36線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新36線KW | 11KV新36線KW | FEEDER |  |  | KW_CAL |  |  | 107 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新37線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新37線KVA | 11KV新37線KVA | FEEDER |  |  | KVA_CAL |  |  | 108 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新37線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新37線KW | 11KV新37線KW | FEEDER |  |  | KW_CAL |  |  | 109 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新38線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新38線KVA | 11KV新38線KVA | FEEDER |  |  | KVA_CAL |  |  | 110 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新38線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新38線KW | 11KV新38線KW | FEEDER |  |  | KW_CAL |  |  | 111 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新39線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新39線KVA | 11KV新39線KVA | FEEDER |  |  | KVA_CAL |  |  | 112 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新39線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新39線KW | 11KV新39線KW | FEEDER |  |  | KW_CAL |  |  | 113 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新40線KVA | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新40線KVA | 11KV新40線KVA | FEEDER |  |  | KVA_CAL |  |  | 114 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  |  |  |  | 新40線KW | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.新40線KW | 11KV新40線KW | FEEDER |  |  | KW_CAL |  |  | 115 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 610_CB | 備用線(610_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.610_CB_3 | 610(備用線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 116 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 620_CB | 新營新東線(620_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.620_CB_3 | 620(新營新東線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 117 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 630_CB | 新營白河水上線(630_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.630_CB_3 | 630(新營白河水上線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 118 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 650_CB | 隆田線(650_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.650_CB_3 | 650(隆田線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 119 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 660_CB | 官田二路(660_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.660_CB_3 | 660(官田二路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 120 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 670_CB | 大寮二路(670_CB) | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.670_CB_2 | 670(大寮二路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 121 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 680_CB | 大寮一路(680_CB) | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.680_CB_2 | 680(大寮一路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 122 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 720_CB | 新營學甲二路(720_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.720_CB_3 | 720(新營學甲二路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 123 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 730_CB | 新西線(730_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.730_CB_3 | 730(新西線) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 124 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 100_CB | 100(100_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.100_CB_3 | 100 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 125 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 200_CB | 200(200_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.200_CB_3 | 200 CB (D3) | TIE |  |  | AD_LAMP_DD_1 |  |  | 126 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | MTR | MTR |  | A_M | [25 empty] | RPDC_AD | [8 empty] | 新營PS.MTR_A/M | MTR OLTC A/M | MTR |  |  | LCP_4PTR |  |  | 127 | CalcDIPoint | [38 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.1760_CB_3 | 1760(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 128 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 330_CB | #2DTR(330_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.330_CB_3 | 330(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 129 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 340_CB | #2DTR(340_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.340_CB_3 | 340(#2DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 130 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.1770_CB_3 | 1770(#3DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 131 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 350_CB | #3DTR(350_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.350_CB_3 | 350(#3DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 132 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 360_CB | #3DTR(360_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.360_CB_3 | 360(#3DTR) CB (D3) | MTR |  |  | AD_LAMP_DD_1 |  |  | 133 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.210_CB_3 | 210(11KV #1SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 134 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.220_CB_3 | 220(11KV #2SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 135 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 230_CB | #3SC(230_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.230_CB_3 | 230(23KV #3SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 136 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.240_CB_3 | 240(11KV #4SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 137 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 250_CB | #5SC(250_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.250_CB_3 | 250(23KV #5SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 138 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 260_CB | #6SC(260_CB) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.260_CB_3 | 260(23KV #6SC) CB (D3) | SC |  |  | AD_LAMP_DD_1 |  |  | 139 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | _CBA | 斷路器重故障點燈(_CBA) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.11KV_CBA_3 | 11KV斷路器重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 140 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | _CBF | 斷路器輕故障(_CBF) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.11KV_CBF_3 | 11KV斷路器輕故障 (D3) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 141 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | _OSCA | 示波器啟動警報 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.69KV_OSCA_3 | 69KV示波器啟動警報 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 142 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | _OSCA | 示波器啟動警報 | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.69KV_OSCA_2 | 69KV示波器啟動警報 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 143 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | RTU_S_L | RTU |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.RTU_S/L_3 | RTU SUPY/LOCAL (D3) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 144 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P01 | 新營PS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 新營PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | P01/0/CalcPoint/SUBA |  | STATION_FAULT_28 |  |  | 145 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 新營PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | P01/0/CalcPoint/SUBF |  | STATION_FAULT_6 |  |  | 146 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.變電所重故障_3 | 變電所重故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 147 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.變電所輕故障_3 | 變電所輕故障點燈 (D3) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 148 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 149 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 150 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新營PS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 151 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 新營PS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 152 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530_AMP | 新營柳營山線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1530_AMP_A | 新營柳營山線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 153 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 161 | 161kV | 1540_AMP | 新營柳營海線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1540_AMP_A | 新營柳營海線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 154 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 161 | 161kV | 1580_AMP | 新營下營二路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1580_AMP_A | 新營下營二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 155 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 610_AMP | 備用線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.610_AMP_A | 備用線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 156 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 610_AMP | 備用線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.610_AMP_3 | 備用線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 157 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 620_AMP | 新營新東線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.620_AMP_A | 新營新東線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 158 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 620_AMP | 新營新東線 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.620_AMP_3 | 新營新東線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 159 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 630_AMP | 新營白河水上線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.630_AMP_A | 新營白河水上線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 160 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 630_AMP | 新營白河水上線 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.630_AMP_3 | 新營白河水上線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 161 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 640_AMP | 營糖線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.640_AMP_A | 營糖線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 162 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 650_AMP | 隆田線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.650_AMP_A | 隆田線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 163 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 650_AMP | 隆田線 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.650_AMP_3 | 隆田線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 164 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 660_AMP | 官田二路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.660_AMP_A | 官田二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 165 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 660_AMP | 官田二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.660_AMP_3 | 官田二路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 166 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 670_AMP | 大寮二路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.670_AMP_A | 大寮二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 167 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 670_AMP | 大寮二路 | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.670_AMP_2 | 大寮二路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 168 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 680_AMP | 大寮一路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.680_AMP_A | 大寮一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 169 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 680_AMP | 大寮一路 | [27 empty] | DDCS2_1 | [8 empty] | 新營PS.680_AMP_2 | 大寮一路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 170 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 710_AMP | 東盟榮剛榮重線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.710_AMP_A | 東盟榮剛榮重線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 171 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 720_AMP | 新營學甲二路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.720_AMP_A | 新營學甲二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 172 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 720_AMP | 新營學甲二路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.720_AMP_3 | 新營學甲二路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 173 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 730_AMP | 新西線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.730_AMP_A | 新西線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 174 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 730_AMP | 新西線 |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.730_AMP_3 | 新西線 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 175 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_MVA_A | #1MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 176 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | P01//1MTR/TR_PERM |  | MTR_PERM |  |  | 177 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_MVA_A | #2MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 178 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | P01//2MTR/TR_PERM |  | MTR_PERM |  |  | 179 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_MVA_A | #3MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 180 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | P01//3MTR/TR_PERM |  | MTR_PERM |  |  | 181 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | P01//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 182 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | P01//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 183 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | P01//3DTR(A)/TR_PERM |  | DTR_PERM |  |  | 184 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | P01//3DTR(B)/TR_PERM |  | DTR_PERM |  |  | 185 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 186 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.#2DTR_MVA_3 | #2DTR(A) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 187 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 4 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.#2DTR_MVA_4 | #2DTR(B) MVA 點燈(D3) |  |  |  | MAP_SET |  |  | 188 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 189 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3DTR_MVA | #3DTR(A) |  | 3 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.#3DTR_MVA_3 | #3DTR(A) MVA 點燈 (D3) | MTR |  |  | MAP_SET |  |  | 190 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3DTR_MVA | #3DTR(B) |  | 4 | [25 empty] | DDCS3_1 | [8 empty] | 新營PS.#3DTR_MVA_4 | #3DTR(B) MVA 點燈(D3) |  |  |  | MAP_SET |  |  | 191 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 4MTR_MVA | #4MTR | [27 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_MVA_A | #4MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 192 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | MTR | P01//4MTR/TR_PERM |  | MTR_PERM |  |  | 193 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 161 | 161kV | 1550_AMP | 嘉義山上紅線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1550_AMP_A | 嘉義山上紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 194 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 161 | 161kV | 1560_AMP | 嘉義山上白線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1560_AMP_A | 嘉義山上白線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 195 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 新營PS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_PS |  |  | 196 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570_AMP | 新營下營一路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1570_AMP_A | 新營下營一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 197 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 910_AMP | 新營學甲一路 | [27 empty] | ADCS_N | [8 empty] | 新營PS.910_AMP_A | 新營學甲一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 198 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 69 | 69kV | 910_CB | 新營學甲一路(910_CB) |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.910_CB_3 | 910(新營學甲一路) CB (D3) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 199 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 910_AMP | 新營學甲一路 |  | 3 | [25 empty] | DDCS3_2 | [8 empty] | 新營PS.910_AMP_3 | 新營學甲一路 AMP 點燈 (D3) | LINE69 |  |  | MAP_SET |  |  | 200 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 新營PS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 201 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 2BBUS | #2BBUS |  | 23KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 新營PS.23KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 202 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3ABUS | #3ABUS |  | 11KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 新營PS.11KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 203 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 新營PS.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 204 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_N | [8 empty] | 新營PS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T4 |  |  | 205 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_N | [8 empty] | 新營PS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B4 |  |  | 206 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_N | [8 empty] | 新營PS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 207 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1520_AMP | 華卡線 | [27 empty] | ADCS_N | [8 empty] | 新營PS.1520_AMP_A | 華卡線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 208 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P01 | 新營PS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_N | [8 empty] | 新營PS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_1 |  |  | 209 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | P01/0/RTU/ADCH1 |  |  |  | CDC | 210 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | P01/0/RTU/ADCH2 |  |  |  | CDC | 211 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | P01/0/RTU/ADCH3 |  |  |  | CDC | 212 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | P01/0/RTU/ADCH4 |  |  |  | CDC | 213 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | P01/0/RTU/ADCL1 |  |  |  | CDC | 214 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | P01/0/RTU/ADCL2 |  |  |  | CDC | 215 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | P01/0/RTU/ADCL3 |  |  |  | CDC | 216 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | P01/0/RTU/ADCL4 |  |  |  | CDC | 217 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-95 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | P01/161/1BUS/V |  |  |  | CDC | 218 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-96 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | P01/161/2BUS/V |  |  |  | CDC | 219 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P01 | 新營PS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-D1 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | P01/69/1BUS/V |  |  |  | CDC | 220 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P01 | 新營PS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-D2 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | P01/69/2BUS/V |  |  |  | CDC | 221 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1530_MW | 新營柳營山線 MW | LINE161 | P01/161/1530/MW |  |  |  | CDC | 222 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1530_MVAR | 新營柳營山線 MVAR | LINE161 | P01/161/1530/MVAR |  |  |  | CDC | 223 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1530LPD | 新營柳營山線(1530) |  | V | [17 empty] | 1-EF | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1530LPD_KV | 新營柳營山線(1530) LPD KV | LINE161 | P01/161/1530/V |  |  |  | CDC | 224 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1540_MW | 新營柳營海線 MW | LINE161 | P01/161/1540/MW |  |  |  | CDC | 225 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1540_MVAR | 新營柳營海線 MVAR | LINE161 | P01/161/1540/MVAR |  |  |  | CDC | 226 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1540LPD | 新營柳營海線(1540) |  | V | [17 empty] | 1-EE | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1540LPD_KV | 新營柳營海線(1540) LPD KV | LINE161 | P01/161/1540/V |  |  |  | CDC | 227 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1580_MW | 新營下營二路 MW | LINE161 | P01/161/1580/MW |  |  |  | CDC | 228 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1580_MVAR | 新營下營二路 MVAR | LINE161 | P01/161/1580/MVAR |  |  |  | CDC | 229 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1580LPD | 新營下營二路(1580) |  | V | [17 empty] | 1-F3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1580LPD_KV | 新營下營二路(1580) LPD KV | LINE161 | P01/161/1580/V |  |  |  | CDC | 230 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | MW | [17 empty] | 1-B8 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.610_MW | 備用線 MW | LINE69 | P01/69/610/MW |  |  |  | CDC | 231 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | MVAR | [17 empty] | 1-B9 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.610_MVAR | 備用線 MVAR | LINE69 | P01/69/610/MVAR |  |  |  | CDC | 232 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | MW | [17 empty] | 1-BC | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.620_MW | 新營新東線 MW | LINE69 | P01/69/620/MW |  |  |  | CDC | 233 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | MVAR | [17 empty] | 1-BD | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.620_MVAR | 新營新東線 MVAR | LINE69 | P01/69/620/MVAR |  |  |  | CDC | 234 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | MW | [17 empty] | 1-C4 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.630_MW | 新營白河水上線 MW | LINE69 | P01/69/630/MW |  |  |  | CDC | 235 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | MVAR | [17 empty] | 1-C5 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.630_MVAR | 新營白河水上線 MVAR | LINE69 | P01/69/630/MVAR |  |  |  | CDC | 236 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | MW | [17 empty] | 1-CA | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.640_MW | 營糖線 MW | LINE69 | P01/69/640/MW |  |  |  | CDC | 237 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | MVAR | [17 empty] | 1-CB | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.640_MVAR | 營糖線 MVAR | LINE69 | P01/69/640/MVAR |  |  |  | CDC | 238 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | MW | [17 empty] | 1-C8 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.650_MW | 隆田線 MW | LINE69 | P01/69/650/MW |  |  |  | CDC | 239 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | MVAR | [17 empty] | 1-C9 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.650_MVAR | 隆田線 MVAR | LINE69 | P01/69/650/MVAR |  |  |  | CDC | 240 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | MW | [17 empty] | 1-C2 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.660_MW | 官田二路 MW | LINE69 | P01/69/660/MW |  |  |  | CDC | 241 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | MVAR | [17 empty] | 1-C3 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.660_MVAR | 官田二路 MVAR | LINE69 | P01/69/660/MVAR |  |  |  | CDC | 242 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | MW | [17 empty] | 1-B6 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.670_MW | 大寮二路 MW | LINE69 | P01/69/670/MW |  |  |  | CDC | 243 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | MVAR | [17 empty] | 1-B7 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.670_MVAR | 大寮二路 MVAR | LINE69 | P01/69/670/MVAR |  |  |  | CDC | 244 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | MW | [17 empty] | 1-BE | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.680_MW | 大寮一路 MW | LINE69 | P01/69/680/MW |  |  |  | CDC | 245 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | MVAR | [17 empty] | 1-BF | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.680_MVAR | 大寮一路 MVAR | LINE69 | P01/69/680/MVAR |  |  |  | CDC | 246 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | MW | [17 empty] | 1-C6 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.710_MW | 東盟榮剛榮重線 MW | LINE69 | P01/69/710/MW |  |  |  | CDC | 247 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | MVAR | [17 empty] | 1-C7 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.710_MVAR | 東盟榮剛榮重線 MVAR | LINE69 | P01/69/710/MVAR |  |  |  | CDC | 248 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | MW | [17 empty] | 1-CC | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.720_MW | 新營學甲二路 MW | LINE69 | P01/69/720/MW |  |  |  | CDC | 249 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | MVAR | [17 empty] | 1-CD | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.720_MVAR | 新營學甲二路 MVAR | LINE69 | P01/69/720/MVAR |  |  |  | CDC | 250 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | MW | [17 empty] | 1-B0 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.730_MW | 新西線 MW | LINE69 | P01/69/730/MW |  |  |  | CDC | 251 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | MVAR | [17 empty] | 1-B1 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.730_MVAR | 新西線 MVAR | LINE69 | P01/69/730/MVAR |  |  |  | CDC | 252 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-94 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1500TIE_AMP | 1500TIE AMP | TIE | P01/161/1500/I_R |  |  |  | CDC | 253 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.600TIE_AMP | 600TIE AMP | TIE | P01/69/600/I_R |  |  |  | CDC | 254 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | C20R1500 | 1350.000000 | 1350.000000 | 1500.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 2-A0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.11KV_100_A1 | 11KV 100 R相AMP | TIE | P01/11/100/I_R |  |  |  | CDC | 255 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 2-A1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.11KV_100_A2 | 11KV 100 S相AMP | TIE | P01/11/1BUS/I_S |  |  |  | CDC | 256 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 2-A2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.11KV_100_A3 | 11KV 100 T相AMP | TIE | P01/11/1BUS/I_T |  |  |  | CDC | 257 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-B2 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#1MTR_MW | #1MTR二次側 MW | MTR | P01/69/750/MW |  |  |  | CDC | 258 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-B3 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | P01/69/750/MVAR |  |  |  | CDC | 259 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 1-97 |  | 1-28 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | P01//1MTR/TapPosMv |  |  |  | CDC | 260 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 1-98 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#1MTR_OIL | #1MTR 油溫 | MTR | P01//1MTR/OilTemp |  |  |  | CDC | 261 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 1-99 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#1MTR_COIL | #1MTR 線溫 | MTR | P01//1MTR/CoilTemp |  |  |  | CDC | 262 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-BA | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2MTR_MW | #2MTR二次側 MW | MTR | P01/69/760/MW |  |  |  | CDC | 263 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-BB | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | P01/69/760/MVAR |  |  |  | CDC | 264 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-9A |  | 1-2C |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | P01//2MTR/TapPosMv |  |  |  | CDC | 265 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-9B | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2MTR_OIL | #2MTR 油溫 | MTR | P01//2MTR/OilTemp |  |  |  | CDC | 266 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-9C | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2MTR_COIL | #2MTR 線溫 | MTR | P01//2MTR/CoilTemp |  |  |  | CDC | 267 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-B4 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3MTR_MW | #3MTR二次側 MW | MTR | P01/69/770/MW |  |  |  | CDC | 268 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-B5 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | P01/69/770/MVAR |  |  |  | CDC | 269 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-9D |  | 1-30 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | P01//3MTR/TapPosMv |  |  |  | CDC | 270 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-9E | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3MTR_OIL | #3MTR 油溫 | MTR | P01//3MTR/OilTemp |  |  |  | CDC | 271 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-9F | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3MTR_COIL | #3MTR 線溫 | MTR | P01//3MTR/CoilTemp |  |  |  | CDC | 272 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 2-83 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | P01/11/330/MVAR |  |  |  | CDC | 273 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 2-82 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | P01/11/330/MW |  |  |  | CDC | 274 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 2-84 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | P01/11/330/I_R |  |  |  | CDC | 275 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 2-85 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | P01/11/330/I_S |  |  |  | CDC | 276 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 2-86 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | P01/11/330/I_T |  |  |  | CDC | 277 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 1-A5 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR_OIL | #2DTR 油溫 | MTR | P01//2DTR/OilTemp |  |  |  | CDC | 278 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 1-A6 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | P01//2DTR(A)/CoilTemp |  |  |  | CDC | 279 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 1-A3 |  | 1-36 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | P01//2DTR(A)/TapPosMv |  |  |  | CDC | 280 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 2-BA | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | P01/22/340/MVAR |  |  |  | CDC | 281 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 2-B9 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | P01/22/340/MW |  |  |  | CDC | 282 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 2-BB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | P01/22/340/I_R |  |  |  | CDC | 283 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 2-BC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | P01/22/340/I_S |  |  |  | CDC | 284 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 2-BD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | P01/22/340/I_T |  |  |  | CDC | 285 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 1-A7 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | P01//2DTR(B)/CoilTemp |  |  |  | CDC | 286 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 1-A4 |  | 1-38 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | P01//2DTR(B)/TapPosMv |  |  |  | CDC | 287 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [17 empty] | 2-A4 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | P01/11/350/MVAR |  |  |  | CDC | 288 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [17 empty] | 2-A3 | [5 empty] | MVAR_-54_54(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | P01/11/350/MW |  |  |  | CDC | 289 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [17 empty] | 2-A5 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | P01/11/350/I_R |  |  |  | CDC | 290 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [17 empty] | 2-A6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | P01/11/350/I_S |  |  |  | CDC | 291 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [17 empty] | 2-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | P01/11/350/I_T |  |  |  | CDC | 292 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 1-AA | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR_OIL | #3DTR 油溫 | MTR | P01//3DTR/OilTemp |  |  |  | CDC | 293 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | CoilTemp | [17 empty] | 1-AB | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | P01//3DTR(A)/CoilTemp |  |  |  | CDC | 294 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | TapPosMv | [17 empty] | 1-A8 |  | 1-3A |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | P01//3DTR(A)/TapPosMv |  |  |  | CDC | 295 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [17 empty] | 2-D5 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | P01/22/360/MVAR |  |  |  | CDC | 296 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [17 empty] | 2-D4 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | P01/22/360/MW |  |  |  | CDC | 297 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [17 empty] | 2-D6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | P01/22/360/I_R |  |  |  | CDC | 298 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [17 empty] | 2-D7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | P01/22/360/I_S |  |  |  | CDC | 299 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [17 empty] | 2-D8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | P01/22/360/I_T |  |  |  | CDC | 300 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR(B) |  | CoilTemp | [17 empty] | 1-AC | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | P01//3DTR(B)/CoilTemp |  |  |  | CDC | 301 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR(B) |  | TapPosMv | [17 empty] | 1-A9 |  | 1-3C |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | P01//3DTR(B)/TapPosMv |  |  |  | CDC | 302 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P01 | 新營PS | 0 |  |  |  |  | DCV_N | [17 empty] | 2-F3 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.直流N電源電壓 | 直流N電源電壓 | OTHER | P01/0/StaDev/DCV_N |  |  |  | CDC | 303 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P01 | 新營PS | 0 |  |  |  |  | DCV_P | [17 empty] | 2-F2 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.直流P電源電壓 | 直流P電源電壓 | OTHER | P01/0/StaDev/DCV_P |  |  |  | CDC | 304 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P01 | 新營PS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 1-D6 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#4MTR_MW | #4MTR二次側 MW | MTR | P01/69/780/MW |  |  |  | CDC | 305 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P01 | 新營PS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 1-D7 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#4MTR_MVAR | #4MTR二次側 MVAR | MTR | P01/69/780/MVAR |  |  |  | CDC | 306 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 1-D5 |  | 2-7F |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 新營PS.#4MTR_TAP | #4MTR OLTC TAP | MTR | P01//4MTR/TapPosMv |  |  |  | CDC | 307 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 1-D3 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#4MTR_OIL | #4MTR 油溫 | MTR | P01//4MTR/OilTemp |  |  |  | CDC | 308 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 1-D4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.#4MTR_COIL | #4MTR 線溫 | MTR | P01//4MTR/CoilTemp |  |  |  | CDC | 309 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1550_MW | 嘉義山上紅線 MW | LINE161 | P01/161/1550/MW |  |  |  | CDC | 310 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1550_MVAR | 嘉義山上紅線 MVAR | LINE161 | P01/161/1550/MVAR |  |  |  | CDC | 311 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1550LPD | 嘉義山上紅線(1550) |  | V | [17 empty] | 1-F1 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1550LPD_KV | 嘉義山上紅線(1550) LPD KV | LINE161 | P01/161/1550/V |  |  |  | CDC | 312 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1560_MW | 嘉義山上白線 MW | LINE161 | P01/161/1560/MW |  |  |  | CDC | 313 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1560_MVAR | 嘉義山上白線 MVAR | LINE161 | P01/161/1560/MVAR |  |  |  | CDC | 314 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1560LPD | 嘉義山上白線(1560) |  | V | [17 empty] | 1-F0 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1560LPD_KV | 嘉義山上白線(1560) LPD KV | LINE161 | P01/161/1560/V |  |  |  | CDC | 315 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 2-9F | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | P01/11/2ABUS/V |  |  |  | CDC | 316 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P01 | 新營PS | 11 | 11kV | 3ABUS | #3ABUS |  | V | [17 empty] | 2-D0 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.11KV#3ABUS_KV | 11KV #3ABUS KV | BUS | P01/11/3ABUS/V |  |  |  | CDC | 317 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1570_MW | 新營下營一路 MW | LINE161 | P01/161/1570/MW |  |  |  | CDC | 318 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1570_MVAR | 新營下營一路 MVAR | LINE161 | P01/161/1570/MVAR |  |  |  | CDC | 319 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1570LPD | 新營下營一路(1570) |  | V | [17 empty] | 1-F2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1570LPD_KV | 新營下營一路(1570) LPD KV | LINE161 | P01/161/1570/V |  |  |  | CDC | 320 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 22 | 22kV | 2BBUS | #2BBUS |  | V | [17 empty] | 2-B8 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.23KV#2BBUS_KV | 23KV #2BBUS KV | BUS | P01/22/2BBUS/V |  |  |  | CDC | 321 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P01 | 新營PS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-F1 | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | P01/22/3BBUS/V |  |  |  | CDC | 322 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P01 | 新營PS | 22 | 22kV | 新61線 | 新61線 |  | 新61線KVAR | [17 empty] | 2-BE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新61線KVAR | 23KV新61線 KVAR | FEEDER | P01/22/VC61/MVAR |  |  |  | CDC | 323 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新61線 | 新61線 |  | 新61線A1 | [17 empty] | 2-BF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新61線A1 | 23KV新61線 R相AMP | FEEDER | P01/22/VC61/I_R |  |  |  | CDC | 324 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新61線 | 新61線 |  | 新61線A2 | [17 empty] | 2-C2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新61線A2 | 23KV新61線 S相AMP | FEEDER | P01/22/VC61/I_S |  |  |  | CDC | 325 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新61線 | 新61線 |  | 新61線A3 | [17 empty] | 2-C3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新61線A3 | 23KV新61線 T相AMP | FEEDER | P01/22/VC61/I_T |  |  |  | CDC | 326 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新62線 | 新62線 |  | 新62線KVAR | [17 empty] | 2-C4 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新62線KVAR | 23KV新62線 KVAR | FEEDER | P01/22/VC62/MVAR |  |  |  | CDC | 327 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新62線 | 新62線 |  | 新62線A1 | [17 empty] | 2-C5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新62線A1 | 23KV新62線 R相AMP | FEEDER | P01/22/VC62/I_R |  |  |  | CDC | 328 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新62線 | 新62線 |  | 新62線A2 | [17 empty] | 2-C6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新62線A2 | 23KV新62線 S相AMP | FEEDER | P01/22/VC62/I_S |  |  |  | CDC | 329 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新62線 | 新62線 |  | 新62線A3 | [17 empty] | 2-C7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新62線A3 | 23KV新62線 T相AMP | FEEDER | P01/22/VC62/I_T |  |  |  | CDC | 330 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新63線 | 新63線 |  | 新63線KVAR | [17 empty] | 2-C8 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新63線KVAR | 23KV新63線 KVAR | FEEDER | P01/22/VC63/MVAR |  |  |  | CDC | 331 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新63線 | 新63線 |  | 新63線A1 | [17 empty] | 2-C9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新63線A1 | 23KV新63線 R相AMP | FEEDER | P01/22/VC63/I_R |  |  |  | CDC | 332 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新63線 | 新63線 |  | 新63線A2 | [17 empty] | 2-CA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新63線A2 | 23KV新63線 S相AMP | FEEDER | P01/22/VC63/I_S |  |  |  | CDC | 333 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新63線 | 新63線 |  | 新63線A3 | [17 empty] | 2-CB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新63線A3 | 23KV新63線 T相AMP | FEEDER | P01/22/VC63/I_T |  |  |  | CDC | 334 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新64線 | 新64線 |  | 新64線KVAR | [17 empty] | 2-CC | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新64線KVAR | 23KV新64線 KVAR | FEEDER | P01/22/VC64/MVAR |  |  |  | CDC | 335 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新64線 | 新64線 |  | 新64線A1 | [17 empty] | 2-CD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新64線A1 | 23KV新64線 R相AMP | FEEDER | P01/22/VC64/I_R |  |  |  | CDC | 336 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新64線 | 新64線 |  | 新64線A2 | [17 empty] | 2-CE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新64線A2 | 23KV新64線 S相AMP | FEEDER | P01/22/VC64/I_S |  |  |  | CDC | 337 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新64線 | 新64線 |  | 新64線A3 | [17 empty] | 2-CF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新64線A3 | 23KV新64線 T相AMP | FEEDER | P01/22/VC64/I_T |  |  |  | CDC | 338 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新65線 | 新65線 |  | 新65線KVAR | [17 empty] | 2-D9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新65線KVAR | 23KV新65線 KVAR | FEEDER | P01/22/VC65/MVAR |  |  |  | CDC | 339 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新65線 | 新65線 |  | 新65線A1 | [17 empty] | 2-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新65線A1 | 23KV新65線 R相AMP | FEEDER | P01/22/VC65/I_R |  |  |  | CDC | 340 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新65線 | 新65線 |  | 新65線A2 | [17 empty] | 2-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新65線A2 | 23KV新65線 S相AMP | FEEDER | P01/22/VC65/I_S |  |  |  | CDC | 341 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新65線 | 新65線 |  | 新65線A3 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新65線A3 | 23KV新65線 T相AMP | FEEDER | P01/22/VC65/I_T |  |  |  | CDC | 342 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新66線 | 新66線 |  | 新66線KVAR | [17 empty] | 2-DD | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新66線KVAR | 23KV新66線 KVAR | FEEDER | P01/22/VC66/MVAR |  |  |  | CDC | 343 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新66線 | 新66線 |  | 新66線A1 | [17 empty] | 2-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新66線A1 | 23KV新66線 R相AMP | FEEDER | P01/22/VC66/I_R |  |  |  | CDC | 344 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新66線 | 新66線 |  | 新66線A2 | [17 empty] | 2-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新66線A2 | 23KV新66線 S相AMP | FEEDER | P01/22/VC66/I_S |  |  |  | CDC | 345 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新66線 | 新66線 |  | 新66線A3 | [17 empty] | 2-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新66線A3 | 23KV新66線 T相AMP | FEEDER | P01/22/VC66/I_T |  |  |  | CDC | 346 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新67線 | 新67線 |  | 新67線KVAR | [17 empty] | 2-E1 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新67線KVAR | 23KV新67線 KVAR | FEEDER | P01/22/VC67/MVAR |  |  |  | CDC | 347 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新67線 | 新67線 |  | 新67線A1 | [17 empty] | 2-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新67線A1 | 23KV新67線 R相AMP | FEEDER | P01/22/VC67/I_R |  |  |  | CDC | 348 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新67線 | 新67線 |  | 新67線A2 | [17 empty] | 2-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新67線A2 | 23KV新67線 S相AMP | FEEDER | P01/22/VC67/I_S |  |  |  | CDC | 349 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新67線 | 新67線 |  | 新67線A3 | [17 empty] | 2-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新67線A3 | 23KV新67線 T相AMP | FEEDER | P01/22/VC67/I_T |  |  |  | CDC | 350 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新68線 | 新68線 |  | 新68線KVAR | [17 empty] | 2-E5 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新68線KVAR | 23KV新68線 KVAR | FEEDER | P01/22/VC68/MVAR |  |  |  | CDC | 351 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新68線 | 新68線 |  | 新68線A1 | [17 empty] | 2-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新68線A1 | 23KV新68線 R相AMP | FEEDER | P01/22/VC68/I_R |  |  |  | CDC | 352 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新68線 | 新68線 |  | 新68線A2 | [17 empty] | 2-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新68線A2 | 23KV新68線 S相AMP | FEEDER | P01/22/VC68/I_S |  |  |  | CDC | 353 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新68線 | 新68線 |  | 新68線A3 | [17 empty] | 2-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新68線A3 | 23KV新68線 T相AMP | FEEDER | P01/22/VC68/I_T |  |  |  | CDC | 354 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新69線 | 新69線 |  | 新69線KVAR | [17 empty] | 2-E9 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新69線KVAR | 23KV新69線 KVAR | FEEDER | P01/22/VC69/MVAR |  |  |  | CDC | 355 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新69線 | 新69線 |  | 新69線A1 | [17 empty] | 2-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新69線A1 | 23KV新69線 R相AMP | FEEDER | P01/22/VC69/I_R |  |  |  | CDC | 356 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新69線 | 新69線 |  | 新69線A2 | [17 empty] | 2-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新69線A2 | 23KV新69線 S相AMP | FEEDER | P01/22/VC69/I_S |  |  |  | CDC | 357 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新69線 | 新69線 |  | 新69線A3 | [17 empty] | 2-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新69線A3 | 23KV新69線 T相AMP | FEEDER | P01/22/VC69/I_T |  |  |  | CDC | 358 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新70線 | 新70線 |  | 新70線KVAR | [17 empty] | 2-ED | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新70線KVAR | 23KV新70線 KVAR | FEEDER | P01/22/VC70/MVAR |  |  |  | CDC | 359 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新70線 | 新70線 |  | 新70線A1 | [17 empty] | 2-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新70線A1 | 23KV新70線 R相AMP | FEEDER | P01/22/VC70/I_R |  |  |  | CDC | 360 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新70線 | 新70線 |  | 新70線A2 | [17 empty] | 2-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新70線A2 | 23KV新70線 S相AMP | FEEDER | P01/22/VC70/I_S |  |  |  | CDC | 361 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新70線 | 新70線 |  | 新70線A3 | [17 empty] | 2-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新70線A3 | 23KV新70線 T相AMP | FEEDER | P01/22/VC70/I_T |  |  |  | CDC | 362 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | _200 | 200 |  | I_R | [17 empty] | 2-D1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.23KV_200_A1 | 23KV 200 R相AMP | TIE | P01/22/200/I_R |  |  |  | CDC | 363 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | _200 | 200 |  | I_S | [17 empty] | 2-D2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.23KV_200_A2 | 23KV 200 S相AMP | TIE | P01/22/200/I_S |  |  |  | CDC | 364 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | _200 | 200 |  | I_T | [17 empty] | 2-D3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.23KV_200_A3 | 23KV 200 T相AMP | TIE | P01/22/200/I_T |  |  |  | CDC | 365 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | MW | [17 empty] | 1-CE | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.910_MW | 新營學甲一路 MW | LINE69 | P01/69/910/MW |  |  |  | CDC | 366 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | MVAR | [17 empty] | 1-CF | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.910_MVAR | 新營學甲一路 MVAR | LINE69 | P01/69/910/MVAR |  |  |  | CDC | 367 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新61線 | 新61線 |  | 新61線A0 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新61線A0 | 23KV新61線 N相AMP | FEEDER | P01/22/VC61/I_N |  |  |  | CDC | 368 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新62線 | 新62線 |  | 新62線A0 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新62線A0 | 23KV新62線 N相AMP | FEEDER | P01/22/VC62/I_N |  |  |  | CDC | 369 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新63線 | 新63線 |  | 新63線A0 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新63線A0 | 23KV新63線 N相AMP | FEEDER | P01/22/VC63/I_N |  |  |  | CDC | 370 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新64線 | 新64線 |  | 新64線A0 | [17 empty] | 1-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新64線A0 | 23KV新64線 N相AMP | FEEDER | P01/22/VC64/I_N |  |  |  | CDC | 371 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新65線 | 新65線 |  | 新65線A0 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新65線A0 | 23KV新65線 N相AMP | FEEDER | P01/22/VC65/I_N |  |  |  | CDC | 372 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新66線 | 新66線 |  | 新66線A0 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新66線A0 | 23KV新66線 N相AMP | FEEDER | P01/22/VC66/I_N |  |  |  | CDC | 373 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新67線 | 新67線 |  | 新67線A0 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新67線A0 | 23KV新67線 N相AMP | FEEDER | P01/22/VC67/I_N |  |  |  | CDC | 374 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新68線 | 新68線 |  | 新68線A0 | [17 empty] | 1-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新68線A0 | 23KV新68線 N相AMP | FEEDER | P01/22/VC68/I_N |  |  |  | CDC | 375 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新69線 | 新69線 |  | 新69線A0 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新69線A0 | 23KV新69線 N相AMP | FEEDER | P01/22/VC69/I_N |  |  |  | CDC | 376 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 22 | 22kV | 新70線 | 新70線 |  | 新70線A0 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新70線A0 | 23KV新70線 N相AMP | FEEDER | P01/22/VC70/I_N |  |  |  | CDC | 377 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1520_MW | 華卡線 MW | LINE161 | P01/161/1520/MW |  |  |  | CDC | 378 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1520_MVAR | 華卡線 MVAR | LINE161 | P01/161/1520/MVAR |  |  |  | CDC | 379 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1520LPD | 華卡線(1520) |  | V | [17 empty] | 1-F4 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 新營PS.1520LPD_KV | 華卡線(1520) LPD KV | LINE161 | P01/161/1520/V |  |  |  | CDC | 380 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 11 | 11kV | 新31線 | 新31線 |  | 新31線KVAR | [17 empty] | 2-87 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新31線KVAR | 11KV新31線 KVAR | FEEDER | P01/11/VC31/MVAR |  |  |  | CDC | 381 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A1 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新31線A1 | 11KV新31線 R相AMP | FEEDER | P01/11/VC31/I_R |  |  |  | CDC | 382 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A2 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新31線A2 | 11KV新31線 S相AMP | FEEDER | P01/11/VC31/I_S |  |  |  | CDC | 383 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A3 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新31線A3 | 11KV新31線 T相AMP | FEEDER | P01/11/VC31/I_T |  |  |  | CDC | 384 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新31線 | 新31線 |  | 新31線A0 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新31線A0 | 11KV新31線 N相AMP | FEEDER | P01/11/VC31/I_N |  |  |  | CDC | 385 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新32線 | 新32線 |  | 新32線KVAR | [17 empty] | 2-8B | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新32線KVAR | 11KV新32線 KVAR | FEEDER | P01/11/VC32/MVAR |  |  |  | CDC | 386 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A1 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新32線A1 | 11KV新32線 R相AMP | FEEDER | P01/11/VC32/I_R |  |  |  | CDC | 387 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A2 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新32線A2 | 11KV新32線 S相AMP | FEEDER | P01/11/VC32/I_S |  |  |  | CDC | 388 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A3 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新32線A3 | 11KV新32線 T相AMP | FEEDER | P01/11/VC32/I_T |  |  |  | CDC | 389 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新32線 | 新32線 |  | 新32線A0 | [17 empty] | 1-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新32線A0 | 11KV新32線 N相AMP | FEEDER | P01/11/VC32/I_N |  |  |  | CDC | 390 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新33線 | 新33線 |  | 新33線KVAR | [17 empty] | 2-8F | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新33線KVAR | 11KV新33線 KVAR | FEEDER | P01/11/VC33/MVAR |  |  |  | CDC | 391 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A1 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新33線A1 | 11KV新33線 R相AMP | FEEDER | P01/11/VC33/I_R |  |  |  | CDC | 392 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A2 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新33線A2 | 11KV新33線 S相AMP | FEEDER | P01/11/VC33/I_S |  |  |  | CDC | 393 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A3 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新33線A3 | 11KV新33線 T相AMP | FEEDER | P01/11/VC33/I_T |  |  |  | CDC | 394 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新33線 | 新33線 |  | 新33線A0 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新33線A0 | 11KV新33線 N相AMP | FEEDER | P01/11/VC33/I_N |  |  |  | CDC | 395 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新34線 | 新34線 |  | 新34線KVAR | [17 empty] | 2-93 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新34線KVAR | 11KV新34線 KVAR | FEEDER | P01/11/VC34/MVAR |  |  |  | CDC | 396 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A1 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新34線A1 | 11KV新34線 R相AMP | FEEDER | P01/11/VC34/I_R |  |  |  | CDC | 397 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A2 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新34線A2 | 11KV新34線 S相AMP | FEEDER | P01/11/VC34/I_S |  |  |  | CDC | 398 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A3 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新34線A3 | 11KV新34線 T相AMP | FEEDER | P01/11/VC34/I_T |  |  |  | CDC | 399 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新34線 | 新34線 |  | 新34線A0 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新34線A0 | 11KV新34線 N相AMP | FEEDER | P01/11/VC34/I_N |  |  |  | CDC | 400 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新35線 | 新35線 |  | 新35線KVAR | [17 empty] | 2-97 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新35線KVAR | 11KV新35線 KVAR | FEEDER | P01/11/VC35/MVAR |  |  |  | CDC | 401 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A1 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新35線A1 | 11KV新35線 R相AMP | FEEDER | P01/11/VC35/I_R |  |  |  | CDC | 402 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A2 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新35線A2 | 11KV新35線 S相AMP | FEEDER | P01/11/VC35/I_S |  |  |  | CDC | 403 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A3 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新35線A3 | 11KV新35線 T相AMP | FEEDER | P01/11/VC35/I_T |  |  |  | CDC | 404 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新35線 | 新35線 |  | 新35線A0 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新35線A0 | 11KV新35線 N相AMP | FEEDER | P01/11/VC35/I_N |  |  |  | CDC | 405 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新36線 | 新36線 |  | 新36線KVAR | [17 empty] | 2-9B | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新36線KVAR | 11KV新36線 KVAR | FEEDER | P01/11/VC36/MVAR |  |  |  | CDC | 406 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A1 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新36線A1 | 11KV新36線 R相AMP | FEEDER | P01/11/VC36/I_R |  |  |  | CDC | 407 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A2 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新36線A2 | 11KV新36線 S相AMP | FEEDER | P01/11/VC36/I_S |  |  |  | CDC | 408 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A3 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新36線A3 | 11KV新36線 T相AMP | FEEDER | P01/11/VC36/I_T |  |  |  | CDC | 409 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新36線 | 新36線 |  | 新36線A0 | [17 empty] | 1-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新36線A0 | 11KV新36線 N相AMP | FEEDER | P01/11/VC36/I_N |  |  |  | CDC | 410 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新37線 | 新37線 |  | 新37線KVAR | [17 empty] | 2-A8 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新37線KVAR | 11KV新37線 KVAR | FEEDER | P01/11/VC37/MVAR |  |  |  | CDC | 411 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A1 | [17 empty] | 2-A9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新37線A1 | 11KV新37線 R相AMP | FEEDER | P01/11/VC37/I_R |  |  |  | CDC | 412 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A2 | [17 empty] | 2-AA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新37線A2 | 11KV新37線 S相AMP | FEEDER | P01/11/VC37/I_S |  |  |  | CDC | 413 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A3 | [17 empty] | 2-AB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新37線A3 | 11KV新37線 T相AMP | FEEDER | P01/11/VC37/I_T |  |  |  | CDC | 414 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新37線 | 新37線 |  | 新37線A0 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新37線A0 | 11KV新37線 N相AMP | FEEDER | P01/11/VC37/I_N |  |  |  | CDC | 415 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新38線 | 新38線 |  | 新38線KVAR | [17 empty] | 2-AC | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新38線KVAR | 11KV新38線 KVAR | FEEDER | P01/11/VC38/MVAR |  |  |  | CDC | 416 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A1 | [17 empty] | 2-AD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新38線A1 | 11KV新38線 R相AMP | FEEDER | P01/11/VC38/I_R |  |  |  | CDC | 417 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A2 | [17 empty] | 2-AE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新38線A2 | 11KV新38線 S相AMP | FEEDER | P01/11/VC38/I_S |  |  |  | CDC | 418 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A3 | [17 empty] | 2-AF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新38線A3 | 11KV新38線 T相AMP | FEEDER | P01/11/VC38/I_T |  |  |  | CDC | 419 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新38線 | 新38線 |  | 新38線A0 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新38線A0 | 11KV新38線 N相AMP | FEEDER | P01/11/VC38/I_N |  |  |  | CDC | 420 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新39線 | 新39線 |  | 新39線KVAR | [17 empty] | 2-B0 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新39線KVAR | 11KV新39線 KVAR | FEEDER | P01/11/VC39/MVAR |  |  |  | CDC | 421 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A1 | [17 empty] | 2-B1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新39線A1 | 11KV新39線 R相AMP | FEEDER | P01/11/VC39/I_R |  |  |  | CDC | 422 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A2 | [17 empty] | 2-B2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新39線A2 | 11KV新39線 S相AMP | FEEDER | P01/11/VC39/I_S |  |  |  | CDC | 423 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A3 | [17 empty] | 2-B3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新39線A3 | 11KV新39線 T相AMP | FEEDER | P01/11/VC39/I_T |  |  |  | CDC | 424 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新39線 | 新39線 |  | 新39線A0 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新39線A0 | 11KV新39線 N相AMP | FEEDER | P01/11/VC39/I_N |  |  |  | CDC | 425 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新40線 | 新40線 |  | 新40線KVAR | [17 empty] | 2-B4 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新40線KVAR | 11KV新40線 KVAR | FEEDER | P01/11/VC40/MVAR |  |  |  | CDC | 426 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A1 | [17 empty] | 2-B5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新40線A1 | 11KV新40線 R相AMP | FEEDER | P01/11/VC40/I_R |  |  |  | CDC | 427 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A2 | [17 empty] | 2-B6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新40線A2 | 11KV新40線 S相AMP | FEEDER | P01/11/VC40/I_S |  |  |  | CDC | 428 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A3 | [17 empty] | 2-B7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新40線A3 | 11KV新40線 T相AMP | FEEDER | P01/11/VC40/I_T |  |  |  | CDC | 429 | GENERICAIPoint | PS014_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 11 | 11kV | 新40線 | 新40線 |  | 新40線A0 | [17 empty] | 1-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS3_1 | [8 empty] | 新營PS.新40線A0 | 11KV新40線 N相AMP | FEEDER | P01/11/VC40/I_N |  |  |  | CDC | 430 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | MW | [17 empty] | 1-F8 | [5 empty] | MW_-162_162(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_MW | 新營華卡線(PV) MW | LINE161 |  |  |  |  | CDC | 431 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | MVAR | [17 empty] | 1-F9 | [5 empty] | MVAR_-162_162(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_MVAR | 新營華卡線(PV) MVAR | LINE161 |  |  |  |  | CDC | 432 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.280000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1510_KV | 新營華卡線(PV) |  | R | [17 empty] | 1-FD | [5 empty] | kV_-364_364(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_KV_R | 新營華卡線(PV) R相 KV | LINE161 |  |  |  |  | CDC | 433 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1510_KV | 新營華卡線(PV) |  | S | [17 empty] | 1-FE | [5 empty] | kV_-364_364(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_KV_S | 新營華卡線(PV) S相 KV | LINE161 |  |  |  |  | CDC | 434 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1510_KV | 新營華卡線(PV) |  | T | [17 empty] | 1-FF | [5 empty] | kV_-364_364(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_KV_T | 新營華卡線(PV) T相 KV | LINE161 |  |  |  |  | CDC | 435 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | I_R | [17 empty] | 1-FA | [5 empty] | A_-500_500(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_A1 | 新營華卡線(PV) R相 AMP | LINE161 |  |  |  |  | CDC | 436 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | I_S | [17 empty] | 1-FB | [5 empty] | A_-500_500(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_A2 | 新營華卡線(PV) S相 AMP | LINE161 |  |  |  |  | CDC | 437 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | I_T | [17 empty] | 1-FC | [5 empty] | A_-500_500(-2000_2000) |  | ADCS_N | [8 empty] | 華卡CS.1510_A3 | 新營華卡線(PV) T相 AMP | LINE161 |  |  |  |  | CDC | 438 | GENERICAIPoint | PS014_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | PHA | [17 empty] | 1-02-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1530_PHA | 新營柳營山線(1530) 相間RY | LINE161 | P01/161/1530/PHA |  |  |  | CDC | 439 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | GDA | [17 empty] | 1-02-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1530_GDA | 新營柳營山線(1530) 接地RY | LINE161 | P01/161/1530/GDA |  |  |  | CDC | 440 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | CB | [17 empty] | 1-01-01 |  | 1-03 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1530_CB | 1530(新營柳營山線) CB | LINE161 | P01/161/1530/CB |  |  |  | CDC | 441 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | 79UL | [17 empty] | 2-3A-07 |  | 2-57 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1530_79UL | 新營柳營山線(1530) 79RY U/L | LINE161 | P01/161/1530/79UL |  |  |  | CDC | 442 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | DS1 | 1531 | [16 empty] | 1-39-06 | 1-39-07 | 1-48 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1531_DS | 1531(新營柳營山線) DS | LINE161 | P01/161/1530/DS1 |  |  |  | CDC | 443 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | DS2 | 1532 | [16 empty] | 1-39-08 | 1-39-09 | 1-49 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1532_DS | 1532(新營柳營山線) DS | LINE161 | P01/161/1530/DS2 |  |  |  | CDC | 444 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | DS3 | 1533 | [16 empty] | 1-39-10 | 1-39-11 | 1-4A | [5 empty] | ADCS_N | [8 empty] | 新營PS.1533_DS | 1533(新營柳營山線) DS | LINE161 | P01/161/1530/DS3 |  |  |  | CDC | 445 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | E3 | 1533E | [16 empty] | 1-39-12 | 1-39-13 | 1-4B | [5 empty] | ADCS_N | [8 empty] | 新營PS.1533E_ES | 1533E(新營柳營山線) ES | LINE161 | P01/161/1530/ES3 |  |  |  | CDC | 446 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | PHA | [17 empty] | 1-01-07 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1540_PHA | 新營柳營海線(1540) 相間RY | LINE161 | P01/161/1540/PHA |  |  |  | CDC | 447 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | GDA | [17 empty] | 1-02-00 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1540_GDA | 新營柳營海線(1540) 接地RY | LINE161 | P01/161/1540/GDA |  |  |  | CDC | 448 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | CB | [17 empty] | 1-00-05 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1540_CB | 1540(新營柳營海線) CB | LINE161 | P01/161/1540/CB |  |  |  | CDC | 449 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | 79UL | [17 empty] | 2-3A-05 |  | 2-55 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1540_79UL | 新營柳營海線(1540) 79RY U/L | LINE161 | P01/161/1540/79UL |  |  |  | CDC | 450 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | DS1 | 1541 | [16 empty] | 1-38-14 | 1-38-15 | 1-44 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1541_DS | 1541(新營柳營海線) DS | LINE161 | P01/161/1540/DS1 |  |  |  | CDC | 451 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | DS2 | 1542 | [16 empty] | 1-39-00 | 1-39-01 | 1-45 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1542_DS | 1542(新營柳營海線) DS | LINE161 | P01/161/1540/DS2 |  |  |  | CDC | 452 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | DS3 | 1543 | [16 empty] | 1-39-02 | 1-39-03 | 1-46 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1543_DS | 1543(新營柳營海線) DS | LINE161 | P01/161/1540/DS3 |  |  |  | CDC | 453 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | E3 | 1543E | [16 empty] | 1-39-04 | 1-39-05 | 1-47 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1543E_ES | 1543E(新營柳營海線) ES | LINE161 | P01/161/1540/ES3 |  |  |  | CDC | 454 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | PHA | [17 empty] | 1-0D-00 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1580_PHA | 新營下營二路(1580) 相間RY | LINE161 | P01/161/1580/PHA |  |  |  | CDC | 455 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | GDA | [17 empty] | 1-0D-01 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1580_GDA | 新營下營二路(1580) 接地RY | LINE161 | P01/161/1580/GDA |  |  |  | CDC | 456 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | CB | [17 empty] | 1-0C-06 |  | 1-07 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1580_CB | 1580(新營下營二路) CB | LINE161 | P01/161/1580/CB |  |  |  | CDC | 457 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | 79UL | [17 empty] | 2-39-15 |  | 3-1D | [5 empty] | ADCS_N | [8 empty] | 新營PS.1580_79UL | 新營下營二路(1580) 79RY U/L | LINE161 | P01/161/1580/79UL |  |  |  | CDC | 458 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | DS1 | 1581 | [16 empty] | 1-3B-06 | 1-3B-07 | 1-58 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1581_DS | 1581(新營下營二路) DS | LINE161 | P01/161/1580/DS1 |  |  |  | CDC | 459 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | DS2 | 1582 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-59 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1582_DS | 1582(新營下營二路) DS | LINE161 | P01/161/1580/DS2 |  |  |  | CDC | 460 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | DS3 | 1583 | [16 empty] | 1-3B-10 | 1-3B-11 | 1-5A | [5 empty] | ADCS_N | [8 empty] | 新營PS.1583_DS | 1583(新營下營二路) DS | LINE161 | P01/161/1580/DS3 |  |  |  | CDC | 461 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | E3 | 1583E | [16 empty] | 1-3B-12 | 1-3B-13 | 1-5B | [5 empty] | ADCS_N | [8 empty] | 新營PS.1583E_ES | 1583E(新營下營二路) ES | LINE161 | P01/161/1580/ES3 |  |  |  | CDC | 462 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | PHA | [17 empty] | 1-18-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.610_PHA | 備用線(610) 相間RY | LINE69 | P01/69/610/PHA |  |  |  | CDC | 463 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | GDA | [17 empty] | 1-18-03 | [7 empty] | 69KV_N | [8 empty] | 新營PS.610_GDA | 備用線(610) 接地RY | LINE69 | P01/69/610/GDA |  |  |  | CDC | 464 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | 85A | [17 empty] | 1-18-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.610_85A | 備用線(610) 85RY | LINE69 | P01/69/610/85A |  |  |  | CDC | 465 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | 74A | [17 empty] | 2-3A-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.610_74A | 備用線(610) 74RY | LINE69 | P01/69/610/74A |  |  |  | CDC | 466 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | 85UL | [17 empty] | 2-3A-08 |  | 2-5C | [5 empty] | ADCS_N | [8 empty] | 新營PS.610_85UL | 備用線(610) 85RY U/L | LINE69 | P01/69/610/85UL |  |  |  | CDC | 467 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | CB | [17 empty] | 1-18-00 |  | 1-18 | [5 empty] | 69KV_N | [8 empty] | 新營PS.610_CB | 610(備用線) CB | LINE69 | P01/69/610/CB |  |  |  | CDC | 468 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | DS1 | 611 | [16 empty] | 2-30-00 | 2-30-01 | 2-00 | [5 empty] | ADCS_N | [8 empty] | 新營PS.611_DS | 611(備用線) DS | LINE69 | P01/69/610/DS1 |  |  |  | CDC | 469 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | DS2 | 612 | [16 empty] | 2-30-02 | 2-30-03 | 2-01 | [5 empty] | ADCS_N | [8 empty] | 新營PS.612_DS | 612(備用線) DS | LINE69 | P01/69/610/DS2 |  |  |  | CDC | 470 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | DS3 | 613 | [16 empty] | 2-30-04 | 2-30-05 | 2-02 | [5 empty] | ADCS_N | [8 empty] | 新營PS.613_DS | 613(備用線) DS | LINE69 | P01/69/610/DS3 |  |  |  | CDC | 471 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | E3 | 613E | [16 empty] | 2-30-06 | 2-30-07 | 2-03 | [5 empty] | ADCS_N | [8 empty] | 新營PS.613E_ES | 613E(備用線) ES | LINE69 | P01/69/610/ES3 |  |  |  | CDC | 472 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | 69KV_N | [8 empty] | 新營PS.620_PHA | 新營新東線(620) 相間RY | LINE69 | P01/69/620/PHA |  |  |  | CDC | 473 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.620_GDA | 新營新東線(620) 接地RY | LINE69 | P01/69/620/GDA |  |  |  | CDC | 474 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | CB | [17 empty] | 1-18-04 |  | 1-19 | [5 empty] | 69KV_N | [8 empty] | 新營PS.620_CB | 620(新營新東線) CB | LINE69 | P01/69/620/CB |  |  |  | CDC | 475 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | DS1 | 621 | [16 empty] | 2-30-08 | 2-30-09 | 2-04 | [5 empty] | ADCS_N | [8 empty] | 新營PS.621_DS | 621(新營新東線) DS | LINE69 | P01/69/620/DS1 |  |  |  | CDC | 476 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | DS2 | 622 | [16 empty] | 2-30-10 | 2-30-11 | 2-05 | [5 empty] | ADCS_N | [8 empty] | 新營PS.622_DS | 622(新營新東線) DS | LINE69 | P01/69/620/DS2 |  |  |  | CDC | 477 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | DS3 | 623 | [16 empty] | 2-30-12 | 2-30-13 | 2-06 | [5 empty] | ADCS_N | [8 empty] | 新營PS.623_DS | 623(新營新東線) DS | LINE69 | P01/69/620/DS3 |  |  |  | CDC | 478 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | E3 | 623E | [16 empty] | 2-30-14 | 2-30-15 | 2-07 | [5 empty] | ADCS_N | [8 empty] | 新營PS.623E_ES | 623E(新營新東線) ES | LINE69 | P01/69/620/ES3 |  |  |  | CDC | 479 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | PHA | [17 empty] | 1-19-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.630_PHA | 新營白河水上線(630) 相間RY | LINE69 | P01/69/630/PHA |  |  |  | CDC | 480 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | GDA | [17 empty] | 1-19-03 | [7 empty] | 69KV_N | [8 empty] | 新營PS.630_GDA | 新營白河水上線(630) 接地RY | LINE69 | P01/69/630/GDA |  |  |  | CDC | 481 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | CB | [17 empty] | 1-19-00 |  | 1-1A | [5 empty] | 69KV_N | [8 empty] | 新營PS.630_CB | 630(新營白河水上線) CB | LINE69 | P01/69/630/CB |  |  |  | CDC | 482 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | DS1 | 631 | [16 empty] | 2-31-00 | 2-31-01 | 2-08 | [5 empty] | ADCS_N | [8 empty] | 新營PS.631_DS | 631(新營白河水上線) DS | LINE69 | P01/69/630/DS1 |  |  |  | CDC | 483 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | DS2 | 632 | [16 empty] | 2-31-02 | 2-31-03 | 2-09 | [5 empty] | ADCS_N | [8 empty] | 新營PS.632_DS | 632(新營白河水上線) DS | LINE69 | P01/69/630/DS2 |  |  |  | CDC | 484 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | DS3 | 633 | [16 empty] | 2-31-04 | 2-31-05 | 2-0A | [5 empty] | ADCS_N | [8 empty] | 新營PS.633_DS | 633(新營白河水上線) DS | LINE69 | P01/69/630/DS3 |  |  |  | CDC | 485 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | E3 | 633E | [16 empty] | 2-31-06 | 2-31-07 | 2-0B | [5 empty] | ADCS_N | [8 empty] | 新營PS.633E_ES | 633E(新營白河水上線) ES | LINE69 | P01/69/630/ES3 |  |  |  | CDC | 486 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | PHA | [17 empty] | 1-19-06 | [7 empty] | 69KV_N | [8 empty] | 新營PS.640_PHA | 營糖線(640) 相間RY | LINE69 | P01/69/640/PHA |  |  |  | CDC | 487 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | GDA | [17 empty] | 1-19-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.640_GDA | 營糖線(640) 接地RY | LINE69 | P01/69/640/GDA |  |  |  | CDC | 488 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | 85A | [17 empty] | 1-19-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.640_85A | 營糖線(640) 85RY | LINE69 | P01/69/640/85A |  |  |  | CDC | 489 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | CB | [17 empty] | 1-19-04 |  | 1-1B | [5 empty] | 69KV_N | [8 empty] | 新營PS.640_CB | 640(營糖線) CB | LINE69 | P01/69/640/CB |  |  |  | CDC | 490 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | 81AS | [17 empty] | 1-1F-01 |  | 2-7D | [5 empty] | 69KV_N | [8 empty] | 新營PS.640_81A/S | (640) 81RY A/S | LINE69 | P01/69/640/81A |  |  |  | CDC | 491 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | 81UL | [17 empty] | 2-3B-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.640_81UL | (640) 81RY U/L | LINE69 | P01/69/640/81UL |  |  |  | CDC | 492 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | DS1 | 641 | [16 empty] | 2-31-08 | 2-31-09 | 2-0C | [5 empty] | ADCS_N | [8 empty] | 新營PS.641_DS | 641(營糖線) DS | LINE69 | P01/69/640/DS1 |  |  |  | CDC | 493 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | DS2 | 642 | [16 empty] | 2-31-10 | 2-31-11 | 2-0D | [5 empty] | ADCS_N | [8 empty] | 新營PS.642_DS | 642(營糖線) DS | LINE69 | P01/69/640/DS2 |  |  |  | CDC | 494 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | DS3 | 643 | [16 empty] | 2-31-12 | 2-31-13 | 2-0E | [5 empty] | ADCS_N | [8 empty] | 新營PS.643_DS | 643(營糖線) DS | LINE69 | P01/69/640/DS3 |  |  |  | CDC | 495 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | E3 | 643E | [16 empty] | 2-31-14 | 2-31-15 | 2-0F | [5 empty] | ADCS_N | [8 empty] | 新營PS.643E_ES | 643E(營糖線) ES | LINE69 | P01/69/640/ES3 |  |  |  | CDC | 496 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | PHA | [17 empty] | 1-1A-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.650_PHA | 隆田線(650) 相間RY | LINE69 | P01/69/650/PHA |  |  |  | CDC | 497 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | GDA | [17 empty] | 1-1A-03 | [7 empty] | 69KV_N | [8 empty] | 新營PS.650_GDA | 隆田線(650) 接地RY | LINE69 | P01/69/650/GDA |  |  |  | CDC | 498 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | CB | [17 empty] | 1-1A-00 |  | 1-1C | [5 empty] | 69KV_N | [8 empty] | 新營PS.650_CB | 650(隆田線) CB | LINE69 | P01/69/650/CB |  |  |  | CDC | 499 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | DS1 | 651 | [16 empty] | 2-32-00 | 2-32-01 | 2-10 | [5 empty] | ADCS_N | [8 empty] | 新營PS.651_DS | 651(隆田線) DS | LINE69 | P01/69/650/DS1 |  |  |  | CDC | 500 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | DS2 | 652 | [16 empty] | 2-32-02 | 2-32-03 | 2-11 | [5 empty] | ADCS_N | [8 empty] | 新營PS.652_DS | 652(隆田線) DS | LINE69 | P01/69/650/DS2 |  |  |  | CDC | 501 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | DS3 | 653 | [16 empty] | 2-32-04 | 2-32-05 | 2-12 | [5 empty] | ADCS_N | [8 empty] | 新營PS.653_DS | 653(隆田線) DS | LINE69 | P01/69/650/DS3 |  |  |  | CDC | 502 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | E3 | 653E | [16 empty] | 2-32-06 | 2-32-07 | 2-13 | [5 empty] | ADCS_N | [8 empty] | 新營PS.653E_ES | 653E(隆田線) ES | LINE69 | P01/69/650/ES3 |  |  |  | CDC | 503 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | PHA | [17 empty] | 1-1A-06 | [7 empty] | 69KV_N | [8 empty] | 新營PS.660_PHA | 官田二路(660) 相間RY | LINE69 | P01/69/660/PHA |  |  |  | CDC | 504 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | GDA | [17 empty] | 1-1A-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.660_GDA | 官田二路(660) 接地RY | LINE69 | P01/69/660/GDA |  |  |  | CDC | 505 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | CB | [17 empty] | 1-1A-04 |  | 1-1D | [5 empty] | 69KV_N | [8 empty] | 新營PS.660_CB | 660(官田二路) CB | LINE69 | P01/69/660/CB |  |  |  | CDC | 506 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | DS1 | 661 | [16 empty] | 2-32-08 | 2-32-09 | 2-14 | [5 empty] | ADCS_N | [8 empty] | 新營PS.661_DS | 661(官田二路) DS | LINE69 | P01/69/660/DS1 |  |  |  | CDC | 507 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | DS2 | 662 | [16 empty] | 2-32-10 | 2-32-11 | 2-15 | [5 empty] | ADCS_N | [8 empty] | 新營PS.662_DS | 662(官田二路) DS | LINE69 | P01/69/660/DS2 |  |  |  | CDC | 508 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | DS3 | 663 | [16 empty] | 2-32-12 | 2-32-13 | 2-16 | [5 empty] | ADCS_N | [8 empty] | 新營PS.663_DS | 663(官田二路) DS | LINE69 | P01/69/660/DS3 |  |  |  | CDC | 509 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | E3 | 663E | [16 empty] | 2-32-14 | 2-32-15 | 2-17 | [5 empty] | ADCS_N | [8 empty] | 新營PS.663E_ES | 663E(官田二路) ES | LINE69 | P01/69/660/ES3 |  |  |  | CDC | 510 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | PHA | [17 empty] | 1-1B-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.670_PHA | 大寮二路(670) 相間RY | LINE69 | P01/69/670/PHA |  |  |  | CDC | 511 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | GDA | [17 empty] | 1-1B-03 | [7 empty] | 69KV_N | [8 empty] | 新營PS.670_GDA | 大寮二路(670) 接地RY | LINE69 | P01/69/670/GDA |  |  |  | CDC | 512 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | CB | [17 empty] | 1-1B-00 |  | 1-1E | [5 empty] | 69KV_N | [8 empty] | 新營PS.670_CB | 670(大寮二路) CB | LINE69 | P01/69/670/CB |  |  |  | CDC | 513 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | DS1 | 671 | [16 empty] | 2-33-00 | 2-33-01 | 2-18 | [5 empty] | ADCS_N | [8 empty] | 新營PS.671_DS | 671(大寮二路) DS | LINE69 | P01/69/670/DS1 |  |  |  | CDC | 514 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | DS2 | 672 | [16 empty] | 2-33-02 | 2-33-03 | 2-19 | [5 empty] | ADCS_N | [8 empty] | 新營PS.672_DS | 672(大寮二路) DS | LINE69 | P01/69/670/DS2 |  |  |  | CDC | 515 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | DS3 | 673 | [16 empty] | 2-33-04 | 2-33-05 | 2-1A | [5 empty] | ADCS_N | [8 empty] | 新營PS.673_DS | 673(大寮二路) DS | LINE69 | P01/69/670/DS3 |  |  |  | CDC | 516 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | E3 | 673E | [16 empty] | 2-33-06 | 2-33-07 | 2-1B | [5 empty] | ADCS_N | [8 empty] | 新營PS.673E_ES | 673E(大寮二路) ES | LINE69 | P01/69/670/ES3 |  |  |  | CDC | 517 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | PHA | [17 empty] | 1-1B-06 | [7 empty] | 69KV_N | [8 empty] | 新營PS.680_PHA | 大寮一路(680) 相間RY | LINE69 | P01/69/680/PHA |  |  |  | CDC | 518 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | GDA | [17 empty] | 1-1B-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.680_GDA | 大寮一路(680) 接地RY | LINE69 | P01/69/680/GDA |  |  |  | CDC | 519 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | CB | [17 empty] | 1-1B-04 |  | 1-1F | [5 empty] | 69KV_N | [8 empty] | 新營PS.680_CB | 680(大寮一路) CB | LINE69 | P01/69/680/CB |  |  |  | CDC | 520 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | DS1 | 681 | [16 empty] | 2-33-08 | 2-33-09 | 2-1C | [5 empty] | ADCS_N | [8 empty] | 新營PS.681_DS | 681(大寮一路) DS | LINE69 | P01/69/680/DS1 |  |  |  | CDC | 521 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | DS2 | 682 | [16 empty] | 2-33-10 | 2-33-11 | 2-1D | [5 empty] | ADCS_N | [8 empty] | 新營PS.682_DS | 682(大寮一路) DS | LINE69 | P01/69/680/DS2 |  |  |  | CDC | 522 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | DS3 | 683 | [16 empty] | 2-33-12 | 2-33-13 | 2-1E | [5 empty] | ADCS_N | [8 empty] | 新營PS.683_DS | 683(大寮一路) DS | LINE69 | P01/69/680/DS3 |  |  |  | CDC | 523 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | E3 | 683E | [16 empty] | 2-33-14 | 2-33-15 | 2-1F | [5 empty] | ADCS_N | [8 empty] | 新營PS.683E_ES | 683E(大寮一路) ES | LINE69 | P01/69/680/ES3 |  |  |  | CDC | 524 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | PHA | [17 empty] | 1-1C-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.710_PHA | 東盟榮剛榮重線(710) 相間RY | LINE69 | P01/69/710/PHA |  |  |  | CDC | 525 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | GDA | [17 empty] | 1-1C-03 | [7 empty] | 69KV_N | [8 empty] | 新營PS.710_GDA | 東盟榮剛榮重線(710) 接地RY | LINE69 | P01/69/710/GDA |  |  |  | CDC | 526 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | 85A | [17 empty] | 1-1C-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.710_85A | 東盟榮剛榮重線(710) 85RY | LINE69 | P01/69/710/85A |  |  |  | CDC | 527 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | CB | [17 empty] | 1-1C-00 |  | 1-20 | [5 empty] | 69KV_N | [8 empty] | 新營PS.710_CB | 710(東盟榮剛榮重線) CB | LINE69 | P01/69/710/CB |  |  |  | CDC | 528 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | DS1 | 711 | [16 empty] | 2-34-00 | 2-34-01 | 2-20 | [5 empty] | ADCS_N | [8 empty] | 新營PS.711_DS | 711(東盟榮剛榮重線) DS | LINE69 | P01/69/710/DS1 |  |  |  | CDC | 529 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | DS2 | 712 | [16 empty] | 2-34-02 | 2-34-03 | 2-21 | [5 empty] | ADCS_N | [8 empty] | 新營PS.712_DS | 712(東盟榮剛榮重線) DS | LINE69 | P01/69/710/DS2 |  |  |  | CDC | 530 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | DS3 | 713 | [16 empty] | 2-34-04 | 2-34-05 | 2-22 | [5 empty] | ADCS_N | [8 empty] | 新營PS.713_DS | 713(東盟榮剛榮重線) DS | LINE69 | P01/69/710/DS3 |  |  |  | CDC | 531 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | E3 | 713E | [16 empty] | 2-34-06 | 2-34-07 | 2-23 | [5 empty] | ADCS_N | [8 empty] | 新營PS.713E_ES | 713E(東盟榮剛榮重線) ES | LINE69 | P01/69/710/ES3 |  |  |  | CDC | 532 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | PHA | [17 empty] | 1-1C-06 | [7 empty] | 69KV_N | [8 empty] | 新營PS.720_PHA | 新營學甲二路(720) 相間RY | LINE69 | P01/69/720/PHA |  |  |  | CDC | 533 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | GDA | [17 empty] | 1-1C-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.720_GDA | 新營學甲二路(720) 接地RY | LINE69 | P01/69/720/GDA |  |  |  | CDC | 534 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | CB | [17 empty] | 1-1C-04 |  | 1-21 | [5 empty] | 69KV_N | [8 empty] | 新營PS.720_CB | 720(新營學甲二路) CB | LINE69 | P01/69/720/CB |  |  |  | CDC | 535 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | DS1 | 721 | [16 empty] | 2-34-08 | 2-34-09 | 2-24 | [5 empty] | ADCS_N | [8 empty] | 新營PS.721_DS | 721(新營學甲二路) DS | LINE69 | P01/69/720/DS1 |  |  |  | CDC | 536 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | DS2 | 722 | [16 empty] | 2-34-10 | 2-34-11 | 2-25 | [5 empty] | ADCS_N | [8 empty] | 新營PS.722_DS | 722(新營學甲二路) DS | LINE69 | P01/69/720/DS2 |  |  |  | CDC | 537 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | DS3 | 723 | [16 empty] | 2-34-12 | 2-34-13 | 2-26 | [5 empty] | ADCS_N | [8 empty] | 新營PS.723_DS | 723(新營學甲二路) DS | LINE69 | P01/69/720/DS3 |  |  |  | CDC | 538 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | E3 | 723E | [16 empty] | 2-34-14 | 2-34-15 | 2-27 | [5 empty] | ADCS_N | [8 empty] | 新營PS.723E_ES | 723E(新營學甲二路) ES | LINE69 | P01/69/720/ES3 |  |  |  | CDC | 539 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | PHA | [17 empty] | 1-1D-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.730_PHA | 新西線(730) 相間RY | LINE69 | P01/69/730/PHA |  |  |  | CDC | 540 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | GDA | [17 empty] | 1-1D-03 | [7 empty] | 69KV_N | [8 empty] | 新營PS.730_GDA | 新西線(730) 接地RY | LINE69 | P01/69/730/GDA |  |  |  | CDC | 541 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | CB | [17 empty] | 1-1D-00 |  | 1-22 | [5 empty] | 69KV_N | [8 empty] | 新營PS.730_CB | 730(新西線) CB | LINE69 | P01/69/730/CB |  |  |  | CDC | 542 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | DS1 | 731 | [16 empty] | 2-35-00 | 2-35-01 | 2-28 | [5 empty] | ADCS_N | [8 empty] | 新營PS.731_DS | 731(新西線) DS | LINE69 | P01/69/730/DS1 |  |  |  | CDC | 543 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | DS2 | 732 | [16 empty] | 2-35-02 | 2-35-03 | 2-29 | [5 empty] | ADCS_N | [8 empty] | 新營PS.732_DS | 732(新西線) DS | LINE69 | P01/69/730/DS2 |  |  |  | CDC | 544 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | DS3 | 733 | [16 empty] | 2-35-04 | 2-35-05 | 2-2A | [5 empty] | ADCS_N | [8 empty] | 新營PS.733_DS | 733(新西線) DS | LINE69 | P01/69/730/DS3 |  |  |  | CDC | 545 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | E3 | 733E | [16 empty] | 2-35-06 | 2-35-07 | 2-2B | [5 empty] | ADCS_N | [8 empty] | 新營PS.733E_ES | 733E(新西線) ES | LINE69 | P01/69/730/ES3 |  |  |  | CDC | 546 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 0 |  | VC31 | 新31線(VC31) |  | PHA | [17 empty] | 2-00-01 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_PHA | 新31線(VC31) 相間RY | FEEDER | P01/11/VC31/PHA |  |  |  | CDC | 547 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC31 | 新31線(VC31) |  | GDA | [17 empty] | 2-00-02 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_GDA | 新31線(VC31) 接地RY | FEEDER | P01/11/VC31/GDA |  |  |  | CDC | 548 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC31 | 新31線(VC31) |  | 79UL | [17 empty] | 2-3B-08 |  | 2-60 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_79UL | 新31線(VC31) 79RY U/L | FEEDER | P01/11/VC31/79UL |  |  |  | CDC | 549 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC31 | 新31線(VC31) |  | ADJ | [17 empty] | 2-3E-08 |  | 3-00 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_ADJ | 新31線(VC31) LCO分流器 U/L | FEEDER | P01/11/VC31/ADJ |  |  |  | CDC | 550 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC31 | VC31(新31線) |  | CB | [17 empty] | 2-00-00 |  | 2-38 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_CB | VC31(新31線) CB | FEEDER | P01/11/VC31/CB |  |  |  | CDC | 551 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC32 | 新32線(VC32) |  | PHA | [17 empty] | 2-00-04 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_PHA | 新32線(VC32) 相間RY | FEEDER | P01/11/VC32/PHA |  |  |  | CDC | 552 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC32 | 新32線(VC32) |  | GDA | [17 empty] | 2-00-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_GDA | 新32線(VC32) 接地RY | FEEDER | P01/11/VC32/GDA |  |  |  | CDC | 553 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC32 | 新32線(VC32) |  | 79UL | [17 empty] | 2-3B-09 |  | 2-61 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_79UL | 新32線(VC32) 79RY U/L | FEEDER | P01/11/VC32/79UL |  |  |  | CDC | 554 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC32 | 新32線(VC32) |  | ADJ | [17 empty] | 2-3E-09 |  | 3-01 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_ADJ | 新32線(VC32) LCO分流器 U/L | FEEDER | P01/11/VC32/ADJ |  |  |  | CDC | 555 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC32 | VC32(新32線) |  | CB | [17 empty] | 2-00-03 |  | 2-39 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_CB | VC32(新32線) CB | FEEDER | P01/11/VC32/CB |  |  |  | CDC | 556 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC33 | 新33線(VC33) |  | PHA | [17 empty] | 2-00-07 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_PHA | 新33線(VC33) 相間RY | FEEDER | P01/11/VC33/PHA |  |  |  | CDC | 557 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC33 | 新33線(VC33) |  | GDA | [17 empty] | 2-01-00 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_GDA | 新33線(VC33) 接地RY | FEEDER | P01/11/VC33/GDA |  |  |  | CDC | 558 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC33 | 新33線(VC33) |  | 79UL | [17 empty] | 2-3B-10 |  | 2-62 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_79UL | 新33線(VC33) 79RY U/L | FEEDER | P01/11/VC33/79UL |  |  |  | CDC | 559 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC33 | 新33線(VC33) |  | ADJ | [17 empty] | 2-3E-10 |  | 3-02 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_ADJ | 新33線(VC33) LCO分流器 U/L | FEEDER | P01/11/VC33/ADJ |  |  |  | CDC | 560 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC33 | VC33(新33線) |  | CB | [17 empty] | 2-00-06 |  | 2-3A | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_CB | VC33(新33線) CB | FEEDER | P01/11/VC33/CB |  |  |  | CDC | 561 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC34 | 新34線(VC34) |  | PHA | [17 empty] | 2-01-02 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_PHA | 新34線(VC34) 相間RY | FEEDER | P01/11/VC34/PHA |  |  |  | CDC | 562 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC34 | 新34線(VC34) |  | GDA | [17 empty] | 2-01-03 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_GDA | 新34線(VC34) 接地RY | FEEDER | P01/11/VC34/GDA |  |  |  | CDC | 563 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC34 | 新34線(VC34) |  | 79UL | [17 empty] | 2-3B-11 |  | 2-63 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_79UL | 新34線(VC34) 79RY U/L | FEEDER | P01/11/VC34/79UL |  |  |  | CDC | 564 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC34 | 新34線(VC34) |  | ADJ | [17 empty] | 2-3E-11 |  | 3-03 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_ADJ | 新34線(VC34) LCO分流器 U/L | FEEDER | P01/11/VC34/ADJ |  |  |  | CDC | 565 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC34 | VC34(新34線) |  | CB | [17 empty] | 2-01-01 |  | 2-3B | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_CB | VC34(新34線) CB | FEEDER | P01/11/VC34/CB |  |  |  | CDC | 566 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC37 | 新37線(VC37) |  | PHA | [17 empty] | 2-03-04 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_PHA | 新37線(VC37) 相間RY | FEEDER | P01/11/VC37/PHA |  |  |  | CDC | 567 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC37 | 新37線(VC37) |  | GDA | [17 empty] | 2-03-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_GDA | 新37線(VC37) 接地RY | FEEDER | P01/11/VC37/GDA |  |  |  | CDC | 568 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC37 | 新37線(VC37) |  | 79UL | [17 empty] | 2-3C-00 |  | 2-68 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_79UL | 新37線(VC37) 79RY U/L | FEEDER | P01/11/VC37/79UL |  |  |  | CDC | 569 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC37 | 新37線(VC37) |  | ADJ | [17 empty] | 2-3E-14 |  | 3-06 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_ADJ | 新37線(VC37) LCO分流器 U/L | FEEDER | P01/11/VC37/ADJ |  |  |  | CDC | 570 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC37 | VC37(新37線) |  | CB | [17 empty] | 2-03-03 |  | 2-41 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_CB | VC37(新37線) CB | FEEDER | P01/11/VC37/CB |  |  |  | CDC | 571 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC38 | 新38線(VC38) |  | PHA | [17 empty] | 2-03-07 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_PHA | 新38線(VC38) 相間RY | FEEDER | P01/11/VC38/PHA |  |  |  | CDC | 572 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC38 | 新38線(VC38) |  | GDA | [17 empty] | 2-04-00 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_GDA | 新38線(VC38) 接地RY | FEEDER | P01/11/VC38/GDA |  |  |  | CDC | 573 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC38 | 新38線(VC38) |  | 79UL | [17 empty] | 2-3C-01 |  | 2-69 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_79UL | 新38線(VC38) 79RY U/L | FEEDER | P01/11/VC38/79UL |  |  |  | CDC | 574 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC38 | 新38線(VC38) |  | ADJ | [17 empty] | 2-3E-15 |  | 3-07 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_ADJ | 新38線(VC38) LCO分流器 U/L | FEEDER | P01/11/VC38/ADJ |  |  |  | CDC | 575 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC38 | VC38(新38線) |  | CB | [17 empty] | 2-03-06 |  | 2-42 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_CB | VC38(新38線) CB | FEEDER | P01/11/VC38/CB |  |  |  | CDC | 576 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC39 | 新39線(VC39) |  | PHA | [17 empty] | 2-04-02 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_PHA | 新39線(VC39) 相間RY | FEEDER | P01/11/VC39/PHA |  |  |  | CDC | 577 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC39 | 新39線(VC39) |  | GDA | [17 empty] | 2-04-03 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_GDA | 新39線(VC39) 接地RY | FEEDER | P01/11/VC39/GDA |  |  |  | CDC | 578 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC39 | 新39線(VC39) |  | 79UL | [17 empty] | 2-3C-02 |  | 2-6A | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_79UL | 新39線(VC39) 79RY U/L | FEEDER | P01/11/VC39/79UL |  |  |  | CDC | 579 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC39 | 新39線(VC39) |  | ADJ | [17 empty] | 2-3F-00 |  | 3-08 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_ADJ | 新39線(VC39) LCO分流器 U/L | FEEDER | P01/11/VC39/ADJ |  |  |  | CDC | 580 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC39 | VC39(新39線) |  | CB | [17 empty] | 2-04-01 |  | 2-43 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_CB | VC39(新39線) CB | FEEDER | P01/11/VC39/CB |  |  |  | CDC | 581 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC40 | 新40線(VC40) |  | PHA | [17 empty] | 2-04-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_PHA | 新40線(VC40) 相間RY | FEEDER | P01/11/VC40/PHA |  |  |  | CDC | 582 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC40 | 新40線(VC40) |  | GDA | [17 empty] | 2-04-06 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_GDA | 新40線(VC40) 接地RY | FEEDER | P01/11/VC40/GDA |  |  |  | CDC | 583 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC40 | 新40線(VC40) |  | 79UL | [17 empty] | 2-3C-03 |  | 2-6B | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_79UL | 新40線(VC40) 79RY U/L | FEEDER | P01/11/VC40/79UL |  |  |  | CDC | 584 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC40 | 新40線(VC40) |  | ADJ | [17 empty] | 2-3F-01 |  | 3-09 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_ADJ | 新40線(VC40) LCO分流器 U/L | FEEDER | P01/11/VC40/ADJ |  |  |  | CDC | 585 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC40 | VC40(新40線) |  | CB | [17 empty] | 2-04-04 |  | 2-44 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_CB | VC40(新40線) CB | FEEDER | P01/11/VC40/CB |  |  |  | CDC | 586 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 2-03-00 |  | 2-40 | [5 empty] | ADCS_N | [8 empty] | 新營PS.100_CB | 100(TIE) CB | TIE | P01/11/100/CB |  |  |  | CDC | 587 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-03-01 |  | 1-0A | [5 empty] | 161KV_N | [8 empty] | 新營PS.1500_CB | 1500(TIE) CB | TIE | P01/161/1500/CB |  |  |  | CDC | 588 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-03-02 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1500_50A | 161KV TIE(1500) 50RY | TIE | P01/161/1500/50A |  |  |  | CDC | 589 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-3C-14 | 1-3C-15 | 1-64 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1501_DS | 1501(TIE) DS | TIE | P01/161/1500/DS1 |  |  |  | CDC | 590 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-3D-00 | 1-3D-01 | 1-65 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1502_DS | 1502(TIE) DS | TIE | P01/161/1500/DS2 |  |  |  | CDC | 591 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 2-07-01 |  | 2-4B | [5 empty] | ADCS_N | [8 empty] | 新營PS.200_CB | 200(TIE) CB | TIE | P01/22/200/CB |  |  |  | CDC | 592 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 2-07-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.200_51A | 23KV TIE(200) 51RY | TIE | P01/22/200/PHA |  |  |  | CDC | 593 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 2-07-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.200_51NA | 23KV TIE(200) 51N RY | TIE | P01/22/200/GDA |  |  |  | CDC | 594 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-0A-04 |  | 1-24 | [5 empty] | 69KV_N | [8 empty] | 新營PS.600_CB | 600(TIE) CB | TIE | P01/69/600/CB |  |  |  | CDC | 595 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 2-36-00 | 2-36-01 | 2-30 | [5 empty] | ADCS_N | [8 empty] | 新營PS.601_DS | 601(TIE) DS | TIE | P01/69/600/DS1 |  |  |  | CDC | 596 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 2-36-02 | 2-36-03 | 2-31 | [5 empty] | ADCS_N | [8 empty] | 新營PS.602_DS | 602(TIE) DS | TIE | P01/69/600/DS2 |  |  |  | CDC | 597 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB | [17 empty] | 1-04-00 |  | 1-0B | [5 empty] | 161KV_N | [8 empty] | 新營PS.1650_CB | 1650(#1MTR) CB | MTR | P01/161/1650/CB |  |  |  | CDC | 598 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-04-01 |  | 1-11 | [5 empty] | 69KV_N | [8 empty] | 新營PS.750_CB | 750(#1MTR) CB | MTR | P01/69/750/CB |  |  |  | CDC | 599 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-04-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | P01//1MTR/51ZA |  |  |  | CDC | 600 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-04-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#1MTR_87A | #1MTR 87RY | MTR | P01//1MTR/87A |  |  |  | CDC | 601 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-04-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | P01//1MTR/96PA |  |  |  | CDC | 602 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 1-35-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_96D | #1MTR 96D RY | MTR | P01//1MTR/96D |  |  |  | CDC | 603 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 1-35-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_96P | #1MTR 96P RY | MTR | P01//1MTR/96P |  |  |  | CDC | 604 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 1-35-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_63Q | #1MTR 63Q RY | MTR | P01//1MTR/63Q |  |  |  | CDC | 605 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 1-35-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | P01//1MTR/96B1 |  |  |  | CDC | 606 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 1-35-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_96B2 | #1MTR 96B2 RY | MTR | P01//1MTR/96B2 |  |  |  | CDC | 607 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-30-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_TRA | #1MTR 重故障 | MTR | P01//1MTR/TRA |  |  |  | CDC | 608 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-30-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_TRF | #1MTR 輕故障 | MTR | P01//1MTR/TRF |  |  |  | CDC | 609 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-30-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | P01//1MTR/SupLocal |  |  |  | CDC | 610 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-30-03 |  | 1-29 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | P01//1MTR/Tap Chan |  |  |  | CDC | 611 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | M/F/I | [17 empty] | 1-38-00 | 1-38-01 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | P01//1MTR/M_F_I |  |  |  | CDC | 612 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 | [16 empty] | 1-3D-02 | 1-3D-03 | 1-66 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1651_DS | 1651(#1MTR) DS | MTR | P01/161/1650/DS1 |  |  |  | CDC | 613 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 | [16 empty] | 1-3D-04 | 1-3D-05 | 1-67 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1652_DS | 1652(#1MTR) DS | MTR | P01/161/1650/DS2 |  |  |  | CDC | 614 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-3E-10 | 1-3E-11 | 1-72 | [5 empty] | ADCS_N | [8 empty] | 新營PS.751_DS | 751(#1MTR) DS | MTR | P01/69/750/DS1 |  |  |  | CDC | 615 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-3E-12 | 1-3E-13 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 新營PS.752_DS | 752(#1MTR) DS | MTR | P01/69/750/DS2 |  |  |  | CDC | 616 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | [17 empty] | 1-05-00 |  | 1-0C | [5 empty] | 161KV_N | [8 empty] | 新營PS.1660_CB | 1660(#2MTR) CB | MTR | P01/161/1660/CB |  |  |  | CDC | 617 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-05-01 |  | 1-12 | [5 empty] | 69KV_N | [8 empty] | 新營PS.760_CB | 760(#2MTR) CB | MTR | P01/69/760/CB |  |  |  | CDC | 618 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-05-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | P01//2MTR/51ZA |  |  |  | CDC | 619 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-05-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2MTR_87A | #2MTR 87RY | MTR | P01//2MTR/87A |  |  |  | CDC | 620 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-05-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | P01//2MTR/96PA |  |  |  | CDC | 621 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 1-35-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_96D | #2MTR 96D RY | MTR | P01//2MTR/96D |  |  |  | CDC | 622 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 1-35-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_96P | #2MTR 96P RY | MTR | P01//2MTR/96P |  |  |  | CDC | 623 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 1-35-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_63Q | #2MTR 63Q RY | MTR | P01//2MTR/63Q |  |  |  | CDC | 624 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 1-35-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | P01//2MTR/96B1 |  |  |  | CDC | 625 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 1-35-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | P01//2MTR/96B2 |  |  |  | CDC | 626 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-30-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_TRA | #2MTR 重故障 | MTR | P01//2MTR/TRA |  |  |  | CDC | 627 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-30-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_TRF | #2MTR 輕故障 | MTR | P01//2MTR/TRF |  |  |  | CDC | 628 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-30-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | P01//2MTR/SupLocal |  |  |  | CDC | 629 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-30-07 |  | 1-2D | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | P01//2MTR/Tap Chan |  |  |  | CDC | 630 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | M/F/I | [17 empty] | 1-38-02 | 1-38-03 | 1-2E | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | P01//2MTR/M_F_I |  |  |  | CDC | 631 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 | [16 empty] | 1-3D-06 | 1-3D-07 | 1-68 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1661_DS | 1661(#2MTR) DS | MTR | P01/161/1660/DS1 |  |  |  | CDC | 632 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 | [16 empty] | 1-3D-08 | 1-3D-09 | 1-69 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1662_DS | 1662(#2MTR) DS | MTR | P01/161/1660/DS2 |  |  |  | CDC | 633 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-3E-14 | 1-3E-15 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 新營PS.761_DS | 761(#2MTR) DS | MTR | P01/69/760/DS1 |  |  |  | CDC | 634 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-3F-00 | 1-3F-01 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 新營PS.762_DS | 762(#2MTR) DS | MTR | P01/69/760/DS2 |  |  |  | CDC | 635 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB | [17 empty] | 1-06-00 |  | 1-0D | [5 empty] | 161KV_N | [8 empty] | 新營PS.1670_CB | 1670(#3MTR) CB | MTR | P01/161/1670/CB |  |  |  | CDC | 636 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-06-01 |  | 1-13 | [5 empty] | 69KV_N | [8 empty] | 新營PS.770_CB | 770(#3MTR) CB | MTR | P01/69/770/CB |  |  |  | CDC | 637 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-06-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | P01//3MTR/51ZA |  |  |  | CDC | 638 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3MTR_87A | #3MTR 87RY | MTR | P01//3MTR/87A |  |  |  | CDC | 639 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-06-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | P01//3MTR/96PA |  |  |  | CDC | 640 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 1-35-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_96D | #3MTR 96D RY | MTR | P01//3MTR/96D |  |  |  | CDC | 641 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 1-35-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_96P | #3MTR 96P RY | MTR |  |  |  |  | CDC | 642 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 1-35-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_63Q | #3MTR 63Q RY | MTR | P01//3MTR/63Q |  |  |  | CDC | 643 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 1-35-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | P01//3MTR/96B1 |  |  |  | CDC | 644 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 1-35-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_96B2 | #3MTR 96B2 RY | MTR | P01//3MTR/96B2 |  |  |  | CDC | 645 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-30-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_TRA | #3MTR 重故障 | MTR | P01//3MTR/TRA |  |  |  | CDC | 646 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-30-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_TRF | #3MTR 輕故障 | MTR | P01//3MTR/TRF |  |  |  | CDC | 647 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-30-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | P01//3MTR/SupLocal |  |  |  | CDC | 648 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-30-11 |  | 1-31 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | P01//3MTR/Tap Chan |  |  |  | CDC | 649 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | M/F/I | [17 empty] | 1-38-04 | 1-38-05 | 1-32 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | P01//3MTR/M_F_I |  |  |  | CDC | 650 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | DS1 | 1671 | [16 empty] | 1-3D-10 | 1-3D-11 | 1-6A | [5 empty] | ADCS_N | [8 empty] | 新營PS.1671_DS | 1671(#3MTR) DS | MTR | P01/161/1670/DS1 |  |  |  | CDC | 651 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | DS2 | 1672 | [16 empty] | 1-3D-12 | 1-3D-13 | 1-6B | [5 empty] | ADCS_N | [8 empty] | 新營PS.1672_DS | 1672(#3MTR) DS | MTR | P01/161/1670/DS2 |  |  |  | CDC | 652 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | DS1 | 771 | [16 empty] | 1-3F-02 | 1-3F-03 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 新營PS.771_DS | 771(#3MTR) DS | MTR | P01/69/770/DS1 |  |  |  | CDC | 653 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | DS2 | 772 | [16 empty] | 1-3F-04 | 1-3F-05 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 新營PS.772_DS | 772(#3MTR) DS | MTR | P01/69/770/DS2 |  |  |  | CDC | 654 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-08-00 |  | 1-0F | [5 empty] | 161KV_N | [8 empty] | 新營PS.1760_CB | 1760(#2DTR) CB | MTR | P01/161/1760/CB |  |  |  | CDC | 655 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-08-01 |  | 1-14 | [5 empty] | ADCS_N | [8 empty] | 新營PS.330_CB | 330(#2DTR) CB | MTR | P01/11/330/CB |  |  |  | CDC | 656 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-08-02 |  | 1-16 | [5 empty] | ADCS_N | [8 empty] | 新營PS.340_CB | 340(#2DTR) CB | MTR | P01/22/340/CB |  |  |  | CDC | 657 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 51A | [17 empty] | 1-08-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2DTR_51A | #2DTR 51RY | MTR | P01/161/1760/PHA |  |  |  | CDC | 658 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 51NA | [17 empty] | 1-08-07 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2DTR_51NA | #2DTR 51N RY | MTR | P01/161/1760/GDA |  |  |  | CDC | 659 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-08-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2DTR_51ZA | #2DTR 51Z RY | MTR | P01//2DTR/51ZA |  |  |  | CDC | 660 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-08-03 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2DTR_87A | #2DTR 87RY | MTR | P01//2DTR/87A |  |  |  | CDC | 661 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-09-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.330_51A | #2DTR二次側(330) 51RY | MTR | P01/11/330/PHA |  |  |  | CDC | 662 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-09-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.340_51A | #2DTR二次側(340) 51RY | MTR | P01/22/340/PHA |  |  |  | CDC | 663 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-08-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | P01//2DTR/96PA |  |  |  | CDC | 664 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 1-36-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_96D | #2DTR 96D RY | MTR | P01//2DTR/96D |  |  |  | CDC | 665 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 1-36-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_96P | #2DTR 96P RY | MTR | P01//2DTR/96P |  |  |  | CDC | 666 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 1-36-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_63Q | #2DTR 63Q RY | MTR | P01//2DTR/63Q |  |  |  | CDC | 667 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 1-36-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | P01//2DTR/96B1 |  |  |  | CDC | 668 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 1-36-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | P01//2DTR/96B2 |  |  |  | CDC | 669 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-31-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_TRA | #2DTR 重故障 | MTR | P01//2DTR/TRA |  |  |  | CDC | 670 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-31-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_TRF | #2DTR 輕故障 | MTR | P01//2DTR/TRF |  |  |  | CDC | 671 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-31-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | P01//2DTR(A)/SupLocal |  |  |  | CDC | 672 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-31-03 |  | 1-37 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | P01//2DTR(A)/Tap Chan |  |  |  | CDC | 673 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-31-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | P01//2DTR(B)/SupLocal |  |  |  | CDC | 674 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-31-05 |  | 1-39 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | P01//2DTR(B)/Tap Chan |  |  |  | CDC | 675 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3E-02 | 1-3E-03 | 1-6E | [5 empty] | ADCS_N | [8 empty] | 新營PS.1761_DS | 1761(#2DTR) DS | MTR | P01/161/1760/DS1 |  |  |  | CDC | 676 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3E-04 | 1-3E-05 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 新營PS.1762_DS | 1762(#2DTR) DS | MTR | P01/161/1760/DS2 |  |  |  | CDC | 677 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 1-09-02 |  | 1-10 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1770_CB | 1770(#3DTR) CB | MTR | P01/161/1770/CB |  |  |  | CDC | 678 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-09-04 |  | 1-15 | [5 empty] | ADCS_N | [8 empty] | 新營PS.350_CB | 350(#3DTR) CB | MTR | P01/11/350/CB |  |  |  | CDC | 679 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 360 | #3DTR(360) |  | CB | [17 empty] | 1-09-03 |  | 1-17 | [5 empty] | ADCS_N | [8 empty] | 新營PS.360_CB | 360(#3DTR) CB | MTR | P01/22/360/CB |  |  |  | CDC | 680 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 51A | [17 empty] | 1-0A-00 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3DTR_51A | #3DTR 51RY | MTR | P01//3DTR/PHA |  |  |  | CDC | 681 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 51NA | [17 empty] | 1-0A-01 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3DTR_51NA | #3DTR 51N RY | MTR | P01//3DTR/GDA |  |  |  | CDC | 682 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 1-09-07 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3DTR_51ZA | #3DTR 51Z RY | MTR | P01//3DTR/51ZA |  |  |  | CDC | 683 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 1-09-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3DTR_87A | #3DTR 87RY | MTR | P01//3DTR/87A |  |  |  | CDC | 684 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-0A-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.350_51A | #3DTR二次側(350) 51RY | MTR | P01/22/360/PHA |  |  |  | CDC | 685 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 360 | #3DTR(360) |  | 51A | [17 empty] | 1-0A-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.360_51A | #3DTR二次側(360) 51RY | MTR | P01/11/350/PHA |  |  |  | CDC | 686 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#3DTR_96PA | #3DTR 機械保護動作 | MTR | P01//3DTR/96PA |  |  |  | CDC | 687 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 1-36-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_96D | #3DTR 96D RY | MTR | P01//3DTR/96D |  |  |  | CDC | 688 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 1-36-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_96P | #3DTR 96P RY | MTR | P01//3DTR/96P |  |  |  | CDC | 689 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 1-36-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_63Q | #3DTR 63Q RY | MTR | P01//3DTR/63Q |  |  |  | CDC | 690 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 1-36-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | P01//3DTR/96B1 |  |  |  | CDC | 691 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 1-36-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | P01//3DTR/96B2 |  |  |  | CDC | 692 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 1-31-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_TRA | #3DTR 重故障 | MTR | P01//3DTR/TRA |  |  |  | CDC | 693 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 1-31-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_TRF | #3DTR 輕故障 | MTR | P01//3DTR/TRF |  |  |  | CDC | 694 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | SupLocal | [17 empty] | 1-31-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | P01//3DTR(A)/SupLocal |  |  |  | CDC | 695 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 3DTR(A) | #3DTR(A) |  | A_M | [17 empty] | 1-31-09 |  | 1-3B | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | P01//3DTR(A)/Tap Chan |  |  |  | CDC | 696 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR(B) |  | SupLocal | [17 empty] | 1-31-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | P01//3DTR(B)/SupLocal |  |  |  | CDC | 697 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 3DTR(B) | #3DTR(B) |  | A_M | [17 empty] | 1-31-11 |  | 1-3D | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | P01//3DTR(B)/Tap Chan |  |  |  | CDC | 698 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 1-3E-06 | 1-3E-07 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1771_DS | 1771(#3DTR) DS | MTR | P01/161/1770/DS1 |  |  |  | CDC | 699 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 1-3E-08 | 1-3E-09 | 1-71 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1772_DS | 1772(#3DTR) DS | MTR | P01/161/1770/DS2 |  |  |  | CDC | 700 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 2-02-02 |  | 2-3E | [5 empty] | ADCS_N | [8 empty] | 新營PS.210_CB | 210(11KV #1SC) CB | SC | P01/11/210/CB |  |  |  | CDC | 701 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 2-3B-14 |  | 2-66 | [5 empty] | ADCS_N | [8 empty] | 新營PS.210_A/M | 11KV #1SC 乏控器 A/M | SC | P01/11/210/SC_A_M |  |  |  | CDC | 702 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 2-02-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.210_SCA | 11KV #1SC 51,51N RY | SC | P01/11/210/SCA |  |  |  | CDC | 703 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 2-02-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | P01/11/210/UVA |  |  |  | CDC | 704 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 2-02-05 |  | 2-3F | [5 empty] | ADCS_N | [8 empty] | 新營PS.220_CB | 220(11KV #2SC) CB | SC | P01/11/220/CB |  |  |  | CDC | 705 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 2-3B-15 |  | 2-67 | [5 empty] | ADCS_N | [8 empty] | 新營PS.220_A/M | 11KV #2SC 乏控器 A/M | SC | P01/11/220/SC_A_M |  |  |  | CDC | 706 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 2-02-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.220_SCA | 11KV #2SC 51,51N RY | SC | P01/11/220/SCA |  |  |  | CDC | 707 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 2-02-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | P01/11/220/UVA |  |  |  | CDC | 708 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | CB | [17 empty] | 2-06-06 |  | 2-4A | [5 empty] | ADCS_N | [8 empty] | 新營PS.230_CB | 230(23KV #3SC) CB | SC | P01/22/230/CB |  |  |  | CDC | 709 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 2-3C-09 |  | 2-71 | [5 empty] | ADCS_N | [8 empty] | 新營PS.230_A/M | 23KV #3SC 乏控器 A/M | SC | P01/22/230/SC_A_M |  |  |  | CDC | 710 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | SCA | [17 empty] | 2-06-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.230_SCA | 23KV #3SC 51,51N RY | SC | P01/22/230/SCA |  |  |  | CDC | 711 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 230 | #3SC(230) |  | UVA | [17 empty] | 2-07-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.230_UVA | 23KV #3SC 27RY(欠壓) | SC | P01/22/230/UVA |  |  |  | CDC | 712 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 2-04-07 |  | 2-45 | [5 empty] | ADCS_N | [8 empty] | 新營PS.240_CB | 240(11KV #4SC) CB | SC | P01/11/240/CB |  |  |  | CDC | 713 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 2-3C-04 |  | 2-6C | [5 empty] | ADCS_N | [8 empty] | 新營PS.240_A/M | 11KV #4SC 乏控器 A/M | SC | P01/11/240/SC_A_M |  |  |  | CDC | 714 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 2-05-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.240_SCA | 11KV #4SC 51,51N RY | SC | P01/11/240/SCA |  |  |  | CDC | 715 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 2-05-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | P01/11/240/UVA |  |  |  | CDC | 716 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | CB | [17 empty] | 2-09-06 |  | 2-52 | [5 empty] | ADCS_N | [8 empty] | 新營PS.250_CB | 250(23KV #5SC) CB | SC | P01/22/250/CB |  |  |  | CDC | 717 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 2-3D-00 |  | 2-78 | [5 empty] | ADCS_N | [8 empty] | 新營PS.250_A/M | 23KV #5SC 乏控器 A/M | SC | P01/22/250/SC_A_M |  |  |  | CDC | 718 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | SCA | [17 empty] | 2-09-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.250_SCA | 23KV #5SC 51,51N RY | SC | P01/22/250/SCA |  |  |  | CDC | 719 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 250 | #5SC(250) |  | UVA | [17 empty] | 2-0A-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.250_UVA | 23KV #5SC 27RY(欠壓) | SC | P01/22/250/UVA |  |  |  | CDC | 720 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | CB | [17 empty] | 2-0A-01 |  | 2-53 | [5 empty] | ADCS_N | [8 empty] | 新營PS.260_CB | 260(23KV #6SC) CB | SC | P01/22/260/CB |  |  |  | CDC | 721 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 2-3D-01 |  | 2-79 | [5 empty] | ADCS_N | [8 empty] | 新營PS.260_A/M | 23KV #6SC 乏控器 A/M | SC | P01/22/260/SC_A_M |  |  |  | CDC | 722 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | SCA | [17 empty] | 2-0A-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.260_SCA | 23KV #6SC 51,51N RY | SC | P01/22/260/SCA |  |  |  | CDC | 723 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 22 | 22kV | 260 | #6SC(260) |  | UVA | [17 empty] | 2-0A-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.260_UVA | 23KV #6SC 27RY(欠壓) | SC | P01/22/260/UVA |  |  |  | CDC | 724 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-1E-00 |  | 1-25 | [5 empty] | 69KV_N | [8 empty] | 新營PS.810_CB | 810(69KV #1SC) CB | SC | P01/69/810/CB |  |  |  | CDC | 725 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 2-36-04 | 2-36-05 | 2-32 | [5 empty] | ADCS_N | [8 empty] | 新營PS.811_DS | 811(69KV #1SC) DS | SC | P01/69/810/DS1 |  |  |  | CDC | 726 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 2-36-06 | 2-36-07 | 2-33 | [5 empty] | ADCS_N | [8 empty] | 新營PS.812_DS | 812(69KV #1SC) DS | SC | P01/69/810/DS2 |  |  |  | CDC | 727 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-1E-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.810_SCA | 69KV #1SC 51,51N RY | SC | P01/69/810/SCA |  |  |  | CDC | 728 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-1E-02 | [7 empty] | 69KV_N | [8 empty] | 新營PS.810_OUVA | 69KV #1SC 27,59RY | SC | P01/69/810/UVA |  |  |  | CDC | 729 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | CB | [17 empty] | 1-1E-03 |  | 1-26 | [5 empty] | 69KV_N | [8 empty] | 新營PS.820_CB | 820(69KV #2SC) CB | SC | P01/69/820/CB |  |  |  | CDC | 730 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | DS1 | 821 | [16 empty] | 2-36-08 | 2-36-09 | 2-34 | [5 empty] | ADCS_N | [8 empty] | 新營PS.821_DS | 821(69KV #2SC) DS | SC | P01/69/820/DS1 |  |  |  | CDC | 731 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | DS2 | 822 | [16 empty] | 2-36-10 | 2-36-11 | 2-35 | [5 empty] | ADCS_N | [8 empty] | 新營PS.822_DS | 822(69KV #2SC) DS | SC | P01/69/820/DS2 |  |  |  | CDC | 732 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | SCA | [17 empty] | 1-1E-04 | [7 empty] | 69KV_N | [8 empty] | 新營PS.820_SCA | 69KV #2SC 51,51N RY | SC | P01/69/820/SCA |  |  |  | CDC | 733 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 820 | #2SC(820) |  | UVA | [17 empty] | 1-1E-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.820_OUVA | 69KV #2SC 27,59RY | SC | P01/69/820/UVA |  |  |  | CDC | 734 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | CB | [17 empty] | 1-1E-06 |  | 1-27 | [5 empty] | 69KV_N | [8 empty] | 新營PS.830_CB | 830(69KV #3SC) CB | SC | P01/69/830/CB |  |  |  | CDC | 735 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | DS1 | 831 | [16 empty] | 2-36-12 | 2-36-13 | 2-36 | [5 empty] | ADCS_N | [8 empty] | 新營PS.831_DS | 831(69KV #3SC) DS | SC | P01/69/830/DS1 |  |  |  | CDC | 736 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | DS2 | 832 | [16 empty] | 2-36-14 | 2-36-15 | 2-37 | [5 empty] | ADCS_N | [8 empty] | 新營PS.832_DS | 832(69KV #3SC) DS | SC | P01/69/830/DS2 |  |  |  | CDC | 737 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | SCA | [17 empty] | 1-1E-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.830_SCA | 69KV #3SC 51,51N RY | SC | P01/69/830/SCA |  |  |  | CDC | 738 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 830 | #3SC(830) |  | UVA | [17 empty] | 1-1F-00 | [7 empty] | 69KV_N | [8 empty] | 新營PS.830_OUVA | 69KV #3SC 27,59RY | SC | P01/69/830/UVA |  |  |  | CDC | 739 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-32-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | P01/161/1BUS/BUS_VUA |  |  |  | CDC | 740 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-03-03 | [7 empty] | 161KV_N | [8 empty] | 新營PS.161#1BUS_87A | 161KV #1BUS 87A | BUS | P01/161/1BUS/87A |  |  |  | CDC | 741 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-31-14 |  | 3-34 | [5 empty] | ADCS_N | [8 empty] | 新營PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | P01/161/1BUS/87UL |  |  |  | CDC | 742 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-32-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | P01/161/2BUS/BUS_VUA |  |  |  | CDC | 743 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-03-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.161#2BUS_87A | 161KV #2BUS 87A | BUS | P01/161/2BUS/87A |  |  |  | CDC | 744 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-31-15 |  | 3-35 | [5 empty] | ADCS_N | [8 empty] | 新營PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | P01/161/2BUS/87UL |  |  |  | CDC | 745 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 2-3D-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | P01/69/1BUS/BUS_VUA |  |  |  | CDC | 746 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-0A-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.69#1BUS_87A | 69KV #1BUS 87A | BUS | P01/69/1BUS/87A |  |  |  | CDC | 747 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 691BUS | #1BUS |  | 87UL | [17 empty] | 2-3B-04 |  | 3-36 | [5 empty] | ADCS_N | [8 empty] | 新營PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | P01/69/1BUS/87UL |  |  |  | CDC | 748 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 2-3D-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | P01/69/2BUS/BUS_VUA |  |  |  | CDC | 749 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-0B-00 | [7 empty] | 69KV_N | [8 empty] | 新營PS.69#2BUS_87A | 69KV #2BUS 87A | BUS | P01/69/2BUS/87A |  |  |  | CDC | 750 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 692BUS | #2BUS |  | 87UL | [17 empty] | 2-3B-05 |  | 3-37 | [5 empty] | ADCS_N | [8 empty] | 新營PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | P01/69/2BUS/87UL |  |  |  | CDC | 751 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 11 | 11kV |  |  |  | CBA | [17 empty] | 2-3B-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.11KV_CBA | 11KV斷路器重故障 | OTHER | P01/22/ComPoint/CBA |  |  |  | CDC | 752 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV |  |  |  | CBF | [17 empty] | 2-3B-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.11KV_CBF | 11KV斷路器輕故障 | OTHER | P01/22/ComPoint/CBF |  |  |  | CDC | 753 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-32-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_CBA | 161KV斷路器重故障 | OTHER | P01/161/ComPoint/CBA |  |  |  | CDC | 754 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-32-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | P01/161/ComPoint/CBF |  |  |  | CDC | 755 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV |  |  |  | OSCA | [17 empty] | 1-0B-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_OSCA | 161KV示波器啟動警報 | OTHER | P01/161/ComPoint/OSCA |  |  |  | CDC | 756 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0B-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | P01/161/ComPoint/RCA |  |  |  | CDC | 757 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV |  |  |  | COMT | [17 empty] | 1-32-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161空壓機COMT | 161KV空壓機運轉超時警報 | OTHER | P01/161/ComPoint/COMT |  |  |  | CDC | 758 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV |  |  |  | CBA | [17 empty] | 2-3D-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_CBA | 69KV斷路器重故障 | OTHER | P01/69/ComPoint/CBA |  |  |  | CDC | 759 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV |  |  |  | CBF | [17 empty] | 2-3D-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | P01/69/ComPoint/CBF |  |  |  | CDC | 760 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV |  |  |  | OSCA | [17 empty] | 1-0B-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_OSCA | 69KV示波器啟動警報 | OTHER | P01/69/ComPoint/OSCA |  |  |  | CDC | 761 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV |  |  |  | COMT | [17 empty] | 2-3D-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69空壓機COMT | 69KV空壓機運轉超時警報 | OTHER | P01/69/ComPoint/COMT |  |  |  | CDC | 762 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | P01/0/RTU/RTU_R_L |  |  |  | CDC | 763 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P01 | 新營PS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 新營PS.TEST_CB | TEST CB | OTHER | P01/0/RTU/Test_CB |  |  |  | CDC | 764 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-34-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.火災警報(2) | 火災警報(2)建物-ADCC大樓 | OTHER | P01/0/StaDev/Fire2 |  |  |  | CDC | 765 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | Fire3 | [17 empty] | 1-34-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.火災警報(3) | 火災警報(3) | OTHER |  |  |  |  | CDC | 766 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | OPA | [17 empty] | 1-33-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | P01/0/ComPoint/OPA |  |  |  | CDC | 767 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 25PFA | [17 empty] | 2-3B-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | P01/0/ComPoint/25PFA |  |  |  | CDC | 768 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 25TA | [17 empty] | 2-3B-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | P01/0/ComPoint/25TA |  |  |  | CDC | 769 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-3D-11 |  | 2-7A | [5 empty] | ADCS_N | [8 empty] | 新營PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | P01/0/StaDev/ACB1 |  |  |  | CDC | 770 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P01 | 新營PS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-3D-13 |  | 2-7C | [5 empty] | ADCS_N | [8 empty] | 新營PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | P01/0/StaDev/ACB2 |  |  |  | CDC | 771 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P01 | 新營PS | 0 |  |  |  |  | STUV | [17 empty] | 1-33-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | P01/0/StaDev/STUV |  |  |  | CDC | 772 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-3D-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | P01/0/StaDev/CHG1 |  |  |  | CDC | 773 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | DCA | [17 empty] | 2-3D-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.直流電源DCA | 直流電源故障警報 | OTHER | P01/0/StaDev/DCA |  |  |  | CDC | 774 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | DCE | [17 empty] | 2-3D-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.直流電源DCE | 直流電源接地故障警報 | OTHER | P01/0/StaDev/DCE |  |  |  | CDC | 775 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 通訊PCM警報 | [17 empty] | 1-33-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.通訊PCM警報 | 通訊設備PCM警報 | OTHER |  |  |  |  | CDC | 776 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-33-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | P01/0/StaDev/CHG2 |  |  |  | CDC | 777 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | CommACF | [17 empty] | 1-33-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | P01/0/StaDev/CommACF |  |  |  | CDC | 778 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-34-00 |  | 1-78 | [5 empty] | ADCS_N | [8 empty] | 新營PS.開關場照明(A) | 開關場照明(A) | OTHER | P01/0/StaDev/Lights1 |  |  |  | CDC | 779 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-34-01 |  | 1-79 | [5 empty] | ADCS_N | [8 empty] | 新營PS.開關場照明(B) | 開關場照明(B) | OTHER | P01/0/StaDev/Lights2 |  |  |  | CDC | 780 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  |  |  |  | Lights3 | [17 empty] | 1-34-02 |  | 1-7A | [5 empty] | ADCS_N | [8 empty] | 新營PS.開關場照明(C) | 開關場照明(C) | OTHER | P01/0/StaDev/Lights3 |  |  |  | CDC | 781 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  |  |  |  | Lights4 | [17 empty] | 1-34-03 |  | 1-7B | [5 empty] | ADCS_N | [8 empty] | 新營PS.開關場照明(D) | 開關場照明(D) | OTHER | P01/0/StaDev/Lights4 |  |  |  | CDC | 782 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 161 | 161kV | _CB79 | _CB79 |  | PA | [17 empty] | 1-32-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_CB79_PA | 161線路復閉壓力不足 | OTHER |  |  |  |  | CDC | 783 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 1-33-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_OSCF | 161KV示波器缺紙或故障警報 | OTHER | P01/161/ComPoint/OSCF |  |  |  | CDC | 784 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV |  |  |  | OSCF | [17 empty] | 2-3D-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_OSCF | 69KV示波器缺紙或故障警報 | OTHER | P01/69/ComPoint/OSCF |  |  |  | CDC | 785 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 所內#1ACBA | [17 empty] | 2-3D-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內#1ACBA | 開關場所內電源#1ACBA | OTHER | P01/0/StaDev/ACBA1 |  |  |  | CDC | 786 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 所內#2ACBA | [17 empty] | 2-3E-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內#2ACBA | 開關場所內電源#2ACBA | OTHER | P01/0/StaDev/ACBA2 |  |  |  | CDC | 787 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | Lights | [17 empty] | 1-34-04 |  | 1-7C | [5 empty] | ADCS_N | [8 empty] | 新營PS.開關場照明(E) | 開關場照明(E) | OTHER | P01/0/StaDev/Lights5 |  |  |  | CDC | 788 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  |  |  |  | Lights | [17 empty] | 1-34-05 |  | 1-7D | [5 empty] | ADCS_N | [8 empty] | 新營PS.開關場照明(F) | 開關場照明(F) | OTHER | P01/0/StaDev/Lights6 |  |  |  | CDC | 789 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | D_KEY | [33 empty] | ON/OFF | OFF
P01 | 新營PS | 11 | 11kV | _SC | 電容器組 |  | 60A | [17 empty] | 1-34-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.11KV_SC_60A | 11KV電容器組 60RY | OTHER | P01/11/ComPoint/FDR_60A |  |  |  | CDC | 790 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC35 | 新35線(VC35) |  | PHA | [17 empty] | 2-01-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_PHA | 新35線(VC35) 相間RY | FEEDER | P01/11/VC35/PHA |  |  |  | CDC | 791 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC35 | 新35線(VC35) |  | GDA | [17 empty] | 2-01-06 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_GDA | 新35線(VC35) 接地RY | FEEDER | P01/11/VC35/GDA |  |  |  | CDC | 792 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC35 | 新35線(VC35) |  | 79UL | [17 empty] | 2-3B-12 |  | 2-64 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_79UL | 新35線(VC35) 79RY U/L | FEEDER | P01/11/VC35/79UL |  |  |  | CDC | 793 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC35 | 新35線(VC35) |  | ADJ | [17 empty] | 2-3E-12 |  | 3-04 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_ADJ | 新35線(VC35) LCO分流器 U/L | FEEDER | P01/11/VC35/ADJ |  |  |  | CDC | 794 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC35 | VC35(新35線) |  | CB | [17 empty] | 2-01-04 |  | 2-3C | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_CB | VC35(新35線) CB | FEEDER | P01/11/VC35/CB |  |  |  | CDC | 795 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC36 | 新36線(VC36) |  | PHA | [17 empty] | 2-02-00 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_PHA | 新36線(VC36) 相間RY | FEEDER | P01/11/VC36/PHA |  |  |  | CDC | 796 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC36 | 新36線(VC36) |  | GDA | [17 empty] | 2-02-01 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_GDA | 新36線(VC36) 接地RY | FEEDER | P01/11/VC36/GDA |  |  |  | CDC | 797 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC36 | 新36線(VC36) |  | 79UL | [17 empty] | 2-3B-13 |  | 2-65 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_79UL | 新36線(VC36) 79RY U/L | FEEDER | P01/11/VC36/79UL |  |  |  | CDC | 798 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC36 | 新36線(VC36) |  | ADJ | [17 empty] | 2-3E-13 |  | 3-05 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_ADJ | 新36線(VC36) LCO分流器 U/L | FEEDER | P01/11/VC36/ADJ |  |  |  | CDC | 799 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC36 | VC36(新36線) |  | CB | [17 empty] | 2-01-07 |  | 2-3D | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_CB | VC36(新36線) CB | FEEDER | P01/11/VC36/CB |  |  |  | CDC | 800 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 調度中心電源 | 調度中心電源 |  | ACB4 | [17 empty] | 2-3E-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內電源ACB4 | 調度中心電源 ACB4(#4SSTR) | OTHER | P01/0/StaDev/ACB4 |  |  |  | CDC | 801 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | CB | [17 empty] | 1-0F-00 |  | 1-0E | [5 empty] | 161KV_N | [8 empty] | 新營PS.1680_CB | 1680(#4MTR) CB | MTR | P01/161/1680/CB |  |  |  | CDC | 802 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 1-0F-01 |  | 1-09 | [5 empty] | 69KV_N | [8 empty] | 新營PS.780_CB | 780(#4MTR) CB | MTR | P01/69/780/CB |  |  |  | CDC | 803 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 1-0F-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#4MTR_51ZA | #4MTR 51Z RY | MTR | P01//4MTR/51ZA |  |  |  | CDC | 804 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-0F-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#4MTR_87A | #4MTR 87RY | MTR | P01//4MTR/87A |  |  |  | CDC | 805 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 1-0F-05 | [7 empty] | 161KV_N | [8 empty] | 新營PS.#4MTR_96PA | #4MTR 機械保護動作 | MTR | P01//4MTR/96PA |  |  |  | CDC | 806 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 96D | [17 empty] | 2-3F-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_96D | #4MTR 96D RY | MTR | P01//4MTR/96D |  |  |  | CDC | 807 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 96P | [17 empty] | 2-3E-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_96P | #4MTR 96P RY | MTR | P01//4MTR/96P |  |  |  | CDC | 808 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 63Q | [17 empty] | 2-3F-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_63Q | #4MTR 63Q RY | MTR | P01//4MTR/63Q |  |  |  | CDC | 809 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 96B1 | [17 empty] | 2-3F-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_96B1 | #4MTR 96B1 RY | MTR | P01//4MTR/96B1 |  |  |  | CDC | 810 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 96B2 | [17 empty] | 2-3F-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_96B2 | #4MTR 96B2 RY | MTR | P01//4MTR/96B2 |  |  |  | CDC | 811 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 1-37-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_TRA | #4MTR 重故障 | MTR | P01//4MTR/TRA |  |  |  | CDC | 812 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 1-37-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_TRF | #4MTR 輕故障 | MTR | P01//4MTR/TRF |  |  |  | CDC | 813 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 1-37-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_S/L | #4MTR OLTC S/L | MTR | P01//4MTR/SupLocal |  |  |  | CDC | 814 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 1-37-11 |  | 3-16 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_A/M | #4MTR OLTC A/M | MTR | P01//4MTR/Tap Chan |  |  |  | CDC | 815 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | M/F/I | [17 empty] | 1-37-14 | 1-37-15 | 3-17 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_M/F/I | #4MTR M/F/I | MTR | P01//4MTR/M_F_I |  |  |  | CDC | 816 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | DS1 | 1681 | [16 empty] | 1-3D-14 | 1-3D-15 | 1-6C | [5 empty] | ADCS_N | [8 empty] | 新營PS.1681_DS | 1681(#4MTR) DS | MTR | P01/161/1680/DS1 |  |  |  | CDC | 817 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | DS2 | 1682 | [16 empty] | 1-3E-00 | 1-3E-01 | 1-6D | [5 empty] | ADCS_N | [8 empty] | 新營PS.1682_DS | 1682(#4MTR) DS | MTR | P01/161/1680/DS2 |  |  |  | CDC | 818 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | DS1 | 781 | [16 empty] | 2-37-00 | 2-37-01 | 3-14 | [5 empty] | ADCS_N | [8 empty] | 新營PS.781_DS | 781(#4MTR) DS | MTR | P01/69/780/DS1 |  |  |  | CDC | 819 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | DS2 | 782 | [16 empty] | 2-37-02 | 2-37-03 | 3-15 | [5 empty] | ADCS_N | [8 empty] | 新營PS.782_DS | 782(#4MTR) DS | MTR | P01/69/780/DS2 |  |  |  | CDC | 820 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | 87A | [17 empty] | 1-02-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1530_87A | 新營柳營山線(1530) 87RY | LINE161 | P01/161/1530/87A |  |  |  | CDC | 821 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | 87A | [17 empty] | 1-01-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1540_87A | 新營柳營海線(1540) 87RY | LINE161 | P01/161/1540/87A |  |  |  | CDC | 822 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | PHA | [17 empty] | 1-00-07 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1550_PHA | 嘉義山上紅線(1550) 相間RY | LINE161 | P01/161/1550/PHA |  |  |  | CDC | 823 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | GDA | [17 empty] | 1-01-00 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1550_GDA | 嘉義山上紅線(1550) 接地RY | LINE161 | P01/161/1550/GDA |  |  |  | CDC | 824 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1550_87A | 嘉義山上紅線(1550) 87RY | LINE161 | P01/161/1550/87A |  |  |  | CDC | 825 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | CB | [17 empty] | 1-01-05 |  | 1-04 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1550_CB | 1550(嘉義山上紅線) CB | LINE161 | P01/161/1550/CB |  |  |  | CDC | 826 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | 79UL | [17 empty] | 2-3A-01 |  | 2-59 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1550_79UL | 嘉義山上紅線(1550) 79RY U/L | LINE161 | P01/161/1550/79UL |  |  |  | CDC | 827 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | DS1 | 1551 | [16 empty] | 1-39-14 | 1-39-15 | 1-4C | [5 empty] | ADCS_N | [8 empty] | 新營PS.1551_DS | 1551(嘉義山上紅線) DS | LINE161 | P01/161/1550/DS1 |  |  |  | CDC | 828 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | DS2 | 1552 | [16 empty] | 1-3A-00 | 1-3A-01 | 1-4D | [5 empty] | ADCS_N | [8 empty] | 新營PS.1552_DS | 1552(嘉義山上紅線) DS | LINE161 | P01/161/1550/DS2 |  |  |  | CDC | 829 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | DS3 | 1553 | [16 empty] | 1-3A-02 | 1-3A-03 | 1-4E | [5 empty] | ADCS_N | [8 empty] | 新營PS.1553_DS | 1553(嘉義山上紅線) DS | LINE161 | P01/161/1550/DS3 |  |  |  | CDC | 830 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | E3 | 1553E | [16 empty] | 1-3A-04 | 1-3A-05 | 1-4F | [5 empty] | ADCS_N | [8 empty] | 新營PS.1553E_ES | 1553E(嘉義山上紅線) ES | LINE161 | P01/161/1550/ES3 |  |  |  | CDC | 831 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | PHA | [17 empty] | 1-01-03 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1560_PHA | 嘉義山上白線(1560) 相間RY | LINE161 | P01/161/1560/PHA |  |  |  | CDC | 832 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | GDA | [17 empty] | 1-01-04 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1560_GDA | 嘉義山上白線(1560) 接地RY | LINE161 | P01/161/1560/GDA |  |  |  | CDC | 833 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | CB | [17 empty] | 1-02-03 |  | 1-05 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1560_CB | 1560(嘉義山上白線) CB | LINE161 | P01/161/1560/CB |  |  |  | CDC | 834 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | 79UL | [17 empty] | 2-3A-03 |  | 2-5B | [5 empty] | ADCS_N | [8 empty] | 新營PS.1560_79UL | 嘉義山上白線(1560) 79RY U/L | LINE161 | P01/161/1560/79UL |  |  |  | CDC | 835 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | DS1 | 1561 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-50 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1561_DS | 1561(嘉義山上白線) DS | LINE161 | P01/161/1560/DS1 |  |  |  | CDC | 836 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | DS2 | 1562 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-51 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1562_DS | 1562(嘉義山上白線) DS | LINE161 | P01/161/1560/DS2 |  |  |  | CDC | 837 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | DS3 | 1563 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1563_DS | 1563(嘉義山上白線) DS | LINE161 | P01/161/1560/DS3 |  |  |  | CDC | 838 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | E3 | 1563E | [16 empty] | 1-3A-12 | 1-3A-13 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1563E_ES | 1563E(嘉義山上白線) ES | LINE161 | P01/161/1560/ES3 |  |  |  | CDC | 839 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 0 |  |  |  |  | OilLeak | [17 empty] | 1-32-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.集油池警報 | DTR,MTR集油池警報 | OTHER | P01/0/StaDev/OilLeak |  |  |  | CDC | 840 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-35-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | P01/161/1500/50SA |  |  |  | CDC | 841 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-36-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.水位警報(1) | 地下室水位警報(1) | OTHER | P01/0/StaDev/Water1 |  |  |  | CDC | 842 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-37-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.水位警報(2) | 地下室水位警報(2) | OTHER | P01/0/StaDev/Water2 |  |  |  | CDC | 843 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | UPSA | [17 empty] | 1-33-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.UPSA | ADCC大樓UPS警報 | OTHER | P01/0/StaDev/UPSA |  |  |  | CDC | 844 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | 87A | [17 empty] | 1-01-02 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1560_87A | 嘉義山上白線(1560) 87RY | LINE161 | P01/161/1560/87A |  |  |  | CDC | 845 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | 87UL | [17 empty] | 2-3A-02 |  | 2-5A | [5 empty] | ADCS_N | [8 empty] | 新營PS.1560_87UL | 嘉義山上白線(1560) 87RY U/L | LINE161 | P01/161/1560/87UL |  |  |  | CDC | 846 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 1530 | 新營柳營山線(1530) |  | 87CFA | [17 empty] | 1-32-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1530_87CFA | 新營柳營山線(1530)87RY通訊故障 | OTHER | P01/161/1530/87CFA |  |  |  | CDC | 847 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1530 | 新營柳營山線(1530) |  | RYFA | [17 empty] | 1-33-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1530_RYFA | 新營柳營山線(1530)數位電驛故障 | OTHER | P01/161/1530/RYFA |  |  |  | CDC | 848 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1540 | 新營柳營海線(1540) |  | 87CFA | [17 empty] | 1-32-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1540_87CFA | 新營柳營海線(1540)87RY通訊故障 | OTHER | P01/161/1540/87CFA |  |  |  | CDC | 849 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1540 | 新營柳營海線(1540) |  | RYFA | [17 empty] | 1-33-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1540_RYFA | 新營柳營海線(1540)數位電驛故障 | OTHER | P01/161/1540/RYFA |  |  |  | CDC | 850 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1550 | 嘉義山上紅線(1550) |  | 87CFA | [17 empty] | 1-33-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1550_87CFA | 嘉義山上紅線(1550)87RY通訊故障 | OTHER | P01/161/1550/87CFA |  |  |  | CDC | 851 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1550 | 嘉義山上紅線(1550) |  | RYFA | [17 empty] | 1-33-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1550_RYFA | 嘉義山上紅線(1550)數位電驛故障 | OTHER | P01/161/1550/RYFA |  |  |  | CDC | 852 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1560 | 嘉義山上白線(1560) |  | 87CFA | [17 empty] | 1-33-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1560_87CFA | 嘉義山上白線(1560)87RY通訊故障 | OTHER | P01/161/1560/87CFA |  |  |  | CDC | 853 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1560 | 嘉義山上白線(1560) |  | RYFA | [17 empty] | 1-33-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1560_RYFA | 嘉義山上白線(1560)數位電驛故障 | OTHER | P01/161/1560/RYFA |  |  |  | CDC | 854 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | PHA | [17 empty] | 1-0C-02 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1570_PHA | 新營下營一路(1570) 相間RY | LINE161 | P01/161/1570/PHA |  |  |  | CDC | 855 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | GDA | [17 empty] | 1-0C-03 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1570_GDA | 新營下營一路(1570) 接地RY | LINE161 | P01/161/1570/GDA |  |  |  | CDC | 856 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | 87A | [17 empty] | 1-0C-01 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1570_87A | 新營下營一路(1570) 87RY | LINE161 | P01/161/1570/87A |  |  |  | CDC | 857 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | 87UL | [17 empty] | 2-39-12 |  | 3-1A | [5 empty] | ADCS_N | [8 empty] | 新營PS.1570_87UL | 新營下營一路(1570) 87RY U/L | LINE161 | P01/161/1570/87UL |  |  |  | CDC | 858 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | CB | [17 empty] | 1-0C-00 |  | 1-06 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1570_CB | 1570(新營下營一路) CB | LINE161 | P01/161/1570/CB |  |  |  | CDC | 859 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | 79UL | [17 empty] | 2-39-13 |  | 3-1B | [5 empty] | ADCS_N | [8 empty] | 新營PS.1570_79UL | 新營下營一路(1570) 79RY U/L | LINE161 | P01/161/1570/79UL |  |  |  | CDC | 860 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | DS1 | 1571 | [16 empty] | 1-3A-14 | 1-3A-15 | 1-54 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1571_DS | 1571(新營下營一路) DS | LINE161 | P01/161/1570/DS1 |  |  |  | CDC | 861 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | DS2 | 1572 | [16 empty] | 1-3B-00 | 1-3B-01 | 1-55 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1572_DS | 1572(新營下營一路) DS | LINE161 | P01/161/1570/DS2 |  |  |  | CDC | 862 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | DS3 | 1573 | [16 empty] | 1-3B-02 | 1-3B-03 | 1-56 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1573_DS | 1573(新營下營一路) DS | LINE161 | P01/161/1570/DS3 |  |  |  | CDC | 863 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | E3 | 1573E | [16 empty] | 1-3B-04 | 1-3B-05 | 1-57 | [5 empty] | ADCS_N | [8 empty] | 新營PS.1573E_ES | 1573E(新營下營一路) ES | LINE161 | P01/161/1570/ES3 |  |  |  | CDC | 864 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | 87A | [17 empty] | 1-0C-07 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1580_87A | 新營下營二路(1580) 87RY | LINE161 | P01/161/1580/87A |  |  |  | CDC | 865 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | 87UL | [17 empty] | 2-39-14 |  | 3-1C | [5 empty] | ADCS_N | [8 empty] | 新營PS.1580_87UL | 新營下營二路(1580) 87RY U/L | LINE161 | P01/161/1580/87UL |  |  |  | CDC | 866 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 1570 | 新營下營一路(1570) |  | 87CFA | [17 empty] | 1-3F-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1570_87CFA | 新營下營一路(1570)87RY通訊故障 | OTHER | P01/161/1570/87CFA |  |  |  | CDC | 867 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1570 | 新營下營一路(1570) |  | RYFA | [17 empty] | 1-3F-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1570_RYFA | 新營下營一路(1570)數位電驛故障 | OTHER | P01/161/1570/RYFA |  |  |  | CDC | 868 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1580 | 新營下營二路(1580) |  | 87CFA | [17 empty] | 1-3F-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1580_87CFA | 新營下營二路(1580)87RY通訊故障 | OTHER | P01/161/1580/87CFA |  |  |  | CDC | 869 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1580 | 新營下營二路(1580) |  | RYFA | [17 empty] | 1-3F-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1580_RYFA | 新營下營二路(1580)數位電驛故障 | OTHER | P01/161/1580/RYFA |  |  |  | CDC | 870 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC61 | 新61線(VC61) |  | PHA | [17 empty] | 2-05-03 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_PHA | 新61線(VC61) 相間RY | FEEDER | P01/22/VC61/PHA |  |  |  | CDC | 871 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC61 | 新61線(VC61) |  | GDA | [17 empty] | 2-05-04 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_GDA | 新61線(VC61) 接地RY | FEEDER | P01/22/VC61/GDA |  |  |  | CDC | 872 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC61 | 新61線(VC61) |  | 79UL | [17 empty] | 2-3C-05 |  | 2-6D | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_79UL | 新61線(VC61) 79RY U/L | FEEDER | P01/22/VC61/79UL |  |  |  | CDC | 873 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC61 | 新61線(VC61) |  | ADJ | [17 empty] | 2-3F-02 |  | 3-0A | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_ADJ | 新61線(VC61) LCO分流器 U/L | FEEDER | P01/22/VC61/ADJ |  |  |  | CDC | 874 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC61 | VC61(新61線) |  | CB | [17 empty] | 2-05-02 |  | 2-46 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_CB | VC61(新61線) CB | FEEDER | P01/22/VC61/CB |  |  |  | CDC | 875 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC62 | 新62線(VC62) |  | PHA | [17 empty] | 2-05-06 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_PHA | 新62線(VC62) 相間RY | FEEDER | P01/22/VC62/PHA |  |  |  | CDC | 876 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC62 | 新62線(VC62) |  | GDA | [17 empty] | 2-05-07 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_GDA | 新62線(VC62) 接地RY | FEEDER | P01/22/VC62/GDA |  |  |  | CDC | 877 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC62 | 新62線(VC62) |  | 79UL | [17 empty] | 2-3C-06 |  | 2-6E | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_79UL | 新62線(VC62) 79RY U/L | FEEDER | P01/22/VC62/79UL |  |  |  | CDC | 878 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC62 | 新62線(VC62) |  | ADJ | [17 empty] | 2-3F-03 |  | 3-0B | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_ADJ | 新62線(VC62) LCO分流器 U/L | FEEDER | P01/22/VC62/ADJ |  |  |  | CDC | 879 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC62 | VC62(新62線) |  | CB | [17 empty] | 2-05-05 |  | 2-47 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_CB | VC62(新62線) CB | FEEDER | P01/22/VC62/CB |  |  |  | CDC | 880 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC63 | 新63線(VC63) |  | PHA | [17 empty] | 2-06-01 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_PHA | 新63線(VC63) 相間RY | FEEDER | P01/22/VC63/PHA |  |  |  | CDC | 881 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC63 | 新63線(VC63) |  | GDA | [17 empty] | 2-06-02 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_GDA | 新63線(VC63) 接地RY | FEEDER | P01/22/VC63/GDA |  |  |  | CDC | 882 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC63 | 新63線(VC63) |  | 79UL | [17 empty] | 2-3C-07 |  | 2-6F | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_79UL | 新63線(VC63) 79RY U/L | FEEDER | P01/22/VC63/79UL |  |  |  | CDC | 883 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC63 | 新63線(VC63) |  | ADJ | [17 empty] | 2-3F-04 |  | 3-0C | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_ADJ | 新63線(VC63) LCO分流器 U/L | FEEDER | P01/22/VC63/ADJ |  |  |  | CDC | 884 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC63 | VC63(新63線) |  | CB | [17 empty] | 2-06-00 |  | 2-48 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_CB | VC63(新63線) CB | FEEDER | P01/22/VC63/CB |  |  |  | CDC | 885 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC64 | 新64線(VC64) |  | PHA | [17 empty] | 2-06-04 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_PHA | 新64線(VC64) 相間RY | FEEDER | P01/22/VC64/PHA |  |  |  | CDC | 886 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC64 | 新64線(VC64) |  | GDA | [17 empty] | 2-06-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_GDA | 新64線(VC64) 接地RY | FEEDER | P01/22/VC64/GDA |  |  |  | CDC | 887 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC64 | 新64線(VC64) |  | 79UL | [17 empty] | 2-3C-08 |  | 2-70 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_79UL | 新64線(VC64) 79RY U/L | FEEDER | P01/22/VC64/79UL |  |  |  | CDC | 888 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC64 | 新64線(VC64) |  | ADJ | [17 empty] | 2-3F-05 |  | 3-0D | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_ADJ | 新64線(VC64) LCO分流器 U/L | FEEDER | P01/22/VC64/ADJ |  |  |  | CDC | 889 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC64 | VC64(新64線) |  | CB | [17 empty] | 2-06-03 |  | 2-49 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_CB | VC64(新64線) CB | FEEDER | P01/22/VC64/CB |  |  |  | CDC | 890 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC65 | 新65線(VC65) |  | PHA | [17 empty] | 2-07-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_PHA | 新65線(VC65) 相間RY | FEEDER | P01/22/VC65/PHA |  |  |  | CDC | 891 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC65 | 新65線(VC65) |  | GDA | [17 empty] | 2-07-06 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_GDA | 新65線(VC65) 接地RY | FEEDER | P01/22/VC65/GDA |  |  |  | CDC | 892 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC65 | 新65線(VC65) |  | 79UL | [17 empty] | 2-3C-10 |  | 2-72 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_79UL | 新65線(VC65) 79RY U/L | FEEDER | P01/22/VC65/79UL |  |  |  | CDC | 893 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC65 | 新65線(VC65) |  | ADJ | [17 empty] | 2-3F-06 |  | 3-0E | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_ADJ | 新65線(VC65) LCO分流器 U/L | FEEDER | P01/22/VC65/ADJ |  |  |  | CDC | 894 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC65 | VC65(新65線) |  | CB | [17 empty] | 2-07-04 |  | 2-4C | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_CB | VC65(新65線) CB | FEEDER | P01/22/VC65/CB |  |  |  | CDC | 895 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC66 | 新66線(VC66) |  | PHA | [17 empty] | 2-08-00 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_PHA | 新66線(VC66) 相間RY | FEEDER | P01/22/VC66/PHA |  |  |  | CDC | 896 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC66 | 新66線(VC66) |  | GDA | [17 empty] | 2-08-01 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_GDA | 新66線(VC66) 接地RY | FEEDER | P01/22/VC66/GDA |  |  |  | CDC | 897 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC66 | 新66線(VC66) |  | 79UL | [17 empty] | 2-3C-11 |  | 2-73 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_79UL | 新66線(VC66) 79RY U/L | FEEDER | P01/22/VC66/79UL |  |  |  | CDC | 898 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC66 | 新66線(VC66) |  | ADJ | [17 empty] | 2-3F-07 |  | 3-0F | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_ADJ | 新66線(VC66) LCO分流器 U/L | FEEDER | P01/22/VC66/ADJ |  |  |  | CDC | 899 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC66 | VC66(新66線) |  | CB | [17 empty] | 2-07-07 |  | 2-4D | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_CB | VC66(新66線) CB | FEEDER | P01/22/VC66/CB |  |  |  | CDC | 900 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC67 | 新67線(VC67) |  | PHA | [17 empty] | 2-08-03 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_PHA | 新67線(VC67) 相間RY | FEEDER | P01/22/VC67/PHA |  |  |  | CDC | 901 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC67 | 新67線(VC67) |  | GDA | [17 empty] | 2-08-04 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_GDA | 新67線(VC67) 接地RY | FEEDER | P01/22/VC67/GDA |  |  |  | CDC | 902 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC67 | 新67線(VC67) |  | 79UL | [17 empty] | 2-3C-12 |  | 2-74 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_79UL | 新67線(VC67) 79RY U/L | FEEDER | P01/22/VC67/79UL |  |  |  | CDC | 903 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC67 | 新67線(VC67) |  | ADJ | [17 empty] | 2-3F-08 |  | 3-10 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_ADJ | 新67線(VC67) LCO分流器 U/L | FEEDER | P01/22/VC67/ADJ |  |  |  | CDC | 904 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC67 | VC67(新67線) |  | CB | [17 empty] | 2-08-02 |  | 2-4E | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_CB | VC67(新67線) CB | FEEDER | P01/22/VC67/CB |  |  |  | CDC | 905 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC68 | 新68線(VC68) |  | PHA | [17 empty] | 2-08-06 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_PHA | 新68線(VC68) 相間RY | FEEDER | P01/22/VC68/PHA |  |  |  | CDC | 906 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC68 | 新68線(VC68) |  | GDA | [17 empty] | 2-08-07 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_GDA | 新68線(VC68) 接地RY | FEEDER | P01/22/VC68/GDA |  |  |  | CDC | 907 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC68 | 新68線(VC68) |  | 79UL | [17 empty] | 2-3C-13 |  | 2-75 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_79UL | 新68線(VC68) 79RY U/L | FEEDER | P01/22/VC68/79UL |  |  |  | CDC | 908 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC68 | 新68線(VC68) |  | ADJ | [17 empty] | 2-3F-09 |  | 3-11 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_ADJ | 新68線(VC68) LCO分流器 U/L | FEEDER | P01/22/VC68/ADJ |  |  |  | CDC | 909 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC68 | VC68(新68線) |  | CB | [17 empty] | 2-08-05 |  | 2-4F | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_CB | VC68(新68線) CB | FEEDER | P01/22/VC68/CB |  |  |  | CDC | 910 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC69 | 新69線(VC69) |  | PHA | [17 empty] | 2-09-01 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_PHA | 新69線(VC69) 相間RY | FEEDER | P01/22/VC69/PHA |  |  |  | CDC | 911 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC69 | 新69線(VC69) |  | GDA | [17 empty] | 2-09-02 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_GDA | 新69線(VC69) 接地RY | FEEDER | P01/22/VC69/GDA |  |  |  | CDC | 912 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC69 | 新69線(VC69) |  | 79UL | [17 empty] | 2-3C-14 |  | 2-76 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_79UL | 新69線(VC69) 79RY U/L | FEEDER | P01/22/VC69/79UL |  |  |  | CDC | 913 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC69 | 新69線(VC69) |  | ADJ | [17 empty] | 2-3F-10 |  | 3-12 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_ADJ | 新69線(VC69) LCO分流器 U/L | FEEDER | P01/22/VC69/ADJ |  |  |  | CDC | 914 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC69 | VC69(新69線) |  | CB | [17 empty] | 2-09-00 |  | 2-50 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_CB | VC69(新69線) CB | FEEDER | P01/22/VC69/CB |  |  |  | CDC | 915 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC70 | 新70線(VC70) |  | PHA | [17 empty] | 2-09-04 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_PHA | 新70線(VC70) 相間RY | FEEDER | P01/22/VC70/PHA |  |  |  | CDC | 916 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC70 | 新70線(VC70) |  | GDA | [17 empty] | 2-09-05 | [7 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_GDA | 新70線(VC70) 接地RY | FEEDER | P01/22/VC70/GDA |  |  |  | CDC | 917 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | VC70 | 新70線(VC70) |  | 79UL | [17 empty] | 2-3C-15 |  | 2-77 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_79UL | 新70線(VC70) 79RY U/L | FEEDER | P01/22/VC70/79UL |  |  |  | CDC | 918 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | VC70 | 新70線(VC70) |  | ADJ | [17 empty] | 2-3F-11 |  | 3-13 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_ADJ | 新70線(VC70) LCO分流器 U/L | FEEDER | P01/22/VC70/ADJ |  |  |  | CDC | 919 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P01 | 新營PS | 0 |  | VC70 | VC70(新70線) |  | CB | [17 empty] | 2-09-03 |  | 2-51 | [5 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_CB | VC70(新70線) CB | FEEDER | P01/22/VC70/CB |  |  |  | CDC | 920 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 所內TIE1 | 開關場所內電源#TIE1 |  | ACBA | [17 empty] | 2-3D-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內#TIE1_ACBA | 開關場所內電源#TIE1 ACBA | OTHER | P01/0/StaDev/ACBT |  |  |  | CDC | 921 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 調度中心電源 | 調度中心電源 |  | ACB3 | [17 empty] | 2-3E-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內電源ACB3 | 調度中心電源 ACB3(#3SSTR) | OTHER | P01/0/StaDev/ACB3 |  |  |  | CDC | 922 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P01 | 新營PS | 0 |  | 調度中心電源 | 調度中心電源 |  | ACB5 | [17 empty] | 2-3E-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.所內電源ACB5 | 調度中心電源 ACB5(發電機) | OTHER | P01/0/StaDev/ACB5 |  |  |  | CDC | 923 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  | ACB | 所內電源ACB |  | TIE1 | [17 empty] | 2-3D-12 |  | 2-7B | [5 empty] | ADCS_N | [8 empty] | 新營PS.ACB_TIE1 | 所內電源ACB TIE1 | OTHER | P01/0/StaDev/ACBT1 |  |  |  | CDC | 924 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 0 |  | ACB | 調度中心電源(ACB) |  | TIE2 | [17 empty] | 2-3E-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.ACB_TIE2 | 調度中心電源 ACB TIE2 | OTHER | P01/0/StaDev/ACBT2 |  |  |  | CDC | 925 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | 87A | [17 empty] | 1-18-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.620_87A | 新營新東線(620) 87RY | LINE69 | P01/69/620/87A |  |  |  | CDC | 926 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | 87UL | [17 empty] | 2-3A-09 |  | 2-5D | [5 empty] | ADCS_N | [8 empty] | 新營PS.620_87UL | 新營新東線(620) 87RY U/L | LINE69 | P01/69/620/87UL |  |  |  | CDC | 927 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 620 | 新營新東線(620) |  | 87CFA | [17 empty] | 1-3F-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.620_87CFA | 新營新東線(620)87RY通訊故障 | OTHER | P01/69/620/87CFA |  |  |  | CDC | 928 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 620 | 新營新東線(620) |  | RYFA | [17 empty] | 1-3F-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.620_RYFA | 新營新東線(620)數位電驛故障 | OTHER | P01/69/620/RYFA |  |  |  | CDC | 929 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | PHA | [17 empty] | 1-1D-06 | [7 empty] | 69KV_N | [8 empty] | 新營PS.910_PHA | 新營學甲一路(910) 相間RY | LINE69 | P01/69/910/PHA |  |  |  | CDC | 930 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | GDA | [17 empty] | 1-1D-07 | [7 empty] | 69KV_N | [8 empty] | 新營PS.910_GDA | 新營學甲一路(910) 接地RY | LINE69 | P01/69/910/GDA |  |  |  | CDC | 931 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | 87A | [17 empty] | 1-1D-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.910_87A | 新營學甲一路(910) 87RY | LINE69 | P01/69/910/87A |  |  |  | CDC | 932 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | 87UL | [17 empty] | 2-39-09 |  | 3-21 | [5 empty] | ADCS_N | [8 empty] | 新營PS.910_87UL | 新營學甲一路(910) 87RY U/L | LINE69 | P01/69/910/87UL |  |  |  | CDC | 933 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | CB | [17 empty] | 1-1D-04 |  | 1-23 | [5 empty] | 69KV_N | [8 empty] | 新營PS.910_CB | 910(新營學甲一路) CB | LINE69 | P01/69/910/CB |  |  |  | CDC | 934 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | DS1 | 911 | [16 empty] | 2-35-08 | 2-35-09 | 2-2C | [5 empty] | ADCS_N | [8 empty] | 新營PS.911_DS | 911(新營學甲一路) DS | LINE69 | P01/69/910/DS1 |  |  |  | CDC | 935 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | DS2 | 912 | [16 empty] | 2-35-10 | 2-35-11 | 2-2D | [5 empty] | ADCS_N | [8 empty] | 新營PS.912_DS | 912(新營學甲一路) DS | LINE69 | P01/69/910/DS2 |  |  |  | CDC | 936 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | DS3 | 913 | [16 empty] | 2-35-12 | 2-35-13 | 2-2E | [5 empty] | ADCS_N | [8 empty] | 新營PS.913_DS | 913(新營學甲一路) DS | LINE69 | P01/69/910/DS3 |  |  |  | CDC | 937 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | E3 | 913E | [16 empty] | 2-35-14 | 2-35-15 | 2-2F | [5 empty] | ADCS_N | [8 empty] | 新營PS.913E_ES | 913E(新營學甲一路) ES | LINE69 | P01/69/910/ES3 |  |  |  | CDC | 938 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 69 | 69kV | LINE | LINE |  | RCA | [17 empty] | 1-0B-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_RCA | 69KV LINE 79RY(復閉)動作 | OTHER | P01/69/ComPoint/RCA |  |  |  | CDC | 939 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 910 | 新營學甲一路(910) |  | 87CFA | [17 empty] | 2-39-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.910_87CFA | 新營學甲一路(910)87RY通訊故障 | OTHER | P01/69/910/87CFA |  |  |  | CDC | 940 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 910 | 新營學甲一路(910) |  | RYFA | [17 empty] | 2-39-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.910_RYFA | 新營學甲一路(910)數位電驛故障 | OTHER | P01/69/910/RYFA |  |  |  | CDC | 941 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | PHA | [17 empty] | 1-0D-06 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1520_PHA | 華卡線(1520) 相間RY | LINE161 | P01/161/1520/PHA |  |  |  | CDC | 942 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | GDA | [17 empty] | 1-0D-07 | [7 empty] | 161KV_N | [8 empty] | 新營PS.1520_GDA | 華卡線(1520) 接地RY | LINE161 | P01/161/1520/GDA |  |  |  | CDC | 943 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | CB | [17 empty] | 1-0D-04 |  | 1-08 | [5 empty] | 161KV_N | [8 empty] | 新營PS.1520_CB | 1520(華卡線) CB | LINE161 | P01/161/1520/CB |  |  |  | CDC | 944 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | 79UL | [17 empty] | 2-39-01 |  | 3-1E | [5 empty] | ADCS_N | [8 empty] | 新營PS.1520_79UL | 華卡線(1520) 79RY U/L | LINE161 | P01/161/1520/79UL |  |  |  | CDC | 945 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | DS1 | 1521 | [16 empty] | 1-3B-14 | 1-3B-15 | 1-5C | [5 empty] | ADCS_N | [8 empty] | 新營PS.1521_DS | 1521(華卡線) DS | LINE161 | P01/161/1520/DS1 |  |  |  | CDC | 946 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | DS2 | 1522 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-5D | [5 empty] | ADCS_N | [8 empty] | 新營PS.1522_DS | 1522(華卡線) DS | LINE161 | P01/161/1520/DS2 |  |  |  | CDC | 947 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | DS3 | 1523 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-5E | [5 empty] | ADCS_N | [8 empty] | 新營PS.1523_DS | 1523(華卡線) DS | LINE161 | P01/161/1520/DS3 |  |  |  | CDC | 948 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | E3 | 1523E | [16 empty] | 1-3C-04 | 1-3C-05 | 1-5F | [5 empty] | ADCS_N | [8 empty] | 新營PS.1523E_ES | 1523E(華卡線) ES | LINE161 | P01/161/1520/ES3 |  |  |  | CDC | 949 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 0 |  | 1520 | 華卡線(1520) |  | RYFA | [17 empty] | 1-3F-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.1520_RYFA | 華卡線(1520)數位電驛故障 | OTHER | P01/161/1520/RYFA |  |  |  | CDC | 950 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | 87A | [17 empty] | 1-1D-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.730_87A | 新西線(730) 87RY | LINE69 | P01/69/730/87A |  |  |  | CDC | 951 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | 87UL | [17 empty] | 2-39-07 |  | 3-23 | [5 empty] | ADCS_N | [8 empty] | 新營PS.730_87UL | 新西線(730) 87RY U/L | LINE69 | P01/69/730/87UL |  |  |  | CDC | 952 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 730 | 新西線(730) |  | 87CFA | [17 empty] | 1-3F-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.730_87CFA | 新營新西線(730)87RY通訊故障 | OTHER | P01/69/730/87CFA |  |  |  | CDC | 953 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 730 | 新西線(730) |  | RYFA | [17 empty] | 1-3F-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.730_RYFA | 新營新西線(730)數位電驛故障 | OTHER | P01/69/730/RYFA |  |  |  | CDC | 954 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 81RYFA | [17 empty] | 2-3A-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.81RYFA | 低頻電驛故障 | OTHER | P01/0/ComPoint/RYFA |  |  |  | CDC | 955 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-39-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | P01/0/ComPoint/GRZ100 |  |  |  | CDC | 956 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
P01 | 新營PS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-34-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.火災警報(4) | 火災警報(4)-主(配)變壓器 | OTHER | P01/0/StaDev/Fire4 |  |  |  | CDC | 957 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | 控制室溫度警報 | [17 empty] | 2-3E-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.控制室溫度警報 | 1F控制室溫度警報 | OTHER | P01/0/StaDev/R_Temp |  |  |  | CDC | 958 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | 87A | [17 empty] | 1-1B-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.670_87A | 大寮二路(670) 87RY | LINE69 | P01/69/670/87A |  |  |  | CDC | 959 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | 87UL | [17 empty] | 2-38-02 |  | 3-24 | [5 empty] | ADCS_N | [8 empty] | 新營PS.670_87UL | 大寮二路(670) 87RY U/L | LINE69 | P01/69/670/87UL |  |  |  | CDC | 960 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | 87A | [17 empty] | 1-1B-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.680_87A | 大寮一路(680) 87RY | LINE69 | P01/69/680/87A |  |  |  | CDC | 961 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | 87UL | [17 empty] | 2-38-05 |  | 3-25 | [5 empty] | ADCS_N | [8 empty] | 新營PS.680_87UL | 大寮一路(680) 87RY U/L | LINE69 | P01/69/680/87UL |  |  |  | CDC | 962 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 670 | 大寮二路(670) |  | 87CFA | [17 empty] | 2-38-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.670_87CFA | 新營大寮二路(670)87RY通訊故障 | OTHER | P01/69/670/87CFA |  |  |  | CDC | 963 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 670 | 大寮二路(670) |  | RYFA | [17 empty] | 2-38-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.670_RYFA | 新營大寮二路(670)數位電驛故障 | OTHER | P01/69/670/RYFA |  |  |  | CDC | 964 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 680 | 大寮一路(680) |  | 87CFA | [17 empty] | 2-38-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.680_87CFA | 新營大寮ㄧ路(680)87RY通訊故障 | OTHER | P01/69/680/87CFA |  |  |  | CDC | 965 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 680 | 大寮一路(680) |  | RYFA | [17 empty] | 2-38-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.680_RYFA | 新營大寮ㄧ路(680)數位電驛故障 | OTHER | P01/69/680/RYFA |  |  |  | CDC | 966 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 2-03-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.100_51A | 11KV TIE(100) 51RY | TIE | P01/11/100/PHA |  |  |  | CDC | 967 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 2-03-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.100_51NA | 11KV TIE(100) 51N RY | TIE | P01/11/100/GDA |  |  |  | CDC | 968 | GENERICDIPoint | PS014_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | GEN | [17 empty] | 1-33-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.GEN | 緊急發電機運轉 | OTHER | P01/0/StaDev/2A5Other |  |  |  | CDC | 969 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | 87A | [17 empty] | 1-19-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.630_87A | 新營白河水上線(630) 87RY | LINE69 | P01/69/630/87A |  |  |  | CDC | 970 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | 87UL | [17 empty] | 2-38-08 |  | 3-26 | [5 empty] | ADCS_N | [8 empty] | 新營PS.630_87UL | 新營白河水上線(630) 87RY U/L | LINE69 | P01/69/630/87UL |  |  |  | CDC | 971 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 630 | 新營白河水上線(630) |  | 87CFA | [17 empty] | 2-38-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.630_87CFA | 新營白河水上線 87RY通訊故障 | OTHER | P01/69/630/87CFA |  |  |  | CDC | 972 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 630 | 新營白河水上線(630) |  | RYFA | [17 empty] | 2-38-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.630_RYFA | 新營白河水上線 數位電驛故障 | OTHER | P01/69/630/RYFA |  |  |  | CDC | 973 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | 87A | [17 empty] | 1-1A-01 | [7 empty] | 69KV_N | [8 empty] | 新營PS.650_87A | 隆田線(650) 87RY | LINE69 | P01/69/650/87A |  |  |  | CDC | 974 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | 87UL | [17 empty] | 2-3A-10 |  | 2-5E | [5 empty] | ADCS_N | [8 empty] | 新營PS.650_87UL | 隆田線(650) 87RY U/L | LINE69 | P01/69/650/87UL |  |  |  | CDC | 975 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 650 | 隆田線(650) |  | 87CFA | [17 empty] | 2-38-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.650_87CFA | 新營隆田線(650)87RY通訊故障 | OTHER | P01/69/650/87CFA |  |  |  | CDC | 976 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 650 | 隆田線(650) |  | RYFA | [17 empty] | 2-38-10 | [7 empty] | ADCS_N | [8 empty] | 新營PS.650_RYFA | 新營隆田線(650)數位電驛故障 | OTHER | P01/69/650/RYFA |  |  |  | CDC | 977 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | 87A | [17 empty] | 1-1A-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.660_87A | 官田二路(660) 87RY | LINE69 | P01/69/660/87A |  |  |  | CDC | 978 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | 87UL | [17 empty] | 2-3A-14 |  | 2-5F | [5 empty] | ADCS_N | [8 empty] | 新營PS.660_87UL | 官田二路(660) 87RY U/L | LINE69 | P01/69/660/87UL |  |  |  | CDC | 979 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 660 | 官田二路(660) |  | 87CFA | [17 empty] | 2-38-11 | [7 empty] | ADCS_N | [8 empty] | 新營PS.660_87CFA | 新營官田二路(660)87RY通訊故障 | OTHER | P01/69/660/87CFA |  |  |  | CDC | 980 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 660 | 官田二路(660) |  | RYFA | [17 empty] | 2-38-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.660_RYFA | 新營官田二路(660)數位電驛故障 | OTHER | P01/69/660/RYFA |  |  |  | CDC | 981 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 51Z_UL | [17 empty] | 2-39-05 |  | 3-29 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_51ZUL | #4MTR 51ZRY U/L | OTHER | P01//4MTR/51Z_UL |  |  |  | CDC | 982 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | MTR_86A | [17 empty] | 1-0D-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_86A | #4MTR 86RY | OTHER | P01//4MTR/MTR_86A |  |  |  | CDC | 983 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 1_87UL1 | [17 empty] | 2-3E-06 |  | 3-27 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_87UL1 | #4MTR #1 87RY U/L | OTHER | P01//4MTR/87UL |  |  |  | CDC | 984 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | 1_87UL2 | [17 empty] | 2-39-04 |  | 3-28 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_87UL2 | #4MTR #2 87RY U/L | OTHER | P01//4MTR/1_87UL2 |  |  |  | CDC | 985 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | GDA | [17 empty] | 1-0D-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_GDA | #4MTR GDA | OTHER | P01//4MTR/GDA |  |  |  | CDC | 986 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | PHA | [17 empty] | 1-0F-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_PHA | #4MTR PHA | OTHER | P01//4MTR/PHA |  |  |  | CDC | 987 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 4MTR | #4MTR |  | RYFA | [17 empty] | 2-38-13 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#4MTR_RYFA | #4MTR數位電驛故障 | OTHER | P01//4MTR/RYFA |  |  |  | CDC | 988 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 2-39-03 |  | 3-2C | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER | P01//3MTR/51Z_UL |  |  |  | CDC | 989 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-06-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_86A | #3MTR 86RY | OTHER | P01//3MTR/MTR_86A |  |  |  | CDC | 990 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 1-32-02 |  | 3-2A | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | P01//3MTR/1_87UL1 |  |  |  | CDC | 991 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 2-38-15 |  | 3-2B | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER | P01//3MTR/1_87UL2 |  |  |  | CDC | 992 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | GDA | [17 empty] | 1-05-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_GDA | #3MTR GDA | OTHER | P01//3MTR/GDA |  |  |  | CDC | 993 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | PHA | [17 empty] | 1-06-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_PHA | #3MTR PHA | OTHER | P01//3MTR/PHA |  |  |  | CDC | 994 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 2-38-14 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER | P01//3MTR/RYFA |  |  |  | CDC | 995 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 1-34-11 |  | 3-2F | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | P01//2MTR/51Z_UL |  |  |  | CDC | 996 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-03-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_86A | #2MTR 86RY | OTHER | P01//2MTR/MTR_86A |  |  |  | CDC | 997 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-32-01 |  | 3-2D | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | P01//2MTR/1_87UL1 |  |  |  | CDC | 998 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 1-34-10 |  | 3-2E | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | P01//2MTR/1_87UL2 |  |  |  | CDC | 999 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | GDA | [17 empty] | 1-03-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_GDA | #2MTR GDA | OTHER | P01//2MTR/GDA |  |  |  | CDC | 1000 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | PHA | [17 empty] | 1-05-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_PHA | #2MTR PHA | OTHER | P01//2MTR/PHA |  |  |  | CDC | 1001 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 1-34-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | P01//2MTR/RYFA |  |  |  | CDC | 1002 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 1-34-14 |  | 2-58 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER | P01//1MTR/51Z_UL |  |  |  | CDC | 1003 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 1-04-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_86A | #1MTR 86RY | OTHER | P01//1MTR/MTR_86A |  |  |  | CDC | 1004 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-32-00 |  | 2-54 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | P01//1MTR/1_87UL1 |  |  |  | CDC | 1005 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 1-34-13 |  | 2-56 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER | P01//1MTR/1_87UL2 |  |  |  | CDC | 1006 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | GDA | [17 empty] | 1-03-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_GDA | #1MTR GDA | OTHER | P01//1MTR/GDA |  |  |  | CDC | 1007 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | PHA | [17 empty] | 1-04-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_PHA | #1MTR PHA | OTHER | P01//1MTR/PHA |  |  |  | CDC | 1008 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 1-34-12 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER | P01//1MTR/RYFA |  |  |  | CDC | 1009 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-39-06 |  | 3-22 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | P01//2DTR/51Z_UL |  |  |  | CDC | 1010 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 1-02-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_86A | #2DTR 86RY | OTHER | P01//2DTR/DTR_86A |  |  |  | CDC | 1011 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 1-32-04 |  | 3-1F | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | P01//2DTR/87UL |  |  |  | CDC | 1012 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 2-39-00 |  | 3-20 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | P01//2DTR/1_87UL2 |  |  |  | CDC | 1013 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 2-3A-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | P01//2DTR/RYFA |  |  |  | CDC | 1014 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  |  |  |  | TEST3 | [17 empty] | 3-31-00 |  | 3-38 | [5 empty] | ADCS_N | [8 empty] | 新營PS.TEST3 | TEST3 | OTHER |  |  |  |  | CDC | 1015 | GENERICDIPoint | PS014_L3 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-3A-11 |  | 3-32 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | P01//3DTR/51Z_UL |  |  |  | CDC | 1016 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [17 empty] | 1-02-01 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_86A | #3DTR 86RY | OTHER | P01//3DTR/DTR_86A |  |  |  | CDC | 1017 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [17 empty] | 1-32-05 |  | 3-30 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | P01//3DTR/87UL |  |  |  | CDC | 1018 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [17 empty] | 2-3A-06 |  | 3-31 | [5 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | P01//3DTR/1_87UL2 |  |  |  | CDC | 1019 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 3DTR | #3DTR |  | RYFA | [17 empty] | 2-3A-15 | [7 empty] | ADCS_N | [8 empty] | 新營PS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | P01//3DTR/RYFA |  |  |  | CDC | 1020 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | 87A | [17 empty] | 1-1C-05 | [7 empty] | 69KV_N | [8 empty] | 新營PS.720_87A | 新營學甲二路(720) 87RY | LINE69 | P01/69/720/87A |  |  |  | CDC | 1021 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | 87UL | [17 empty] | 1-37-01 |  | 3-33 | [5 empty] | ADCS_N | [8 empty] | 新營PS.720_87UL | 新營學甲二路(720) 87RY U/L | LINE69 | P01/69/720/87UL |  |  |  | CDC | 1022 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 720 | 新營學甲二路(720) |  | 87CFA | [17 empty] | 1-37-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.720_87CFA | 新營學甲二路(720)87RY通訊故障 | OTHER | P01/69/720/87CFA |  |  |  | CDC | 1023 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 720 | 新營學甲二路(720) |  | RYFA | [17 empty] | 1-37-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.720_RYFA | 新營學甲二路(720)數位電驛故障 | OTHER | P01/69/720/RYFA |  |  |  | CDC | 1024 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 | [17 empty] | 1-0A-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | P01/69/600/GDA1 |  |  |  | CDC | 1025 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 | [17 empty] | 1-1F-03 | [7 empty] | ADCS_N | [8 empty] | 新營PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | P01/69/600/GDA2 |  |  |  | CDC | 1026 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 | [17 empty] | 1-0A-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | P01/69/600/PHA1 |  |  |  | CDC | 1027 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 | [17 empty] | 1-1F-02 | [7 empty] | ADCS_N | [8 empty] | 新營PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | P01/69/600/PHA2 |  |  |  | CDC | 1028 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | RYFA | [17 empty] | 1-37-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | P01/69/600/RYFA |  |  |  | CDC | 1029 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-37-06 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | P01/161/ComPoint/87CTFA |  |  |  | CDC | 1030 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 1-37-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | P01/161/ComPoint/BUS_RYFA |  |  |  | CDC | 1031 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 1-37-08 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | P01/69/ComPoint/87CTFA |  |  |  | CDC | 1032 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 1-37-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | P01/69/ComPoint/RYFA |  |  |  | CDC | 1033 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P01 | 新營PS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-37-09 | [7 empty] | ADCS_N | [8 empty] | 新營PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | P01/0/ComPoint/OLTC_A |  |  |  | CDC | 1034 | GENERICDIPoint | PS014_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-02-07 | [7 empty] | ADCS_N | [8 empty] | 新營PS.330_GDA | 11KV M2A(330) 51N RY | OTHER |  |  |  |  | CDC | 1035 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-03-00 | [7 empty] | ADCS_N | [8 empty] | 新營PS.340_GDA | 22KV M2B(340) 51N RY | OTHER |  |  |  |  | CDC | 1036 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 350 | #3DTR(350) |  | GDA | [17 empty] | 1-0C-04 | [7 empty] | ADCS_N | [8 empty] | 新營PS.350_GDA | 11KV M3A(350) 51N RY | OTHER |  |  |  |  | CDC | 1037 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 0 |  | 360 | #3DTR(360) |  | GDA | [17 empty] | 1-0C-05 | [7 empty] | ADCS_N | [8 empty] | 新營PS.360_GDA | 22KV M3B(360) 51N RY | OTHER |  |  |  |  | CDC | 1038 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | CB | [17 empty] | 1-10-00 | [7 empty] | ADCS_N | [8 empty] | 華卡CS.1510_CB | 新營華卡線(PV) CB | LINE161 |  |  |  |  | CDC | 1039 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 1510 | 新營華卡線(PV)(1510) |  | RYFA | [17 empty] | 1-10-01 | [7 empty] | ADCS_N | [8 empty] | 華卡CS.1510_RYA | 新營華卡線(PV)電驛動作 | OTHER |  |  |  |  | CDC | 1040 | GENERICDIPoint | PS014_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | ABS1 | 1511 | [16 empty] | 2-37-08 | 2-37-09 | [6 empty] | ADCS_N | [8 empty] | 華卡CS.1511_ABS | 新營華卡線(PV) ABS | LINE161 |  |  |  |  | CDC | 1041 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P01 | 新營PS | 161 | 161kV | 1510 | 新營華卡線(PV)(1510) |  | ABS1 | 1511E | [16 empty] | 2-37-10 | 2-37-11 | [6 empty] | ADCS_N | [8 empty] | 華卡CS.1511E_ABS | 新營華卡線(PV) ES | LINE161 |  |  |  |  | CDC | 1042 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | D_KEY | [33 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P01 | 新營PS | 0 |  | 1510 | 新營華卡線(PV)(1510) |  | PMA | [17 empty] | 2-37-15 | [7 empty] | ADCS_N | [8 empty] | 華卡CS.1510_PMA | 新營華卡線(PV) PMA | OTHER |  |  |  |  | CDC | 1043 | GENERICDIPoint | PS014_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P01 | 新營PS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 1044 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 1045 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 22 | 22kV | 230_SC | #3SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.230_SC_CAP | 23KV#3SC 容量 | SC | [5 empty] | 1046 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 1047 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 22 | 22kV | 250_SC | #5SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.250_SC_CAP | 23KV#5SC 容量 | SC | [5 empty] | 1048 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 22 | 22kV | 260_SC | #6SC | 9 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.260_SC_CAP | 23KV#6SC 容量 | SC | [5 empty] | 1049 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 810_SC | #1SC | 43.200001 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 1050 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.820_SC_CAP | 69KV#2SC 容量 | SC | [5 empty] | 1051 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | CAP | [25 empty] | ADCS_N | [8 empty] | 新營PS.830_SC_CAP | 69KV#3SC 容量 | SC | [5 empty] | 1052 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 000 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_000 | 新營PS NT for ISO_Desc | [6 empty] | 1053 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 001 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_001 | 新營PS NT 69KV_Hi_Limit | [6 empty] | 1054 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 002 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_002 | 新營PS NT 69KV_Lo_Limit | [6 empty] | 1055 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 003 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_003 | 新營PS NT#3ADTR 11KV_Hi_Limit | [6 empty] | 1056 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 004 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_004 | 新營PS NT#3ADTR 11KV_Lo_Limit | [6 empty] | 1057 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 005 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_005 | 新營PS NT#3BDTR 11KV_Hi_Limit | [6 empty] | 1058 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 006 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_006 | 新營PS NT#3BDTR 11KV_Lo_Limit | [6 empty] | 1059 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 007 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_007 | 新營PS NT#2BDTR 11KV_Hi_Limit | [6 empty] | 1060 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 008 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_008 | 新營PS NT#2BDTR 11KV_Lo_Limit | [6 empty] | 1061 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 009 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_009 | 新營PS NT#2ADTR 11KV_Hi_Limit | [6 empty] | 1062 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 0 |  | TRD | 新營PS |  | 010 | [25 empty] | TRAIN_AD | [8 empty] | 新營PS.TRD_010 | 新營PS NT#2ADTR 11KV_Lo_Limit | [6 empty] | 1063 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1530LE | 1530LE (非取樣點) | LINE161 | P01/161/1530/LE0 |  |  |  |  | 1064 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1530 | 新營柳營山線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1530BE | 1530BE (非取樣點) | LINE161 | P01/161/1530/BE0 |  |  |  |  | 1065 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | LE0 | 1540LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1540LE | 1540LE (非取樣點) | LINE161 | P01/161/1540/LE0 |  |  |  |  | 1066 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1540 | 新營柳營海線(1540) |  | BE0 | 1540BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1540BE | 1540BE (非取樣點) | LINE161 | P01/161/1540/BE0 |  |  |  |  | 1067 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1580LE | 1580LE (非取樣點) | LINE161 | P01/161/1580/LE0 |  |  |  |  | 1068 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1580 | 新營下營二路(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1580BE | 1580BE (非取樣點) | LINE161 | P01/161/1580/BE0 |  |  |  |  | 1069 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.610LE | 610LE (非取樣點) | LINE69 | P01/69/610/LE0 |  |  |  |  | 1070 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.610BE | 610BE (非取樣點) | LINE69 | P01/69/610/BE0 |  |  |  |  | 1071 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.620LE | 620LE (非取樣點) | LINE69 | P01/69/620/LE0 |  |  |  |  | 1072 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.620BE | 620BE (非取樣點) | LINE69 | P01/69/620/BE0 |  |  |  |  | 1073 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.630LE | 630LE (非取樣點) | LINE69 | P01/69/630/LE0 |  |  |  |  | 1074 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 630 | 新營白河水上線(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.630BE | 630BE (非取樣點) | LINE69 | P01/69/630/BE0 |  |  |  |  | 1075 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.640LE | 640LE (非取樣點) | LINE69 | P01/69/640/LE0 |  |  |  |  | 1076 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 640 | 營糖線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.640BE | 640BE (非取樣點) | LINE69 | P01/69/640/BE0 |  |  |  |  | 1077 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | LE0 | 650LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.650LE | 650LE (非取樣點) | LINE69 | P01/69/650/LE0 |  |  |  |  | 1078 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | BE0 | 650BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.650BE | 650BE (非取樣點) | LINE69 | P01/69/650/BE0 |  |  |  |  | 1079 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | LE0 | 660LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.660LE | 660LE (非取樣點) | LINE69 | P01/69/660/LE0 |  |  |  |  | 1080 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | BE0 | 660BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.660BE | 660BE (非取樣點) | LINE69 | P01/69/660/BE0 |  |  |  |  | 1081 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | LE0 | 670LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.670LE | 670LE (非取樣點) | LINE69 | P01/69/670/LE0 |  |  |  |  | 1082 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 670 | 大寮二路(670) |  | BE0 | 670BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.670BE | 670BE (非取樣點) | LINE69 | P01/69/670/BE0 |  |  |  |  | 1083 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | LE0 | 680LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.680LE | 680LE (非取樣點) | LINE69 | P01/69/680/LE0 |  |  |  |  | 1084 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 680 | 大寮一路(680) |  | BE0 | 680BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.680BE | 680BE (非取樣點) | LINE69 | P01/69/680/BE0 |  |  |  |  | 1085 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | LE0 | 710LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.710LE | 710LE (非取樣點) | LINE69 | P01/69/710/LE0 |  |  |  |  | 1086 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 710 | 東盟榮剛榮重線(710) |  | BE0 | 710BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.710BE | 710BE (非取樣點) | LINE69 | P01/69/710/BE0 |  |  |  |  | 1087 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | LE0 | 720LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.720LE | 720LE (非取樣點) | LINE69 | P01/69/720/LE0 |  |  |  |  | 1088 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 720 | 新營學甲二路(720) |  | BE0 | 720BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.720BE | 720BE (非取樣點) | LINE69 | P01/69/720/BE0 |  |  |  |  | 1089 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | LE0 | 730LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.730LE | 730LE (非取樣點) | LINE69 | P01/69/730/LE0 |  |  |  |  | 1090 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 730 | 新西線(730) |  | BE0 | 730BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.730BE | 730BE (非取樣點) | LINE69 | P01/69/730/BE0 |  |  |  |  | 1091 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC31 | VC31_DS |  | DS1 | VC31_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_DS | VC31_DS (非取樣點) | FEEDER | P01/11/VC31/DS |  |  |  |  | 1092 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC31 | VC31_ES |  | LE0 | VC31_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC31_ES | VC31_ES (非取樣點) | FEEDER | P01/11/VC31/ES |  |  |  |  | 1093 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC32 | VC32_DS |  | DS1 | VC32_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_DS | VC32_DS (非取樣點) | FEEDER | P01/11/VC32/DS |  |  |  |  | 1094 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC32 | VC32_ES |  | LE0 | VC32_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC32_ES | VC32_ES (非取樣點) | FEEDER | P01/11/VC32/ES |  |  |  |  | 1095 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC33 | VC33_DS |  | DS1 | VC33_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_DS | VC33_DS (非取樣點) | FEEDER | P01/11/VC33/DS |  |  |  |  | 1096 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC33 | VC33_ES |  | LE0 | VC33_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC33_ES | VC33_ES (非取樣點) | FEEDER | P01/11/VC33/ES |  |  |  |  | 1097 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC34 | VC34_DS |  | DS1 | VC34_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_DS | VC34_DS (非取樣點) | FEEDER | P01/11/VC34/DS |  |  |  |  | 1098 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC34 | VC34_ES |  | LE0 | VC34_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC34_ES | VC34_ES (非取樣點) | FEEDER | P01/11/VC34/ES |  |  |  |  | 1099 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC37 | VC37_DS |  | DS1 | VC37_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_DS | VC37_DS (非取樣點) | FEEDER | P01/11/VC37/DS |  |  |  |  | 1100 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC37 | VC37_ES |  | LE0 | VC37_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC37_ES | VC37_ES (非取樣點) | FEEDER | P01/11/VC37/ES |  |  |  |  | 1101 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC38 | VC38_DS |  | DS1 | VC38_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_DS | VC38_DS (非取樣點) | FEEDER | P01/11/VC38/DS |  |  |  |  | 1102 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC38 | VC38_ES |  | LE0 | VC38_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC38_ES | VC38_ES (非取樣點) | FEEDER | P01/11/VC38/ES |  |  |  |  | 1103 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC39 | VC39_DS |  | DS1 | VC39_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_DS | VC39_DS (非取樣點) | FEEDER | P01/11/VC39/DS |  |  |  |  | 1104 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC39 | VC39_ES |  | LE0 | VC39_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC39_ES | VC39_ES (非取樣點) | FEEDER | P01/11/VC39/ES |  |  |  |  | 1105 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC40 | VC40_DS |  | DS1 | VC40_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_DS | VC40_DS (非取樣點) | FEEDER | P01/11/VC40/DS |  |  |  |  | 1106 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC40 | VC40_ES |  | LE0 | VC40_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC40_ES | VC40_ES (非取樣點) | FEEDER | P01/11/VC40/ES |  |  |  |  | 1107 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 100 | TIE(100) |  | DS1 | 100_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.100_DS | 100_DS (非取樣點) | TIE | P01/11/100/DS |  |  |  |  | 1108 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 新營PS.1501E | 1501E (非取樣點) | TIE | P01/161/1500/E1 |  |  |  |  | 1109 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 新營PS.1502E | 1502E (非取樣點) | TIE | P01/161/1500/E2 |  |  |  |  | 1110 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 200 | TIE(200) |  | DS1 | 200_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.200_DS | 200_DS (非取樣點) | TIE | P01/22/200/DS |  |  |  |  | 1111 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 新營PS.601E | 601E (非取樣點) | TIE | P01/69/600/E1 |  |  |  |  | 1112 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 新營PS.602E | 602E (非取樣點) | TIE | P01/69/600/E2 |  |  |  |  | 1113 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | 1650TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1650TE | 1650TE (非取樣點) | MTR | P01/161/1650/TE0 |  |  |  |  | 1114 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.750TE | 750TE (非取樣點) | MTR | P01/69/750/TE0 |  |  |  |  | 1115 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | NE0 | 1651N | [24 empty] | ADCS_N | [8 empty] | 新營PS.1651N | 1651N (非取樣點) | MTR | P01/161/1650/NE0 |  |  |  |  | 1116 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | 1650BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1650BE | 1650BE (非取樣點) | MTR | P01/161/1650/BE0 |  |  |  |  | 1117 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.750BE | 750BE (非取樣點) | MTR | P01/69/750/BE0 |  |  |  |  | 1118 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1660TE | 1660TE (非取樣點) | MTR | P01/161/1660/TE0 |  |  |  |  | 1119 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.760TE | 760TE (非取樣點) | MTR | P01/69/760/TE0 |  |  |  |  | 1120 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | NE0 | 1661N | [24 empty] | ADCS_N | [8 empty] | 新營PS.1661N | 1661N (非取樣點) | MTR | P01/161/1660/NE0 |  |  |  |  | 1121 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1660BE | 1660BE (非取樣點) | MTR | P01/161/1660/BE0 |  |  |  |  | 1122 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.760BE | 760BE (非取樣點) | MTR | P01/69/760/BE0 |  |  |  |  | 1123 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | 1670TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1670TE | 1670TE (非取樣點) | MTR | P01/161/1670/TE0 |  |  |  |  | 1124 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.770TE | 770TE (非取樣點) | MTR | P01/69/770/TE0 |  |  |  |  | 1125 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | NE0 | 1671N | [24 empty] | ADCS_N | [8 empty] | 新營PS.1671N | 1671N (非取樣點) | MTR | P01/161/1670/NE0 |  |  |  |  | 1126 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | 1670BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1670BE | 1670BE (非取樣點) | MTR | P01/161/1670/BE0 |  |  |  |  | 1127 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.770BE | 770BE (非取樣點) | MTR | P01/69/770/BE0 |  |  |  |  | 1128 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1760TE | 1760TE (非取樣點) | MTR | P01/161/1760/TE0 |  |  |  |  | 1129 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1760BE | 1760BE (非取樣點) | MTR | P01/161/1760/BE0 |  |  |  |  | 1130 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 330 | #2DTR(330) |  | DS1 | 330_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.330_DS | 330_DS (非取樣點) | MTR | P01/11/330/DS |  |  |  |  | 1131 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 330 | #2DTR(330) |  | LE0 | 330_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.330_ES | 330_ES (非取樣點) | MTR | P01/11/330/ES |  |  |  |  | 1132 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 340 | #2DTR(340) |  | DS1 | 340_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.340_DS | 340_DS (非取樣點) | MTR | P01/22/340/DS |  |  |  |  | 1133 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 340 | #2DTR(340) |  | LE0 | 340_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.340_ES | 340_ES (非取樣點) | MTR | P01/22/340/ES |  |  |  |  | 1134 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1770TE | 1770TE (非取樣點) | MTR | P01/161/1770/TE0 |  |  |  |  | 1135 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1770BE | 1770BE (非取樣點) | MTR | P01/161/1770/BE0 |  |  |  |  | 1136 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 350 | #3DTR(350) |  | DS1 | 350_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.350_DS | 350_DS (非取樣點) | MTR | P01/11/350/DS |  |  |  |  | 1137 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 350 | #3DTR(350) |  | LE0 | 350_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.350_ES | 350_ES (非取樣點) | MTR | P01/11/350/ES |  |  |  |  | 1138 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 360 | #3DTR(360) |  | DS1 | 360_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.360_DS | 360_DS (非取樣點) | MTR | P01/22/360/DS |  |  |  |  | 1139 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 360 | #3DTR(360) |  | LE0 | 360_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.360_ES | 360_ES (非取樣點) | MTR | P01/22/360/ES |  |  |  |  | 1140 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.210_ES | 210_ES (非取樣點) | SC | P01/11/210/ES |  |  |  |  | 1141 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 210 | #1SC(210) |  | SC0 | 210SC | [24 empty] | ADCS_N | [8 empty] | 新營PS.210SC_ES | 210SC_ES (非取樣點) | SC | [5 empty] | 1142 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.210_DS | 210_DS (非取樣點) | SC | P01/11/210/DS |  |  |  |  | 1143 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.220_ES | 220_ES (非取樣點) | SC | P01/11/220/ES |  |  |  |  | 1144 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 220 | #2SC(220) |  | SC0 | 220SC | [24 empty] | ADCS_N | [8 empty] | 新營PS.220SC_ES | 220SC_ES (非取樣點) | SC | [5 empty] | 1145 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.220_DS | 220_DS (非取樣點) | SC | P01/11/220/DS |  |  |  |  | 1146 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.230_ES | 230_ES (非取樣點) | SC | P01/22/230/ES |  |  |  |  | 1147 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 230 | #3SC(230) |  | SC0 | 230SC | [24 empty] | ADCS_N | [8 empty] | 新營PS.230SC_ES | 230SC_ES (非取樣點) | SC | [5 empty] | 1148 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.230_DS | 230_DS (非取樣點) | SC | P01/22/230/DS |  |  |  |  | 1149 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.240_ES | 240_ES (非取樣點) | SC | P01/11/240/ES |  |  |  |  | 1150 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 240 | #4SC(240) |  | SC0 | 240SC | [24 empty] | ADCS_N | [8 empty] | 新營PS.240SC_ES | 240SC_ES (非取樣點) | SC | [5 empty] | 1151 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.240_DS | 240_DS (非取樣點) | SC | P01/11/240/DS |  |  |  |  | 1152 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.250_ES | 250_ES (非取樣點) | SC | P01/22/250/ES |  |  |  |  | 1153 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 250 | #5SC(250) |  | SC0 | 250SC | [24 empty] | ADCS_N | [8 empty] | 新營PS.250SC_ES | 250SC_ES (非取樣點) | SC | [5 empty] | 1154 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.250_DS | 250_DS (非取樣點) | SC | P01/22/250/DS |  |  |  |  | 1155 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_N | [8 empty] | 新營PS.260_ES | 260_ES (非取樣點) | SC | P01/22/260/ES |  |  |  |  | 1156 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 260 | #6SC(260) |  | SC0 | 260SC | [24 empty] | ADCS_N | [8 empty] | 新營PS.260SC_ES | 260SC_ES (非取樣點) | SC | [5 empty] | 1157 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_N | [8 empty] | 新營PS.260_DS | 260_DS (非取樣點) | SC | P01/22/260/DS |  |  |  |  | 1158 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.810BE | 810BE (非取樣點) | SC | P01/69/810/BE0 |  |  |  |  | 1159 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 810CE | 810CE |  | 810CE | 810CE | [24 empty] | ADCS_N | [8 empty] | 新營PS.810CE | 810CE (非取樣點) | SC | P01/69/810/CE0 |  |  |  |  | 1160 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 820BE | 820BE |  | 820BE | 820BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.820BE | 820BE (非取樣點) | SC | P01/69/820/BE0 |  |  |  |  | 1161 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 820CE | 820CE |  | 820CE | 820CE | [24 empty] | ADCS_N | [8 empty] | 新營PS.820CE | 820CE (非取樣點) | SC | P01/69/820/CE0 |  |  |  |  | 1162 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 830BE | 830BE |  | 830BE | 830BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.830BE | 830BE (非取樣點) | SC | P01/69/830/BE0 |  |  |  |  | 1163 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 830CE | 830CE |  | 830CE | 830CE | [24 empty] | ADCS_N | [8 empty] | 新營PS.830CE | 830CE (非取樣點) | SC | P01/69/830/CE0 |  |  |  |  | 1164 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_N | [8 empty] | 新營PS.161B1E | 161B1E (非取樣點) | BUS | P01/161/161B1E/BE1 |  |  |  |  | 1165 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_N | [8 empty] | 新營PS.161B2E | 161B2E (非取樣點) | BUS | P01/161/161B2E/BE2 |  |  |  |  | 1166 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 新營PS.69B1E | 69B1E (非取樣點) | BUS | P01/69/69B1E/BE1 |  |  |  |  | 1167 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 新營PS.69B2E | 69B2E (非取樣點) | BUS | P01/69/69B2E/BE2 |  |  |  |  | 1168 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 新營PS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 1169 | NotelDIPoint | [38 empty] | START/STOP | STOP
P01 | 新營PS | 0 |  | VC35 | VC35_DS |  | DS1 | VC35_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_DS | VC35_DS (非取樣點) | FEEDER | P01/11/VC35/DS |  |  |  |  | 1170 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC35 | VC35_ES |  | LE0 | VC35_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC35_ES | VC35_ES (非取樣點) | FEEDER | P01/11/VC35/ES |  |  |  |  | 1171 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC36 | VC36_DS |  | DS1 | VC36_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_DS | VC36_DS (非取樣點) | FEEDER | P01/11/VC36/DS |  |  |  |  | 1172 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC36 | VC36_ES |  | LE0 | VC36_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC36_ES | VC36_ES (非取樣點) | FEEDER | P01/11/VC36/ES |  |  |  |  | 1173 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | PW1UL | 610_PW1UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.610_PW1UL | 官田一路(610)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1174 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | PW2UL | 610_PW2UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.610_PW2UL | 官田一路(610)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1175 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P01 | 新營PS | 69 | 69kV | 610 | 備用線(610) |  | HCBUL | 610_HCBUL | [24 empty] | ADCS_N | [8 empty] | 新營PS.610_HCBUL | 官田一路(610)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1176 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.620_PW1UL | 新東線(620)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1177 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.620_PW2UL | 新東線(620)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1178 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P01 | 新營PS | 69 | 69kV | 620 | 新營新東線(620) |  | HCBUL | 620_HCBUL | [24 empty] | ADCS_N | [8 empty] | 新營PS.620_HCBUL | 新東線(620)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1179 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | PW1UL | 650_PW1UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.650_PW1UL | 隆田線(650)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1180 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | PW2UL | 650_PW2UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.650_PW2UL | 隆田線(650)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1181 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P01 | 新營PS | 69 | 69kV | 650 | 隆田線(650) |  | HCBUL | 650_HCBUL | [24 empty] | ADCS_N | [8 empty] | 新營PS.650_HCBUL | 隆田線(650)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1182 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | PW1UL | 660_PW1UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.660_PW1UL | 官田二路(660)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1183 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | PW2UL | 660_PW2UL | [24 empty] | ADCS_N | [8 empty] | 新營PS.660_PW2UL | 官田二路(660)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1184 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P01 | 新營PS | 69 | 69kV | 660 | 官田二路(660) |  | HCBUL | 660_HCBUL | [24 empty] | ADCS_N | [8 empty] | 新營PS.660_HCBUL | 官田二路(660)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1185 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P01 | 新營PS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_N | [8 empty] | 新營PS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 1186 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_N | [8 empty] | 新營PS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 1187 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_N | [8 empty] | 新營PS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 1188 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_N | [8 empty] | 新營PS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 1189 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3SSTRB | #3SSTRB |  | LBS1 | #3SSTRB_LBS1 | [24 empty] | ADCS_N | [8 empty] | 新營PS.#3SSTRB_LBS1 | #3SSTRB LBS1(非取樣點) | OTHER | [5 empty] | 1190 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3SSTRB | #3SSTRB |  | LBS2 | #3SSTRB_LBS2 | [24 empty] | ADCS_N | [8 empty] | 新營PS.#3SSTRB_LBS2 | #3SSTRB LBS2(非取樣點) | OTHER | [5 empty] | 1191 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3SSTRB | #3SSTRB |  | PF | #3SSTRB_PF | [24 empty] | ADCS_N | [8 empty] | 新營PS.#3SSTRB_PF | #3SSTRB PF(非取樣點) | OTHER | [5 empty] | 1192 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 4SSTRB | #4SSTRB |  | LBS | #4SSTRB_LBS | [24 empty] | ADCS_N | [8 empty] | 新營PS.#4SSTRB_LBS | #4SSTRB LBS(非取樣點) | OTHER | [5 empty] | 1193 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 4SSTRB | #4SSTRB |  | PF | #4SSTRB_PF | [24 empty] | ADCS_N | [8 empty] | 新營PS.#4SSTRB_PF | #4SSTRB PF(非取樣點) | OTHER | [5 empty] | 1194 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 | 1680TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1680TE | 1680TE (非取樣點) | MTR | P01/161/1680/TE0 |  |  |  |  | 1195 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE | [24 empty] | ADCS_N | [8 empty] | 新營PS.780TE | 780TE (非取樣點) | MTR | P01/69/780/TE0 |  |  |  |  | 1196 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | NE0 | 1681N | [24 empty] | ADCS_N | [8 empty] | 新營PS.1681N | 1681N (非取樣點) | MTR | P01/161/1680/NE0 |  |  |  |  | 1197 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 161 | 161kV | 1680 | #4MTR(1680) |  | BE0 | 1680BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1680BE | 1680BE (非取樣點) | MTR | P01/161/1680/BE0 |  |  |  |  | 1198 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.780BE | 780BE (非取樣點) | MTR | P01/69/780/BE0 |  |  |  |  | 1199 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1550LE | 1550LE (非取樣點) | LINE161 | P01/161/1550/LE0 |  |  |  |  | 1200 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1550 | 嘉義山上紅線(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1550BE | 1550BE (非取樣點) | LINE161 | P01/161/1550/BE0 |  |  |  |  | 1201 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1560LE | 1560LE (非取樣點) | LINE161 | P01/161/1560/LE0 |  |  |  |  | 1202 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1560 | 嘉義山上白線(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1560BE | 1560BE (非取樣點) | LINE161 | P01/161/1560/BE0 |  |  |  |  | 1203 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1570LE | 1570LE (非取樣點) | LINE161 | P01/161/1570/LE0 |  |  |  |  | 1204 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1570 | 新營下營一路(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1570BE | 1570BE (非取樣點) | LINE161 | P01/161/1570/BE0 |  |  |  |  | 1205 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC61 | VC61_DS |  | DS1 | VC61_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_DS | VC61_DS (非取樣點) | FEEDER | P01/22/VC61/DS |  |  |  |  | 1206 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC61 | VC61_ES |  | LE0 | VC61_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC61_ES | VC61_ES (非取樣點) | FEEDER | P01/22/VC61/ES |  |  |  |  | 1207 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC62 | VC62_DS |  | DS1 | VC62_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_DS | VC62_DS (非取樣點) | FEEDER | P01/22/VC62/DS |  |  |  |  | 1208 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC62 | VC62_ES |  | LE0 | VC62_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC62_ES | VC62_ES (非取樣點) | FEEDER | P01/22/VC62/ES |  |  |  |  | 1209 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC63 | VC63_DS |  | DS1 | VC63_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_DS | VC63_DS (非取樣點) | FEEDER | P01/22/VC63/DS |  |  |  |  | 1210 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC63 | VC63_ES |  | LE0 | VC63_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC63_ES | VC63_ES (非取樣點) | FEEDER | P01/22/VC63/ES |  |  |  |  | 1211 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC64 | VC64_DS |  | DS1 | VC64_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_DS | VC64_DS (非取樣點) | FEEDER | P01/22/VC64/DS |  |  |  |  | 1212 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC64 | VC64_ES |  | LE0 | VC64_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC64_ES | VC64_ES (非取樣點) | FEEDER | P01/22/VC64/ES |  |  |  |  | 1213 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC65 | VC65_DS |  | DS1 | VC65_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_DS | VC65_DS (非取樣點) | FEEDER | P01/22/VC65/DS |  |  |  |  | 1214 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC65 | VC65_ES |  | LE0 | VC65_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC65_ES | VC65_ES (非取樣點) | FEEDER | P01/22/VC65/ES |  |  |  |  | 1215 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC66 | VC66_DS |  | DS1 | VC66_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_DS | VC66_DS (非取樣點) | FEEDER | P01/22/VC66/DS |  |  |  |  | 1216 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC66 | VC66_ES |  | LE0 | VC66_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC66_ES | VC66_ES (非取樣點) | FEEDER | P01/22/VC66/ES |  |  |  |  | 1217 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC67 | VC67_DS |  | DS1 | VC67_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_DS | VC67_DS (非取樣點) | FEEDER | P01/22/VC67/DS |  |  |  |  | 1218 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC67 | VC67_ES |  | LE0 | VC67_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC67_ES | VC67_ES (非取樣點) | FEEDER | P01/22/VC67/ES |  |  |  |  | 1219 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC68 | VC68_DS |  | DS1 | VC68_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_DS | VC68_DS (非取樣點) | FEEDER | P01/22/VC68/DS |  |  |  |  | 1220 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC68 | VC68_ES |  | LE0 | VC68_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC68_ES | VC68_ES (非取樣點) | FEEDER | P01/22/VC68/ES |  |  |  |  | 1221 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC69 | VC69_DS |  | DS1 | VC69_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_DS | VC69_DS (非取樣點) | FEEDER | P01/22/VC69/DS |  |  |  |  | 1222 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC69 | VC69_ES |  | LE0 | VC69_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC69_ES | VC69_ES (非取樣點) | FEEDER | P01/22/VC69/ES |  |  |  |  | 1223 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | VC70 | VC70_DS |  | DS1 | VC70_DS | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_DS | VC70_DS (非取樣點) | FEEDER | P01/22/VC70/DS |  |  |  |  | 1224 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | VC70 | VC70_ES |  | LE0 | VC70_ES | [24 empty] | DDCS3_1 | [8 empty] | 新營PS.VC70_ES | VC70_ES (非取樣點) | FEEDER | P01/22/VC70/ES |  |  |  |  | 1225 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | LE0 | 910LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.910LE | 910LE (非取樣點) | LINE69 | P01/69/910/LE0 |  |  |  |  | 1226 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 69 | 69kV | 910 | 新營學甲一路(910) |  | BE0 | 910BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.910BE | 910BE (非取樣點) | LINE69 | P01/69/910/BE0 |  |  |  |  | 1227 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1520LE | 1520LE (非取樣點) | LINE161 | P01/161/1520/LE0 |  |  |  |  | 1228 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 161 | 161kV | 1520 | 華卡線(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 新營PS.1520BE | 1520BE (非取樣點) | LINE161 | P01/161/1520/BE0 |  |  |  |  | 1229 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P01 | 新營PS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 新營PS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1230 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 新營PS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1231 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_N | [8 empty] | 新營PS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1232 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P01 | 新營PS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_N | [8 empty] | 新營PS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1233 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo