## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 2 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 3 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 4 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 5 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1530LE | 1530LE (非取樣點) | LINE161 | [5 empty] | 6 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1530BE | 1530BE (非取樣點) | LINE161 | [5 empty] | 7 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1710LE | 1710LE (非取樣點) | LINE161 | [5 empty] | 8 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1710BE | 1710BE (非取樣點) | LINE161 | [5 empty] | 9 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1720LE | 1720LE (非取樣點) | LINE161 | [5 empty] | 10 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1720BE | 1720BE (非取樣點) | LINE161 | [5 empty] | 11 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1740LE | 1740LE (非取樣點) | LINE161 | [5 empty] | 12 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1740BE | 1740BE (非取樣點) | LINE161 | [5 empty] | 13 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1650TE | 1650TE (非取樣點) | MTR | [5 empty] | 14 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1650NE | #1MTR(1650) |  | NE0 | 1651N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/1MTR | [13 empty] | no rule | B2/P02_A1 | [8 empty] | 安南PS.1651N | 1651N (非取樣點) | MTR | [5 empty] | 15 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1650BE | 1650BE (非取樣點) | MTR | [5 empty] | 16 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.750TE | 750TE (非取樣點) | MTR | [5 empty] | 17 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.750BE | 750BE (非取樣點) | MTR | [5 empty] | 18 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1660TE | 1660TE (非取樣點) | MTR | [5 empty] | 19 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1660NE | #2MTR(1660) |  | NE0 | 1661N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/2MTR | [13 empty] | no rule | B2/P02_A1 | [8 empty] | 安南PS.1661N | 1661N (非取樣點) | MTR | [5 empty] | 20 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1660BE | 1660BE (非取樣點) | MTR | [5 empty] | 21 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.760TE | 760TE (非取樣點) | MTR | [5 empty] | 22 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.760BE | 760BE (非取樣點) | MTR | [5 empty] | 23 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1760TE | 1760TE (非取樣點) | MTR | [5 empty] | 26 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1760BE | 1760BE (非取樣點) | MTR | [5 empty] | 27 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 28 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 29 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.601E | 601E (非取樣點) | TIE | [5 empty] | 30 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.602E | 602E (非取樣點) | TIE | [5 empty] | 31 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 32 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 33 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 34 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 35 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 36 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 37 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.830BE | 830BE (非取樣點) | SC | [5 empty] | 38 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | DS3 | 833_DS(非取樣點) | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.833_DS | 833_DS (非取樣點) | SC | [5 empty] | 39 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.830LE | 830LE (非取樣點) | SC | [5 empty] | 40 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | E3 | 833CE(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.833CE | 833CE(非取樣點) | OTHER | [5 empty] | 41 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT21_DS | KT21_DS (非取樣點) | FEEDER | [5 empty] | 42 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT21_ES | KT21_ES (非取樣點) | FEEDER | [5 empty] | 43 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT22_DS | KT22_DS (非取樣點) | FEEDER | [5 empty] | 44 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT22_ES | KT22_ES (非取樣點) | FEEDER | [5 empty] | 45 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT23_DS | KT23_DS (非取樣點) | FEEDER | [5 empty] | 46 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT23_ES | KT23_ES (非取樣點) | FEEDER | [5 empty] | 47 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT24_DS | KT24_DS (非取樣點) | FEEDER | [5 empty] | 48 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT24_ES | KT24_ES (非取樣點) | FEEDER | [5 empty] | 49 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT25_DS | KT25_DS (非取樣點) | FEEDER | [5 empty] | 50 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT25_ES | KT25_ES (非取樣點) | FEEDER | [5 empty] | 51 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT26_DS | KT26_DS (非取樣點) | FEEDER | [5 empty] | 52 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT26_ES | KT26_ES (非取樣點) | FEEDER | [5 empty] | 53 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT27_DS | KT27_DS (非取樣點) | FEEDER | [5 empty] | 54 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT27_ES | KT27_ES (非取樣點) | FEEDER | [5 empty] | 55 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT28_DS | KT28_DS (非取樣點) | FEEDER | [5 empty] | 56 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT28_ES | KT28_ES (非取樣點) | FEEDER | [5 empty] | 57 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT29_DS | KT29_DS (非取樣點) | FEEDER | [5 empty] | 58 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT29_ES | KT29_ES (非取樣點) | FEEDER | [5 empty] | 59 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT30_DS | KT30_DS (非取樣點) | FEEDER | [5 empty] | 60 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT30_ES | KT30_ES (非取樣點) | FEEDER | [5 empty] | 61 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT31_DS | KT31_DS (非取樣點) | FEEDER | [5 empty] | 62 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT31_ES | KT31_ES (非取樣點) | FEEDER | [5 empty] | 63 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT32_DS | KT32_DS (非取樣點) | FEEDER | [5 empty] | 64 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT32_ES | KT32_ES (非取樣點) | FEEDER | [5 empty] | 65 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT33_DS | KT33_DS (非取樣點) | FEEDER | [5 empty] | 66 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT33_ES | KT33_ES (非取樣點) | FEEDER | [5 empty] | 67 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT34_DS | KT34_DS (非取樣點) | FEEDER | [5 empty] | 68 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT34_ES | KT34_ES (非取樣點) | FEEDER | [5 empty] | 69 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT35_DS | KT35_DS (非取樣點) | FEEDER | [5 empty] | 70 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT35_ES | KT35_ES (非取樣點) | FEEDER | [5 empty] | 71 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT36_DS | KT36_DS (非取樣點) | FEEDER | [5 empty] | 72 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT36_ES | KT36_ES (非取樣點) | FEEDER | [5 empty] | 73 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT37_DS | KT37_DS (非取樣點) | FEEDER | [5 empty] | 74 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT37_ES | KT37_ES (非取樣點) | FEEDER | [5 empty] | 75 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT38_DS | KT38_DS (非取樣點) | FEEDER | [5 empty] | 76 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT38_ES | KT38_ES (非取樣點) | FEEDER | [5 empty] | 77 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT39_DS | KT39_DS (非取樣點) | FEEDER | [5 empty] | 78 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT39_ES | KT39_ES (非取樣點) | FEEDER | [5 empty] | 79 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT40_DS | KT40_DS (非取樣點) | FEEDER | [5 empty] | 80 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT40_ES | KT40_ES (非取樣點) | FEEDER | [5 empty] | 81 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.310_DS | 310_DS (非取樣點) | MTR | [5 empty] | 82 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.310_ES | 310_ES (非取樣點) | MTR | [5 empty] | 83 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.320_DS | 320_DS (非取樣點) | MTR | [5 empty] | 84 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.320_ES | 320_ES (非取樣點) | MTR | [5 empty] | 85 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.330_DS | 330_DS (非取樣點) | MTR | [5 empty] | 86 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.330_ES | 330_ES (非取樣點) | MTR | [5 empty] | 87 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.340_DS | 340_DS (非取樣點) | MTR | [5 empty] | 88 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | ES | (非取樣點) | Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.340_ES | 340_ES (非取樣點) | MTR | [5 empty] | 89 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.820BE | 820BE (非取樣點) | SC | [5 empty] | 90 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.820CE | 820CE (非取樣點) | SC | [5 empty] | 91 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.810BE | 810BE (非取樣點) | SC | [5 empty] | 92 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.810CE | 810CE (非取樣點) | SC | [5 empty] | 93 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.210_ES | 210_ES (非取樣點) | SC | [5 empty] | 94 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.210_DS | 210_DS (非取樣點) | SC | [5 empty] | 95 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | CE0 | 210E | del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.210E | 210E (非取樣點) | SC | [5 empty] | 96 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.220_ES | 220_ES (非取樣點) | SC | [5 empty] | 97 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.220_DS | 220_DS (非取樣點) | SC | [5 empty] | 98 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | CE0 | 220E | del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.220E | 220E (非取樣點) | SC | [5 empty] | 99 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.240_ES | 240_ES (非取樣點) | SC | [5 empty] | 100 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.240_DS | 240_DS (非取樣點) | SC | [5 empty] | 101 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | CE0 | 240E | del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.240E | 240E (非取樣點) | SC | [5 empty] | 102 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.230_ES | 230_ES (非取樣點) | SC | [5 empty] | 103 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.230_DS | 230_DS (非取樣點) | SC | [5 empty] | 104 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | CE0 | 230E | del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.230E | 230E (非取樣點) | SC | [5 empty] | 105 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.260_ES | 260_ES (非取樣點) | SC | [5 empty] | 106 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.260_DS | 260_DS (非取樣點) | SC | [5 empty] | 107 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | CE0 | 260E | del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.260E | 260E (非取樣點) | SC | [5 empty] | 108 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.250_ES | 250_ES (非取樣點) | SC | [5 empty] | 109 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.250_DS | 250_DS (非取樣點) | SC | [5 empty] | 110 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | CE0 | 250E | del | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.250E | 250E (非取樣點) | SC | [5 empty] | 111 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.100_DS | 100_DS (非取樣點) | TIE | [5 empty] | 112 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | DS | (非取樣點) | Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.200_DS | 200_DS (非取樣點) | TIE | [5 empty] | 113 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.350_DS | 350_DS (非取樣點) | MTR | [5 empty] | 114 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.350_ES | 350_ES (非取樣點) | MTR | [5 empty] | 115 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.360_DS | 360_DS (非取樣點) | MTR | [5 empty] | 116 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | ES | (非取樣點) | B2,Element | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.360_ES | 360_ES (非取樣點) | MTR | [5 empty] | 117 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.270_ES | 270_ES (非取樣點) | SC | [5 empty] | 118 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.270_DS | 270_DS (非取樣點) | SC | [5 empty] | 119 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.280_ES | 280_ES (非取樣點) | SC | [5 empty] | 120 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.280_DS | 280_DS (非取樣點) | SC | [5 empty] | 121 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT71_DS | KT71_DS (非取樣點) | FEEDER | [5 empty] | 122 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT71_ES | KT71_ES (非取樣點) | FEEDER | [5 empty] | 123 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT72_DS | KT72_DS (非取樣點) | FEEDER | [5 empty] | 124 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT72_ES | KT72_ES (非取樣點) | FEEDER | [5 empty] | 125 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT73_DS | KT73_DS (非取樣點) | FEEDER | [5 empty] | 126 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT73_ES | KT73_ES (非取樣點) | FEEDER | [5 empty] | 127 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT74_DS | KT74_DS (非取樣點) | FEEDER | [5 empty] | 128 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT74_ES | KT74_ES (非取樣點) | FEEDER | [5 empty] | 129 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT75_DS | KT75_DS (非取樣點) | FEEDER | [5 empty] | 130 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT75_ES | KT75_ES (非取樣點) | FEEDER | [5 empty] | 131 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT76_DS | KT76_DS (非取樣點) | FEEDER | [5 empty] | 132 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT76_ES | KT76_ES (非取樣點) | FEEDER | [5 empty] | 133 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT77_DS | KT77_DS (非取樣點) | FEEDER | [5 empty] | 134 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT77_ES | KT77_ES (非取樣點) | FEEDER | [5 empty] | 135 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT78_DS | KT78_DS (非取樣點) | FEEDER | [5 empty] | 136 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT78_ES | KT78_ES (非取樣點) | FEEDER | [5 empty] | 137 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | DS | (非取樣點) |  | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT79_DS | KT79_DS (非取樣點) | FEEDER | [5 empty] | 138 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | ES | (非取樣點) |  | Status | ES(接地開關) | Open/Close | Y | 5 | DI-SP | [17 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT79_ES | KT79_ES (非取樣點) | FEEDER | [5 empty] | 139 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | DS | (非取樣點) | B2,Element | Status | DS | Open/Close | Y | 7 | DI-SP | [17 empty] | B3/P02_A1 | [8 empty] | 安南PS.300_DS | 300_DS (非取樣點) | TIE | [5 empty] | 140 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 141 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 142 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 143 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 144 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/P02_A1 | [8 empty] | 安南PS.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 145 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/1Bus | [13 empty] | aaaz | B2/P02_A1 | [8 empty] | 安南PS.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 146 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aaaz | B2/P02_A1 | [8 empty] | 安南PS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 147 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/1Bus | [13 empty] | aaaz | B2/P02_A1 | [8 empty] | 安南PS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 148 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 149 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 150 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0002 |  |  | 1-82 |  |  | 1530 | W | 1530 安南鹽行線 W | MW_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1530_MW | 安南鹽行線 MW | LINE161 | [5 empty] | 151 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-83 |  |  | 1530 | Q | 1530 安南鹽行線 Q | MVAR_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1530_MVAR | 安南鹽行線 MVAR | LINE161 | [5 empty] | 152 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-84 |  |  | 1710 | W | 1710 山上安南豐華紅線 | MW_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1710_MW | 山上豐華紅線 MW | LINE161 | [5 empty] | 153 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0005 |  |  | 1-85 |  |  | 1710 | Q | 1710 山上安南豐華紅線 | MVAR_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1710_MVAR | 山上豐華紅線 MVAR | LINE161 | [5 empty] | 154 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-86 |  |  | 1510 | W | 1510 安南小北一路 W | MW_-336_336(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1510_MW | 安南小北一路 MW | LINE161 | [5 empty] | 155 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-87 |  |  | 1510 | Q | 1510 安南小北一路 Q | MVAR_-336_336(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1510_MVAR | 安南小北一路 MVAR | LINE161 | [5 empty] | 156 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0008 |  |  | 1-88 |  |  | 1520 | W | 1520 安南小北二路 W | MW_-336_336(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1520_MW | 安南小北二路 MW | LINE161 | [5 empty] | 157 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-89 |  |  | 1520 | Q | 1520 安南小北二路 Q | MVAR_-336_336(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1520_MVAR | 安南小北二路 MVAR | LINE161 | [5 empty] | 158 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-8A |  |  | 1720 | W | 1720 道爺安南新化線 W | MW_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1720_MW | 道爺安南新化線 MW | LINE161 | [5 empty] | 159 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0011 |  |  | 1-8B |  |  | 1720 | Q | 1720 道爺安南新化線 Q | MVAR_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1720_MVAR | 道爺安南新化線 MVAR | LINE161 | [5 empty] | 160 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0012 |  |  | 1-8C |  |  | 1740 | W | 1740 安南和順線 W | MW_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1740_MW | 安南和順線 MW | LINE161 | [5 empty] | 161 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8D |  |  | 1740 | Q | 1740 安南和順線 Q | MVAR_-448_448(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1740_MVAR | 安南和順線 MVAR | LINE161 | [5 empty] | 162 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0016 |  |  | 1-90 |  |  | BUS | V | #1 161KV BUS V | kV_-210_210(-2000_2000) | aaa | B2/P02_A1 | [8 empty] | 安南PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 163 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P02 | 安南PS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0017 |  |  | 1-91 |  |  | BUS | V | #2 161KV BUS V | kV_-210_210(-2000_2000) | aab | B2/P02_A1 | [8 empty] | 安南PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 164 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0023 |  |  | 1-97 |  |  | 750 | W | #1MTR二次750 W | MW_-360_360(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.#1MTR_MW | #1MTR二次側 MW | MTR | [5 empty] | 165 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-98 |  |  | 750 | Q | #1MTR二次750 Q | MVAR_-240_240(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | [5 empty] | 166 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0026 |  |  | 1-9A |  |  | 760 | W | #2MTR二次760 W | MW_-360_360(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.#2MTR_MW | #2MTR二次側 MW | MTR | [5 empty] | 167 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0027 |  |  | 1-9B |  |  | 760 | Q | #2MTR二次760 Q | MVAR_-240_240(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | [5 empty] | 168 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-9C |  |  | 310 | A | D1A 310 (R) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | [5 empty] | 169 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0029 |  |  | 1-9D |  |  | 310 | A | D1A 310 (S) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | [5 empty] | 170 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-9E |  |  | 310 | A | D1A 310 (T) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | [5 empty] | 171 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-9F |  |  | 310 | W | D1A 310 (A) W | MW_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | [5 empty] | 172 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0032 |  |  | 1-A0 |  |  | 310 | Q | D1A 310(A) Q | MVAR_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | [5 empty] | 173 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-A1 |  |  | 320 | A | D1B 320 (R) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | [5 empty] | 174 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-A2 |  |  | 320 | A | D1B 320 (S) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | [5 empty] | 175 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0035 |  |  | 1-A3 |  |  | 320 | A | D1B 320 (T) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | [5 empty] | 176 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-A4 |  |  | 320 | W | D1B 320 (B) W | MW_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | [5 empty] | 177 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-A5 |  |  | 320 | Q | D1B 320 (B) Q | MVAR_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | [5 empty] | 178 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0038 |  |  | 1-A6 |  |  | 330 | A | D2A 330 (R) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | [5 empty] | 179 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-A7 |  |  | 330 | A | D2A 330 (S) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | [5 empty] | 180 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-A8 |  |  | 330 | A | D2A 330 (T) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | [5 empty] | 181 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0041 |  |  | 1-A9 |  |  | 330 | W | D2A 330 (A) W | MW_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | [5 empty] | 182 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-AA |  |  | 330 | Q | D2A 330 (A) Q | MVAR_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | [5 empty] | 183 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.072 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-AB |  |  | 340 | A | D2B 340 (R) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | [5 empty] | 184 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0044 |  |  | 1-AC |  |  | 340 | A | D2B 340 (S) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | [5 empty] | 185 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-AD |  |  | 340 | A | D2B 340 (T) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | [5 empty] | 186 |  |  |  |  | AI | [5 empty] | LG_1450 | 1305 | 1450 | 1595 | 1812.5 | 0.1 | -1305 | -1450 | -1595 | -1812.5 | 1 | 0.01 | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-AE |  |  | 340 | W | D2B 340 (B) W | MW_-54_54(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | [5 empty] | 187 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0047 |  |  | 1-AF |  |  | 340 | Q | D2B 340 (B) Q | MVAR_-36_36(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | [5 empty] | 188 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.108 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-B0 |  |  | 1500 | A | 161KV TIE 1500 A | A_-2000_2000(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 189 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-B1 |  |  | 600 | A | 69KV TIE 600 A | A_-2000_2000(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 190 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P02 | 安南PS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0050 |  |  | 1-B2 |  |  | #1 69KV | KV | #1 69KV BUS電壓 | kV_-90_90(-2000_2000) | aaa | B2/P02_A1 | [8 empty] | 安南PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | [5 empty] | 191 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P02 | 安南PS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0051 |  |  | 1-B3 |  |  | #2 69KV | KV | #2 69KV BUS電壓 | kV_-90_90(-2000_2000) | aab | B2/P02_A1 | [8 empty] | 安南PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 192 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0053 |  |  | 1-B5 |  |  | 630 | W | 安南安順白線630 W | MW_-144_144(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.630_MW | 安順白線 MW | LINE69 | [5 empty] | 193 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-B6 |  |  | 630 | Q | 安南安順白線630 Q | MVAR_-144_144(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.630_MVAR | 安順白線 MVAR | LINE69 | [5 empty] | 194 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0056 |  |  | 1-B8 |  |  | 640 | W | 安南安順紅線640 W | MW_-144_144(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.640_MW | 安順紅線 MW | LINE69 | [5 empty] | 195 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-B9 |  |  | 640 | Q | 安南安順紅線640 Q | MVAR_-144_144(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.640_MVAR | 安順紅線 MVAR | LINE69 | [5 empty] | 196 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0059 |  |  | 1-BB |  |  | 620 | W | 安南運河線620 W | MW_-144_144(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.620_MW | 安南運河線 MW | LINE69 | [5 empty] | 197 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-BC |  |  | 620 | Q | 安南運河線620 Q | MVAR_-144_144(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.620_MVAR | 安南運河線 MVAR | LINE69 | [5 empty] | 198 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | Locate Empty |  | 10% AI REF | ADCL_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 199 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | Locate Empty |  | 90% AI REF | ADCH_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 200 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 1ABUS | #1ABUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0070 |  |  | 1-C6 |  |  | D1A | KV | D1A 電壓 BUS PT | kV_-9_9(-2000_2000) | aaa | B3/P02_A1 | [8 empty] | 安南PS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | [5 empty] | 201 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 2ABUS | #2ABUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0071 |  |  | 1-C7 |  |  | D2A | KV | D2A 電壓 BUS PT | kV_-9_9(-2000_2000) | aba | B3/P02_A1 | [8 empty] | 安南PS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | [5 empty] | 202 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 1BBUS | #1BBUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0074 |  |  | 1-CA |  |  | D1B | KV | D1B 電壓 BUS PT | kV_-9_9(-2000_2000) | baa | B3/P02_A1 | [8 empty] | 安南PS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | [5 empty] | 203 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 2BBUS | #2BBUS |  | V |  | B3 | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0075 |  |  | 1-CB |  |  | D2B | KV | D2B 電壓 BUS PT | kV_-9_9(-2000_2000) | bba | B3/P02_A1 | [8 empty] | 安南PS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | [5 empty] | 204 |  |  |  |  | AI | [5 empty] | LG_11 | 7.2 | 8.2 | 9.2 | 10.2 | 0.2 | 6.5 | 5.5 | 4.5 | 0 | 4 | 1.5 | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-CC |  |  | 100 | A | 11KV #1TIE 100 A (R) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.11KV_100_A1 | 11KV 100 R相AMP | TIE | [5 empty] | 205 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0077 |  |  | 1-CD |  |  | 100 | A | 11KV #1TIE 100 A (S) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.11KV_100_A2 | 11KV 100 S相AMP | TIE | [5 empty] | 206 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0078 |  |  | 1-CE |  |  | 100 | A | 11KV #1TIE 100 A (T) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.11KV_100_A3 | 11KV 100 T相AMP | TIE | [5 empty] | 207 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0079 |  |  | 1-CF |  |  | 200 | A | 11KV #2TIE 200 A (R) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.11KV_200_A1 | 11KV 200 R相AMP | TIE | [5 empty] | 208 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-D0 |  |  | 200 | A | 11KV #2TIE 200 A (S) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.11KV_200_A2 | 11KV 200 S相AMP | TIE | [5 empty] | 209 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-D1 |  |  | 200 | A | 11KV #2TIE 200 A (T) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.11KV_200_A3 | 11KV 200 T相AMP | TIE | [5 empty] | 210 |  |  |  |  | AI | [5 empty] | C20R1000 | 950 | 1000 | 1100 | 1230 | 0.45 | -950 | -1000 | -1100 | -1230 | 1 | 0.01 | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-D2 |  |  | 南21線 | A | 南21線F1 KT21 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南21線A1 | 11KV南21線 R相AMP | FEEDER | [5 empty] | 211 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-D3 |  |  | 南21線 | A | 南21線F1 KT21 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南21線A2 | 11KV南21線 S相AMP | FEEDER | [5 empty] | 212 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-D4 |  |  | 南21線 | A | 南21線F1 KT21 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南21線A3 | 11KV南21線 T相AMP | FEEDER | [5 empty] | 213 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-D5 |  |  | 南21線 | Q | 南21線F1 KT21 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南21線KVAR | 11KV南21線 KVAR | FEEDER | [5 empty] | 214 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-D6 |  |  | 南22線 | A | 南22線F2 KT22 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南22線A1 | 11KV南22線 R相AMP | FEEDER | [5 empty] | 215 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-D7 |  |  | 南22線 | A | 南22線F2 KT22 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南22線A2 | 11KV南22線 S相AMP | FEEDER | [5 empty] | 216 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-D8 |  |  | 南22線 | A | 南22線F2 KT22 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南22線A3 | 11KV南22線 T相AMP | FEEDER | [5 empty] | 217 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-D9 |  |  | 南22線 | Q | 南22線F2 KT22 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南22線KVAR | 11KV南22線 KVAR | FEEDER | [5 empty] | 218 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-DA |  |  | 南23線 | A | 南23線F3 KT23 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南23線A1 | 11KV南23線 R相AMP | FEEDER | [5 empty] | 219 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-DB |  |  | 南23線 | A | 南23線F3 KT23 A(S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南23線A2 | 11KV南23線 S相AMP | FEEDER | [5 empty] | 220 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-DC |  |  | 南23線 | A | 南23線F3 KT23 A(T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南23線A3 | 11KV南23線 T相AMP | FEEDER | [5 empty] | 221 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-DD |  |  | 南23線 | Q | 南23線F3 KT23 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南23線KVAR | 11KV南23線 KVAR | FEEDER | [5 empty] | 222 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-DE |  |  | 南24線 | A | 南24線F4 KT24 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南24線A1 | 11KV南24線 R相AMP | FEEDER | [5 empty] | 223 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-DF |  |  | 南24線 | A | 南24線F4 KT24 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南24線A2 | 11KV南24線 S相AMP | FEEDER | [5 empty] | 224 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0096 |  |  | 1-E0 |  |  | 南24線 | A | 南24線F4 KT24 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南24線A3 | 11KV南24線 T相AMP | FEEDER | [5 empty] | 225 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0097 |  |  | 1-E1 |  |  | 南24線 | Q | 南24線F4 KT24 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南24線KVAR | 11KV南24線 KVAR | FEEDER | [5 empty] | 226 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0098 |  |  | 1-E2 |  |  | 南25線 | A | 南25線F5 KT25 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南25線A1 | 11KV南25線 R相AMP | FEEDER | [5 empty] | 227 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0099 |  |  | 1-E3 |  |  | 南25線 | A | 南25線F5 KT25 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南25線A2 | 11KV南25線 S相AMP | FEEDER | [5 empty] | 228 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0100 |  |  | 1-E4 |  |  | 南25線 | T | 南25線F5 KT25 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南25線A3 | 11KV南25線 T相AMP | FEEDER | [5 empty] | 229 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0101 |  |  | 1-E5 |  |  | 南25線 | Q | 南25線F5 KT25 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南25線KVAR | 11KV南25線 KVAR | FEEDER | [5 empty] | 230 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0102 |  |  | 1-E6 |  |  | 南26線 | A | 南26線 F6 KT26 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南26線A1 | 11KV南26線 R相AMP | FEEDER | [5 empty] | 231 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0103 |  |  | 1-E7 |  |  | 南26線 | A | 南26線 F6 KT26 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南26線A2 | 11KV南26線 S相AMP | FEEDER | [5 empty] | 232 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0104 |  |  | 1-E8 |  |  | 南26線 | A | 南26線 F6 KT26 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南26線A3 | 11KV南26線 T相AMP | FEEDER | [5 empty] | 233 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0105 |  |  | 1-E9 |  |  | 南26線 | Q | 南26線 F6 KT26 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南26線KVAR | 11KV南26線 KVAR | FEEDER | [5 empty] | 234 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0106 |  |  | 1-EA |  |  | 南27線 | A | 南27線F7 KT27 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南27線A1 | 11KV南27線 R相AMP | FEEDER | [5 empty] | 235 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0107 |  |  | 1-EB |  |  | 南27線 | A | 南27線F7 KT27 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南27線A2 | 11KV南27線 S相AMP | FEEDER | [5 empty] | 236 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0108 |  |  | 1-EC |  |  | 南27線 | A | 南27線F7 KT27 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南27線A3 | 11KV南27線 T相AMP | FEEDER | [5 empty] | 237 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0109 |  |  | 1-ED |  |  | 南27線 | Q | 南27線F7 KT27 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南27線KVAR | 11KV南27線 KVAR | FEEDER | [5 empty] | 238 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0110 |  |  | 1-EE |  |  | 南28線 | A | 南28線F8 KT28 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南28線A1 | 11KV南28線 R相AMP | FEEDER | [5 empty] | 239 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0111 |  |  | 1-EF |  |  | 南28線 | A | 南28線F8 KT28 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南28線A2 | 11KV南28線 S相AMP | FEEDER | [5 empty] | 240 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0112 |  |  | 1-F0 |  |  | 南28線 | A | 南28線F8 KT28 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南28線A3 | 11KV南28線 T相AMP | FEEDER | [5 empty] | 241 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0113 |  |  | 1-F1 |  |  | 南28線 | Q | 南28線F8 KT28 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南28線KVAR | 11KV南28線 KVAR | FEEDER | [5 empty] | 242 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0114 |  |  | 1-F2 |  |  | 南29線 | A | 南29線F9 KT29 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南29線A1 | 11KV南29線 R相AMP | FEEDER | [5 empty] | 243 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0115 |  |  | 1-F3 |  |  | 南29線 | A | 南29線F9 KT29 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南29線A2 | 11KV南29線 S相AMP | FEEDER | [5 empty] | 244 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0116 |  |  | 1-F4 |  |  | 南29線 | A | 南29線F9 KT29 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南29線A3 | 11KV南29線 T相AMP | FEEDER | [5 empty] | 245 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0117 |  |  | 1-F5 |  |  | 南29線 | Q | 南29線F9 KT29 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南29線KVAR | 11KV南29線 KVAR | FEEDER | [5 empty] | 246 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0118 |  |  | 1-F6 |  |  | 南30線 | A | 南30線F10 KT30 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南30線A1 | 11KV南30線 R相AMP | FEEDER | [5 empty] | 247 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0119 |  |  | 1-F7 |  |  | 南30線 | A | 南30線F10 KT30 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南30線A2 | 11KV南30線 S相AMP | FEEDER | [5 empty] | 248 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0120 |  |  | 1-F8 |  |  | 南30線 | A | 南30線F10 KT30 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南30線A3 | 11KV南30線 T相AMP | FEEDER | [5 empty] | 249 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0121 |  |  | 1-F9 |  |  | 南30線 | Q | 南30線F10 KT30 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南30線KVAR | 11KV南30線 KVAR | FEEDER | [5 empty] | 250 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0122 |  |  | 1-FA |  |  | 南31線 | A | 南31線F11 KT31 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南31線A1 | 11KV南31線 R相AMP | FEEDER | [5 empty] | 251 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0123 |  |  | 1-FB |  |  | 南31線 | A | 南31線F11 KT31 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南31線A2 | 11KV南31線 S相AMP | FEEDER | [5 empty] | 252 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0124 |  |  | 1-FC |  |  | 南31線 | A | 南31線F11 KT31 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南31線A3 | 11KV南31線 T相AMP | FEEDER | [5 empty] | 253 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0125 |  |  | 1-FD |  |  | 南31線 | Q | 南31線F11 KT31 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南31線KVAR | 11KV南31線 KVAR | FEEDER | [5 empty] | 254 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0126 |  |  | 1-FE |  |  | 南32線 | A | 南32線F12 KT32 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南32線A1 | 11KV南32線 R相AMP | FEEDER | [5 empty] | 255 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0127 |  |  | 1-FF |  |  | 南32線 | A | 南32線F12 KT32 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南32線A2 | 11KV南32線 S相AMP | FEEDER | [5 empty] | 256 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCL3 |  |  | MvMoment | No3 AI參考點 10% |  | Y |  | AI | [6 empty] | 0128 |  |  | 2-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.3AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | [5 empty] | 257 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCH3 |  |  | MvMoment | No3 AI參考點 90% |  | Y |  | AI | [6 empty] | 0129 |  |  | 2-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No3AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | [5 empty] | 258 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0130 |  |  | 2-82 |  |  | 南32線 | A | 南32線F12 KT32 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南32線A3 | 11KV南32線 T相AMP | FEEDER | [5 empty] | 259 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0131 |  |  | 2-83 |  |  | 南32線 | Q | 南32線F12 KT32 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南32線KVAR | 11KV南32線 KVAR | FEEDER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0132 |  |  | 2-84 |  |  | 南33線 | A | 南33線F13 KT33 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南33線A1 | 11KV南33線 R相AMP | FEEDER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0133 |  |  | 2-85 |  |  | 南33線 | A | 南33線F13 KT33 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南33線A2 | 11KV南33線 S相AMP | FEEDER | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0134 |  |  | 2-86 |  |  | 南33線 | A | 南33線F13 KT33 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南33線A3 | 11KV南33線 T相AMP | FEEDER | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0135 |  |  | 2-87 |  |  | 南33線 | Q | 南33線F13 KT33 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南33線KVAR | 11KV南33線 KVAR | FEEDER | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0136 |  |  | 2-88 |  |  | 南34線 | A | 南34線F14 KT34 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南34線A1 | 11KV南34線 R相AMP | FEEDER | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0137 |  |  | 2-89 |  |  | 南34線 | A | 南34線F14 KT34 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南34線A2 | 11KV南34線 S相AMP | FEEDER | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0138 |  |  | 2-8A |  |  | 南34線 | A | 南34線F14 KT34 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南34線A3 | 11KV南34線 T相AMP | FEEDER | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0139 |  |  | 2-8B |  |  | 南34線 | Q | 南34線F14 KT34 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南34線KVAR | 11KV南34線 KVAR | FEEDER | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0140 |  |  | 2-8C |  |  | 南35線 | A | 南35線F15 KT35 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南35線A1 | 11KV南35線 R相AMP | FEEDER | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0141 |  |  | 2-8D |  |  | 南35線 | A | 南35線F15 KT35 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南35線A2 | 11KV南35線 S相AMP | FEEDER | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0142 |  |  | 2-8E |  |  | 南35線 | A | 南35線F15 KT35 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南35線A3 | 11KV南35線 T相AMP | FEEDER | [5 empty] | 271 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0143 |  |  | 2-8F |  |  | 南35線 | Q | 南35線F15 KT35 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南35線KVAR | 11KV南35線 KVAR | FEEDER | [5 empty] | 272 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0144 |  |  | 2-90 |  |  | 南36線 | A | 南36線F16 KT36 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南36線A1 | 11KV南36線 R相AMP | FEEDER | [5 empty] | 273 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0145 |  |  | 2-91 |  |  | 南36線 | A | 南36線F16 KT36 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南36線A2 | 11KV南36線 S相AMP | FEEDER | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0146 |  |  | 2-92 |  |  | 南36線 | A | 南36線F16 KT36 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南36線A3 | 11KV南36線 T相AMP | FEEDER | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0147 |  |  | 2-93 |  |  | 南36線 | Q | 南36線F16 KT36 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南36線KVAR | 11KV南36線 KVAR | FEEDER | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0148 |  |  | 2-94 |  |  | 南37線 | A | 南37線F17 KT37 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南37線A1 | 11KV南37線 R相AMP | FEEDER | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0149 |  |  | 2-95 |  |  | 南37線 | A | 南37線F17 KT37 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南37線A2 | 11KV南37線 S相AMP | FEEDER | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0150 |  |  | 2-96 |  |  | 南37線 | A | 南37線F17 KT37 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南37線A3 | 11KV南37線 T相AMP | FEEDER | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0151 |  |  | 2-97 |  |  | 南37線 | Q | 南37線F17 KT37 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南37線KVAR | 11KV南37線 KVAR | FEEDER | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0152 |  |  | 2-98 |  |  | 南38線 | A | 南38線F18 KT38 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南38線A1 | 11KV南38線 R相AMP | FEEDER | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0153 |  |  | 2-99 |  |  | 南38線 | A | 南38線F18 KT38 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南38線A2 | 11KV南38線 S相AMP | FEEDER | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0154 |  |  | 2-9A |  |  | 南38線 | A | 南38線F18 KT38 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南38線A3 | 11KV南38線 T相AMP | FEEDER | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0155 |  |  | 2-9B |  |  | 南38線 | Q | 南38線F18 KT38 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南38線KVAR | 11KV南38線 KVAR | FEEDER | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0156 |  |  | 2-9C |  |  | 南39線 | A | 南39線F19 KT39 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南39線A1 | 11KV南39線 R相AMP | FEEDER | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0157 |  |  | 2-9D |  |  | 南39線 | A | 南39線F19 KT39 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南39線A2 | 11KV南39線 S相AMP | FEEDER | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0158 |  |  | 2-9E |  |  | 南39線 | A | 南39線F19 KT39 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南39線A3 | 11KV南39線 T相AMP | FEEDER | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0159 |  |  | 2-9F |  |  | 南39線 | Q | 南39線F19 KT39 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南39線KVAR | 11KV南39線 KVAR | FEEDER | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0160 |  |  | 2-A0 |  |  | 南40線 | A | 南40線F20 KT40 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南40線A1 | 11KV南40線 R相AMP | FEEDER | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0161 |  |  | 2-A1 |  |  | 南40線 | A | 南40線F20 KT40 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南40線A2 | 11KV南40線 S相AMP | FEEDER | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0162 |  |  | 2-A2 |  |  | 南40線 | A | 南40線F20 KT40 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南40線A3 | 11KV南40線 T相AMP | FEEDER | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0163 |  |  | 2-A3 |  |  | 南40線 | Q | 南40線F20 KT40 Q | KVAR_-10800_10800(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南40線KVAR | 11KV南40線 KVAR | FEEDER | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 10.8 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS |  |  | 1MTR | #1MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0164 |  |  | 2-A4 |  |  | #1MTR | 升/降 | #1MTR TAP位置 | TAP_-6.5_6.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P02 | 安南PS |  |  | 1MTR | #1MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0165 |  |  | 2-A5 |  |  | #1MTR | ℃ | #1MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_OIL | #1MTR 油溫 | MTR | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 1MTR | #1MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0166 |  |  | 2-A6 |  |  | #1MTR | ℃ | #1MTR二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_COIL | #1MTR 線溫 | MTR | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0167 |  |  | 2-A7 |  |  | #2MTR | 升/降 | #2MTR TAP位置 | TAP_-6.5_6.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P02 | 安南PS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0168 |  |  | 2-A8 |  |  | #2MTR | ℃ | #2MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_OIL | #2MTR 油溫 | MTR | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0169 |  |  | 2-A9 |  |  | #2MTR | ℃ | #2MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_COIL | #2MTR 線溫 | MTR | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0170 |  |  | 2-AA |  |  | D1A | 升/降 | D1A TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0171 |  |  | 2-AB |  |  | D1A | ℃ | D1A 油溫 | OIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_OIL | #1DTR 油溫 | MTR | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0172 |  |  | 2-AC |  |  | D1A | ℃ | D1A 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0173 |  |  | 2-AD |  |  | D1B | 升/降 | D1B TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0174 |  |  | 2-AE |  |  | 1510 | KG | 1510 安南小北一路 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1510_OF_R | 安南小北一路 R相 油壓 | OTHER | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0175 |  |  | 2-AF |  |  | D1B | ℃ | D1B 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0176 |  |  | 2-B0 |  |  | D2A | 升/降 | D2A TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0177 |  |  | 2-B1 |  |  | D2A | ℃ | D2A 油溫 | OIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_OIL | #2DTR 油溫 | MTR | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0178 |  |  | 2-B2 |  |  | D2A | ℃ | D2A 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0179 |  |  | 2-B3 |  |  | D2B | 升/降 | D2B TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0180 |  |  | 2-B4 |  |  | 1510 | KG | 1510 安南小北一路 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1510_OF_S | 安南小北一路 S相 油壓 | OTHER | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0181 |  |  | 2-B5 |  |  | D2B | ℃ | D2B 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0182 |  |  | 2-B6 |  |  | 1550 | W | 安南南濱一路 1550 W | MW_-560_560(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1550_MW | 安南南濱一路 MW | LINE161 | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0183 |  |  | 2-B7 |  |  | 1550 | Q | 安南南濱一路 1550 Q | MVAR_-560_560(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1550_MVAR | 安南南濱一路 MVAR | LINE161 | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0184 |  |  | 2-B8 |  |  | 1560 | W | 安南南濱二路 1560 W | MW_-560_560(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1560_MW | 安南南濱二路 MW | LINE161 | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0185 |  |  | 2-B9 |  |  | 1560 | Q | 安南南濱二路 1560 Q | MVAR_-560_560(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1560_MVAR | 安南南濱二路 MVAR | LINE161 | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | OilPreR |  |  | MvMoment | R相油壓 |  | Y |  | AI | [6 empty] | 0186 |  |  | 2-BA |  |  | 1520 | KG | 1520 安南小北二路 R相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1520_OF_R | 安南小北二路 R相 油壓 | OTHER | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | OilPreS |  |  | MvMoment | S相油壓 |  | Y |  | AI | [6 empty] | 0187 |  |  | 2-BB |  |  | 1520 | KG | 1520 安南小北二路 S相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1520_OF_S | 安南小北二路 S相 油壓 | OTHER | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0188 |  |  | 2-BC |  |  | 1520 | KG | 1520 安南小北二路 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1520_OF_T | 安南小北二路 T相 油壓 | OTHER | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0189 |  |  | 2-BD |  |  | DC電源箱 | V | DCP-EV | kV_-150_150(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0190 |  |  | 2-BE |  |  | DC電源箱 | V | DCN-EV | kV_-150_150(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | OilPreT |  |  | MvMoment | T相油壓 |  | Y |  | AI | [6 empty] | 0191 |  |  | 2-BF |  |  | 1510 | KG | 1510 安南小北一路 T相充油電纜油壓 | OilPre_-9.3_9.3(-2000_2000) |  | B2/P02_A1 | [8 empty] | 安南PS.1510_OF_T | 安南小北一路 T相 油壓 | OTHER | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | KG_10 | 8 | 9 | 10 | 20 | 0 | -10 | -11 | -12 | -13 | 1 | 0.01 | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCL4 |  |  | MvMoment | No4 AI參考點 10% |  | Y |  | AI | [6 empty] | 0192 |  |  | 2-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.4AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | RTU | RTU |  | ADCH4 |  |  | MvMoment | No4 AI參考點 90% |  | Y |  | AI | [6 empty] | 0193 |  |  | 2-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No4AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0194 |  |  | 2-C2 |  |  | 350 | A | D3A 350 (R) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0195 |  |  | 2-C3 |  |  | 350 | A | D3A 350 (S) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0196 |  |  | 2-C4 |  |  | 350 | A | D3A 350 (T) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | MW |  | B2 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0197 |  |  | 2-C5 |  |  | 350 | W | D3A 350 (B) W | MW_-72_72(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | MVAR |  | B2 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0198 |  |  | 2-C6 |  |  | 350 | Q | D3A 350 (B) Q | MVAR_-72_72(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0199 |  |  | 2-C7 |  |  | 360 | A | D3B 360 (R) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0200 |  |  | 2-C8 |  |  | 360 | A | D3B 360 (S) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0201 |  |  | 2-C9 |  |  | 360 | A | D3B 360 (T) A | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | LG_725 | 652.5 | 725 | 797.5 | 906.2 | 0.1 | -652.5 | -725 | -797.5 | -906.2 | 1 | 0.01 | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | MW |  | B2 | MvMoment | MW |  | Y |  | AI | [6 empty] | 0202 |  |  | 2-CA |  |  | 360 | W | D3B 360 (B) W | MW_-72_72(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | [5 empty] | 331 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | MVAR |  | B2 | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0203 |  |  | 2-CB |  |  | 360 | Q | D3B 360 (B) Q | MVAR_-72_72(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | [5 empty] | 332 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.144 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 11 | 11kV | 3ABUS | #3ABUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0204 |  |  | 2-CC |  |  | D3A | KV | D3A電壓 BUS PT | kV_-18_18(-2000_2000) | not found | B3/P02_A1 | [8 empty] | 安南PS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | [5 empty] | 333 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P02 | 安南PS | 11 | 11kV | 3BBUS | #3BBUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS |  |  |  |  | 0205 |  |  | 2-CD |  |  | D3B | KV | D3B 電壓 BUS PT | kV_-18_18(-2000_2000) | not found | B3/P02_A1 | [8 empty] | 安南PS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | [5 empty] | 334 |  |  |  |  | AI | [5 empty] | LG_23 | 14.2 | 15.2 | 16.2 | 18 | 0.2 | 12.4 | 11.4 | 10.4 | 0 | 4 | 3 | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | I_R |  | B2 | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0206 |  |  | 2-CE |  |  | 11KV | A | 11KV #3TIE 300 A (R) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.23KV_300_A1 | 23KV 300 R相AMP | TIE | [5 empty] | 335 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | I_S |  | B2 | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0207 |  |  | 2-CF |  |  | 11KV | A | 11KV #3TIE 300 A (S) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.23KV_300_A2 | 23KV 300 S相AMP | TIE | [5 empty] | 336 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | I_T |  | B2 | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0208 |  |  | 2-D0 |  |  | 11KV | A | 11KV #3TIE 300 A (T) | A_-2000_2000(-2000_2000) |  | B3/P02_A1 | [8 empty] | 安南PS.23KV_300_A3 | 23KV 300 T相AMP | TIE | [5 empty] | 337 |  |  |  |  | AI | [5 empty] | C20R0750 | 712.5 | 750 | 825 | 922.5 | 0.45 | -712.5 | -750 | -825 | -922.5 | 1 | 0.01 | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0209 |  |  | 2-D1 |  |  | D3A | 升/降 | D3A TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | [5 empty] | 338 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0210 |  |  | 2-D2 |  |  | D3A | ℃ | D3A 油溫 | OIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_OIL | #3DTR 油溫 | MTR | [5 empty] | 339 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0211 |  |  | 2-D3 |  |  | D3A | ℃ | D3A 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | [5 empty] | 340 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0212 |  |  | 2-D4 |  |  | D3B | 升/降 | D3B TAP位置 | TAP_-8.5_8.5(0_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | [5 empty] | 341 |  |  |  |  | AI | [5 empty] | TAP8_8 | 7 | 8 | 9 | 10 | 0 | -7 | -8 | -9 | -10 | 0.1 |  | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0214 |  |  | 2-D6 |  |  | D3B | ℃ | D3B 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | [5 empty] | 342 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0215 |  |  | 2-D7 |  |  | 南71線 | A | 南71線F1 KT71 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南71線A1 | 23KV南71線 R相AMP | FEEDER | [5 empty] | 343 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0216 |  |  | 2-D8 |  |  | 南71線 | A | 南71線F1 KT71 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南71線A2 | 23KV南71線 S相AMP | FEEDER | [5 empty] | 344 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0217 |  |  | 2-D9 |  |  | 南71線 | A | 南71線F1 KT71 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南71線A3 | 23KV南71線 T相AMP | FEEDER | [5 empty] | 345 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0218 |  |  | 2-DA |  |  | 南71線 | Q | 南71線F1 KT71 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南71線KVAR | 23KV南71線 KVAR | FEEDER | [5 empty] | 346 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0219 |  |  | 2-DB |  |  | 南72線 | A | 南72線F2 KT72 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南72線A1 | 23KV南72線 R相AMP | FEEDER | [5 empty] | 347 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0220 |  |  | 2-DC |  |  | 南72線 | A | 南72線F2 KT72 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南72線A2 | 23KV南72線 S相AMP | FEEDER | [5 empty] | 348 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0221 |  |  | 2-DD |  |  | 南72線 | A | 南72線F2 KT72 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南72線A3 | 23KV南72線 T相AMP | FEEDER | [5 empty] | 349 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0222 |  |  | 2-DE |  |  | 南72線 | Q | 南72線F2 KT72 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南72線KVAR | 23KV南72線 KVAR | FEEDER | [5 empty] | 350 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0223 |  |  | 2-DF |  |  | 南73線 | A | 南73線F3 KT73 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南73線A1 | 23KV南73線 R相AMP | FEEDER | [5 empty] | 351 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0224 |  |  | 2-E0 |  |  | 南73線 | A | 南73線F3 KT73 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南73線A2 | 23KV南73線 S相AMP | FEEDER | [5 empty] | 352 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0225 |  |  | 2-E1 |  |  | 南73線 | A | 南73線F3 KT73 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南73線A3 | 23KV南73線 T相AMP | FEEDER | [5 empty] | 353 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0226 |  |  | 2-E2 |  |  | 南73線 | Q | 南73線F3 K73 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南73線KVAR | 23KV南73線 KVAR | FEEDER | [5 empty] | 354 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0227 |  |  | 2-E3 |  |  | 南74線 | A | 南74線F4 KT74 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南74線A1 | 23KV南74線 R相AMP | FEEDER | [5 empty] | 355 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0228 |  |  | 2-E4 |  |  | 南74線 | A | 南74線F4 KT74 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南74線A2 | 23KV南74線 S相AMP | FEEDER | [5 empty] | 356 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0229 |  |  | 2-E5 |  |  | 南74線 | A | 南74線F4 KT74 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南74線A3 | 23KV南74線 T相AMP | FEEDER | [5 empty] | 357 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0230 |  |  | 2-E6 |  |  | 南74線 | Q | 南74線F4 KT74 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南74線KVAR | 23KV南74線 KVAR | FEEDER | [5 empty] | 358 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0231 |  |  | 2-E7 |  |  | F5 | A | F5 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南75線A1 | 23KV南75線 R相AMP | FEEDER | [5 empty] | 359 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0232 |  |  | 2-E8 |  |  | F5 | A | F5 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南75線A2 | 23KV南75線 S相AMP | FEEDER | [5 empty] | 360 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0233 |  |  | 2-E9 |  |  | F5 | A | F5 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南75線A3 | 23KV南75線 T相AMP | FEEDER | [5 empty] | 361 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0234 |  |  | 2-EA |  |  | F5 | Q | F5 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南75線KVAR | 23KV南75線 KVAR | FEEDER | [5 empty] | 362 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0235 |  |  | 2-EB |  |  | 南76線 | A | 南76線F6 KT76 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南76線A1 | 23KV南76線 R相AMP | FEEDER | [5 empty] | 363 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0236 |  |  | 2-EC |  |  | 南76線 | A | 南76線F6 KT76 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南76線A2 | 23KV南76線 S相AMP | FEEDER | [5 empty] | 364 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0237 |  |  | 2-ED |  |  | 南76線 | A | 南76線F6 KT76 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南76線A3 | 23KV南76線 T相AMP | FEEDER | [5 empty] | 365 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0238 |  |  | 2-EE |  |  | 南76線 | Q | 南76線F6 KT76 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南76線KVAR | 23KV南76線 KVAR | FEEDER | [5 empty] | 366 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0239 |  |  | 2-EF |  |  | 南77線 | A | 南77線F7 KT77 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南77線A1 | 23KV南77線 R相AMP | FEEDER | [5 empty] | 367 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0240 |  |  | 2-F0 |  |  | 南77線 | A | 南77線F7 KT77 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南77線A2 | 23KV南77線 S相AMP | FEEDER | [5 empty] | 368 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0241 |  |  | 2-F1 |  |  | 南77線 | A | 南77線F7 KT77 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南77線A3 | 23KV南77線 T相AMP | FEEDER | [5 empty] | 369 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0242 |  |  | 2-F2 |  |  | 南77線 | Q | 南77線F7 KT77 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南77線KVAR | 23KV南77線 KVAR | FEEDER | [5 empty] | 370 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0243 |  |  | 2-F3 |  |  | 南78線 | A | 南78線F8 KT78 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南78線A1 | 23KV南78線 R相AMP | FEEDER | [5 empty] | 371 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0244 |  |  | 2-F4 |  |  | 南78線 | A | 南78線F8 KT78 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南78線A2 | 23KV南78線 S相AMP | FEEDER | [5 empty] | 372 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0245 |  |  | 2-F5 |  |  | 南78線 | A | 南78線F8 KT78 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南78線A3 | 23KV南78線 T相AMP | FEEDER | [5 empty] | 373 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0246 |  |  | 2-F6 |  |  | 南78線 | Q | 南78線F8 KT78 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南78線KVAR | 23KV南78線 KVAR | FEEDER | [5 empty] | 374 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI | [6 empty] | 0247 |  |  | 2-F7 |  |  | 南79線 | A | 南79線F9 KT79 A (R) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南79線A1 | 23KV南79線 R相AMP | FEEDER | [5 empty] | 375 |  |  |  |  | AI | [5 empty] | C06R480R | 432 | 433 | 480 | 600 | 1.25 | 8 | -200 | -201 | -202 | 1 | 0.01 | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI | [6 empty] | 0248 |  |  | 2-F8 |  |  | 南79線 | A | 南79線F9 KT79 A (S) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南79線A2 | 23KV南79線 S相AMP | FEEDER | [5 empty] | 376 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI | [6 empty] | 0249 |  |  | 2-F9 |  |  | 南79線 | A | 南79線F9 KT79 A (T) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南79線A3 | 23KV南79線 T相AMP | FEEDER | [5 empty] | 377 |  |  |  |  | AI | [5 empty] | C06R0480 | 456 | 480 | 528 | 590.4 | 1.25 | -456 | -480 | -528 | -590.4 | 1 | 0.01 | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0250 |  |  | 2-FA |  |  | 南79線 | Q | 南79線F9 KT79 Q | KVAR_-21600_21600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南79線KVAR | 23KV南79線 KVAR | FEEDER | [5 empty] | 378 |  |  |  |  | AI | [5 empty] | LG_KVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 21.6 | 0.01 | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0258 |  |  | 3-82 |  |  | 南21線F1 KT21 A (N) | A | 南21線F1 KT21 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南21線A0 | 11KV南21線 N相AMP | FEEDER | [5 empty] | 379 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0259 |  |  | 3-83 |  |  | 南22線F2 KT22 A (N) | A | 南22線F2 KT22 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南22線A0 | 11KV南22線 N相AMP | FEEDER | [5 empty] | 380 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0260 |  |  | 3-84 |  |  | 南23線F3 KT23 A (N) | A | 南23線F3 KT23 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南23線A0 | 11KV南23線 N相AMP | FEEDER | [5 empty] | 381 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0261 |  |  | 3-85 |  |  | 南24線F4 KT24 A (N) | A | 南24線F4 KT24 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南24線A0 | 11KV南24線 N相AMP | FEEDER | [5 empty] | 382 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0262 |  |  | 3-86 |  |  | 南25線F5 KT25 A (N) | A | 南25線F5 KT25 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南25線A0 | 11KV南25線 N相AMP | FEEDER | [5 empty] | 383 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0263 |  |  | 3-87 |  |  | 南26線F6 KT26 A (N) | A | 南26線F6 KT26 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南26線A0 | 11KV南26線 N相AMP | FEEDER | [5 empty] | 384 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0264 |  |  | 3-88 |  |  | 南27線F7 KT27 A (N) | A | 南27線F7 KT27 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南27線A0 | 11KV南27線 N相AMP | FEEDER | [5 empty] | 385 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0265 |  |  | 3-89 |  |  | 南28線F8 KT28 A (N) | A | 南28線F8 KT28 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南28線A0 | 11KV南28線 N相AMP | FEEDER | [5 empty] | 386 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0266 |  |  | 3-8A |  |  | 南29線F9 KT29 A (N) | A | 南29線F9 KT29 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南29線A0 | 11KV南29線 N相AMP | FEEDER | [5 empty] | 387 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0267 |  |  | 3-8B |  |  | 南30線F10 KT30 A (N) | A | 南30線F10 KT30 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南30線A0 | 11KV南30線 N相AMP | FEEDER | [5 empty] | 388 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0268 |  |  | 3-8C |  |  | 南31線F11 KT31 A (N) | A | 南31線F11 KT31 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南31線A0 | 11KV南31線 N相AMP | FEEDER | [5 empty] | 389 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0269 |  |  | 3-8D |  |  | 南32線F12 KT32 A (N) | A | 南32線F12 KT32 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南32線A0 | 11KV南32線 N相AMP | FEEDER | [5 empty] | 390 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0270 |  |  | 3-8E |  |  | 南33線F13 KT33 A (N) | A | 南33線F13 KT33 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南33線A0 | 11KV南33線 N相AMP | FEEDER | [5 empty] | 391 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0271 |  |  | 3-8F |  |  | 南34線F14 KT34 A (N) | A | 南34線F14 KT34 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南34線A0 | 11KV南34線 N相AMP | FEEDER | [5 empty] | 392 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0272 |  |  | 3-90 |  |  | 南35線F15 KT35 A (N) | A | 南35線F15 KT35 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南35線A0 | 11KV南35線 N相AMP | FEEDER | [5 empty] | 393 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0273 |  |  | 3-91 |  |  | 南36線F16 KT36 A (N) | A | 南36線F16 KT36 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南36線A0 | 11KV南36線 N相AMP | FEEDER | [5 empty] | 394 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0274 |  |  | 3-92 |  |  | 南37線F17 KT37 A (N) | A | 南37線F17 KT37 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南37線A0 | 11KV南37線 N相AMP | FEEDER | [5 empty] | 395 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0275 |  |  | 3-93 |  |  | 南38線F18 KT38 A (N) | A | 南38線F18 KT38 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南38線A0 | 11KV南38線 N相AMP | FEEDER | [5 empty] | 396 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0276 |  |  | 3-94 |  |  | 南39線F19 KT39 A (N) | A | 南39線F19 KT39 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南39線A0 | 11KV南39線 N相AMP | FEEDER | [5 empty] | 397 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0277 |  |  | 3-95 |  |  | 南40線F20 KT40 A (N) | A | 南40線F20 KT40 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南40線A0 | 11KV南40線 N相AMP | FEEDER | [5 empty] | 398 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0278 |  |  | 3-96 |  |  | 南71線F1 KT71 A (N) | A | 南71線F1 KT71 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南71線A0 | 23KV南71線 N相AMP | FEEDER | [5 empty] | 399 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0279 |  |  | 3-97 |  |  | 南72線F2 KT72 A (N) | A | 南72線F2 KT72 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南72線A0 | 23KV南72線 N相AMP | FEEDER | [5 empty] | 400 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0280 |  |  | 3-98 |  |  | 南73線F3 KT73 A (N) | A | 南73線F3 KT73 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南73線A0 | 23KV南73線 N相AMP | FEEDER | [5 empty] | 401 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0281 |  |  | 3-99 |  |  | 南74線F4 KT74 A (N) | A | 南74線F4 KT74 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南74線A0 | 23KV南74線 N相AMP | FEEDER | [5 empty] | 402 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0282 |  |  | 3-9A |  |  | 南75線F5 KT75 A (N) | A | 南75線F5 KT75 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南75線A0 | 23KV南75線 N相AMP | FEEDER | [5 empty] | 403 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0283 |  |  | 3-9B |  |  | 南76線F6 KT76 A (N) | A | 南76線F6 KT76 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南76線A0 | 23KV南76線 N相AMP | FEEDER | [5 empty] | 404 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0284 |  |  | 3-9C |  |  | 南77線F7 KT77 A (N) | A | 南77線F7 KT77 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南77線A0 | 23KV南77線 N相AMP | FEEDER | [5 empty] | 405 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0285 |  |  | 3-9D |  |  | 南78線F8 KT78 A (N) | A | 南78線F8 KT78 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南78線A0 | 23KV南78線 N相AMP | FEEDER | [5 empty] | 406 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | I_N |  |  | MvMoment | N相AMP |  | Y |  | AI | [6 empty] | 0286 |  |  | 3-9E |  |  | 南79線F9 KT79 A (N) |  | 南79線F9 KT79 A (N) | A_-600_600(-2000_2000) |  | B2/P02_D1 | [8 empty] | 安南PS.南79線A0 | 23KV南79線 N相AMP | FEEDER | [5 empty] | 407 |  |  |  |  | AI | [5 empty] | LGA0_100 | 80 | 90 | 95 | 600 | 0.5 | -200 | -201 | -202 | -203 | 1 | 0.01 | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D261/T1 |  | 0136 |  |  | 1-11-00 |  |  | 1510 | ON/OFF | 安南小北一路1510 CB |  | aaga | B2/P02_A1 | [8 empty] | 安南PS.1510_CB | 1510(安南小北一路) CB | LINE161 | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0137 |  |  | 1-11-01 |  |  | 1510 | 87A | 安南小北一路1510 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1510_87A | 安南小北一路(1510) 87RY | LINE161 | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0139 |  |  | 1-11-03 |  |  | 1510 | GDA | 安南小北一路1510 GDA接地 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1510_GDA | 安南小北一路(1510) 接地RY | LINE161 | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D262/T1 |  | 0140 |  |  | 1-11-04 |  |  | 1520 | ON/OFF | 安南小北二路1520 CB |  | aaha | B2/P02_A1 | [8 empty] | 安南PS.1520_CB | 1520(安南小北二路) CB | LINE161 | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0141 |  |  | 1-11-05 |  |  | 1520 | 87A | 安南小北二路1520 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_87A | 安南小北二路(1520) 87RY | LINE161 | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0142 |  |  | 1-11-06 |  |  | 1520 | PHA | 安南小北二路1520 PHA相間 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_PHA | 安南小北二路(1520) 相間RY | LINE161 | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0143 |  |  | 1-11-07 |  |  | 1520 | GDA | 安南小北二路1520 GDA接地 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_GDA | 安南小北二路(1520) 接地RY | LINE161 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D27/T1 |  | 0128 |  |  | 1-10-00 |  |  | 1530 | ON/OFF | 安南鹽行線1530 CB |  | aada | B2/P02_A1 | [8 empty] | 安南PS.1530_CB | 1530(安南鹽行線) CB | LINE161 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 1530 | 87A | 安南鹽行線1530 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_87A | 安南鹽行線(1530) 87RY | LINE161 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | 1530 | PHA | 安南鹽行線1530 PHA相間 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_PHA | 安南鹽行線(1530) 相間RY | LINE161 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0131 |  |  | 1-10-03 |  |  | 1530 | GDA | 安南鹽行線1530 GDA接地 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_GDA | 安南鹽行線(1530) 接地RY | LINE161 | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02TN15R/T2 |  | 0132 |  |  | 1-10-04 |  |  | 1710 | ON/OFF | 山上安南豐華紅線1710 CB |  | aaea | B2/P02_A1 | [8 empty] | 安南PS.1710_CB | 1710(山上豐華紅線) CB | LINE161 | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0133 |  |  | 1-10-05 |  |  | 1710 | 87A 1 | 山上安南豐華紅線1710 #1 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_87A1 | 山上豐華紅線(1710) #1 87RY | LINE161 | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0134 |  |  | 1-10-06 |  |  | 1710 | PHA | 山上安南豐華紅線1710 PHA RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_PHA | 山上豐華紅線(1710) 相間RY | LINE161 | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0135 |  |  | 1-10-07 |  |  | 1710 | GDA | 山上安南豐華紅線1710 GDA RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_GDA | 山上豐華紅線(1710) 接地RY | LINE161 | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02TN03/T2 |  | 0144 |  |  | 1-12-00 |  |  | 1720 | ON/OFF | 道爺安南新化線1720 CB |  | aaia | B2/P02_A1 | [8 empty] | 安南PS.1720_CB | 1720(道爺安南新化線) CB | LINE161 | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0145 |  |  | 1-12-01 |  |  | 1720 | 87A | 道爺安南新化線1720 87A |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_87A | 道爺安南新化線(1720) 87RY | LINE161 | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0146 |  |  | 1-12-02 |  |  | 1720 | PHA | 道爺安南新化線1720 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_PHA | 道爺安南新化線(1720) 相間RY | LINE161 | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0147 |  |  | 1-12-03 |  |  | 1720 | GDA | 道爺安南新化線1720 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_GDA | 道爺安南新化線(1720) 接地RY | LINE161 | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02D20/T1 |  | 0148 |  |  | 1-12-04 |  |  | 1740 | ON/OFF | 安南和順線1740 CB |  | aaja | B2/P02_A1 | [8 empty] | 安南PS.1740_CB | 1740(安南和順線) CB | LINE161 | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0149 |  |  | 1-12-05 |  |  | 1740 | 87A | 安南和順線1740 87A |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_87A | 安南和順線(1740) 87RY | LINE161 | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0150 |  |  | 1-12-06 |  |  | 1740 | PHA | 安南和順線1740 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_PHA | 安南和順線(1740) 相間RY | LINE161 | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0151 |  |  | 1-12-07 |  |  | 1740 | GDA | 安南和順線1740 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_GDA | 安南和順線(1740) 接地RY | LINE161 | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0152 |  |  | 1-13-00 |  |  | 1710 | 87A 2 | 山上安南豐華紅線1710 #2 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_87A2 | 山上豐華紅線(1710) #2 87RY | LINE161 | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0156 |  |  | 1-13-04 |  |  | #1MTR | 87A | #1MTR 87 RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_87A | #1MTR 87RY | MTR | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0157 |  |  | 1-13-05 |  |  | #1MTR | PHA | #1MTR .PHA |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_PHA | #1MTR PHA | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0159 |  |  | 1-13-07 |  |  | #1MTR | 96PA | #1MTR 機械保護動作(96PA) |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0160 |  |  | 1-14-00 |  |  | 1650 | ON/OFF | #1MTR一次1650 CB |  | aacb | B2/P02_A1 | [8 empty] | 安南PS.1650_CB | 1650(#1MTR) CB | MTR | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1MTR |  | 0161 |  |  | 1-14-01 |  |  | 750 | ON/OFF | #1MTR二次750 CB |  | aaea | B2/P02_A1 | [8 empty] | 安南PS.750_CB | 750(#1MTR) CB | MTR | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0162 |  |  | 1-14-02 |  |  | #1MTR | 51ZA | #1MTR 51Z RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0163 |  |  | 1-14-03 |  |  | #2MTR | 87A | #2MTR 87 RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_87A | #2MTR 87RY | MTR | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0164 |  |  | 1-14-04 |  |  | #2MTR | PHA | #2MTR .PHA |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_PHA | #2MTR PHA | OTHER | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0166 |  |  | 1-14-06 |  |  | #2MTR | 96PA | #2MTR 機械保護動作(96PA) |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0167 |  |  | 1-14-07 |  |  | #2MTR | ON/OFF | #2MTR一次1660 CB |  | aafb | B2/P02_A1 | [8 empty] | 安南PS.1660_CB | 1660(#2MTR) CB | MTR | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR |  | 0168 |  |  | 1-15-00 |  |  | #2MTR | ON/OFF | #2MTR二次760 CB |  | aaja | B2/P02_A1 | [8 empty] | 安南PS.760_CB | 760(#2MTR) CB | MTR | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | #2MTR | 51ZA | #2MTR 51Z RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | #1DTR | 87A | #1DTR 87 RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_87A | #1DTR 87RY | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | #1DTR | PHA | #1DTR.PHA |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_PHA | #1DTR PHA | OTHER | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | #1DTR | 96PA | #1DTR 機械保護動作(96PA) |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/1DTR |  | 0173 |  |  | 1-15-05 |  |  | #1DTR | ON/OFF | #1DTR一次1750 CB |  | aakb | ELEM/P02_A1 | [8 empty] | 安南PS.1750_CB | 1750(#1DTR) CB | MTR | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0175 |  |  | 1-15-07 |  |  | #1DTR | 51ZA | #1DTR 51Z RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_51ZA | #1DTR 51Z RY | MTR | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0176 |  |  | 1-16-00 |  |  | #2DTR | 87A | #2DTR 87 RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_87A | #2DTR 87RY | MTR | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0177 |  |  | 1-16-01 |  |  | #2DTR | PHA | #2DTR.PHA |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_PHA | #2DTR PHA | OTHER | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0178 |  |  | 1-16-02 |  |  | #2DTR | 96PA | #2DTR 機械保護動作(96PA) |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2DTR |  | 0179 |  |  | 1-16-03 |  |  | #2DTR | ON/OFF | #2DTR一次1760 CB |  | aanb | ELEM/P02_A1 | [8 empty] | 安南PS.1760_CB | 1760(#2DTR) CB | MTR | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0181 |  |  | 1-16-05 |  |  | #2DTR | 51ZA | #2DTR 51Z RY |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_51ZA | #2DTR 51Z RY | MTR | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0182 |  |  | 1-16-06 |  |  | 161KV | ON/OFF | 161KV TIE 1500 CB |  | aabz | B2/P02_A1 | [8 empty] | 安南PS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0183 |  |  | 1-16-07 |  |  | 161KV | 51A | 161KV TIE 1500 50 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0184 |  |  | 1-17-00 |  |  | 69KV | ON/OFF | 69KV TIE 600 CB |  | aabz | B2/P02_A1 | [8 empty] | 安南PS.600_CB | 600(TIE) CB | TIE | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0185 |  |  | 1-17-01 |  |  | 600 | #1 PHA | 600 TIE #1 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  |  | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0186 |  |  | 1-17-02 |  |  | 600 | #1 GDA | 600 TIE #1 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0187 |  |  | 1-17-03 |  |  | 161KV#1BUS | 87B1A | 161KVBUS 87B1A |  |  | B2/P02_A1 | [8 empty] | 安南PS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0188 |  |  | 1-17-04 |  |  | 161KV#2BUS | 87B2A | 161KVBUS 87B2A |  |  | B2/P02_A1 | [8 empty] | 安南PS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0190 |  |  | 1-17-06 |  |  | 69KV#1BUS | 87B1A | 69KVBUS 87B1A |  |  | B2/P02_A1 | [8 empty] | 安南PS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0191 |  |  | 1-17-07 |  |  | 69KV#2BUS | 87B2A | 69KVBUS 87B2A |  |  | B2/P02_A1 | [8 empty] | 安南PS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0193 |  |  | 1-18-01 |  |  | 79 RELAY | RCA | 79 RELAY警報RCA |  |  | B3/P02_A1 | [8 empty] | 安南PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0194 |  |  | 1-18-02 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/P02_A1 | [8 empty] | 安南PS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0195 |  |  | 1-18-03 |  |  | 1550 | PHA | 安南南濱一路 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_PHA | 安南南濱一路(1550) 相間RY | LINE161 | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0196 |  |  | 1-18-04 |  |  | 1550 | GDA | 安南南濱一路 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_GDA | 安南南濱一路(1550) 接地RY | LINE161 | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0197 |  |  | 1-18-05 |  |  | 1550 | 87A | 安南南濱一路 87A |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_87A | 安南南濱一路(1550) 87RY | LINE161 | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0198 |  |  | 1-18-06 |  |  | 1560 | PHA | 安南南濱二路 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_PHA | 安南南濱二路(1560) 相間RY | LINE161 | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0199 |  |  | 1-18-07 |  |  | 1560 | GDA | 安南南濱二路 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_GDA | 安南南濱二路(1560) 接地RY | LINE161 | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0200 |  |  | 1-19-00 |  |  | 1560 | 87A | 安南南濱二路 87A |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_87A | 安南南濱二路(1560) 87RY | LINE161 | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0201 |  |  | 1-19-01 |  |  | OSCA | A/N | 69KV示波器啟動警報OSCA |  |  | B3/P02_A1 | [8 empty] | 安南PS.69KV_OSCA | 69KV示波器啟動 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0202 |  |  | 1-19-02 |  |  | 600 | #2PHA | 600 TIE #2 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  |  | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0203 |  |  | 1-19-03 |  |  | 600 | #2GDA | 600 TIE #2 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0204 |  |  | 1-19-04 |  |  | RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/P02_A1 | [16 empty] | 474 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02S72/T1 |  | 0000 |  |  | 1-00-00 |  |  | 620 | ON/OFF | 安南運河線620 CB |  | aagb | B2/P02_A1 | [8 empty] | 安南PS.620_CB | 620(安南運河線) CB | LINE69 | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 620 | 87A | 安南運河線620 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.620_87A | 安南運河線(620) 87RY | LINE69 | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 620 | PHA | 安南運河線620 PHA |  |  | B2/P02_A1 | [8 empty] | 安南PS.620_PHA | 安南運河線(620) 相間RY | LINE69 | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0003 |  |  | 1-00-03 |  |  | 620 | GDA | 安南運河線620 GDA |  |  | B2/P02_A1 | [8 empty] | 安南PS.620_GDA | 安南運河線(620) 接地RY | LINE69 | [5 empty] | 478 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02S73W/T1 |  | 0004 |  |  | 1-00-04 |  |  | 630 | ON/OFF | 安南安順白線630 CB |  | aacb | B2/P02_A1 | [8 empty] | 安南PS.630_CB | 630(安順白線) CB | LINE69 | [5 empty] | 479 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 630 | 51A | 安南安順白線630 51 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.630_PHA | 安順白線(630) 相間RY | LINE69 | [5 empty] | 480 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0006 |  |  | 1-00-06 |  |  | 630 | 87A | 安南安順白線630 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.630_87A | 安順白線(630) 87RY | LINE69 | [5 empty] | 481 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 630 | 51NA | 安南安順白線630 51N RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.630_GDA | 安順白線(630) 接地RY | LINE69 | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P02S73R/T1 |  | 0008 |  |  | 1-01-00 |  |  | 640 | ON/OFF | 安南安順紅線640 CB |  | aadb | B2/P02_A1 | [8 empty] | 安南PS.640_CB | 640(安順紅線) CB | LINE69 | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0009 |  |  | 1-01-01 |  |  | 640 | 87A | 安南安順紅線640 87 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.640_87A | 安順紅線(640) 87RY | LINE69 | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 640 | 51A | 安南安順紅線640 51 RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.640_PHA | 安順紅線(640) 相間RY | LINE69 | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 640 | 51NA | 安南安順紅線640 51N RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.640_GDA | 安順紅線(640) 接地RY | LINE69 | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbC | B/1Bus | B/2Bus | C/3SC |  | 0020 |  |  | 1-02-04 |  |  | 830 | ON/OFF | 69KV#3SC 830 CB |  | aalb | B2/P02_A1 | [8 empty] | 安南PS.830_CB | 830(69KV #3SC) CB | SC | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 830 | SCA | 69KV #3SC 830 SCA RY |  |  | B2/P02_A1 | [8 empty] | 安南PS.830_SCA | 69KV #3SC 51,51N RY | SC | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 830 | UVA | 69KV #3SC 830 UVARY |  |  | B2/P02_A1 | [8 empty] | 安南PS.830_OUVA | 69KV #3SC 27,59RY | SC | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KT21/T1 |  |  | 0024 |  |  | 1-03-00 |  |  | 南21線 | ON/OFF | 南21線F1KT21 CB |  | aadb | B2/P02_D1 | [8 empty] | 安南PS.KT21_CB | KT21(11KV南21線) CB | FEEDER | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 南21線 | 51A | 南21線F1 KT21 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT21_PHA | 11KV南21線(KT21) 相間RY | FEEDER | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 南21線 | 51NA | 南21線F1 KT21 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT21_GDA | 11KV南21線(KT21) 接地RY | FEEDER | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KT22/T1 |  |  | 0027 |  |  | 1-03-03 |  |  | 南22線 | ON/OFF | 南22線F2 KT22 CB |  | aaeb | B2/P02_D1 | [8 empty] | 安南PS.KT22_CB | KT22(11KV南22線) CB | FEEDER | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 南22線 | 51A | 南22線F2 KT22 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT22_PHA | 11KV南22線(KT22) 相間RY | FEEDER | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 南22線 | 51NA | 南22線F2 KT22 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT22_GDA | 11KV南22線(KT22) 接地RY | FEEDER | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KT23/T1 |  |  | 0030 |  |  | 1-03-06 |  |  | 南23線 | ON/OFF | 南23線F3 KT23 CB |  | aafb | B2/P02_D1 | [8 empty] | 安南PS.KT23_CB | KT23(11KV南23線) CB | FEEDER | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 南23線 | 51A | 南23線F3 KT23 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT23_PHA | 11KV南23線(KT23) 相間RY | FEEDER | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 南23線 | 51NA | 南23線F3 KT23 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT23_GDA | 11KV南23線(KT23) 接地RY | FEEDER | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KT24/T1 |  |  | 0033 |  |  | 1-04-01 |  |  | 南24線 | ON/OFF | 南24線F4 KT24 CB |  | aagb | B2/P02_D1 | [8 empty] | 安南PS.KT24_CB | KT24(11KV南24線) CB | FEEDER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 南24線 | 51A | 南24線F4 KT24 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT24_PHA | 11KV南24線(KT24) 相間RY | FEEDER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0035 |  |  | 1-04-03 |  |  | 南24線 | 51NA | 南24線F4 KT24 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT24_GDA | 11KV南24線(KT24) 接地RY | FEEDER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KT25/T1 |  |  | 0036 |  |  | 1-04-04 |  |  | 南25線 | ON/OFF | 南25線F5 KT25 CB |  | aahb | B2/P02_D1 | [8 empty] | 安南PS.KT25_CB | KT25(11KV南25線) CB | FEEDER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 南25線 | 51A | 南25線F5 KT25 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT25_PHA | 11KV南25線(KT25) 相間RY | FEEDER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0038 |  |  | 1-04-06 |  |  | 南25線 | 51NA | 南25線F5 KT25 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT25_GDA | 11KV南25線(KT25) 接地RY | FEEDER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | L/KT26/T1 |  |  | 0039 |  |  | 1-04-07 |  |  | 南26線 | ON/OFF | 南26線F6 KT26 CB |  | aaib | B2/P02_D1 | [8 empty] | 安南PS.KT26_CB | KT26(11KV南26線) CB | FEEDER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0040 |  |  | 1-05-00 |  |  | 南26線 | 51A | 南26線F6 KT26 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT26_PHA | 11KV南26線(KT26) 相間RY | FEEDER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 南26線 | 51NA | 南26線F6 KT26 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT26_GDA | 11KV南26線(KT26) 接地RY | FEEDER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KT27/T1 |  |  | 0042 |  |  | 1-05-02 |  |  | 南27線 | ON/OFF | 南27線F7 KT27 CB |  | abab | B2/P02_D1 | [8 empty] | 安南PS.KT27_CB | KT27(11KV南27線) CB | FEEDER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 南27線 | 51A | 南27線F7 KT27 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT27_PHA | 11KV南27線(KT27) 相間RY | FEEDER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0044 |  |  | 1-05-04 |  |  | 南27線 | 51NA | 南27線F7 KT27 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT27_GDA | 11KV南27線(KT27) 接地RY | FEEDER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KT28/T1 |  |  | 0045 |  |  | 1-05-05 |  |  | 南28線 | ON/OFF | 南28線F8 KT28 CB |  | abbb | B2/P02_D1 | [8 empty] | 安南PS.KT28_CB | KT28(11KV南28線) CB | FEEDER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | 南28線 | 51A | 南28線F8 KT28 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT28_PHA | 11KV南28線(KT28) 相間RY | FEEDER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | 南28線 | 51NA | 南28線F8 KT28 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT28_GDA | 11KV南28線(KT28) 接地RY | FEEDER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KT29/T1 |  |  | 0048 |  |  | 1-06-00 |  |  | 南29線 | ON/OFF | 南29線F9 KT29CB |  | abcb | B2/P02_D1 | [8 empty] | 安南PS.KT29_CB | KT29(11KV南29線) CB | FEEDER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 南29線 | 51A | 南29線F9 KT29 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT29_PHA | 11KV南29線(KT29) 相間RY | FEEDER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | 南29線 | 51NA | 南29線F9 KT29 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT29_GDA | 11KV南29線(KT29) 接地RY | FEEDER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | L/KT30/T1 |  |  | 0051 |  |  | 1-06-03 |  |  | 南30線 | ON/OFF | 南30線 F10 KT30 CB |  | abdb | B2/P02_D1 | [8 empty] | 安南PS.KT30_CB | KT30(11KV南30線) CB | FEEDER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | 南30線 | 51A | 南30線 F10 KT30 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT30_PHA | 11KV南30線(KT30) 相間RY | FEEDER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | 南30線 | 51NA | 南30線 F10 KT30 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT30_GDA | 11KV南30線(KT30) 接地RY | FEEDER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KT31/T1 |  |  | 0054 |  |  | 1-06-06 |  |  | 南31線 | ON/OFF | 南31線F11 KT31 CB |  | badb | B2/P02_D1 | [8 empty] | 安南PS.KT31_CB | KT31(11KV南31線) CB | FEEDER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | 南31線 | 51A | 南31線F11 KT31 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT31_PHA | 11KV南31線(KT31) 相間RY | FEEDER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0056 |  |  | 1-07-00 |  |  | 南31線 | 51NA | 南31線F11 KT31 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT31_GDA | 11KV南31線(KT31) 接地RY | FEEDER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KT32/T1 |  |  | 0057 |  |  | 1-07-01 |  |  | 南32線 | ON/OFF | 南32線F12 KT32 CB |  | baeb | B2/P02_D1 | [8 empty] | 安南PS.KT32_CB | KT32(11KV南32線) CB | FEEDER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | 南32線 | 51A | 南32線F12 KT32 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT32_PHA | 11KV南32線(KT32) 相間RY | FEEDER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | 南32線 | 51NA | 南32線F12 KT32 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT32_GDA | 11KV南32線(KT32) 接地RY | FEEDER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KT33/T1 |  |  | 0060 |  |  | 1-07-04 |  |  | 南33線 | ON/OFF | 南33線F13 KT33 CB |  | bafb | B2/P02_D1 | [8 empty] | 安南PS.KT33_CB | KT33(11KV南33線) CB | FEEDER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | 南33線 | 51A | 南33線F13 KT33 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT33_PHA | 11KV南33線(KT33) 相間RY | FEEDER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | 南33線 | 51NA | 南33線F13 KT33 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT33_GDA | 11KV南33線(KT33) 接地RY | FEEDER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | L/KT34/T1 |  |  | 0063 |  |  | 1-07-07 |  |  | 南34線 | ON/OFF | 南34線F14 KT34 CB |  | bagb | B2/P02_D1 | [8 empty] | 安南PS.KT34_CB | KT34(11KV南34線) CB | FEEDER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0064 |  |  | 1-08-00 |  |  | 南34線 | 51A | 南34線F14 KT34 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT34_PHA | 11KV南34線(KT34) 相間RY | FEEDER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | 南34線 | 51NA | 南34線F14 KT34 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT34_GDA | 11KV南34線(KT34) 接地RY | FEEDER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KT35/T1 |  |  | 0066 |  |  | 1-08-02 |  |  | 南35線 | ON/OFF | 南35線F15 KT35 CB |  | bbbb | B2/P02_D1 | [8 empty] | 安南PS.KT35_CB | KT35(11KV南35線) CB | FEEDER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | 南35線 | 51A | 南35線F15 KT35 51RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT35_PHA | 11KV南35線(KT35) 相間RY | FEEDER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | 南35線 | 51NA | 南35線F15 KT35 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT35_GDA | 11KV南35線(KT35) 接地RY | FEEDER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KT36/T1 |  |  | 0069 |  |  | 1-08-05 |  |  | 南36線 | ON/OFF | 南36線F16 KT36 CB |  | bbcb | B2/P02_D1 | [8 empty] | 安南PS.KT36_CB | KT36(11KV南36線) CB | FEEDER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0070 |  |  | 1-08-06 |  |  | 南36線 | 51A | 南36線F16 KT36 51RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT36_PHA | 11KV南36線(KT36) 相間RY | FEEDER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0071 |  |  | 1-08-07 |  |  | 南36線 | 51NA | 南36線F16 KT36 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT36_GDA | 11KV南36線(KT36) 接地RY | FEEDER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KT37/T1 |  |  | 0072 |  |  | 1-09-00 |  |  | 南37線 | ON/OFF | 南37線F17 KT37 CB |  | bbdb | B2/P02_D1 | [8 empty] | 安南PS.KT37_CB | KT37(11KV南37線) CB | FEEDER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0073 |  |  | 1-09-01 |  |  | 南37線 | 51A | 南37線F17 KT37 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT37_PHA | 11KV南37線(KT37) 相間RY | FEEDER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 南37線 | 51NA | 南37線F17 KT37 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT37_GDA | 11KV南37線(KT37) 接地RY | FEEDER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KT38/T1 |  |  | 0075 |  |  | 1-09-03 |  |  | 南38線 | ON/OFF | 南38線F18 KT38 CB |  | bbeb | B2/P02_D1 | [8 empty] | 安南PS.KT38_CB | KT38(11KV南38線) CB | FEEDER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 南38線 | 51A | 南38線F18 KT38 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT38_PHA | 11KV南38線(KT38) 相間RY | FEEDER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 南38線 | 51NA | 南38線F18 KT38 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT38_GDA | 11KV南38線(KT38) 接地RY | FEEDER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KT39/T1 |  |  | 0078 |  |  | 1-09-06 |  |  | 南39線 | ON/OFF | 南39線F19 KT39 CB |  | bbfb | B2/P02_D1 | [8 empty] | 安南PS.KT39_CB | KT39(11KV南39線) CB | FEEDER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 南39線 | 51A | 南39線F19 KT39 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT39_PHA | 11KV南39線(KT39) 相間RY | FEEDER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0080 |  |  | 1-OA-00 |  |  | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B2/P02_D1 | [16 empty] | 546 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | L/KT40/T1 |  |  | 0081 |  |  | 1-OA-01 |  |  | ACB2 | ON/OFF | 所內電源 ACB2 |  | bbgb | B2/P02_D1 | [8 empty] | 安南PS.KT40_CB | KT40(11KV南40線) CB | FEEDER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-OA-02 |  |  | ACB TIE | ON/OFF | 所內電源 ACB TIE |  |  | B2/P02_D1 | [16 empty] | 548 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0083 |  |  | 1-OA-03 |  |  | 81A | A/N | 欠頻電驛81A(#2DTR 330 340) |  |  | B2/P02_D1 | [16 empty] | 549 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | T/1DTR(A) |  |  | 0084 |  |  | 1-OA-04 |  |  | 25TA | A/N | 自動同步校核器25TA |  | aaba | ELEM/P02_A1 | [16 empty] | 550 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | T/1DTR(B) |  |  | 0085 |  |  | 1-OA-05 |  |  | 25PFA | A/N | 自動同步校核器25PFA |  | baba | ELEM/P02_A1 | [16 empty] | 551 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0086 |  |  | 1-OA-06 |  |  | CHG1 | A/N | 變電充電機CHG1 |  |  | B3/P02_A1 | [16 empty] | 552 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  |  | 1-OA-07 |  |  | CHG2 | A/N | 通訊充電機故障 |  |  | B3/P02_A1 | [16 empty] | 553 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | T/2DTR(A) |  |  | 0088 |  |  | 1-OB-00 |  |  | DCE | A/N | DC 接地DCE |  | abfa | ELEM/P02_A1 | [16 empty] | 554 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | T/2DTR(B) |  |  | 0089 |  |  | 1-OB-01 |  |  | DOOR#1 | ON/OFF | 控制室門 DOOR#1 |  | bbia | ELEM/P02_A1 | [16 empty] | 555 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0090 |  |  | 1-OB-02 |  |  | 1550 | U/L | 安南南濱一路 79RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.820_OUVA | 69KV #2SC 27,59RY | SC | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/2SC |  | 0091 |  |  | 1-OB-03 |  |  | FLA | ON/OFF | 開關場照明FLA |  | aakb | B2/P02_A1 | [8 empty] | 安南PS.820_CB | 820(69KV #2SC) CB | SC | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0092 |  |  | 1-OB-04 |  |  | FLB | ON/OFF | 開關場照明FLB |  |  | B2/P02_A1 | [8 empty] | 安南PS.810_SCA | 69KV #1SC 51,51N RY | SC | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0093 |  |  | 1-OB-05 |  |  | 1560 | U/L | 安南南濱二路 79RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.810_OUVA | 69KV #1SC 27,59RY | SC | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/1SC |  | 0094 |  |  | 1-OB-06 |  |  | 161KV | A/N | 161KV C.B輕警報 |  | aafb | B2/P02_A1 | [8 empty] | 安南PS.810_CB | 810(69KV #1SC) CB | SC | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0095 |  |  | 1-OB-07 |  |  | 161KV | A/N | 161KV C.B重警報 |  |  | B2/P02_A1 | [8 empty] | 安南PS.820_SCA | 69KV #2SC 51,51N RY | SC | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0096 |  |  | 1-OC-00 |  |  | 69KV | A/N | 69KV C.B輕警報 |  |  | B3/P02_A1 | [16 empty] | 562 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0097 |  |  | 1-OC-01 |  |  | 69KV | A/N | 69KV C.B重警報 |  |  | B3/P02_A1 | [16 empty] | 563 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0098 |  |  | 1-OC-02 |  |  | 11KV | A/N | 11KV C.B輕警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.210_SCA | 11KV #1SC 51,51N RY | SC | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0099 |  |  | 1-OC-03 |  |  | 11KV | A/N | 11KV C.B重警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | C/1SC |  |  | 0100 |  |  | 1-OC-04 |  |  | 1740 | A/N | 1740 安南和順線 87CFA |  | aacb | B3/P02_A1 | [8 empty] | 安南PS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 566 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0101 |  |  | 1-OC-05 |  |  | 1740 | A/N | 1740 安南和順線 RYFA |  |  | B3/P02_A1 | [8 empty] | 安南PS.220_SCA | 11KV #2SC 51,51N RY | SC | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0102 |  |  | 1-OC-06 |  |  | 161KV | A/N | 161KV 空壓機#1 16COMT |  |  | B3/P02_A1 | [8 empty] | 安南PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1ABus | C/2SC |  |  | 0103 |  |  | 1-OC-07 |  |  | 161KV | A/N | 161KV 空壓機#2 16COMT |  | aajb | B3/P02_A1 | [8 empty] | 安南PS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 569 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0104 |  |  | 1-OD-00 |  |  | 69KV | A/N | 69KV 空壓機 6COMT |  |  | B3/P02_A1 | [8 empty] | 安南PS.240_SCA | 11KV #4SC 51,51N RY | SC | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0105 |  |  | 1-OD-01 |  |  | OPA | A/N | 油壓電力電纜OPA |  |  | B3/P02_A1 | [8 empty] | 安南PS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2ABus | C/4SC |  |  | 0106 |  |  | 1-OD-02 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  | abeb | B3/P02_A1 | [8 empty] | 安南PS.240_CB_4 | 240(11KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 572 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0107 |  |  | 1-OD-03 |  |  | 161KV | ON/OFF | 161KV ABS電源跳脫 |  |  | B3/P02_A1 | [8 empty] | 安南PS.230_SCA | 11KV #3SC 51,51N RY | SC | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0108 |  |  | 1-OD-04 |  |  | 161KV | ON/OFF | 69KV ABS電源跳脫 |  |  | B3/P02_A1 | [8 empty] | 安南PS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/1BBus | C/3SC |  |  | 0109 |  |  | 1-OD-05 |  |  | 22/11KV | A/N | 22/11KV MCSG電源跳脫MCSGA |  | bacb | B3/P02_A1 | [8 empty] | 安南PS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 575 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0110 |  |  | 1-OD-06 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/P02_A1 | [8 empty] | 安南PS.260_SCA | 11KV #6SC 51,51N RY | SC | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0111 |  |  | 1-OD-07 |  |  | Locate Empty | A/N |  |  |  | B3/P02_A1 | [8 empty] | 安南PS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | C/6SC |  |  | 0112 |  |  | 1-OE-00 |  |  | Locate Empty | A/N |  |  | bbab | B3/P02_A1 | [8 empty] | 安南PS.260_CB_4 | 260(11KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 578 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0114 |  |  | 1-OE-02 |  |  | 火災警報(4) | A/N | 火災警報(4)-主(配)變火警 |  |  | B3/P02_A1 | [8 empty] | 安南PS.250_SCA | 11KV #5SC 51,51N RY | SC | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0115 |  |  | 1-OE-03 |  |  | 大小門 | A/N | 變電所監視系統保全門窗監視 |  |  | B3/P02_A1 | [8 empty] | 安南PS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | BayFdrD | B/2BBus | C/5SC |  |  | 0116 |  |  | 1-OE-04 |  |  | 火災警報(3) | A/N | 火災警報(3) |  | bbhb | B3/P02_A1 | [8 empty] | 安南PS.250_CB_4 | 250(11KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 581 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/1ABus | B/2ABus |  |  | 0117 |  |  | 1-OE-05 |  |  | SC 60RY | A/N | 11KV 22KV SC 60A |  | aakb | B3/P02_A1 | [16 empty] | 582 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-OE-06 |  |  | DCA | A/N | DC NFB DCA |  |  | B3/P02_A1 | [16 empty] | 583 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 100 | TIE(100) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-OE-07 |  |  | 冷氣機房 | A/N | 冷氣機運轉監視 |  |  | B3/P02_A1 | [16 empty] | 584 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | SctFdrB | B/1BBus | B/2BBus |  |  | 0120 |  |  | 1-OF-00 |  |  | 控制室 | A/N | 極早期火災預警 |  | bahb | B3/P02_A1 | [16 empty] | 585 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-OF-01 |  |  | 1710 | A/N | 山上安南豐華紅線1710 87 RYFA(數位電驛故障) |  |  | B3/P02_A1 | [16 empty] | 586 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 200 | TIE(200) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0122 |  |  | 1-OF-02 |  |  | 1710 | A/N | 山上安南豐華紅線1710 CFA(87RY通訊故障) |  |  | B3/P02_A1 | [16 empty] | 587 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-OF-04 |  |  | 1510 | A/N | 安南小北一路 1510 RYFA(電驛故障) |  |  | B3/P02_A1 | [16 empty] | 588 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-OF-05 |  |  | 1510 | A/N | 安南小北一路 1510 87CFA (87L通訊故障) |  |  | B3/P02_A1 | [16 empty] | 589 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0208 |  |  | 1-1A-00 |  |  | 350 | ON/OFF | D3A 350 CB |  | not found | ELEM/P02_A1 | [8 empty] | 安南PS.350_CB | 350(#3DTR) CB | MTR | [5 empty] | 590 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0209 |  |  | 1-1A-01 |  |  | 360 | ON/OFF | D3B 360 CB |  | not found | ELEM/P02_A1 | [8 empty] | 安南PS.360_CB | 360(#3DTR) CB | MTR | [5 empty] | 591 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 350 | #3DTR(A)(350) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0210 |  |  | 1-1A-02 |  |  | 350 | 51A | D3A 350 51RY |  |  | B3/P02_A1 | [8 empty] | 安南PS.350_51A | #3DTR二次側(350) 51RY | MTR | [5 empty] | 592 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 360 | #3DTR(B)(360) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0211 |  |  | 1-1A-03 |  |  | 360 | 51A | D3B 360 51RY |  |  | B3/P02_A1 | [8 empty] | 安南PS.360_51A | #3DTR二次側(360) 51RY | MTR | [5 empty] | 593 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0212 |  |  | 1-1A-04 |  |  | 270 | SCA | 22KV#7SC270SCA |  |  | B3/P02_A1 | [8 empty] | 安南PS.270_SCA | 23KV #7SC 51,51N RY | SC | [5 empty] | 594 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0213 |  |  | 1-1A-05 |  |  | 270 | UVA | 22KV#7SC270UVA |  |  | B3/P02_A1 | [8 empty] | 安南PS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | [5 empty] | 595 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0214 |  |  | 1-1A-06 |  |  | 270 | ON/OFF | 22KV#7SC270CB |  | not found | B3/P02_A1 | [8 empty] | 安南PS.270_CB | 270(23KV #7SC) CB | SC | [5 empty] | 596 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0215 |  |  | 1-1A-07 |  |  | 280 | SCA | 22KV#8SC280SCA |  |  | B3/P02_A1 | [8 empty] | 安南PS.280_SCA | 23KV #8SC 51,51N RY | SC | [5 empty] | 597 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0216 |  |  | 1-1B-00 |  |  | 280 | UVA | 22KV#8SC280UVA |  |  | B3/P02_A1 | [8 empty] | 安南PS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | [5 empty] | 598 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0217 |  |  | 1-1B-01 |  |  | 280 | ON/OFF | 22KV#8SC280CB |  | not found | B3/P02_A1 | [8 empty] | 安南PS.280_CB | 280(23KV #8SC) CB | SC | [5 empty] | 599 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0218 |  |  | 1-1B-02 |  |  | 南71線 | ON/OFF | 南71線F1 KT71 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT71_CB | KT71(23KV南71線) CB | FEEDER | [5 empty] | 600 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0219 |  |  | 1-1B-03 |  |  | 南71線 | 51A | 南71線F1 KT71 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT71_PHA | 23KV南71線(KT71) 相間RY | FEEDER | [5 empty] | 601 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0220 |  |  | 1-1B-04 |  |  | 南71線 | 51NA | 南71線F1 KT71 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT71_GDA | 23KV南71線(KT71) 接地RY | FEEDER | [5 empty] | 602 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0221 |  |  | 1-1B-05 |  |  | 南72線 | ON/OFF | 南72線F2 KT72 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT72_CB | KT72(23KV南72線) CB | FEEDER | [5 empty] | 603 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0222 |  |  | 1-1B-06 |  |  | 南72線 | 51A | 南72線F2 KT72 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT72_PHA | 23KV南72線(KT72) 相間RY | FEEDER | [5 empty] | 604 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0223 |  |  | 1-1B-07 |  |  | 南72線 | 51NA | 南72線F2 KT72 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT72_GDA | 23KV南72線(KT72) 接地RY | FEEDER | [5 empty] | 605 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0224 |  |  | 1-1C-00 |  |  | 南73線 | ON/OFF | 南73線F3 KT73 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT73_CB | KT73(23KV南73線) CB | FEEDER | [5 empty] | 606 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0225 |  |  | 1-1C-01 |  |  | 南73線 | 51A | 南73線F3 KT73 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT73_PHA | 23KV南73線(KT73) 相間RY | FEEDER | [5 empty] | 607 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0226 |  |  | 1-1C-02 |  |  | 南73線 | 51NA | 南73線F3 KT73 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT73_GDA | 23KV南73線(KT73) 接地RY | FEEDER | [5 empty] | 608 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0227 |  |  | 1-1C-03 |  |  | 南74線 | ON/OFF | 南74線F4 KT74 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT74_CB | KT74(23KV南74線) CB | FEEDER | [5 empty] | 609 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0228 |  |  | 1-1C-04 |  |  | 南74線 | 51A | 南74線F4 KT74 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT74_PHA | 23KV南74線(KT74) 相間RY | FEEDER | [5 empty] | 610 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0229 |  |  | 1-1C-05 |  |  | 南74線 | 51NA | 南74線F4 KT74 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT74_GDA | 23KV南74線(KT74) 接地RY | FEEDER | [5 empty] | 611 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0230 |  |  | 1-1C-06 |  |  | 備用線 | ON/OFF | 備用線F5 KT75 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT75_CB | KT75(23KV南75線) CB | FEEDER | [5 empty] | 612 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0231 |  |  | 1-1C-07 |  |  | 備用線 | 51A | 備用線F5 KT75 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT75_PHA | 23KV南75線(KT75) 相間RY | FEEDER | [5 empty] | 613 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0232 |  |  | 1-1D-00 |  |  | 備用線 | 51NA | 備用線F5 KT75 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT75_GDA | 23KV南75線(KT75) 接地RY | FEEDER | [5 empty] | 614 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0233 |  |  | 1-1D-01 |  |  | 南76線 | ON/OFF | 南76線F6 KT76 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT76_CB | KT76(23KV南76線) CB | FEEDER | [5 empty] | 615 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0234 |  |  | 1-1D-02 |  |  | 南76線 | 51A | 南76線F6 KT76 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT76_PHA | 23KV南76線(KT76) 相間RY | FEEDER | [5 empty] | 616 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0235 |  |  | 1-1D-03 |  |  | 南76線 | 51NA | 南76線F6 KT76 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT76_GDA | 23KV南76線(KT76) 接地RY | FEEDER | [5 empty] | 617 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0236 |  |  | 1-1D-04 |  |  | 南77線 | CB ON/OFF | 南77線F7 KT77 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT77_CB | KT77(23KV南77線) CB | FEEDER | [5 empty] | 618 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0237 |  |  | 1-1D-05 |  |  | 南77線 | 51A | 南77線F7 KT77 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT77_PHA | 23KV南77線(KT77) 相間RY | FEEDER | [5 empty] | 619 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0238 |  |  | 1-1D-06 |  |  | 南77線 | 51NA | 南77線F7 KT77 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT77_GDA | 23KV南77線(KT77) 接地RY | FEEDER | [5 empty] | 620 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0239 |  |  | 1-1D-07 |  |  | 南78線 | CB ON/OFF | 南78線F8 KT78 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT78_CB | KT78(23KV南78線) CB | FEEDER | [5 empty] | 621 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0240 |  |  | 1-1E-00 |  |  | 南78線 | 51A | 南78線F8 KT78 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT78_PHA | 23KV南78線(KT78) 相間RY | FEEDER | [5 empty] | 622 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0241 |  |  | 1-1E-01 |  |  | 南78線 | 51NA | 南78線F8 KT78 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT78_GDA | 23KV南78線(KT78) 接地RY | FEEDER | [5 empty] | 623 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0242 |  |  | 1-1E-02 |  |  | 南79線 | CB ON/OFF | 南79線F9 KT79 CB |  | not found | B2/P02_D1 | [8 empty] | 安南PS.KT79_CB | KT79(23KV南79線) CB | FEEDER | [5 empty] | 624 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | 51A |  |  | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0243 |  |  | 1-1E-03 |  |  | 南79線 | 51A | 南79線F9 KT79 51 RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT79_PHA | 23KV南79線(KT79) 相間RY | FEEDER | [5 empty] | 625 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | 51NA |  |  | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0244 |  |  | 1-1E-04 |  |  | 南79線 | 51NA | 南79線F9 KT79 51N RY |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT79_GDA | 23KV南79線(KT79) 接地RY | FEEDER | [5 empty] | 626 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | CB |  | B2 | Status | CB | Close/Open | Y | 1 | DI-SP |  | not found |  |  |  |  | 0248 |  |  | 1-1F-00 |  |  | 11KV | CB ON/OFF | 11KV #3TIE 300 CB |  | not found | B3/P02_A1 | [8 empty] | 安南PS.300_CB | 300(TIE) CB | TIE | [5 empty] | 627 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | 51A |  | B2 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0249 |  |  | 1-1F-01 |  |  | 11KV | 51A | 11KV #3TIE 300 51 RY |  |  | B3/P02_A1 | [8 empty] | 安南PS.300_51A | 23KV TIE(300) 51RY | TIE | [5 empty] | 628 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 300 | TIE(300) |  | 51NA |  | B2 | Status | 51N RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0250 |  |  | 1-1F-02 |  |  | 11KV | 51NA | 11KV #3TIE 300 51N RY |  |  | B3/P02_A1 | [8 empty] | 安南PS.300_51NA | 23KV TIE(300) 51N RY | TIE | [5 empty] | 629 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0336 |  |  | 2-OA-00 |  |  | 631 | ON/OFF | 安南安順白線631 ABS |  |  | B1/P02_A1 | [16 empty] | 630 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 3DTR | #3DTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0337 |  |  | 2-OA-01 |  |  | 631 | ON/OFF | 安南安順白線631 ABS |  |  | B1/P02_A1 | [16 empty] | 631 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0338 |  |  | 2-OA-02 |  |  | 632 | ON/OFF | 安南安順白線632 ABS |  |  | B1/P02_A1 | [16 empty] | 632 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3DTR |  | 0339 |  |  | 2-OA-03 |  |  | 632 | ON/OFF | 安南安順白線632 ABS |  | aaqb | ELEM/P02_A1 | [8 empty] | 安南PS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 633 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0341 |  |  | 2-OA-05 |  |  | 633 | ON/OFF | 安南安順白線633 ABS |  |  | B1/P02_A1 | [16 empty] | 634 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L//T1 |  | 0342 |  |  | 2-OA-06 |  |  | 633 | ON/OFF | 安南安順白線633E ABS |  | aala | B2/P02_A1 | [8 empty] | 安南PS.1550_CB | 1550(安南南濱一路) CB | LINE161 | [5 empty] | 635 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L//T1 |  | 0343 |  |  | 2-OA-07 |  |  | 633 | ON/OFF | 安南安順白線633E ABS |  | aama | B2/P02_A1 | [8 empty] | 安南PS.1560_CB | 1560(安南南濱二路) CB | LINE161 | [5 empty] | 636 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS |  |  | 1MTR | #1MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0344 |  |  | 2-OB-00 |  |  | 641 | ON/OFF | 安南安順紅線641 ABS |  |  | B1/P02_A1 | [16 empty] | 637 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 1MTR | #1MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0345 |  |  | 2-OB-01 |  |  | 641 | ON/OFF | 安南安順紅線641 ABS |  |  | B1/P02_A1 | [16 empty] | 638 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 2MTR | #2MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0346 |  |  | 2-OB-02 |  |  | 642 | ON/OFF | 安南安順紅線642 ABS |  |  | B1/P02_A1 | [16 empty] | 639 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 2MTR | #2MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0347 |  |  | 2-OB-03 |  |  | 642 | ON/OFF | 安南安順紅線642 ABS |  |  | B1/P02_A1 | [16 empty] | 640 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 1DTR | #1DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0348 |  |  | 2-OB-04 |  |  | 643 | ON/OFF | 安南安順紅線643 ABS |  |  | B1/P02_A1 | [16 empty] | 641 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 1DTR | #1DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0349 |  |  | 2-OB-05 |  |  | 643 | ON/OFF | 安南安順紅線643 ABS3 |  |  | B1/P02_A1 | [16 empty] | 642 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 2DTR | #2DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0350 |  |  | 2-OB-06 |  |  | 643 | ON/OFF | 安南安順紅線643E ABS |  |  | B1/P02_A1 | [16 empty] | 643 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 2DTR | #2DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0351 |  |  | 2-OB-07 |  |  | 643 | ON/OFF | 安南安順紅線643E ABS |  |  | B1/P02_A1 | [16 empty] | 644 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0352 |  |  | 2-OC-00 |  |  | 661 | ON/OFF | 安南健康線661 ABS |  |  | B1/P02_A1 | [16 empty] | 645 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 3DTR | #3DTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0353 |  |  | 2-OC-01 |  |  | 661 | ON/OFF | 安南健康線661 ABS |  |  | B1/P02_A1 | [16 empty] | 646 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS |  |  | 3DTR | #3DTR |  | DTR_86A |  |  | Status | 86(50/50N/51Z/87/96) | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0354 |  |  | 2-OC-02 |  |  | 662 | ON/OFF | 安南健康線662 ABS |  |  | B1/P02_A1 | [16 empty] | 647 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1024 |  |  | 2-30-00 |  |  | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/P02_A1 | [8 empty] | 安南PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 648 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1025 |  |  | 2-30-01 |  |  | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/P02_A1 | [8 empty] | 安南PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 649 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | ACB3 |  |  | Status | 所內電源ACB3 | Close/Open | Y | 3 | DI-SP | [6 empty] | 1026 |  |  | 2-30-02 |  |  | ACB TIE | ON/OFF | 所內電源 ACB TIE |  |  | B3/P02_A1 | [8 empty] | 安南PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 650 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P02 | 安南PS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1028 |  |  | 2-30-04 |  |  | 25TA | A/N | 自動同步校核器25TA |  |  | B3/P02_A1 | [8 empty] | 安南PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 651 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1029 |  |  | 2-30-05 |  |  | 25PFA | A/N | 自動同步校核器25PFA |  |  | B3/P02_A1 | [8 empty] | 安南PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 652 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1030 |  |  | 2-30-06 |  |  | CHG1 | A/N | 變電充電機CHG1 |  |  | B3/P02_A1 | [8 empty] | 安南PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 653 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1031 |  |  | 2-30-07 |  |  | CHG2 | A/N | 通訊充電機故障 |  |  | B3/P02_A1 | [8 empty] | 安南PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 654 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1032 |  |  | 2-30-08 |  |  | DCE | A/N | DC 接地DCE |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 655 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Door1 | 控制室 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1033 |  |  | 2-30-09 |  |  | DOOR#1 | ON/OFF | 控制室門 DOOR#1 |  |  | B3/P02_A1 | [8 empty] | 安南PS.無人化門禁(1) | 無人化門禁(1)控制室門 | OTHER | [5 empty] | 656 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1034 |  |  | 2-30-10 |  |  | 1550 | U/L | 安南南濱一路 79RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_79UL | 安南南濱一路(1550) 79RY U/L | LINE161 | [5 empty] | 657 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Lights1 | FLA |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1035 |  |  | 2-30-11 |  |  | FLA | ON/OFF | 開關場照明FLA |  |  | B3/P02_A1 | [8 empty] | 安南PS.開關場照明(A) | 開關場照明 | OTHER | [5 empty] | 658 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Lights2 | FLB |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 1036 |  |  | 2-30-12 |  |  | FLB | ON/OFF | 開關場照明FLB |  |  | B3/P02_A1 | [8 empty] | 安南PS.開關場照明(B) | 涵洞照明 | OTHER | [5 empty] | 659 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1037 |  |  | 2-30-13 |  |  | 1560 | U/L | 安南南濱二路 79RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_79UL | 安南南濱二路(1560) 79RY U/L | LINE161 | [5 empty] | 660 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1038 |  |  | 2-30-14 |  |  | 161KV | A/N | 161KV C.B輕警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 661 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1039 |  |  | 2-30-15 |  |  | 161KV | A/N | 161KV C.B重警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 662 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1040 |  |  | 2-31-00 |  |  | 69KV | A/N | 69KV C.B輕警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | [5 empty] | 663 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1041 |  |  | 2-31-01 |  |  | 69KV | A/N | 69KV C.B重警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.69KV_CBA | 69KV斷路器重故障 | OTHER | [5 empty] | 664 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1042 |  |  | 2-31-02 |  |  | 11KV | A/N | 11KV C.B輕警報 |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.11KV_CBF | 11KV斷路器輕故障 | OTHER | [5 empty] | 665 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1043 |  |  | 2-31-03 |  |  | 11KV | A/N | 11KV C.B重警報 |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.11KV_CBA | 11KV斷路器重故障 | OTHER | [5 empty] | 666 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1044 |  |  | 2-31-04 |  |  | 1740 | A/N | 1740 安南和順線 87CFA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_87CFA | 安南和順線(1740)87RY通訊故障 | OTHER | [5 empty] | 667 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1045 |  |  | 2-31-05 |  |  | 1740 | A/N | 1740 安南和順線 RYFA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_RYFA | 安南和順線(1740)數位電驛故障 | OTHER | [5 empty] | 668 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | StaDev | 所內設施 |  | COMT1 | 第一套空壓機超時運轉 | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1046 |  |  | 2-31-06 |  |  | 161KV | A/N | 161KV 空壓機#1 16COMT |  |  | B3/P02_A1 | [8 empty] | 安南PS.161#1空壓機 | 161KV#1空壓機 | OTHER | [5 empty] | 669 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | StaDev | 所內設施 |  | COMT2 | 第二套空壓機超時運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1047 |  |  | 2-31-07 |  |  | 161KV | A/N | 161KV 空壓機#2 16COMT |  |  | B3/P02_A1 | [8 empty] | 安南PS.161#2空壓機 | 161KV#2空壓機 | OTHER | [5 empty] | 670 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint |  |  | COMT |  |  | Status | 空壓機超時運轉 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1048 |  |  | 2-31-08 |  |  | 69KV | A/N | 69KV 空壓機 6COMT |  |  | B3/P02_A1 | [8 empty] | 安南PS.69空壓機COMT | 69KV空壓機運轉超時警報 | OTHER | [5 empty] | 671 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | OPA |  |  | Status | 充油電纜低壓警報 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1049 |  |  | 2-31-09 |  |  | OPA | A/N | 油壓電力電纜OPA |  |  | B3/P02_A1 | [8 empty] | 安南PS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | [5 empty] | 672 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1050 |  |  | 2-31-10 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/P02_A1 | [8 empty] | 安南PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 673 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1051 |  |  | 2-31-11 |  |  | 161KV | ON/OFF | 161KV ABS電源跳脫 |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 674 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1052 |  |  | 2-31-12 |  |  | 161KV | ON/OFF | 69KV ABS電源跳脫 |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 675 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | MCSG_89A |  | Element | Status | MCSG NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1053 |  |  | 2-31-13 |  |  | 22/11KV | A/N | 22/11KV MCSG電源跳脫MCSGA |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.MCSGA | 23/11KV MCSG電源跳脫 | OTHER | [5 empty] | 676 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1054 |  |  | 2-31-14 |  |  | 火災警報(1) | A/N | 火災警報(1)受信總機 |  |  | B3/P02_A1 | [8 empty] | 安南PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 677 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Fire4 | 主(配)變 |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1058 |  |  | 2-32-02 |  |  | 火災警報(4) | A/N | 火災警報(4)-主(配)變火警 |  |  | B3/P02_A1 | [8 empty] | 安南PS.火災警報(4) | 火災警報(4)-主(配)變火警 | OTHER | [5 empty] | 678 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Door | 變電所監視系統 |  | Status | 無人化門禁 | Close/Open | Y | 5 | DI-SP | [6 empty] | 1059 |  |  | 2-32-03 |  |  | 大小門 | A/N | 變電所監視系統保全門窗監視 |  |  | B3/P02_A1 | [8 empty] | 安南PS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | [5 empty] | 679 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Fire3 |  |  | Status | 火災警報3 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1060 |  |  | 2-32-04 |  |  | 火災警報(3) | A/N | 火災警報(3) |  |  | B3/P02_A1 | [8 empty] | 安南PS.火災警報(3) | 火災警報(3) | OTHER | [5 empty] | 680 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | FDR_60A |  |  | Status | 11/22kV電容器組60RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 1061 |  |  | 2-32-05 |  |  | SC 60RY | A/N | 11KV 22KV SC 60A |  |  | B3/P02_A1 | [8 empty] | 安南PS.23KV_SC_60A | 23/11KV SC 60A | OTHER | [5 empty] | 681 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1062 |  |  | 2-32-06 |  |  | DCA | A/N | DC NFB DCA |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 682 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1063 |  |  | 2-32-07 |  |  | 冷氣機房 | A/N | 冷氣機運轉監視 |  |  | B3/P02_A1 | [8 empty] | 安南PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 683 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1065 |  |  | 2-32-09 |  |  | 1710 | A/N | 山上安南豐華紅線1710 87 RYFA(數位電驛故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_RYFA | 山上豐華紅線(1710)數位電驛故障 | OTHER | [5 empty] | 684 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1066 |  |  | 2-32-10 |  |  | 1710 | A/N | 山上安南豐華紅線1710 CFA(87RY通訊故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_87CFA | 山上豐華紅線(1710)87RY通訊故障 | OTHER | [5 empty] | 685 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1068 |  |  | 2-32-12 |  |  | 1510 | A/N | 安南小北一路 1510 RYFA(電驛故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1510_RYFA | 安南小北一路(1510)數位電驛故障 | OTHER | [5 empty] | 686 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1069 |  |  | 2-32-13 |  |  | 1510 | A/N | 安南小北一路 1510 87CFA (87L通訊故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1510_87CFA | 安南小北一路(1510)87RY通訊故障 | OTHER | [5 empty] | 687 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1070 |  |  | 2-32-14 |  |  | 1520 | A/N | 安南小北二路 1520 RYFA(電驛故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_RYFA | 安南小北二路(1520)數位電驛故障 | OTHER | [5 empty] | 688 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1071 |  |  | 2-32-15 |  |  | 1520 | A/N | 安南小北二路 1520 87CFA (87L通訊故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_87CFA | 安南小北二路(1520)87RY通訊故障 | OTHER | [5 empty] | 689 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0768 |  |  | 1-30-00 |  |  | TEST | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 安南PS.TEST_CB | TEST CB | OTHER | [5 empty] | 690 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0769 |  |  | 1-30-01 |  |  | STATUS | ON/OFF | L/R STATUS |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 691 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 1-30-02 |  |  | 1720 | A/N | 道爺安南新化線 1720 電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_RYFA | 道爺安南新化(1720)數位電驛故障 | OTHER | [5 empty] | 692 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0771 |  |  | 1-30-03 |  |  | 11KV | A/M | 11KV #1SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.210_A/M | 11KV #1SC 乏控器 A/M | SC | [5 empty] | 693 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0772 |  |  | 1-30-04 |  |  | 1720 | A/N | 道爺安南新化線 1720 電驛通訊故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_87CFA | 道爺安南新化(1720)87RY通訊故障 | OTHER | [5 empty] | 694 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0773 |  |  | 1-30-05 |  |  | 11KV | A/M | 11KV #2SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.220_A/M | 11KV #2SC 乏控器 A/M | SC | [5 empty] | 695 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 1-30-06 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/P02_A1 | [8 empty] | 安南PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 696 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0775 |  |  | 1-30-07 |  |  | 11KV | A/M | 11KV #4SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.240_A/M | 11KV #4SC 乏控器 A/M | SC | [5 empty] | 697 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0777 |  |  | 1-30-09 |  |  | 11KV | A/M | 11KV #3SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.230_A/M | 11KV #3SC 乏控器 A/M | SC | [5 empty] | 698 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0779 |  |  | 1-30-11 |  |  | 11KV | A/M | 11KV #6SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.260_A/M | 11KV #6SC 乏控器 A/M | SC | [5 empty] | 699 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 0781 |  |  | 1-30-13 |  |  | 11KV | A/M | 11KV #5SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.250_A/M | 11KV #5SC 乏控器 A/M | SC | [5 empty] | 700 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0782 |  |  | 1-30-14 |  |  | 1550 | U/L | 安南南濱一路 87RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_87UL | 安南南濱一路(1550) 87RY U/L | LINE161 | [5 empty] | 701 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0783 |  |  | 1-30-15 |  |  | 1560 | U/L | 安南南濱二路 87RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_87UL | 安南南濱二路(1560) 87RY U/L | LINE161 | [5 empty] | 702 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | DS1 | 1511 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0784 | 785 |  | 1-31-00 | 1-31-01 |  | 1511 | ON/OFF | 安南小北一路1511 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1511_DS | 1511(安南小北一路) DS | LINE161 | [5 empty] | 703 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | DS2 | 1512 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0786 | 787 |  | 1-31-02 | 1-31-03 |  | 1512 | ON/OFF | 安南小北一路1512 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1512_DS | 1512(安南小北一路) DS | LINE161 | [5 empty] | 704 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | DS3 | 1513 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0788 | 789 |  | 1-31-04 | 1-31-05 |  | 1513 | ON/OFF | 安南小北一路1513 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1513_DS | 1513(安南小北一路) DS | LINE161 | [5 empty] | 705 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | ES3 | 1513E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0790 | 279 |  | 1-31-06 | 1-31-07 |  | 1513E | ON/OFF | 安南小北一路1513E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1513E_ES | 1513E(安南小北一路) ES | LINE161 | [5 empty] | 706 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | DS1 | 1521 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0792 | 793 |  | 1-31-08 | 1-31-09 |  | 1521 | ON/OFF | 安南小北二路1521 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1521_DS | 1521(安南小北二路) DS | LINE161 | [5 empty] | 707 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | DS2 | 1522 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0794 | 795 |  | 1-31-10 | 1-31-11 |  | 1522 | ON/OFF | 安南小北二路1522 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1522_DS | 1522(安南小北二路) DS | LINE161 | [5 empty] | 708 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | DS3 | 1523 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0796 | 797 |  | 1-31-12 | 1-31-13 |  | 1523 | ON/OFF | 安南小北二路1523 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1523_DS | 1523(安南小北二路) DS | LINE161 | [5 empty] | 709 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0798 | 287 |  | 1-31-14 | 1-31-15 |  | 1523E | ON/OFF | 安南小北二路1523E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1523E_ES | 1523E(安南小北二路) ES | LINE161 | [5 empty] | 710 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | DS1 | 1531 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0800 | 801 |  | 1-32-00 | 1-32-01 |  | 1531 | ON/OFF | 安南鹽行線1531 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1531_DS | 1531(安南鹽行線) DS | LINE161 | [5 empty] | 711 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | DS2 | 1532 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0802 | 803 |  | 1-32-02 | 1-32-03 |  | 1532 | ON/OFF | 安南鹽行線1532 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1532_DS | 1532(安南鹽行線) DS | LINE161 | [5 empty] | 712 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | DS3 | 1533 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0804 | 805 |  | 1-32-04 | 1-32-05 |  | 1533 | ON/OFF | 安南鹽行線1533 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1533_DS | 1533(安南鹽行線) DS | LINE161 | [5 empty] | 713 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | ES3 | 1533E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0806 | 295 |  | 1-32-06 | 1-32-07 |  | 1533E | ON/OFF | 安南鹽行線1533E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1533E_ES | 1533E(安南鹽行線) ES | LINE161 | [5 empty] | 714 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | DS1 | 1711 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0808 | 809 |  | 1-32-08 | 1-32-09 |  | 1711 | ON/OFF | 山上安南豐華紅線1711 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1711_DS | 1711(山上豐華紅線) DS | LINE161 | [5 empty] | 715 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | DS2 | 1712 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0810 | 811 |  | 1-32-10 | 1-32-11 |  | 1712 | ON/OFF | 山上安南豐華紅線1712 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1712_DS | 1712(山上豐華紅線) DS | LINE161 | [5 empty] | 716 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | DS3 | 1713 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0812 | 813 |  | 1-32-12 | 1-32-13 |  | 1713 | ON/OFF | 山上安南豐華紅線1713 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1713_DS | 1713(山上豐華紅線) DS | LINE161 | [5 empty] | 717 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | ES3 | 1713E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0814 | 303 |  | 1-32-14 | 1-32-15 |  | 1713E | ON/OFF | 山上安南豐華紅線1713E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1713E_ES | 1713E(山上豐華紅線) ES | LINE161 | [5 empty] | 718 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | DS1 | 1721 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0816 | 817 |  | 1-33-00 | 1-33-01 |  | 1721 | ON/OFF | 道爺安南新化線1721 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1721_DS | 1721(道爺安南新化線) DS | LINE161 | [5 empty] | 719 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | DS2 | 1722 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0818 | 819 |  | 1-33-02 | 1-33-03 |  | 1722 | ON/OFF | 道爺安南新化線1722 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1722_DS | 1722(道爺安南新化線) DS | LINE161 | [5 empty] | 720 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | DS3 | 1723 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0820 | 821 |  | 1-33-04 | 1-33-05 |  | 1723 | ON/OFF | 道爺安南新化線1723 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1723_DS | 1723(道爺安南新化線) DS | LINE161 | [5 empty] | 721 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | ES3 | 1723E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0822 | 311 |  | 1-33-06 | 1-33-07 |  | 1723E | ON/OFF | 道爺安南新化線1723E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1723E_ES | 1723E(道爺安南新化線) ES | LINE161 | [5 empty] | 722 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | DS1 | 1741 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0824 | 825 |  | 1-33-08 | 1-33-09 |  | 1741 | ON/OFF | 安南和順線1741 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1741_DS | 1741(安南和順線) DS | LINE161 | [5 empty] | 723 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | DS2 | 1742 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0826 | 827 |  | 1-33-10 | 1-33-11 |  | 1742 | ON/OFF | 安南和順線1742 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1742_DS | 1742(安南和順線) DS | LINE161 | [5 empty] | 724 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | DS3 | 1743 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0828 | 829 |  | 1-33-12 | 1-33-13 |  | 1743 | ON/OFF | 安南和順線1743 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1743_DS | 1743(安南和順線) DS | LINE161 | [5 empty] | 725 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | ES3 | 1743E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0830 | 319 |  | 1-33-14 | 1-33-15 |  | 1743E | ON/OFF | 安南和順線1743E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1743E_ES | 1743E(安南和順線) ES | LINE161 | [5 empty] | 726 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | DS1 | 1551 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0832 | 833 |  | 1-34-00 | 1-34-01 |  | 1551 | ON/OFF | 安南南濱一路 1551 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1551_DS | 1551(安南南濱一路) DS | LINE161 | [5 empty] | 727 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | DS2 | 1552 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0834 | 835 |  | 1-34-02 | 1-34-03 |  | 1552 | ON/OFF | 安南南濱一路 1552 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1552_DS | 1552(安南南濱一路) DS | LINE161 | [5 empty] | 728 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | DS3 | 1553 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0836 | 837 |  | 1-34-04 | 1-34-05 |  | 1553 | ON/OFF | 安南南濱一路 1553 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1553_DS | 1553(安南南濱一路) DS | LINE161 | [5 empty] | 729 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | ES3 | 1553E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0838 | 327 |  | 1-34-06 | 1-34-07 |  | 1553E | ON/OFF | 安南南濱一路 1553E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1553E_ES | 1553E(安南南濱一路) ES | LINE161 | [5 empty] | 730 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | DS1 | 621 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0840 | 841 |  | 1-34-08 | 1-34-09 |  | 621 | ON/OFF | 安南運河線621 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.621_DS | 621(安南運河線) DS | LINE69 | [5 empty] | 731 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | DS2 | 622 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0842 | 843 |  | 1-34-10 | 1-34-11 |  | 622 | ON/OFF | 安南運河線622 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.622_DS | 622(安南運河線) DS | LINE69 | [5 empty] | 732 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | DS3 | 623 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0844 | 845 |  | 1-34-12 | 1-34-13 |  | 623 | ON/OFF | 安南運河線623 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.623_DS | 623(安南運河線) DS | LINE69 | [5 empty] | 733 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | ES3 | 623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0846 | 335 |  | 1-34-14 | 1-34-15 |  | 623 | ON/OFF | 安南運河線623E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.623E_ES | 623E(安南運河線) ES | LINE69 | [5 empty] | 734 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | DS1 | 631 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0848 | 849 |  | 1-35-00 | 1-35-01 |  | 631 | ON/OFF | 安南安順白線631 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.631_DS | 631(安順白線) DS | LINE69 | [5 empty] | 735 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | DS2 | 632 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0850 | 851 |  | 1-35-02 | 1-35-03 |  | 632 | ON/OFF | 安南安順白線632 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.632_DS | 632(安順白線) DS | LINE69 | [5 empty] | 736 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | DS3 | 633 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0852 | 853 |  | 1-35-04 | 1-35-05 |  | 633 | ON/OFF | 安南安順白線633 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.633_DS | 633(安順白線) DS | LINE69 | [5 empty] | 737 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | ES3 | 633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0854 | 855 |  | 1-35-06 | 1-35-07 |  | 633 | ON/OFF | 安南安順白線633E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.633E_ES | 633E(安順白線) ES | LINE69 | [5 empty] | 738 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | DS1 | 641 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0856 | 857 |  | 1-35-08 | 1-35-09 |  | 641 | ON/OFF | 安南安順紅線641 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.641_DS | 641(安順紅線) DS | LINE69 | [5 empty] | 739 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | DS2 | 642 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0858 | 859 |  | 1-35-10 | 1-35-11 |  | 642 | ON/OFF | 安南安順紅線642 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.642_DS | 642(安順紅線) DS | LINE69 | [5 empty] | 740 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | DS3 | 643 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0860 | 861 |  | 1-35-12 | 1-35-13 |  | 643 | ON/OFF | 安南安順紅線643 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.643_DS | 643(安順紅線) DS | LINE69 | [5 empty] | 741 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | ES3 | 643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0862 | 863 |  | 1-35-14 | 1-35-15 |  | 643 | ON/OFF | 安南安順紅線643E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.643E_ES | 643E(安順紅線) ES | LINE69 | [5 empty] | 742 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | DS1 | 831 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0880 | 881 |  | 1-37-00 | 1-37-01 |  | 831 | ON/OFF | 69KV #3SC 831 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.831_DS | 831(69KV #3SC) DS | SC | [5 empty] | 743 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | DS2 | 832 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0882 | 883 |  | 1-37-02 | 1-37-03 |  | 832 | ON/OFF | 69KV #3SC 832 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.832_DS | 832(69KV #3SC) DS | SC | [5 empty] | 744 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0888 | 889 |  | 1-37-08 | 1-37-09 |  | 811 | ON/OFF | 69KV #1SC 811 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.811_DS | 811(69KV #1SC) DS | SC | [5 empty] | 745 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0890 | 891 |  | 1-37-10 | 1-37-11 |  | 812 | ON/OFF | 69KV #1SC 812 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.812_DS | 812(69KV #1SC) DS | SC | [5 empty] | 746 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | DS1 | 821 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0892 | 893 |  | 1-37-12 | 1-37-13 |  | 821 | ON/OFF | 69KV #2SC 821 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.821_DS | 821(69KV #2SC) DS | SC | [5 empty] | 747 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | DS2 | 822 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0894 | 895 |  | 1-37-14 | 1-37-15 |  | 822 | ON/OFF | 69KV #2SC 822 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.822_DS | 822(69KV #2SC) DS | SC | [5 empty] | 748 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0896 | 897 |  | 1-38-00 | 1-38-01 |  | 1501 | ON/OFF | 161KV TIE 1501 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1501_DS | 1501(TIE) DS | TIE | [5 empty] | 749 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0898 | 899 |  | 1-38-02 | 1-38-03 |  | 1502 | ON/OFF | 161KV TIE 1502 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1502_DS | 1502(TIE) DS | TIE | [5 empty] | 750 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0900 | 901 |  | 1-38-04 | 1-38-05 |  | 601 | ON/OFF | 69KV TIE 601 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.601_DS | 601(TIE) DS | TIE | [5 empty] | 751 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0902 | 903 |  | 1-38-06 | 1-38-07 |  | 602 | ON/OFF | 69KV TIE 602 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.602_DS | 602(TIE) DS | TIE | [5 empty] | 752 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0904 |  |  | 1-38-08 |  |  | OSCF | A/N | 69KV示波器缺紙或故障警報OSCF |  |  | B3/P02_A1 | [8 empty] | 安南PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 753 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0905 |  |  | 1-38-09 |  |  | #1DTR | 96D | #1DTR 96D |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_96D | #1DTR 96D RY | MTR | [5 empty] | 754 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0906 |  |  | 1-38-10 |  |  | #1DTR | 96P | #1DTR 96P |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_96P | #1DTR 96P RY | MTR | [5 empty] | 755 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0907 |  |  | 1-38-11 |  |  | #1DTR | 63Q | #1DTR 63Q |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_63Q | #1DTR 63Q RY | MTR | [5 empty] | 756 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0908 |  |  | 1-38-12 |  |  | #1DTR | 96B1 | #1DTR 96B1 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | [5 empty] | 757 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0909 |  |  | 1-38-13 |  |  | #1DTR | 96B2 | #1DTR 96B2 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | [5 empty] | 758 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0910 |  |  | 1-38-14 |  |  | 1510 | U/L | 安南小北一路 1510 87RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1510_87UL | 安南小北一路(1510) 87RY U/L | LINE161 | [5 empty] | 759 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0911 |  |  | 1-38-15 |  |  | 1520 | U/L | 安南小北二路 1520 87RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_87UL | 安南小北二路(1520) 87RY U/L | LINE161 | [5 empty] | 760 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 1-39-00 |  |  | 1530 | U/L | 安南鹽行線 87 RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_87UL | 安南鹽行線(1530) 87RY U/L | LINE161 | [5 empty] | 761 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0913 |  |  | 1-39-01 |  |  | 1530 | U/L | 安南鹽行線 79 RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_79UL | 安南鹽行線(1530) 79RY U/L | LINE161 | [5 empty] | 762 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0914 |  |  | 1-39-02 |  |  | 1710 | U/L 1 | 山上安南豐華紅線 #1 87 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_87UL1 | 山上豐華紅線(1710) #1 87RY U/L | LINE161 | [5 empty] | 763 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0915 |  |  | 1-39-03 |  |  | 1710 | U/L | 山上安南豐華紅線79 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_79UL | 山上豐華紅線(1710) 79RY U/L | LINE161 | [5 empty] | 764 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0916 |  |  | 1-39-04 |  |  | D1A | U/L | D1A 51Z RY U/L |  |  | B3/P02_A1 | [8 empty] | 安南PS.M1A_51Z_U/L | #1A DTR中性點51Z RY閉瑣 | OTHER | [5 empty] | 765 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0917 |  |  | 1-39-05 |  |  | D1B | U/L | D1B 51Z RY U/L |  |  | B3/P02_A1 | [8 empty] | 安南PS.M1B_51Z_U/L | #1B DTR中性點51Z RY閉瑣 | OTHER | [5 empty] | 766 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0918 |  |  | 1-39-06 |  |  | D2A | U/L | D2A 51Z RY U/L |  |  | B3/P02_A1 | [8 empty] | 安南PS.M2A_51Z_U/L | #2A DTR中性點51Z RY閉瑣 | OTHER | [5 empty] | 767 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0919 |  |  | 1-39-07 |  |  | D2B | U/L | D2B 51Z RY U/L |  |  | B3/P02_A1 | [8 empty] | 安南PS.M2B_51Z_U/L | #2B DTR中性點51Z RY閉瑣 | OTHER | [5 empty] | 768 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0920 |  |  | 1-39-08 |  |  | 1720 | U/L | 道爺安南新化線87 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_87UL | 道爺安南新化線(1720) 87RY U/L | LINE161 | [5 empty] | 769 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0921 |  |  | 1-39-09 |  |  | 1720 | U/L | 道爺安南新化線79 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1720_79UL | 道爺安南新化線(1720) 79RY U/L | LINE161 | [5 empty] | 770 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 1-39-10 |  |  | 1740 | U/L | 安南和順線87 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_87UL | 安南和順線(1740) 87RY U/L | LINE161 | [5 empty] | 771 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0923 |  |  | 1-39-11 |  |  | 1740 | U/L | 安南和順線79 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1740_79UL | 安南和順線(1740) 79RY U/L | LINE161 | [5 empty] | 772 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0924 |  |  | 1-39-12 |  |  | 1510 | U/L | 安南小北一路 1510 79RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1510_79UL | 安南小北一路(1510) 79RY U/L | LINE161 | [5 empty] | 773 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0925 |  |  | 1-39-13 |  |  | 1520 | U/L | 安南小北二路 1520 79RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1520_79UL | 安南小北二路(1520) 79RY U/L | LINE161 | [5 empty] | 774 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0926 |  |  | 1-39-14 |  |  | 630 | U/L | 安南安順白線 630 87 RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.630_87UL | 安順白線(630) 87RY U/L | LINE69 | [5 empty] | 775 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0927 |  |  | 1-39-15 |  |  | 630 | 87CFA | 安南安順白線 630 87RY 通訊故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.630_87CFA | 安南安順白線(630)87RY通訊故障 | OTHER | [5 empty] | 776 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  |  | 1-3A-00 |  |  | 640 | U/L | 安南安順紅線 640 87 RY U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.640_87UL | 安順紅線(640) 87RY U/L | LINE69 | [5 empty] | 777 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0929 |  |  | 1-3A-01 |  |  | 640 | 87CFA | 安南安順紅線 640 87RY 通訊故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.640_87CFA | 安南安順紅線(640)87RY通訊故障 | OTHER | [5 empty] | 778 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0930 |  |  | 1-3A-02 |  |  | 620 | U/L | 安南運河線87 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.620_87UL | 安南運河線(620) 87RY U/L | LINE69 | [5 empty] | 779 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0931 |  |  | 1-3A-03 |  |  | 620 | 87CFA | 安南運河線 620 87 Ry通訊故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.620_87CFA | 安南運河線(620)87RY通訊故障 | OTHER | [5 empty] | 780 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0936 |  |  | 1-3A-08 |  |  | 1550 RAOA | N/A | 安南南濱一路 RAOA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_87CFA | 安南南濱一路(1550)87RY通訊故障 | OTHER | [5 empty] | 781 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0937 |  |  | 1-3A-09 |  |  | 1550 87LA | N/A | 安南南濱一路 87LA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1550_RYFA | 安南南濱一路(1550)數位電驛故障 | OTHER | [5 empty] | 782 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0938 |  |  | 1-3A-10 |  |  | 南21線 | U/L | 南21線F1 KT21 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT21_79UL | 11KV南21線(KT21) 79RY U/L | FEEDER | [5 empty] | 783 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0939 |  |  | 1-3A-11 |  |  | 南22線 | U/L | 南22線 F2 KT22 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT22_79UL | 11KV南22線(KT22) 79RY U/L | FEEDER | [5 empty] | 784 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0940 |  |  | 1-3A-12 |  |  | 南23線 | U/L | 南23線 F3 KT23 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT23_79UL | 11KV南23線(KT23) 79RY U/L | FEEDER | [5 empty] | 785 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0941 |  |  | 1-3A-13 |  |  | 南24線 | U/L | 南24線F4 KT24 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT24_79UL | 11KV南24線(KT24) 79RY U/L | FEEDER | [5 empty] | 786 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0942 |  |  | 1-3A-14 |  |  | 南25線 | U/L | 南25線F5 KT25 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT25_79UL | 11KV南25線(KT25) 79RY U/L | FEEDER | [5 empty] | 787 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0943 |  |  | 1-3A-15 |  |  | 南26線 | U/L | 南26線F6 KT26 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT26_79UL | 11KV南26線(KT26) 79RY U/L | FEEDER | [5 empty] | 788 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0944 |  |  | 1-3B-00 |  |  | 南31線 | U/L | 南31線 F11 KT31 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT31_79UL | 11KV南31線(KT31) 79RY U/L | FEEDER | [5 empty] | 789 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0945 |  |  | 1-3B-01 |  |  | 南32線 | U/L | 南32線 F12 KT32 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT32_79UL | 11KV南32線(KT32) 79RY U/L | FEEDER | [5 empty] | 790 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0946 |  |  | 1-3B-02 |  |  | 南33線 | U/L | 南33線 F13 KT33 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT33_79UL | 11KV南33線(KT33) 79RY U/L | FEEDER | [5 empty] | 791 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0947 |  |  | 1-3B-03 |  |  | 南34線 | U/L | 南34線F14 KT34 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT34_79UL | 11KV南34線(KT34) 79RY U/L | FEEDER | [5 empty] | 792 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0948 |  |  | 1-3B-04 |  |  | 南27線 | U/L | 南27線 F7 KT27 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT27_79UL | 11KV南27線(KT27) 79RY U/L | FEEDER | [5 empty] | 793 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0949 |  |  | 1-3B-05 |  |  | 南28線 | U/L | 南28線 F8 KT28 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT28_79UL | 11KV南28線(KT28) 79RY U/L | FEEDER | [5 empty] | 794 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0950 |  |  | 1-3B-06 |  |  | 南29線 | U/L | 南29線F9 KT29 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT29_79UL | 11KV南29線(KT29) 79RY U/L | FEEDER | [5 empty] | 795 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0951 |  |  | 1-3B-07 |  |  | 南30線 | U/L | 南30線F10 KT30 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT30_79UL | 11KV南30線(KT30) 79RY U/L | FEEDER | [5 empty] | 796 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0952 |  |  | 1-3B-08 |  |  | 南35線 | U/L | 南35線F15 KT35 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT35_79UL | 11KV南35線(KT35) 79RY U/L | FEEDER | [5 empty] | 797 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0953 |  |  | 1-3B-09 |  |  | 南36線 | U/L | 南36線 F16 KT36 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT36_79UL | 11KV南36線(KT36) 79RY U/L | FEEDER | [5 empty] | 798 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0954 |  |  | 1-3B-10 |  |  | 南37線 | U/L | 南37線F17 KT37 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT37_79UL | 11KV南37線(KT37) 79RY U/L | FEEDER | [5 empty] | 799 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0955 |  |  | 1-3B-11 |  |  | 南38線 | U/L | 南38線F18 KT38 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT38_79UL | 11KV南38線(KT38) 79RY U/L | FEEDER | [5 empty] | 800 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0956 |  |  | 1-3B-12 |  |  | 南39線 | U/L | 南39線 F19 KT39 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT39_79UL | 11KV南39線(KT39) 79RY U/L | FEEDER | [5 empty] | 801 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0957 |  |  | 1-3B-13 |  |  | 南40線 | U/L | 南40線F20 KT40 79 RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT40_79UL | 11KV南40線(KT40) 79RY U/L | FEEDER | [5 empty] | 802 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0958 |  |  | 1-3B-14 |  |  | 1560 RAOA | N/A | 安南南濱二路 RAOA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_87CFA | 安南南濱二路(1560)87RY通訊故障 | OTHER | [5 empty] | 803 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0959 |  |  | 1-3B-15 |  |  | 1560 87LA | N/A | 安南南濱二路 87LA |  |  | B2/P02_A1 | [8 empty] | 安南PS.1560_RYFA | 安南南濱二路(1560)數位電驛故障 | OTHER | [5 empty] | 804 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0960 | 961 |  | 1-3C-00 | 1-3C-01 |  | 1651 | ON/OFF | #1MTR一次1651 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1651_DS | 1651(#1MTR) DS | MTR | [5 empty] | 805 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0962 | 963 |  | 1-3C-02 | 1-3C-03 |  | 1652 | ON/OFF | #1MTR一次1652 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1652_DS | 1652(#1MTR) DS | MTR | [5 empty] | 806 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0964 | 965 |  | 1-3C-04 | 1-3C-05 |  | 751 | ON/OFF | #1MTR二次751 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.751_DS | 751(#1MTR) DS | MTR | [5 empty] | 807 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0966 | 967 |  | 1-3C-06 | 1-3C-07 |  | 752 | ON/OFF | #1MTR二次752 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.752_DS | 752(#1MTR) DS | MTR | [5 empty] | 808 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS |  |  | 1MTR | #1MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0968 | 457 |  | 1-3C-08 | 1-3C-09 |  | #1MTR | M/I | #1MTR M/I |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | [5 empty] | 809 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P02 | 安南PS |  |  | 1MTR | #1MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0970 |  |  | 1-3C-10 |  |  | #1MTR | A/N | #1MTR重故障 |  | a | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_TRA | #1MTR 重故障 | MTR | [5 empty] | 810 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0971 |  |  | 1-3C-11 |  |  | #1MTR | A/N | #1MTR輕故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_TRF | #1MTR 輕故障 | MTR | [5 empty] | 811 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0972 |  |  | 1-3C-12 |  |  | #1MTR | A/M | #1MTR OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | [5 empty] | 812 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 1MTR | #1MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0973 |  |  | 1-3C-13 |  |  | #1MTR | R/L | #1MTR OLTC R/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | [5 empty] | 813 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0974 |  |  | 1-3C-14 |  |  | #1MTR | U/L | #1MTR #1 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | [5 empty] | 814 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0975 |  |  | 1-3C-15 |  |  | 620 | RYFA | 安南運河線(620) 數位電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.620_RYFA | 安南運河線(620)數位電驛故障 | OTHER | [5 empty] | 815 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0976 | 977 |  | 1-3D-00 | 1-3D-01 |  | 1661 | ON/OFF | #2MTR一次1661 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1661_DS | 1661(#2MTR) DS | MTR | [5 empty] | 816 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0978 | 979 |  | 1-3D-02 | 1-3D-03 |  | 1662 | ON/OFF | #2MTR一次1662 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1662_DS | 1662(#2MTR) DS | MTR | [5 empty] | 817 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0980 | 981 |  | 1-3D-04 | 1-3D-05 |  | 761 | ON/OFF | #2MTR二次761 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.761_DS | 761(#2MTR) DS | MTR | [5 empty] | 818 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0982 | 983 |  | 1-3D-06 | 1-3D-07 |  | 762 | ON/OFF | #2MTR二次762 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.762_DS | 762(#2MTR) DS | MTR | [5 empty] | 819 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS |  |  | 2MTR | #2MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0984 | 473 |  | 1-3D-08 | 1-3D-09 |  | #2MTR | M/I | #2MTR M/I |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | [5 empty] | 820 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P02 | 安南PS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0986 |  |  | 1-3D-10 |  |  | #2MTR | A/N | #2MTR重故障 |  | a | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_TRA | #2MTR 重故障 | MTR | [5 empty] | 821 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0987 |  |  | 1-3D-11 |  |  | #2MTR | A/N | #2MTR輕故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_TRF | #2MTR 輕故障 | MTR | [5 empty] | 822 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0988 |  |  | 1-3D-12 |  |  | #2MTR | A/M | #2MTR OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | [5 empty] | 823 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0989 |  |  | 1-3D-13 |  |  | #2MTR | R/L | #2MTR OLTC R/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | [5 empty] | 824 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0990 |  |  | 1-3D-14 |  |  | #2MTR | U/L | #2MTR #1 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | [5 empty] | 825 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 0 |  | ComPoint |  |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0991 |  |  | 1-3D-15 |  |  | OLTC | OLTCA | OLTC 15分鐘內連動3次警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | [5 empty] | 826 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 993 |  | 1-3E-00 | 1-3E-01 |  | 1751 | ON/OFF | #1DTR 1751 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1751_DS | 1751(#1DTR) DS | MTR | [5 empty] | 827 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 995 |  | 1-3E-02 | 1-3E-03 |  | 1752 | ON/OFF | #1DTR 1752 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1752_DS | 1752(#1DTR) DS | MTR | [5 empty] | 828 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS |  |  | 1DTR | #1DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 0996 |  |  | 1-3E-04 |  |  | #1DTR | A/N | #1DTR重故障 |  | a | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_TRA | #1DTR 重故障 | MTR | [5 empty] | 829 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR | #1DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0997 |  |  | 1-3E-05 |  |  | #1DTR | A/N | #1DTR輕故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_TRF | #1DTR 輕故障 | MTR | [5 empty] | 830 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0998 |  |  | 1-3E-06 |  |  | D1A | A/M | D1A OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | [5 empty] | 831 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0999 |  |  | 1-3E-07 |  |  | D1B | A/M | D1B OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | [5 empty] | 832 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1000 |  |  | 1-3E-08 |  |  | D1A | R/L | D1A OLTC R/L |  | c | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | [5 empty] | 833 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1001 |  |  | 1-3E-09 |  |  | D1B | R/L | D1B OLTC R/L |  | b | B1/P02_A1 | [8 empty] | 安南PS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | [5 empty] | 834 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1002 |  |  | 1-3E-10 |  |  | #1DTR | U/L | #1DTR #1 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | [5 empty] | 835 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 |  | 1-3E-12 | 1-3E-13 |  | 1761 | ON/OFF | #2DTR 1761 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1761_DS | 1761(#2DTR) DS | MTR | [5 empty] | 836 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1006 | 1007 |  | 1-3E-14 | 1-3E-15 |  | 1762 | ON/OFF | #2DTR 1762 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1762_DS | 1762(#2DTR) DS | MTR | [5 empty] | 837 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS |  |  | 2DTR | #2DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 1008 |  |  | 1-3F-00 |  |  | #2DTR | A/N | #2DTR重故障 |  | a | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_TRA | #2DTR 重故障 | MTR | [5 empty] | 838 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1009 |  |  | 1-3F-01 |  |  | #2DTR | A/N | #2DTR輕故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_TRF | #2DTR 輕故障 | MTR | [5 empty] | 839 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1010 |  |  | 1-3F-02 |  |  | D2A | A/M | D2A OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | [5 empty] | 840 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1011 |  |  | 1-3F-03 |  |  | D2B | A/M | D2B OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | [5 empty] | 841 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1012 |  |  | 1-3F-04 |  |  | D2A | R/L | D2A OLTC R/L |  | c | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | [5 empty] | 842 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1013 |  |  | 1-3F-05 |  |  | D2B | R/L | D2B OLTC R/L |  | b | B1/P02_A1 | [8 empty] | 安南PS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | [5 empty] | 843 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1014 |  |  | 1-3F-06 |  |  | #2DTR | U/L | #2DTR #1 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | [5 empty] | 844 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1016 |  |  | 1-3F-08 |  |  | #1BUS | USE/LOCK | 161KV #1 BUS╴87UL |  |  | B2/P02_A1 | [8 empty] | 安南PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 845 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1017 |  |  | 1-3F-09 |  |  | #2BUS | USE/LOCK | 161KV #2 BUS╴87UL |  |  | B2/P02_A1 | [8 empty] | 安南PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 846 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1018 |  |  | 1-3F-10 |  |  | #1BUS | USE/LOCK | 69KV #1 BUS╴87UL |  |  | B2/P02_A1 | [8 empty] | 安南PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | [5 empty] | 847 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1019 |  |  | 1-3F-11 |  |  | #2BUS | USE/LOCK | 69KV #2 BUS╴87UL |  |  | B2/P02_A1 | [8 empty] | 安南PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | [5 empty] | 848 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1020 |  |  | 1-3F-12 |  |  | BUS | VUA | 161KVBUS #1PD VUA |  |  | B2/P02_A1 | [8 empty] | 安南PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 849 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1021 |  |  | 1-3F-13 |  |  | BUS | VUA | 161KVBUS #2PD VUA |  |  | B2/P02_A1 | [8 empty] | 安南PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 850 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1022 |  |  | 1-3F-14 |  |  | BUS | VUA | 69KV BUS #1PT VUA |  |  | B2/P02_A1 | [8 empty] | 安南PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | [5 empty] | 851 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1023 |  |  | 1-3F-15 |  |  | BUS | VUA | 69KV BUS #2PT VUA |  |  | B2/P02_A1 | [8 empty] | 安南PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 852 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1072 |  |  | 2-33-00 |  |  | 南21線 | U/L | 南21線 F1 KT21 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT21_ADJ | 11KV南21線(KT21) LCO分流器 U/L | FEEDER | [5 empty] | 853 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1073 |  |  | 2-33-01 |  |  | 南22線 | U/L | 南22線 F2 KT22 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT22_ADJ | 11KV南22線(KT22) LCO分流器 U/L | FEEDER | [5 empty] | 854 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1074 |  |  | 2-33-02 |  |  | 南23線 | U/L | 南23線 F3 KT23 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT23_ADJ | 11KV南23線(KT23) LCO分流器 U/L | FEEDER | [5 empty] | 855 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1075 |  |  | 2-33-03 |  |  | 南24線 | U/L | 南24線F4 KT24 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT24_ADJ | 11KV南24線(KT24) LCO分流器 U/L | FEEDER | [5 empty] | 856 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1076 |  |  | 2-33-04 |  |  | 南25線 | U/L | 南25線 F5 KT25 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT25_ADJ | 11KV南25線(KT25) LCO分流器 U/L | FEEDER | [5 empty] | 857 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1077 |  |  | 2-33-05 |  |  | 南26線 | U/L | 南26線F6 KT26 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT26_ADJ | 11KV南26線(KT26) LCO分流器 U/L | FEEDER | [5 empty] | 858 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1078 |  |  | 2-33-06 |  |  | 南27線 | U/L | 南27線 F7 KT27 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT27_ADJ | 11KV南27線(KT27) LCO分流器 U/L | FEEDER | [5 empty] | 859 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1079 |  |  | 2-33-07 |  |  | 南28線 | U/L | 南28線 F8 KT28 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT28_ADJ | 11KV南28線(KT28) LCO分流器 U/L | FEEDER | [5 empty] | 860 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1080 |  |  | 2-33-08 |  |  | 南29線 | U/L | 南29線 F9 KT29 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT29_ADJ | 11KV南29線(KT29) LCO分流器 U/L | FEEDER | [5 empty] | 861 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1081 |  |  | 2-33-09 |  |  | 南30線 | U/L | 南30線 F10 KT30 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT30_ADJ | 11KV南30線(KT30) LCO分流器 U/L | FEEDER | [5 empty] | 862 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1082 |  |  | 2-33-10 |  |  | 南31線 | U/L | 南31線 F11 KT31 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT31_ADJ | 11KV南31線(KT31) LCO分流器 U/L | FEEDER | [5 empty] | 863 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1083 |  |  | 2-33-11 |  |  | 南32線 | U/L | 南32線 F12 KT32 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT32_ADJ | 11KV南32線(KT32) LCO分流器 U/L | FEEDER | [5 empty] | 864 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1084 |  |  | 2-33-12 |  |  | 南33線 | U/L | 南33線 F13 KT33 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT33_ADJ | 11KV南33線(KT33) LCO分流器 U/L | FEEDER | [5 empty] | 865 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1085 |  |  | 2-33-13 |  |  | 南34線 | U/L | 南34線F14 KT34 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT34_ADJ | 11KV南34線(KT34) LCO分流器 U/L | FEEDER | [5 empty] | 866 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1086 |  |  | 2-33-14 |  |  | 南35線 | U/L | 南35線F15 KT35 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT35_ADJ | 11KV南35線(KT35) LCO分流器 U/L | FEEDER | [5 empty] | 867 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1087 |  |  | 2-33-15 |  |  | 南36線 | U/L | 南36線F16 KT36 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT36_ADJ | 11KV南36線(KT36) LCO分流器 U/L | FEEDER | [5 empty] | 868 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1088 |  |  | 2-34-00 |  |  | 南37線 | U/L | 南37線 F17 KT37 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT37_ADJ | 11KV南37線(KT37) LCO分流器 U/L | FEEDER | [5 empty] | 869 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1089 |  |  | 2-34-01 |  |  | 南38線 | U/L | 南38線F18 KT38 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT38_ADJ | 11KV南38線(KT38) LCO分流器 U/L | FEEDER | [5 empty] | 870 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1090 |  |  | 2-34-02 |  |  | 南39線 | U/L | 南39線F19 KT39 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT39_ADJ | 11KV南39線(KT39) LCO分流器 U/L | FEEDER | [5 empty] | 871 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1091 |  |  | 2-34-03 |  |  | 南40線 | U/L | 南40線F20 KT40 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT40_ADJ | 11KV南40線(KT40) LCO分流器 U/L | FEEDER | [5 empty] | 872 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1092 |  |  | 2-34-04 |  |  | 1530 | A/N | 安南鹽行線 1530 RYFA(電驛故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_RYFA | 安南鹽行線(1530)數位電驛故障 | OTHER | [5 empty] | 873 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1093 |  |  | 2-34-05 |  |  | 1530 | A/N | 安南鹽行線 1530 87CFA (87L通訊故障) |  |  | B2/P02_A1 | [8 empty] | 安南PS.1530_87CFA | 安南鹽行線(1530)87RY通訊故障 | OTHER | [5 empty] | 874 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Water1 |  |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1094 |  |  | 2-34-06 |  |  | 地下室 |  | 地下室水位第一段警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 875 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | Water2 |  |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1095 |  |  | 2-34-07 |  |  | 地下室 |  | 地下室水位第二段警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 876 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | DS1 | 1561 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1096 | 1097 |  | 2-34-08 | 2-34-09 |  | 1561 | ON/OFF | 安南南濱二路 1561 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1561_DS | 1561(安南南濱二路) DS | LINE161 | [5 empty] | 877 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | DS2 | 1562 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1098 | 1099 |  | 2-34-10 | 2-34-11 |  | 1562 | ON/OFF | 安南南濱二路 1562 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1562_DS | 1562(安南南濱二路) DS | LINE161 | [5 empty] | 878 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | DS3 | 1563 | Element | Status | DS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1100 | 1101 |  | 2-34-12 | 2-34-13 |  | 1563 | ON/OFF | 安南南濱二路 1563 ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1563_DS | 1563(安南南濱二路) DS | LINE161 | [5 empty] | 879 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1102 | 543 |  | 2-34-14 | 2-34-15 |  | 1563E | ON/OFF | 安南南濱二路 1563E ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1563E_ES | 1563E(安南南濱二路) ES | LINE161 | [5 empty] | 880 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1104 |  |  | 2-35-00 |  |  | 22KV | A/M | 22KV#7SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.270_A/M | 23KV #7SC 乏控器 A/M | SC | [5 empty] | 881 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | SC_A_M |  |  | Status | 乏控器 A/M | Auto/Man | Y | 5 | DI-SP | [6 empty] | 1106 |  |  | 2-35-02 |  |  | 22KV | A/M | 22KV#8SC Q-CTL A/M |  |  | B3/P02_A1 | [8 empty] | 安南PS.280_A/M | 23KV #8SC 乏控器 A/M | SC | [5 empty] | 882 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Auto/Man | Man | 1 |  |  | AUTO/MANUAL | MANUAL
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1108 |  |  | 2-35-04 |  |  | 630 | RYFA | 安南安順白線 630 數位電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.630_RYFA | 安南安順白線(630)數位電驛故障 | OTHER | [5 empty] | 883 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1109 |  |  | 2-35-05 |  |  | 640 | RYFA | 安南安順紅線 640 數位電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.640_RYFA | 安南安順紅線(640)數位電驛故障 | OTHER | [5 empty] | 884 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1110 |  |  | 2-35-06 |  |  | 22KV | ON/OFF | 22KV CB 重警報(#3DTR) |  |  | B1/P02_A1 | [8 empty] | 安南PS.23KV_CBA | 23KV斷路器重故障 | OTHER | [5 empty] | 885 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1111 |  |  | 2-35-07 |  |  | 22KV | ON/OFF | 22KV CB 輕警報(#3DTR) |  |  | B1/P02_A1 | [8 empty] | 安南PS.23KV_CBF | 23KV斷路器輕故障 | OTHER | [5 empty] | 886 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | DTR2 |  |  |  |  | 1113 |  |  | 2-35-09 |  |  | #3DTR | A/N | #3DTR 重故障 |  | a | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_TRA | #3DTR 重故障 | MTR | [5 empty] | 887 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 1114 |  |  | 2-35-10 |  |  | #3DTR | A/N | #3DTR 輕故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_TRF | #3DTR 輕故障 | MTR | [5 empty] | 888 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1115 |  |  | 2-35-11 |  |  | #D3A | A/M | #D3A OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | [5 empty] | 889 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 1116 |  |  | 2-35-12 |  |  | #D3B | A/M | #D3B OLTC A/M |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | [5 empty] | 890 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1117 |  |  | 2-35-13 |  |  | #D3A | R/L | #D3A OLTC R/L |  | c | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | [5 empty] | 891 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 1118 |  |  | 2-35-14 |  |  | #D3B | R/L | #D3B OLTC R/L |  | b | B1/P02_A1 | [8 empty] | 安南PS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | [5 empty] | 892 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1119 |  |  | 2-35-15 |  |  | #3DTR | U/L | #3DTR #1 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | [5 empty] | 893 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | Element | Status | DS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1120 | 1121 |  | 2-36-00 | 2-36-01 |  | 1771 | ON/OFF | #3DTR 一次1771ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1771_DS | 1771(#3DTR) DS | MTR | [5 empty] | 894 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | Element | Status | DS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1122 | 1123 |  | 2-36-02 | 2-36-03 |  | 1772 | ON/OFF | #3DTR 一次1772ABS |  |  | B2/P02_A1 | [8 empty] | 安南PS.1772_DS | 1772(#3DTR) DS | MTR | [5 empty] | 895 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1140 |  |  | 2-37-04 |  |  | 南71線 | U/L | 南71線F1 KT71 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT71_79UL | 23KV南71線(KT71) 79RY U/L | FEEDER | [5 empty] | 896 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1141 |  |  | 2-37-05 |  |  | 南72線 | U/L | 南72線F2 KT72 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT72_79UL | 23KV南72線(KT72) 79RY U/L | FEEDER | [5 empty] | 897 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1142 |  |  | 2-37-06 |  |  | 南73線 | U/L | 南73線F3 KT73 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT73_79UL | 23KV南73線(KT73) 79RY U/L | FEEDER | [5 empty] | 898 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1143 |  |  | 2-37-07 |  |  | 南74線 | U/L | 南74線F4 KT74 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT74_79UL | 23KV南74線(KT74) 79RY U/L | FEEDER | [5 empty] | 899 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1145 |  |  | 2-37-09 |  |  | 南76線 | U/L | 南76線F6 KT76 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT76_79UL | 23KV南76線(KT76) 79RY U/L | FEEDER | [5 empty] | 900 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1146 |  |  | 2-37-10 |  |  | 南77線 | U/L | 南77線F7 KT77 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT77_79UL | 23KV南77線(KT77) 79RY U/L | FEEDER | [5 empty] | 901 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1147 |  |  | 2-37-11 |  |  | 南78線 | U/L | 南78線F8 KT78 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT78_79UL | 23KV南78線(KT78) 79RY U/L | FEEDER | [5 empty] | 902 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1148 |  |  | 2-37-12 |  |  | 南79線 | U/L | 南79線F9 KT79 79RY U/L |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT79_79UL | 23KV南79線(KT79) 79RY U/L | FEEDER | [5 empty] | 903 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | ComPoint | BUS |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1150 |  |  | 2-37-14 |  |  | 161kV BUS | RYFA | 161KV BUS數位電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 904 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | ComPoint | BUS |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1151 |  |  | 2-37-15 |  |  | 161kV BUS | CTFA | 161KV BUS 87RY CT 迴路故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.161KV_BUS_CTFA | 161KV BUS CT迴路故障 | OTHER | [5 empty] | 905 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1152 |  |  | 2-38-00 |  |  | 南71線 | U/L | 南71線F1 KT71 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT71_ADJ | 23KV南71線(KT71) LCO分流器 U/L | FEEDER | [5 empty] | 906 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1153 |  |  | 2-38-01 |  |  | 南72線 | U/L | 南72線F2 KT72 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT72_ADJ | 23KV南72線(KT72) LCO分流器 U/L | FEEDER | [5 empty] | 907 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1154 |  |  | 2-38-02 |  |  | 南73線 | U/L | 南73線F3 KT73 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT73_ADJ | 23KV南73線(KT73) LCO分流器 U/L | FEEDER | [5 empty] | 908 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1155 |  |  | 2-38-03 |  |  | 南74線 | U/L | 南74線F4 KT74 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT74_ADJ | 23KV南74線(KT74) LCO分流器 U/L | FEEDER | [5 empty] | 909 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1157 |  |  | 2-38-05 |  |  | 南76線 | U/L | 南76線F6 KT76 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT76_ADJ | 23KV南76線(KT76) LCO分流器 U/L | FEEDER | [5 empty] | 910 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1158 |  |  | 2-38-06 |  |  | 南77線 | U/L | 南77線F7 KT77 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT77_ADJ | 23KV南77線(KT77) LCO分流器 U/L | FEEDER | [5 empty] | 911 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1159 |  |  | 2-38-07 |  |  | 南78線 | U/L | 南78線F8 KT78 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT78_ADJ | 23KV南78線(KT78) LCO分流器 U/L | FEEDER | [5 empty] | 912 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1160 |  |  | 2-38-08 |  |  | 南79線 | U/L | 南79線F9 KT79 LCO分流器 |  |  | B2/P02_D1 | [8 empty] | 安南PS.KT79_ADJ | 23KV南79線(KT79) LCO分流器 U/L | FEEDER | [5 empty] | 913 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1162 |  |  | 2-38-10 |  |  | #1MTR | 96D | #1MTR 96D |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_96D | #1MTR 96D RY | MTR | [5 empty] | 914 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1163 |  |  | 2-38-11 |  |  | #1MTR | 96P | #1MTR 96P |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_96P | #1MTR 96P RY | MTR | [5 empty] | 915 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1164 |  |  | 2-38-12 |  |  | #1MTR | 63Q | #1MTR 63Q |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_63Q | #1MTR 63Q RY | MTR | [5 empty] | 916 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1165 |  |  | 2-38-13 |  |  | #1MTR | 96B1 | #1MTR 96B1 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | [5 empty] | 917 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1166 |  |  | 2-38-14 |  |  | #1MTR | 96B2 | #1MTR 96B2 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_96B2 | #1MTR 96B2 RY | MTR | [5 empty] | 918 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1167 |  |  | 2-38-15 |  |  | #2MTR | 96D | #2MTR 96D |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_96D | #2MTR 96D RY | MTR | [5 empty] | 919 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1168 |  |  | 2-39-00 |  |  | #2MTR | 96P | #2MTR 96P |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_96P | #2MTR 96P RY | MTR | [5 empty] | 920 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1169 |  |  | 2-39-01 |  |  | #2MTR | 63Q | #2MTR 63Q |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_63Q | #2MTR 63Q RY | MTR | [5 empty] | 921 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1170 |  |  | 2-39-02 |  |  | #2MTR | 96B1 | #2MTR 96B1 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | [5 empty] | 922 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1171 |  |  | 2-39-03 |  |  | #2MTR | 96B2 | #2MTR 96B2 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | [5 empty] | 923 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1172 |  |  | 2-39-04 |  |  | #2DTR | 96D | #2DTR 96D |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_96D | #2DTR 96D RY | MTR | [5 empty] | 924 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1173 |  |  | 2-39-05 |  |  | #2DTR | 96P | #2DTR 96P |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_96P | #2DTR 96P RY | MTR | [5 empty] | 925 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1174 |  |  | 2-39-06 |  |  | #2DTR | 63Q | #2DTR 63Q |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_63Q | #2DTR 63Q RY | MTR | [5 empty] | 926 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1175 |  |  | 2-39-07 |  |  | #2DTR | 96B1 | #2DTR 96B1 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | [5 empty] | 927 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1176 |  |  | 2-39-08 |  |  | #2DTR | 96B2 | #2DTR 96B2 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | [5 empty] | 928 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1177 |  |  | 2-39-09 |  |  | #3DTR | 96D | #3DTR 96D |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_96D | #3DTR 96D RY | MTR | [5 empty] | 929 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1178 |  |  | 2-39-10 |  |  | #3DTR | 96P | #3DTR 96P |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_96P | #3DTR 96P RY | MTR | [5 empty] | 930 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1179 |  |  | 2-39-11 |  |  | #3DTR | 63Q | #2DTR 63Q |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_63Q | #3DTR 63Q RY | MTR | [5 empty] | 931 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1180 |  |  | 2-39-12 |  |  | #3DTR | 96B1 | #3DTR 96B1 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | [5 empty] | 932 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 1181 |  |  | 2-39-13 |  |  | #3DTR | 96B2 | #3DTR 96B2 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | [5 empty] | 933 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1182 |  |  | 2-39-14 |  |  | Locate Empty | A/N | 通訊設備 AC故障 |  |  | B3/P02_A1 | [8 empty] | 安南PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 934 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1185 |  |  | 2-3A-01 |  |  | Locate Empty | A/N | 通信室溫控警報 |  |  | B3/P02_A1 | [8 empty] | 安南PS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 935 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | RYFA | 低頻電驛故障 |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1186 |  |  | 2-3A-02 |  |  | RYFA | A/N | 低頻電驛故障 |  |  | B3/P02_A1 | [8 empty] | 安南PS.81RYFA | 低頻電驛故障 | OTHER | [5 empty] | 936 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | ComPoint |  |  | GRZ100 |  |  | Status | 電驛GRZ100閉鎖 | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1187 |  |  | 2-3A-03 |  |  | BVS盤 | LOCK/USE | 本所各GRZ100 Ry U/L |  |  | B3/P02_A1 | [8 empty] | 安南PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | [5 empty] | 937 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | LOCK/USE | USE
P02 | 安南PS | 161 | 161kV | 1710 | 安南～王行、豐華線(1710) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1188 |  |  | 2-3A-04 |  |  | 1710 | U/L 2 | 山上安南豐華紅線 #2 87 U/L |  |  | B2/P02_A1 | [8 empty] | 安南PS.1710_87UL2 | 山上豐華紅線(1710) #2 87RY U/L | LINE161 | [5 empty] | 938 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作3 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 1189 |  |  | 2-3A-05 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/P02_A1 | [8 empty] | 安南PS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 939 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
P02 | 安南PS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 1190 |  |  | 2-3A-06 |  |  | Locate Empty | A/N | 所內電源欠壓警報 |  |  | ELEM/P02_A1 | [8 empty] | 安南PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 940 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1191 |  |  | 2-3A-07 |  |  | #1MTR | U/L | #1MTR #2 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER | [5 empty] | 941 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 1MTR | #1MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1192 |  |  | 2-3A-08 |  |  | #1MTR | RYFA | #1MTR . 數位電驛故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER | [5 empty] | 942 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 1MTR | #1MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1193 |  |  | 2-3A-09 |  |  | #1MTR | U/L | #1MTR 51Z RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER | [5 empty] | 943 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1194 |  |  | 2-3A-10 |  |  | #2MTR | U/L | #2MTR #2 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | [5 empty] | 944 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 2MTR | #2MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1195 |  |  | 2-3A-11 |  |  | #2MTR | RYFA | #2MTR . 數位電驛故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | [5 empty] | 945 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1196 |  |  | 2-3A-12 |  |  | #2MTR | U/L | #2MTR 51Z RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | [5 empty] | 946 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1197 |  |  | 2-3A-13 |  |  | #1DTR | U/L | #1DTR #2 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | [5 empty] | 947 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 1DTR | #1DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1198 |  |  | 2-3A-14 |  |  | #1DTR | U/L | #1DTR 51Z RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | [5 empty] | 948 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1199 |  |  | 2-3A-15 |  |  | #2DTR | U/L | #2DTR #2 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | [5 empty] | 949 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 2DTR | #2DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1200 |  |  | 2-3B-00 |  |  | #2DTR | U/L | #2DTR 51Z RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | [5 empty] | 950 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 2MTR | #2MTR |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 1201 |  |  | 2-3B-01 |  |  | 81S | U/L | 低頻電驛 81S |  |  | B1/P02_A1 | [8 empty] | 安南PS.81RY_U/L(1) | #2DTR 81RY U/L | OTHER | [5 empty] | 951 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Normal | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1202 |  |  | 2-3B-02 |  |  | #3DTR | U/L | #3DTR #2 87RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | [5 empty] | 952 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 3DTR | #3DTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1203 |  |  | 2-3B-03 |  |  | #3DTR | U/L | #3DTR 51Z RY U/L |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | [5 empty] | 953 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS |  |  | 1DTR | #1DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1204 |  |  | 2-3B-04 |  |  | #1DTR | RYFA | #1DTR. 數位電驛故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | [5 empty] | 954 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 2DTR | #2DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1205 |  |  | 2-3B-05 |  |  | #2DTR | RYFA | #2DTR . 數位電驛故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | [5 empty] | 955 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS |  |  | 3DTR | #3DTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1206 |  |  | 2-3B-06 |  |  | #3DTR | RYFA | #3DTR . 數位電驛故障 |  |  | B1/P02_A1 | [8 empty] | 安南PS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | [5 empty] | 956 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1207 |  |  | 2-3B-07 |  |  | 600 | RYFA | 69KV TIE 600數位電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | [5 empty] | 957 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint | BUS |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1208 |  |  | 2-3B-08 |  |  | 69kV BUS | RYFA | 69KV BUS數位電驛故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | [5 empty] | 958 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | ComPoint | BUS |  | 87CTFA |  |  | Status | 87RY CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 1209 |  |  | 2-3B-09 |  |  | 69kV BUS | A/N | 69KV BUS 87RY CT 迴路故障 |  |  | B2/P02_A1 | [8 empty] | 安南PS.69KV_BUS_CTFA | 69KV BUS CT迴路故障 | OTHER | [5 empty] | 959 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0138 | [10 empty] | B2/P02_A1 | [8 empty] | 安南PS.1510_PHA | 安南小北一路(1510) 相間RY | LINE161 | [5 empty] | 960 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 310 | #1DTR(A)(310) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0174 | [10 empty] | B3/P02_A1 | [16 empty] | 961 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 320 | #1DTR(B)(320) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0180 | [10 empty] | B3/P02_A1 | [16 empty] | 962 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 330 | #2DTR(A)(330) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0189 | [10 empty] | B3/P02_A1 | [16 empty] | 963 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 11 | 11kV | 340 | #2DTR(B)(340) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0192 | [10 empty] | B3/P02_A1 | [16 empty] | 964 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 1144 | [10 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT75_79UL | 23KV南75線(KT75) 79RY U/L | FEEDER | [5 empty] | 965 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | ADJ |  |  | Status | LCO分流器 U/L | Use/Lock | Y | 7 | DI-SP | [6 empty] | 1156 | [10 empty] | B2/P02_D1 | [8 empty] | 安南PS.KT75_ADJ | 23KV南75線(KT75) LCO分流器 U/L | FEEDER | [5 empty] | 966 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Lock | 1 |  |  | USE/LOCK | LOCK
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1750TE | 1750TE (非取樣點) | MTR | [5 empty] | 24 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P02_A1 | [8 empty] | 安南PS.1750BE | 1750BE (非取樣點) | MTR | [5 empty] | 25 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
P02 | 安南PS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: P02/161/1BUS/V; OPRD2: P02/161/2BUS/V
P02 | 安南PS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: P02/69/1BUS/V; OPRD2: P02/69/2BUS/V
P02 | 安南PS |  |  | 1DTR | 1DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#1DTR_MVAR | #1DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: P02/11/310/MVAR; OPRD2: P02/11/320/MVAR
P02 | 安南PS |  |  | 1DTR | 1DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#1DTR_MW | #1DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: P02/11/310/MW; OPRD2: P02/11/320/MW
P02 | 安南PS |  |  | 2DTR | 2DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#2DTR_MVAR | #2DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: P02/11/330/MVAR; OPRD2: P02/11/340/MVAR
P02 | 安南PS |  |  | 2DTR | 2DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#2DTR_MW | #2DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: P02/11/330/MW; OPRD2: P02/11/340/MW
P02 | 安南PS |  |  | 3DTR | 3DTR |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#3DTR_MVAR | #3DTR MVAR | MTR | MTR_PQ_CAL | LG_MVAR | dtr_sum_cal | OPRD1: P02/22/350/MVAR; OPRD2: P02/22/360/MVAR
P02 | 安南PS |  |  | 3DTR | 3DTR |  | MW |  |  | MvMoment | MW |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#3DTR_MW | #3DTR MW | MTR | MTR_PQ_CAL | LG_MW | dtr_sum_cal | OPRD1: P02/22/350/MW; OPRD2: P02/22/360/MW
P02 | 安南PS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/P02_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: P02/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: P02/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
P02 | 安南PS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/P02_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_13 | OPRD1: P02/161/1510/MW; OPRD2: P02/161/1520/MW; OPRD3: P02/161/1530/MW; OPRD4: P02/161/1550/MW; OPRD5: P02/161/1560/MW; OPRD6: P02/161/1710/MW; OPRD7: P02/161/1720/MW; OPRD8: P02/161/1740/MW; OPRD9: P02/69/620/MW; OPRD10: P02/69/630/MW; OPRD11: P02/69/640/MW; OPRD12: P02/69/750/MW; OPRD13: P02/69/760/MW
P02 | 安南PS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/P02_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: P02/0/CalcPoint/OPRN2_MW
P02 | 安南PS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/P02_A1 | [17 empty] | none
P02 | 安南PS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/P02_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: P02/0/CalcPoint/OPRN1; OPRD2: P02/0/CalcPoint/OPRN2; OPRD3: P02/0/CalcPoint/PRFL_UL
P02 | 安南PS |  |  | 1DTR | 1DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/11/310/I_R; OPRD2: P02/11/320/I_R
P02 | 安南PS |  |  | 1DTR | 1DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/11/310/I_S; OPRD2: P02/11/320/I_S
P02 | 安南PS |  |  | 1DTR | 1DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/11/310/I_T; OPRD2: P02/11/320/I_T
P02 | 安南PS |  |  | 2DTR | 2DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/11/330/I_R; OPRD2: P02/11/340/I_R
P02 | 安南PS |  |  | 2DTR | 2DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/11/330/I_S; OPRD2: P02/11/340/I_S
P02 | 安南PS |  |  | 2DTR | 2DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/11/330/I_T; OPRD2: P02/11/340/I_T
P02 | 安南PS |  |  | 3DTR | 3DTR |  | I_R |  |  | MvMoment | R相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/22/350/I_R; OPRD2: P02/22/360/I_R
P02 | 安南PS |  |  | 3DTR | 3DTR |  | I_S |  |  | MvMoment | S相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/22/350/I_S; OPRD2: P02/22/360/I_S
P02 | 安南PS |  |  | 3DTR | 3DTR |  | I_T |  |  | MvMoment | T相AMP |  | Y |  | AI |  | B1/P02_A1 | [15 empty] | MTR_PQ_CAL |  | dtr_sum_cal | OPRD1: P02/22/350/I_T; OPRD2: P02/22/360/I_T
P02 | 安南PS |  |  | 1MTR | 1MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P02/69/750/MW; OPRD2: P02/69/750/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P02_A1 | [12 empty] | 安南PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P02/69/760/MW; OPRD2: P02/69/760/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT21/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT22/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT23/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT24/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT25/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT26/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT27/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT28/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT29/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT30/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT31/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT32/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT33/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT34/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT35/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT36/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT37/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT38/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT39/MVAR; OPRD3: NULL
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/11/KT40/MVAR; OPRD3: NULL
P02 | 安南PS | 161 | 161kV | 1510 | 安南～小北一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1510_AMP | 安南小北一路 AMP | LINE161 | AMP_CAL | C12R0929 | amp_cal | OPRD1: P02/161/1510/MW; OPRD2: P02/161/1510/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1520 | 安南～小北二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1520_AMP | 安南小北二路 AMP | LINE161 | AMP_CAL | C12R0929 | amp_cal | OPRD1: P02/161/1520/MW; OPRD2: P02/161/1520/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1530 | 安南～鹽行線(1530) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1530_AMP | 安南鹽行線 AMP | LINE161 | AMP_CAL | C16R1600 | amp_cal | OPRD1: P02/161/1530/MW; OPRD2: P02/161/1530/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1550 | 安南～南濱一路(1550) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1550_AMP | 安南南濱一路 AMP | LINE161 | AMP_CAL | C20R1328 | amp_cal | OPRD1: P02/161/1550/MW; OPRD2: P02/161/1550/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1560 | 安南～南濱二路(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1560_AMP | 安南南濱二路 AMP | LINE161 | AMP_CAL | C20R1930 | amp_cal | OPRD1: P02/161/1560/MW; OPRD2: P02/161/1560/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1710 | 山上～安南、豐華紅線(1710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1710_AMP | 山上豐華紅線 AMP | LINE161 | AMP_CAL | C16R1600 | amp_cal | OPRD1: P02/161/1710/MW; OPRD2: P02/161/1710/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1720 | 道爺~安南~新化線(1720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1720_AMP | 道爺安南新化線 AMP | LINE161 | AMP_CAL | C16R1600 | amp_cal | OPRD1: P02/161/1720/MW; OPRD2: P02/161/1720/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 161 | 161kV | 1740 | 安南～和順線(1740) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.1740_AMP | 安南和順線 AMP | LINE161 | AMP_CAL | C16R1600 | amp_cal | OPRD1: P02/161/1740/MW; OPRD2: P02/161/1740/MVAR; OPRD3: P02/0/CalcPoint/Vbs4
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT71/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT72/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT73/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT74/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT75/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT76/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT77/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT78/MVAR; OPRD3: NULL
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | AMP_CAL |  | amp_cal | OPRD1: NULL; OPRD2: P02/22/KT79/MVAR; OPRD3: NULL
P02 | 安南PS | 69 | 69kV | 620 | 安南～運河線(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.620_AMP | 安南運河線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: P02/69/620/MW; OPRD2: P02/69/620/MVAR; OPRD3: P02/0/CalcPoint/Vbs2
P02 | 安南PS | 69 | 69kV | 630 | 安南～安順白線(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.630_AMP | 安順白線 AMP | LINE69 | AMP_CAL | C12R0896 | amp_cal | OPRD1: P02/69/630/MW; OPRD2: P02/69/630/MVAR; OPRD3: P02/0/CalcPoint/Vbs2
P02 | 安南PS | 69 | 69kV | 640 | 安南～安順紅線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.640_AMP | 安順紅線 AMP | LINE69 | AMP_CAL | C12R0896 | amp_cal | OPRD1: P02/69/640/MW; OPRD2: P02/69/640/MVAR; OPRD3: P02/0/CalcPoint/Vbs2
P02 | 安南PS | 11 | 11kV | 1ABUS | #1ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P02_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P02/11/1ABUS/V
P02 | 安南PS | 11 | 11kV | 1BBUS | #1BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P02_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P02/11/1BBUS/V
P02 | 安南PS | 11 | 11kV | 2ABUS | #2ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P02_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P02/11/2ABUS/V
P02 | 安南PS | 11 | 11kV | 2BBUS | #2BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P02_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P02/11/2BBUS/V
P02 | 安南PS | 11 | 11kV | 3ABUS | #3ABUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P02_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P02/11/3ABUS/V
P02 | 安南PS | 11 | 11kV | 3BBUS | #3BBUS |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP |  | B3/P02_A1 | [15 empty] | BUS_UV |  | bus_uv | OPRD1: P02/11/3BBUS/V
P02 | 安南PS |  |  | 1DTR | 1DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 安南PS.#1DTR_MVA | #1DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: P02//1DTR/MW; OPRD2: P02//1DTR/MVAR
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 安南PS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P02/11/310/MW; OPRD2: P02/11/310/MVAR
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 安南PS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P02/11/320/MW; OPRD2: P02/11/320/MVAR
P02 | 安南PS |  |  | 1MTR | #1MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 安南PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P02/69/750/MW; OPRD2: P02/69/750/MVAR
P02 | 安南PS |  |  | 2DTR | 2DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 安南PS.#2DTR_MVA | #2DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: P02//2DTR/MW; OPRD2: P02//2DTR/MVAR
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 安南PS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P02/11/330/MW; OPRD2: P02/11/330/MVAR
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 安南PS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P02/11/340/MW; OPRD2: P02/11/340/MVAR
P02 | 安南PS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 安南PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P02/69/760/MW; OPRD2: P02/69/760/MVAR
P02 | 安南PS |  |  | 3DTR | 3DTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_60 | 57 | 66 | 75 | 119 | 1 | -57 | -66 | -75 | -119 |  |  | 安南PS.#3DTR_MVA | #3DTR二次側 MVA | MTR | MVA_CAL | LG_60 | va_million | OPRD1: P02//3DTR/MW; OPRD2: P02//3DTR/MVAR
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 安南PS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P02/22/350/MW; OPRD2: P02/22/350/MVAR
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P02_A1 | LG_30 | 28.5 | 33 | 37.5 | 59 | 1 | -28.5 | -33 | -37.5 | -59 |  |  | 安南PS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR | MVA_CAL | LG_30 | va_million | OPRD1: P02/22/360/MW; OPRD2: P02/22/360/MVAR
P02 | 安南PS |  |  | 1DTR | 1DTR |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR_LOAD | #1DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: P02//1DTR/MVA; OPRD2: 0
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P02//1DTR(A)/MVA; OPRD2: 0
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P02//1DTR(B)/MVA; OPRD2: 0
P02 | 安南PS |  |  | 1MTR | #1MTR |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1MTR_LOAD | #1MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P02//1MTR/MVA; OPRD2: 0
P02 | 安南PS |  |  | 2DTR | 2DTR |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR_LOAD | #2DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: P02//2DTR/MVA; OPRD2: 0
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P02//2DTR(A)/MVA; OPRD2: 0
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P02//2DTR(B)/MVA; OPRD2: 0
P02 | 安南PS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2MTR_LOAD | #2MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P02//2MTR/MVA; OPRD2: 0
P02 | 安南PS |  |  | 3DTR | 3DTR |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR_LOAD | #3DTR 負載率 | MTR | TR_LOAD_60 | LG_LOAD | tr_loading | OPRD1: P02//3DTR/MVA; OPRD2: 0
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P02//3DTR(A)/MVA; OPRD2: 0
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | LOAD | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR | TR_LOAD_30 | LG_LOAD | tr_loading | OPRD1: P02//3DTR(B)/MVA; OPRD2: 0
P02 | 安南PS |  |  | 1DTR | 1DTR |  | PF | [9 empty] | B1/P02_A1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: P02//1DTR/MW; OPRD2: P02//1DTR/MVAR
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/11/310/MW; OPRD2: P02/11/310/MVAR
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/11/320/MW; OPRD2: P02/11/320/MVAR
P02 | 安南PS |  |  | 1MTR | #1MTR |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1MTR_PF | #1MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/69/750/MW; OPRD2: P02/69/750/MVAR
P02 | 安南PS |  |  | 2DTR | 2DTR |  | PF | [9 empty] | B1/P02_A1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: P02//2DTR/MW; OPRD2: P02//2DTR/MVAR
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/11/330/MW; OPRD2: P02/11/330/MVAR
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/11/340/MW; OPRD2: P02/11/340/MVAR
P02 | 安南PS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2MTR_PF | #2MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/69/760/MW; OPRD2: P02/69/760/MVAR
P02 | 安南PS |  |  | 3DTR | 3DTR |  | PF | [9 empty] | B1/P02_A1 | [15 empty] | RPDC_PF_CAL |  | pf_cal | OPRD1: P02//3DTR/MW; OPRD2: P02//3DTR/MVAR
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/22/350/MW; OPRD2: P02/22/350/MVAR
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | PF | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P02/22/360/MW; OPRD2: P02/22/360/MVAR
P02 | 安南PS |  |  | 1DTR(A) | #1DTR(A) |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P02//1DTR(A)/SupLocal; OPRD2: P02//1DTR(A)/Tap Chan
P02 | 安南PS |  |  | 1DTR(B) | #1DTR(B) |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P02//1DTR(B)/SupLocal; OPRD2: P02//1DTR(B)/Tap Chan
P02 | 安南PS |  |  | 2DTR(A) | #2DTR(A) |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P02//2DTR(A)/SupLocal; OPRD2: P02//2DTR(A)/Tap Chan
P02 | 安南PS |  |  | 2DTR(B) | #2DTR(B) |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P02//2DTR(B)/SupLocal; OPRD2: P02//2DTR(B)/Tap Chan
P02 | 安南PS |  |  | 3DTR(A) | #3DTR(A) |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P02//3DTR(A)/SupLocal; OPRD2: P02//3DTR(A)/Tap Chan
P02 | 安南PS |  |  | 3DTR(B) | #3DTR(B) |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | DTR_PERM |  | dtr_perm | OPRD1: P02//3DTR(B)/SupLocal; OPRD2: P02//3DTR(B)/Tap Chan
P02 | 安南PS |  |  | 1MTR | 1MTR |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P02//1MTR/SupLocal; OPRD2: P02//1MTR/Tap Chan; OPRD3: P02//1MTR/M_F_I
P02 | 安南PS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/P02_A1 | [12 empty] | 安南PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P02//2MTR/SupLocal; OPRD2: P02//2MTR/Tap Chan; OPRD3: P02//2MTR/M_F_I
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1ABUS/V; OPRD2: P02/11/KT21/I_R; OPRD3: P02/11/KT21/I_S; OPRD4: P02/11/KT21/I_T
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1ABUS/V; OPRD2: P02/11/KT22/I_R; OPRD3: P02/11/KT22/I_S; OPRD4: P02/11/KT22/I_T
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1ABUS/V; OPRD2: P02/11/KT23/I_R; OPRD3: P02/11/KT23/I_S; OPRD4: P02/11/KT23/I_T
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1ABUS/V; OPRD2: P02/11/KT24/I_R; OPRD3: P02/11/KT24/I_S; OPRD4: P02/11/KT24/I_T
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1ABUS/V; OPRD2: P02/11/KT25/I_R; OPRD3: P02/11/KT25/I_S; OPRD4: P02/11/KT25/I_T
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1ABUS/V; OPRD2: P02/11/KT26/I_R; OPRD3: P02/11/KT26/I_S; OPRD4: P02/11/KT26/I_T
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2ABUS/V; OPRD2: P02/11/KT27/I_R; OPRD3: P02/11/KT27/I_S; OPRD4: P02/11/KT27/I_T
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2ABUS/V; OPRD2: P02/11/KT28/I_R; OPRD3: P02/11/KT28/I_S; OPRD4: P02/11/KT28/I_T
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2ABUS/V; OPRD2: P02/11/KT29/I_R; OPRD3: P02/11/KT29/I_S; OPRD4: P02/11/KT29/I_T
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2ABUS/V; OPRD2: P02/11/KT30/I_R; OPRD3: P02/11/KT30/I_S; OPRD4: P02/11/KT30/I_T
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1BBUS/V; OPRD2: P02/11/KT31/I_R; OPRD3: P02/11/KT31/I_S; OPRD4: P02/11/KT31/I_T
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1BBUS/V; OPRD2: P02/11/KT32/I_R; OPRD3: P02/11/KT32/I_S; OPRD4: P02/11/KT32/I_T
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1BBUS/V; OPRD2: P02/11/KT33/I_R; OPRD3: P02/11/KT33/I_S; OPRD4: P02/11/KT33/I_T
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/1BBUS/V; OPRD2: P02/11/KT34/I_R; OPRD3: P02/11/KT34/I_S; OPRD4: P02/11/KT34/I_T
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2BBUS/V; OPRD2: P02/11/KT35/I_R; OPRD3: P02/11/KT35/I_S; OPRD4: P02/11/KT35/I_T
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2BBUS/V; OPRD2: P02/11/KT36/I_R; OPRD3: P02/11/KT36/I_S; OPRD4: P02/11/KT36/I_T
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2BBUS/V; OPRD2: P02/11/KT37/I_R; OPRD3: P02/11/KT37/I_S; OPRD4: P02/11/KT37/I_T
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2BBUS/V; OPRD2: P02/11/KT38/I_R; OPRD3: P02/11/KT38/I_S; OPRD4: P02/11/KT38/I_T
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2BBUS/V; OPRD2: P02/11/KT39/I_R; OPRD3: P02/11/KT39/I_S; OPRD4: P02/11/KT39/I_T
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: P02/11/2BBUS/V; OPRD2: P02/11/KT40/I_R; OPRD3: P02/11/KT40/I_S; OPRD4: P02/11/KT40/I_T
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT71/I_R; OPRD3: P02/22/KT71/I_S; OPRD4: P02/22/KT71/I_T
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT72/I_R; OPRD3: P02/22/KT72/I_S; OPRD4: P02/22/KT72/I_T
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT73/I_R; OPRD3: P02/22/KT73/I_S; OPRD4: P02/22/KT73/I_T
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT74/I_R; OPRD3: P02/22/KT74/I_S; OPRD4: P02/22/KT74/I_T
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT75/I_R; OPRD3: P02/22/KT75/I_S; OPRD4: P02/22/KT75/I_T
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT76/I_R; OPRD3: P02/22/KT76/I_S; OPRD4: P02/22/KT76/I_T
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT77/I_R; OPRD3: P02/22/KT77/I_S; OPRD4: P02/22/KT77/I_T
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT78/I_R; OPRD3: P02/22/KT78/I_S; OPRD4: P02/22/KT78/I_T
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | kVA |  |  | MvMoment | KVA |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KVA_CAL |  | kva_cal | OPRD1: NULL; OPRD2: P02/22/KT79/I_R; OPRD3: P02/22/KT79/I_S; OPRD4: P02/22/KT79/I_T
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT21/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT22/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT23/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT24/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT25/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT26/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT27/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT28/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT29/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT30/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT31/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT32/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT33/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT34/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT35/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT36/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT37/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT38/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT39/kVA; OPRD2: NULL
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/11/KT40/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT71/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT72/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT73/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT74/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT75/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT76/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT77/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT78/kVA; OPRD2: NULL
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | kW |  |  | MvMoment | KW |  | Y |  | AI |  | B2/P02_D1 | [15 empty] | KW_CAL |  | kw_cal | OPRD1: P02/22/KT79/kVA; OPRD2: NULL
P02 | 安南PS | 0 |  | CalcPoint |  |  | DTR_MW | [9 empty] | B1/P02_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_5 | OPRD1: P02//1DTR/MW; OPRD2: P02//2DTR/MW; OPRD3: P02//3DTR/MW; OPRD4: P02/69/750/MW; OPRD5: P02/69/760/MW
P02 | 安南PS | 0 |  | CalcPoint |  |  | DTR_MVAR | [9 empty] | B1/P02_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_5 | OPRD1: P02//1DTR/MVAR; OPRD2: P02//2DTR/MVAR; OPRD3: P02//3DTR/MVAR; OPRD4: P02/69/750/MVAR; OPRD5: P02/69/760/MVAR
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.210_SC_MVAR | 11KV#1SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P02/11/210/CB; OPRD2: 6.9; OPRD3: 0
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.220_SC_MVAR | 11KV#2SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P02/11/220/CB; OPRD2: 6.9; OPRD3: 0
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.230_SC_MVAR | 11KV#3SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P02/11/230/CB; OPRD2: 6.9; OPRD3: 0
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.240_SC_MVAR | 11KV#4SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P02/11/240/CB; OPRD2: 6.9; OPRD3: 0
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.250_SC_MVAR | 11KV#5SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P02/11/250/CB; OPRD2: 6.9; OPRD3: 0
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.260_SC_MVAR | 11KV#6SC MVAR | SC | SC_CAL_11 | LG_MVAR | sc_mvar | OPRD1: P02/11/260/CB; OPRD2: 6.9; OPRD3: 0
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.270_SC_MVAR | 23KV#7SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P02/22/270/CB; OPRD2: 13.8; OPRD3: 0
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B3/P02_A1 | [12 empty] | 安南PS.280_SC_MVAR | 23KV#8SC MVAR | SC | SC_CAL_23 | LG_MVAR | sc_mvar | OPRD1: P02/22/280/CB; OPRD2: 13.8; OPRD3: 0
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.810_SC_MVAR | 69KV#1SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P02/69/810/CB; OPRD2: 69; OPRD3: 0
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.820_SC_MVAR | 69KV#2SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P02/69/820/CB; OPRD2: 69; OPRD3: 0
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P02_A1 | [12 empty] | 安南PS.830_SC_MVAR | 69KV#3SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P02/69/830/CB; OPRD2: 69; OPRD3: 0
P02 | 安南PS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/P02_A1 | [12 empty] | 安南PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_24 |  | com_alarm_62 | P02//1DTR/51ZA | P02//1DTR/GDA | P02//1DTR/PHA | P02//1DTR/96PA | P02//1DTR/96D | P02//1DTR/96B2 | P02//1DTR/TRA | P02//1DTR/63Q | P02//1DTR/96B1 | P02//1DTR/87A | P02//1MTR/PHA | P02//1MTR/TRA | P02//1MTR/96PA | P02//1MTR/GDA | P02//1MTR/51ZA | P02//1MTR/96B1 | P02//1MTR/96B2 | P02//1MTR/63Q | P02//1MTR/87A | P02//1MTR/96D | P02//2DTR/TRA | P02//2DTR/PHA | P02//2DTR/96PA | P02//2DTR/GDA | P02//2DTR/51ZA | P02//2DTR/96B1 | P02//2DTR/96B2 | P02//2DTR/63Q | P02//2DTR/87A | P02//2DTR/96D | P02//2MTR/51ZA | P02//2MTR/96PA | P02//2MTR/TRA | P02//2MTR/96D | P02//2MTR/96B2 | P02//2MTR/96B1 | P02//2MTR/63Q | P02//2MTR/87A | P02//2MTR/GDA | P02//2MTR/PHA | P02//3DTR/51ZA | P02//3DTR/63Q | P02//3DTR/GDA | P02//3DTR/96B2 | P02//3DTR/96D | P02//3DTR/TRA | P02//3DTR/96PA | P02//3DTR/PHA | P02//3DTR/96B1 | P02//3DTR/87A
P02 | 安南PS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/P02_A1 | [12 empty] | 安南PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_5 |  | com_alarm_5 | OPRD1: P02//1DTR/TRF; OPRD2: P02//1MTR/TRF; OPRD3: P02//2DTR/TRF; OPRD4: P02//2MTR/TRF; OPRD5: P02//3DTR/TRF
P02 | 安南PS | 161 | 161kV | 1750_D1 | #1DTR(1750) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/161/1750/CB
P02 | 安南PS | 161 | 161kV | 1760_D1 | #2DTR(1760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/161/1760/CB
P02 | 安南PS | 11 | 11kV | 310_D1 | #1DTR(A)(310) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/11/310/CB
P02 | 安南PS | 11 | 11kV | 320_D1 | #1DTR(B)(320) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/11/320/CB
P02 | 安南PS | 11 | 11kV | 330_D1 | #2DTR(A)(330) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/11/330/CB
P02 | 安南PS | 11 | 11kV | 340_D1 | #2DTR(B)(340) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/11/340/CB
P02 | 安南PS | 22 | 22kV | 350_D1 | #3DTR(A)(350) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/22/350/CB
P02 | 安南PS | 22 | 22kV | 360_D1 | #3DTR(B)(360) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/22/360/CB
P02 | 安南PS | 161 | 161kV | 1770_D1 | #3DTR(1770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/161/1770/CB
P02 | 安南PS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/0/StaDev/DCE
P02 | 安南PS | 11 | 11kV | ComPoint_D1 |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/11/ComPoint/CBF
P02 | 安南PS | 11 | 11kV | ComPoint_D1 |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/11/ComPoint/CBA
P02 | 安南PS | 161 | 161kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/161/ComPoint/ABS_89A
P02 | 安南PS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/69/ComPoint/ABS_89A
P02 | 安南PS | 0 |  | ComPoint_D1 |  |  | MCSG_89A | MCSG_89A |  | Status | MCSG NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/0/ComPoint/MCSG_89A
P02 | 安南PS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/0/StaDev/DCA
P02 | 安南PS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/0/RTU/RTU_R_L
P02 | 安南PS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P02_D1 | [17 empty] | lamp2CC | OPRD1: P02/0/StaDev/STUV

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P02 | 安南PS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 安南PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | P02/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
P02 | 安南PS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_S | [8 empty] | 安南PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | P02/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1510_AMP | 安南小北一路 AMP | LINE161 | P02/161/1510/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C12R0929 | 836.200012 | 836.200012 | 929.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1520_AMP | 安南小北二路 AMP | LINE161 | P02/161/1520/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C12R0929 | 836.200012 | 836.200012 | 929.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1530_AMP | 安南鹽行線 AMP | LINE161 | P02/161/1530/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C16R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 1600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1710_AMP | 山上豐華紅線 AMP | LINE161 | P02/161/1710/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C16R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 1600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1720_AMP | 道爺安南新化線 AMP | LINE161 | P02/161/1720/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C16R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 1600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.630_AMP | 安順白線 AMP | LINE69 | P02/69/630/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C12R0896 | 806.400024 | 806.400024 | 896.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.640_AMP | 安順紅線 AMP | LINE69 | P02/69/640/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C12R0896 | 806.400024 | 806.400024 | 896.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 0 |  | 1MTR | #1MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_MVA | #1MTR二次側 MVA | MTR | P02//1MTR/MVA |  | MVA_CAL |  |  | 11 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_LOAD | #1MTR 負載率 | MTR | P02//1MTR/Loading |  | TR_LOAD_200 |  |  | 12 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_PF | #1MTR 功率因素 | MTR | P02//1MTR/PF |  | RPDC_PF_CAL |  |  | 13 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_AMP | #1MTR 二次側 AMP | MTR | P02//1MTR/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P02 | 安南PS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | P02//2MTR/MVA |  | MVA_CAL |  |  | 15 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_LOAD | #2MTR 負載率 | MTR | P02//2MTR/Loading |  | TR_LOAD_200 |  |  | 16 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_PF | #2MTR 功率因素 | MTR | P02//2MTR/PF |  | RPDC_PF_CAL |  |  | 17 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | P02//2MTR/I |  | AMP_CAL |  |  | 18 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P02 | 安南PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MW) |  | MW | [25 empty] | ADCS_S | [8 empty] | 安南PS.RPDC_MTR_MW | SUM(161/69KV MTR MW) | MTR |  |  | RPDC_2MTR_MW_CAL |  |  | 19 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MVAR) |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.RPDC_MTR_MVAR | SUM(161/69KV MTR MVAR) | MTR |  |  | RPDC_2MTR_MVAR_CAL |  |  | 20 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | RPDC_MTR | RPDC |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.RPDC_MTR_PF | RPDC MTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_MVA | #1DTR二次側(A) MVA | MTR | P02//1DTR(A)/MVA |  | MVA_CAL |  |  | 22 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_LOAD | #1DTR(A) 負載率 | MTR | P02//1DTR(A)/Loading |  | TR_LOAD_30 |  |  | 23 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_PF | #1DTR(A) 功率因素 | MTR | P02//1DTR(A)/PF |  | RPDC_PF_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_MVA | #1DTR二次側(B) MVA | MTR | P02//1DTR(B)/MVA |  | MVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_LOAD | #1DTR(B) 負載率 | MTR | P02//1DTR(B)/Loading |  | TR_LOAD_30 |  |  | 26 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_PF | #1DTR(B) 功率因素 | MTR | P02//1DTR(B)/PF |  | RPDC_PF_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_MVA | #2DTR二次側(A) MVA | MTR | P02//2DTR(A)/MVA |  | MVA_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_LOAD | #2DTR(A) 負載率 | MTR | P02//2DTR(A)/Loading |  | TR_LOAD_30 |  |  | 29 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_PF | #2DTR(A) 功率因素 | MTR | P02//2DTR(A)/PF |  | RPDC_PF_CAL |  |  | 30 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_MVA | #2DTR二次側(B) MVA | MTR | P02//2DTR(B)/MVA |  | MVA_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_LOAD | #2DTR(B) 負載率 | MTR | P02//2DTR(B)/Loading |  | TR_LOAD_30 |  |  | 32 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_PF | #2DTR(B) 功率因素 | MTR | P02//2DTR(B)/PF |  | RPDC_PF_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_MVA | #3DTR二次側(A) MVA | MTR | P02//3DTR(A)/MVA |  | MVA_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_LOAD | #3DTR(A) 負載率 | MTR | P02//3DTR(A)/Loading |  | TR_LOAD_30 |  |  | 35 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_PF | #3DTR(A) 功率因素 | MTR | P02//3DTR(A)/PF |  | RPDC_PF_CAL |  |  | 36 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_MVA | #3DTR二次側(B) MVA | MTR | P02//3DTR(B)/MVA |  | MVA_CAL |  |  | 37 | CalcAIPoint | [21 empty] | LG_30 | 27.000000 | 30.000000 | 37.500000 | 39.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR(B) |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_LOAD | #3DTR(B) 負載率 | MTR | P02//3DTR(B)/Loading |  | TR_LOAD_30 |  |  | 38 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR(B) |  | PF | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_PF | #3DTR(B) 功率因素 | MTR | P02//3DTR(B)/PF |  | RPDC_PF_CAL |  |  | 39 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_MW | #1DTR MW | MTR | P02//1DTR/MW |  | MTR_PQ_CAL |  |  | 40 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_MVAR | #1DTR MVAR | MTR | P02//1DTR/MVAR |  | MTR_PQ_CAL |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | 1DTR | #1DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_MVA | #1DTR二次側 MVA | MTR | P02//1DTR/MVA |  | MVA_CAL |  |  | 42 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_LOAD | #1DTR 負載率 | MTR | P02//1DTR/Loading |  | TR_LOAD_60 |  |  | 43 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_MW | #2DTR MW | MTR | P02//2DTR/MW |  | MTR_PQ_CAL |  |  | 44 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_MVAR | #2DTR MVAR | MTR | P02//2DTR/MVAR |  | MTR_PQ_CAL |  |  | 45 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | 2DTR | #2DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_MVA | #2DTR二次側 MVA | MTR | P02//2DTR/MVA |  | MVA_CAL |  |  | 46 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_LOAD | #2DTR 負載率 | MTR | P02//2DTR/Loading |  | TR_LOAD_60 |  |  | 47 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | MW | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_MW | #3DTR MW | MTR | P02//3DTR/MW |  | MTR_PQ_CAL |  |  | 48 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_MVAR | #3DTR MVAR | MTR | P02//3DTR/MVAR |  | MTR_PQ_CAL |  |  | 49 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | 3DTR | #3DTR二次側 |  | MVA | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_MVA | #3DTR二次側 MVA | MTR | P02//3DTR/MVA |  | MVA_CAL |  |  | 50 | CalcAIPoint | [21 empty] | LG_60 | 54.000000 | 60.000000 | 75.000000 | 78.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | LOAD | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_LOAD | #3DTR 負載率 | MTR | P02//3DTR/Loading |  | TR_LOAD_60 |  |  | 51 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P02 | 安南PS | 11 | 11kV | 210_SC | #1SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.210_SC_MVAR | 11KV#1SC MVAR | SC | P02/11/210/MVAR |  | SC_CAL_11 |  |  | 52 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 220_SC | #2SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.220_SC_MVAR | 11KV#2SC MVAR | SC | P02/11/220/MVAR |  | SC_CAL_11 |  |  | 53 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 230_SC | #3SC | 3 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.230_SC_MVAR | 11KV#3SC MVAR | SC | P02/11/230/MVAR |  | SC_CAL_11 |  |  | 54 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 240_SC | #4SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.240_SC_MVAR | 11KV#4SC MVAR | SC | P02/11/240/MVAR |  | SC_CAL_11 |  |  | 55 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 250_SC | #5SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.250_SC_MVAR | 11KV#5SC MVAR | SC | P02/11/250/MVAR |  | SC_CAL_11 |  |  | 56 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 260_SC | #6SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.260_SC_MVAR | 11KV#6SC MVAR | SC | P02/11/260/MVAR |  | SC_CAL_11 |  |  | 57 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 22 | 22kV | 270_SC | #7SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.270_SC_MVAR | 23KV#7SC MVAR | SC | P02/22/270/MVAR |  | SC_CAL_23 |  |  | 58 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 22 | 22kV | 280_SC | #8SC | 6 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.280_SC_MVAR | 23KV#8SC MVAR | SC | P02/22/280/MVAR |  | SC_CAL_23 |  |  | 59 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 810_SC | #1SC | 28.799999 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.810_SC_MVAR | 69KV#1SC MVAR | SC | P02/69/810/MVAR |  | SC_CAL_69 |  |  | 60 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 820_SC | #2SC | 28.799999 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.820_SC_MVAR | 69KV#2SC MVAR | SC | P02/69/820/MVAR |  | SC_CAL_69 |  |  | 61 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | MVAR | [25 empty] | ADCS_S | [8 empty] | 安南PS.830_SC_MVAR | 69KV#3SC MVAR | SC | P02/69/830/MVAR |  | SC_CAL_69 |  |  | 62 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | TRTOT | 安南主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 安南PS.TRTOT_MW | 安南主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_5 |  |  | 63 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | TRTOT | 安南主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 安南PS.TRTOT_MVAR | 安南主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_5 |  |  | 64 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南21線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南21線KVA | 11KV南21線KVA | FEEDER |  |  | KVA_CAL |  |  | 65 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南21線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南21線KW | 11KV南21線KW | FEEDER |  |  | KW_CAL |  |  | 66 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南22線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南22線KVA | 11KV南22線KVA | FEEDER |  |  | KVA_CAL |  |  | 67 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南22線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南22線KW | 11KV南22線KW | FEEDER |  |  | KW_CAL |  |  | 68 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南23線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南23線KVA | 11KV南23線KVA | FEEDER |  |  | KVA_CAL |  |  | 69 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南23線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南23線KW | 11KV南23線KW | FEEDER |  |  | KW_CAL |  |  | 70 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南24線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南24線KVA | 11KV南24線KVA | FEEDER |  |  | KVA_CAL |  |  | 71 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南24線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南24線KW | 11KV南24線KW | FEEDER |  |  | KW_CAL |  |  | 72 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南25線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南25線KVA | 11KV南25線KVA | FEEDER |  |  | KVA_CAL |  |  | 73 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南25線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南25線KW | 11KV南25線KW | FEEDER |  |  | KW_CAL |  |  | 74 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南26線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南26線KVA | 11KV南26線KVA | FEEDER |  |  | KVA_CAL |  |  | 75 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南26線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南26線KW | 11KV南26線KW | FEEDER |  |  | KW_CAL |  |  | 76 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南27線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南27線KVA | 11KV南27線KVA | FEEDER |  |  | KVA_CAL |  |  | 77 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南27線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南27線KW | 11KV南27線KW | FEEDER |  |  | KW_CAL |  |  | 78 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南28線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南28線KVA | 11KV南28線KVA | FEEDER |  |  | KVA_CAL |  |  | 79 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南28線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南28線KW | 11KV南28線KW | FEEDER |  |  | KW_CAL |  |  | 80 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南29線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南29線KVA | 11KV南29線KVA | FEEDER |  |  | KVA_CAL |  |  | 81 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南29線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南29線KW | 11KV南29線KW | FEEDER |  |  | KW_CAL |  |  | 82 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南30線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南30線KVA | 11KV南30線KVA | FEEDER |  |  | KVA_CAL |  |  | 83 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南30線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南30線KW | 11KV南30線KW | FEEDER |  |  | KW_CAL |  |  | 84 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南31線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南31線KVA | 11KV南31線KVA | FEEDER |  |  | KVA_CAL |  |  | 85 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南31線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南31線KW | 11KV南31線KW | FEEDER |  |  | KW_CAL |  |  | 86 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南32線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南32線KVA | 11KV南32線KVA | FEEDER |  |  | KVA_CAL |  |  | 87 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南32線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南32線KW | 11KV南32線KW | FEEDER |  |  | KW_CAL |  |  | 88 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南33線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南33線KVA | 11KV南33線KVA | FEEDER |  |  | KVA_CAL |  |  | 89 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南33線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南33線KW | 11KV南33線KW | FEEDER |  |  | KW_CAL |  |  | 90 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南34線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南34線KVA | 11KV南34線KVA | FEEDER |  |  | KVA_CAL |  |  | 91 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南34線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南34線KW | 11KV南34線KW | FEEDER |  |  | KW_CAL |  |  | 92 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南35線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南35線KVA | 11KV南35線KVA | FEEDER |  |  | KVA_CAL |  |  | 93 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南35線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南35線KW | 11KV南35線KW | FEEDER |  |  | KW_CAL |  |  | 94 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南36線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南36線KVA | 11KV南36線KVA | FEEDER |  |  | KVA_CAL |  |  | 95 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南36線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南36線KW | 11KV南36線KW | FEEDER |  |  | KW_CAL |  |  | 96 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南37線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南37線KVA | 11KV南37線KVA | FEEDER |  |  | KVA_CAL |  |  | 97 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南37線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南37線KW | 11KV南37線KW | FEEDER |  |  | KW_CAL |  |  | 98 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南38線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南38線KVA | 11KV南38線KVA | FEEDER |  |  | KVA_CAL |  |  | 99 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南38線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南38線KW | 11KV南38線KW | FEEDER |  |  | KW_CAL |  |  | 100 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南39線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南39線KVA | 11KV南39線KVA | FEEDER |  |  | KVA_CAL |  |  | 101 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南39線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南39線KW | 11KV南39線KW | FEEDER |  |  | KW_CAL |  |  | 102 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南40線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南40線KVA | 11KV南40線KVA | FEEDER |  |  | KVA_CAL |  |  | 103 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南40線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南40線KW | 11KV南40線KW | FEEDER |  |  | KW_CAL |  |  | 104 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南71線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南71線KVA | 23KV南71線KVA | FEEDER |  |  | KVA_CAL |  |  | 105 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南71線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南71線KW | 23KV南71線KW | FEEDER |  |  | KW_CAL |  |  | 106 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南72線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南72線KVA | 23KV南72線KVA | FEEDER |  |  | KVA_CAL |  |  | 107 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南72線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南72線KW | 23KV南72線KW | FEEDER |  |  | KW_CAL |  |  | 108 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南73線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南73線KVA | 23KV南73線KVA | FEEDER |  |  | KVA_CAL |  |  | 109 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南73線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南73線KW | 23KV南73線KW | FEEDER |  |  | KW_CAL |  |  | 110 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南74線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南74線KVA | 23KV南74線KVA | FEEDER |  |  | KVA_CAL |  |  | 111 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南74線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南74線KW | 23KV南74線KW | FEEDER |  |  | KW_CAL |  |  | 112 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南75線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南75線KVA | 23KV南75線KVA | FEEDER |  |  | KVA_CAL |  |  | 113 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南75線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南75線KW | 23KV南75線KW | FEEDER |  |  | KW_CAL |  |  | 114 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南76線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南76線KVA | 23KV南76線KVA | FEEDER |  |  | KVA_CAL |  |  | 115 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南76線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南76線KW | 23KV南76線KW | FEEDER |  |  | KW_CAL |  |  | 116 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南77線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南77線KVA | 23KV南77線KVA | FEEDER |  |  | KVA_CAL |  |  | 117 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南77線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南77線KW | 23KV南77線KW | FEEDER |  |  | KW_CAL |  |  | 118 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南78線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南78線KVA | 23KV南78線KVA | FEEDER |  |  | KVA_CAL |  |  | 119 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南78線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南78線KW | 23KV南78線KW | FEEDER |  |  | KW_CAL |  |  | 120 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南79線KVA | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南79線KVA | 23KV南79線KVA | FEEDER |  |  | KVA_CAL |  |  | 121 | CalcAIPoint | [21 empty] | LG_KVA | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  |  |  |  | 南79線KW | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.南79線KW | 23KV南79線KW | FEEDER |  |  | KW_CAL |  |  | 122 | CalcAIPoint | [21 empty] | LG_KW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1550_AMP | 安南南濱一路 AMP | LINE161 | P02/161/1550/I |  | AMP_CAL |  |  | 123 | CalcAIPoint | [21 empty] | C20R1328 | 1195.199951 | 1195.199951 | 1328.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1560_AMP | 安南南濱二路 AMP | LINE161 | P02/161/1560/I |  | AMP_CAL |  |  | 124 | CalcAIPoint | [21 empty] | C20R1930 | 1737.800049 | 1737.800049 | 1930.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 0 |  | MTR_TOT | 安南MTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 安南PS.MTR_TOT_MW | 安南MTR瞬時供電量 MW |  |  |  | MTR_PQ_CAL |  |  | 125 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | DTR_TOT | 安南DTR瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 安南PS.DTR_TOT_MW | 安南DTR瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 126 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.620_AMP | 安南運河線 AMP | LINE69 | P02/69/620/I |  | AMP_CAL |  |  | 127 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | I | [25 empty] | ADCS_S | [8 empty] | 安南PS.1740_AMP | 安南和順線 AMP | LINE161 | P02/161/1740/I |  | AMP_CAL |  |  | 128 | CalcAIPoint | [21 empty] | C16R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 1600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P02 | 安南PS | 69 | 69kV | 630_CB | 安順白線(630_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 安南PS.630_CB_4 | 630(安順白線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 129 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 640_CB | 安順紅線(640_CB) |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 安南PS.640_CB_4 | 640(安順紅線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 130 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | MTR | MTR |  | A_M | [25 empty] | RPDC_AD | [8 empty] | 安南PS.MTR_A/M | MTR OLTC A/M | MTR |  |  | LCP_2PTR |  |  | 131 | CalcDIPoint | [38 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 0 |  | 1750_CB | #1DTR(1750_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.1750_CB_4 | 1750(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 132 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 310_CB | #1DTR(310_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.310_CB_4 | 310(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 133 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 320_CB | #1DTR(320_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.320_CB_4 | 320(#1DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 134 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1760_CB | #2DTR(1760_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.1760_CB_4 | 1760(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 135 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 330_CB | #2DTR(330_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.330_CB_4 | 330(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 136 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 340_CB | #2DTR(340_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.340_CB_4 | 340(#2DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 137 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1770_CB | #3DTR(1770_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.1770_CB_4 | 1770(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 138 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 350_CB | #3DTR(350_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.350_CB_4 | 350(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 139 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 360_CB | #3DTR(360_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.360_CB_4 | 360(#3DTR) CB (D4) | MTR |  |  | AD_LAMP_DD_1 |  |  | 140 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 210_CB | #1SC(210_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.210_CB_4 | 210(11KV #1SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 141 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 220_CB | #2SC(220_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.220_CB_4 | 220(11KV #2SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 142 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 230_CB | #3SC(230_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.230_CB_4 | 230(11KV #3SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 143 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 240_CB | #4SC(240_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.240_CB_4 | 240(11KV #4SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 144 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 250_CB | #5SC(250_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.250_CB_4 | 250(11KV #5SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 145 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 260_CB | #6SC(260_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.260_CB_4 | 260(11KV #6SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 146 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 270_CB | #7SC(270_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.270_CB_4 | 270(23KV #7SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 147 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 280_CB | #8SC(280_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.280_CB_4 | 280(23KV #8SC) CB (D4) | SC |  |  | AD_LAMP_DD_1 |  |  | 148 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | _CBA | 斷路器重故障點燈(_CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.11KV_CBA_4 | 11KV斷路器重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 149 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | _CBF | 斷路器輕故障(_CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.11KV_CBF_4 | 11KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 150 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | _CBA | 斷路器重故障點燈(_CBA) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.23KV_CBA_4 | 23KV斷路器重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 151 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | _CBF | 斷路器輕故障(_CBF) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.23KV_CBF_4 | 23KV斷路器輕故障 (D4) | OTHER |  |  | AD_LAMP_DD_3 |  |  | 152 | CalcDIPoint | [38 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | OSC啟動 | 示波器啟動警報點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.OSC啟動_4 | 示波器啟動警報點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 153 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | RTU_S_L | RTU |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.RTU_S/L_4 | RTU SUPY/LOCAL (D4) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 154 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P02 | 安南PS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_S | [8 empty] | 安南PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | P02/0/CalcPoint/SUBA |  | STATION_FAULT_24 |  |  | 155 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_S | [8 empty] | 安南PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | P02/0/CalcPoint/SUBF |  | STATION_FAULT_5 |  |  | 156 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.變電所重故障_4 | 變電所重故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 157 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.變電所輕故障_4 | 變電所輕故障點燈 (D4) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 158 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510_AMP | 安南小北一路 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1510_AMP_A | 安南小北一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 159 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 161 | 161kV | 1520_AMP | 安南小北二路 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1520_AMP_A | 安南小北二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 160 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 161 | 161kV | 1530_AMP | 安南鹽行線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1530_AMP_A | 安南鹽行線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 161 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 161 | 161kV | 1710_AMP | 山上豐華紅線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1710_AMP_A | 山上豐華紅線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 162 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 161 | 161kV | 1720_AMP | 道爺安南新化線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1720_AMP_A | 道爺安南新化線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 163 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 69 | 69kV | 630_AMP | 安順白線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.630_AMP_A | 安順白線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 164 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 69 | 69kV | 630_AMP | 安順白線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 安南PS.630_AMP_4 | 安順白線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 165 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 69 | 69kV | 640_AMP | 安順紅線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.640_AMP_A | 安順紅線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 166 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 69 | 69kV | 640_AMP | 安順紅線 |  | 4 | [25 empty] | DDCS4_2 | [8 empty] | 安南PS.640_AMP_4 | 安順紅線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 167 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1MTR_MVA | #1MTR | [27 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_MVA_A | #1MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 168 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_PERM | #1MTR TAP PERMISSION POINT | MTR | P02//1MTR/TR_PERM |  | MTR_PERM |  |  | 169 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_MVA_A | #2MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 170 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | P02//2MTR/TR_PERM |  | MTR_PERM |  |  | 171 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_PERM | #1DTR(A) TAP PERMISSION POINT | MTR | P02//1DTR(A)/TR_PERM |  | DTR_PERM |  |  | 172 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_PERM | #1DTR TAP PERMISSION POINT | MTR | P02//1DTR(B)/TR_PERM |  | DTR_PERM |  |  | 173 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_PERM | #2DTR(A) TAP PERMISSION POINT | MTR | P02//2DTR(A)/TR_PERM |  | DTR_PERM |  |  | 174 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_PERM | #2DTR TAP PERMISSION POINT | MTR | P02//2DTR(B)/TR_PERM |  | DTR_PERM |  |  | 175 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_PERM | #3DTR(A) TAP PERMISSION POINT | MTR | P02//3DTR(A)/TR_PERM |  | DTR_PERM |  |  | 176 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR |  | PERM | [25 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_PERM | #3DTR TAP PERMISSION POINT | MTR | P02//3DTR(B)/TR_PERM |  | DTR_PERM |  |  | 177 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1DTR_MVA | #1DTR | [27 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_MVA_A | #1DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 178 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1DTR_MVA | #1DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.#1DTR_MVA_4 | #1DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 179 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1DTR_MVA | #1DTR(B) |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.#1DTR_MVA_5 | #1DTR(B) MVA 點燈 |  |  |  | MAP_SET |  |  | 180 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2DTR_MVA | #2DTR | [27 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_MVA_A | #2DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 181 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2DTR_MVA | #2DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.#2DTR_MVA_4 | #2DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 182 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2DTR_MVA | #2DTR(B) |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.#2DTR_MVA_5 | #2DTR(B) MVA 點燈 |  |  |  | MAP_SET |  |  | 183 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3DTR_MVA | #3DTR | [27 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_MVA_A | #3DTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 184 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3DTR_MVA | #3DTR(A) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.#3DTR_MVA_4 | #3DTR(A) MVA 點燈 (D4) | MTR |  |  | MAP_SET |  |  | 185 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3DTR_MVA | #3DTR(B) |  | 5 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.#3DTR_MVA_5 | #3DTR(B) MVA 點燈 |  |  |  | MAP_SET |  |  | 186 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 81RY_A_S(1) | #2DTR |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.81RY_A/S(1)_4 | #2DTR 330/340低頻電驛動作 (D4) | OTHER |  |  | AD_LAMP_DD_7 |  |  | 187 | CalcDIPoint | [38 empty] | TRIP/RESET | RESET
P02 | 安南PS | 161 | 161kV | 1550_AMP | 安南南濱一路 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1550_AMP_A | 安南南濱一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 188 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 161 | 161kV | 1560_AMP | 安南南濱二路 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1560_AMP_A | 安南南濱二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 189 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_S | [8 empty] | 安南PS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_PS |  |  | 190 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620_AMP | 安南運河線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.620_AMP_A | 安南運河線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 191 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 69 | 69kV | 620_CB | 安南運河線(620_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.620_CB_4 | 620(安南運河線) CB (D4) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 192 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 620_AMP | 安南運河線 |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.620_AMP_4 | 安南運河線 AMP 點燈 (D4) | LINE69 |  |  | MAP_SET |  |  | 193 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 100_CB | 100(100_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.100_CB_4 | 100 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 194 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 200_CB | 200(200_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.200_CB_4 | 200 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 195 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 300_CB | 300(300_CB) |  | 4 | [25 empty] | DDCS4_1 | [8 empty] | 安南PS.300_CB_4 | 300 CB (D4) | TIE |  |  | AD_LAMP_DD_1 |  |  | 196 | CalcDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 1ABUS | #1ABUS |  | 11KV#1ABUSC | [25 empty] | CDCS | [8 empty] | 安南PS.11KV#1ABUSC | #1ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 197 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 1BBUS | #1BBUS |  | 11KV#1BBUSC | [25 empty] | CDCS | [8 empty] | 安南PS.11KV#1BBUSC | #1BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 198 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2ABUS | #2ABUS |  | 11KV#2ABUSC | [25 empty] | CDCS | [8 empty] | 安南PS.11KV#2ABUSC | #2ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 199 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 2BBUS | #2BBUS |  | 11KV#2BBUSC | [25 empty] | CDCS | [8 empty] | 安南PS.11KV#2BBUSC | #2BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 200 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3ABUS | #3ABUS |  | 23KV#3ABUSC | [25 empty] | CDCS | [8 empty] | 安南PS.23KV#3ABUSC | #3ABUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 201 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 3BBUS | #3BBUS |  | 23KV#3BBUSC | [25 empty] | CDCS | [8 empty] | 安南PS.23KV#3BBUSC | #3BBUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B |  |  | 202 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | TAP_OVER | TAP |  | SET | [25 empty] | ADCS_S | [8 empty] | 安南PS.TAP_OVER_SET | TAP OVER HI/LO ALARM | MTR |  |  | 5000_CB_T6 |  |  | 203 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | BUS_OVER | BUS |  | SET | [25 empty] | ADCS_S | [8 empty] | 安南PS.BUS_OVER_SET | BUS OVER HI/LO ALARM | MTR |  |  | 5000_CB_B6 |  |  | 204 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 5000 | 虛擬5000 |  | CB動作 | [25 empty] | ADCS_S | [8 empty] | 安南PS.5000_CB動作 | 虛擬5000 CB動作,請查明原因處理 | MTR |  |  | 5000_CB_M |  |  | 205 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1740_AMP | 安南和順線 | [27 empty] | ADCS_S | [8 empty] | 安南PS.1740_AMP_A | 安南和順線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 206 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P02 | 安南PS | 0 |  | 注意OLTC | 注意OLTC |  | BUS電壓異常 | [25 empty] | ADCS_S | [8 empty] | 安南PS.BUS電壓異常 | 注意OLTC Tap位置,並將RPDC閉鎖 | OTHER |  |  | STATION_FAULT_1 |  |  | 207 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | P02/0/RTU/ADCH1 |  |  |  | CDC | 208 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | P02/0/RTU/ADCH2 |  |  |  | CDC | 209 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCH3 | [17 empty] | 2-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCH3 | AI 90%參考點 ADCH3 | OTHER | P02/0/RTU/ADCH3 |  |  |  | CDC | 210 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCH4 | [17 empty] | 2-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCH4 | AI 90%參考點 ADCH4 | OTHER | P02/0/RTU/ADCH4 |  |  |  | CDC | 211 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | P02/0/RTU/ADCL1 |  |  |  | CDC | 212 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | P02/0/RTU/ADCL2 |  |  |  | CDC | 213 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCL3 | [17 empty] | 2-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCL3 | AI 10%參考點 ADCL3 | OTHER | P02/0/RTU/ADCL3 |  |  |  | CDC | 214 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | AI | AI |  | ADCL4 | [17 empty] | 2-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.AI_ADCL4 | AI 10%參考點 ADCL4 | OTHER | P02/0/RTU/ADCL4 |  |  |  | CDC | 215 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-90 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | P02/161/1BUS/V |  |  |  | CDC | 216 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P02 | 安南PS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-91 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | P02/161/2BUS/V |  |  |  | CDC | 217 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P02 | 安南PS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-B2 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | P02/69/1BUS/V |  |  |  | CDC | 218 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P02 | 安南PS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-B3 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | P02/69/2BUS/V |  |  |  | CDC | 219 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P02 | 安南PS | 11 | 11kV | 1ABUS | #1ABUS |  | V | [17 empty] | 1-C6 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV#1ABUS_KV | 11KV #1ABUS KV | BUS | P02/11/1ABUS/V |  |  |  | CDC | 220 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 1BBUS | #1BBUS |  | V | [17 empty] | 1-CA | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV#1BBUS_KV | 11KV #1BBUS KV | BUS | P02/11/1BBUS/V |  |  |  | CDC | 221 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 2ABUS | #2ABUS |  | V | [17 empty] | 1-C7 | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV#2ABUS_KV | 11KV #2ABUS KV | BUS | P02/11/2ABUS/V |  |  |  | CDC | 222 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 11 | 11kV | 2BBUS | #2BBUS |  | V | [17 empty] | 1-CB | [5 empty] | kV_-9_9(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV#2BBUS_KV | 11KV #2BBUS KV | BUS | P02/11/2BBUS/V |  |  |  | CDC | 223 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000 | 4.000000 | 1.500000
P02 | 安南PS | 22 | 22kV | 3ABUS | #3ABUS |  | V | [17 empty] | 2-CC | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.23KV#3ABUS_KV | 23KV #3ABUS KV | BUS | P02/11/3ABUS/V |  |  |  | CDC | 224 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P02 | 安南PS | 22 | 22kV | 3BBUS | #3BBUS |  | V | [17 empty] | 2-CD | [5 empty] | kV_-18_18(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.23KV#3BBUS_KV | 23KV #3BBUS KV | BUS | P02/11/3BBUS/V |  |  |  | CDC | 225 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000 | 4.000000 | 3.000000
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-336_336(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1510_MW | 安南小北一路 MW | LINE161 | P02/161/1510/MW |  |  |  | CDC | 226 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-336_336(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1510_MVAR | 安南小北一路 MVAR | LINE161 | P02/161/1510/MVAR |  |  |  | CDC | 227 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | MW | [17 empty] | 1-88 | [5 empty] | MW_-336_336(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1520_MW | 安南小北二路 MW | LINE161 | P02/161/1520/MW |  |  |  | CDC | 228 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | MVAR | [17 empty] | 1-89 | [5 empty] | MVAR_-336_336(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1520_MVAR | 安南小北二路 MVAR | LINE161 | P02/161/1520/MVAR |  |  |  | CDC | 229 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | MW | [17 empty] | 1-82 | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1530_MW | 安南鹽行線 MW | LINE161 | P02/161/1530/MW |  |  |  | CDC | 230 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | MVAR | [17 empty] | 1-83 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1530_MVAR | 安南鹽行線 MVAR | LINE161 | P02/161/1530/MVAR |  |  |  | CDC | 231 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1710_MW | 山上豐華紅線 MW | LINE161 | P02/161/1710/MW |  |  |  | CDC | 232 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1710_MVAR | 山上豐華紅線 MVAR | LINE161 | P02/161/1710/MVAR |  |  |  | CDC | 233 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | MW | [17 empty] | 1-8A | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1720_MW | 道爺安南新化線 MW | LINE161 | P02/161/1720/MW |  |  |  | CDC | 234 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | MVAR | [17 empty] | 1-8B | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1720_MVAR | 道爺安南新化線 MVAR | LINE161 | P02/161/1720/MVAR |  |  |  | CDC | 235 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | MW | [17 empty] | 1-B5 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.630_MW | 安順白線 MW | LINE69 | P02/69/630/MW |  |  |  | CDC | 236 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | MVAR | [17 empty] | 1-B6 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.630_MVAR | 安順白線 MVAR | LINE69 | P02/69/630/MVAR |  |  |  | CDC | 237 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | MW | [17 empty] | 1-B8 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.640_MW | 安順紅線 MW | LINE69 | P02/69/640/MW |  |  |  | CDC | 238 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | MVAR | [17 empty] | 1-B9 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.640_MVAR | 安順紅線 MVAR | LINE69 | P02/69/640/MVAR |  |  |  | CDC | 239 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-B0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1500TIE_AMP | 1500TIE AMP | TIE | P02/161/1500/I |  |  |  | CDC | 240 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-B1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.600TIE_AMP | 600TIE AMP | TIE | P02/69/600/I |  |  |  | CDC | 241 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1MTR | #1MTR二次側 |  | MW | [17 empty] | 1-97 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1MTR_MW | #1MTR二次側 MW | MTR | P02/69/750/MW |  |  |  | CDC | 242 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P02 | 安南PS | 0 |  | 1MTR | #1MTR二次側 |  | MVAR | [17 empty] | 1-98 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1MTR_MVAR | #1MTR二次側 MVAR | MTR | P02/69/750/MVAR |  |  |  | CDC | 243 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | TapPosMv | [17 empty] | 2-A4 |  | 1-7E |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#1MTR_TAP | #1MTR OLTC TAP | MTR | P02//1MTR/TapPosMv |  |  |  | CDC | 244 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | OilTemp | [17 empty] | 2-A5 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1MTR_OIL | #1MTR 油溫 | MTR | P02//1MTR/OilTemp |  |  |  | CDC | 245 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | CoilTemp | [17 empty] | 2-A6 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1MTR_COIL | #1MTR 線溫 | MTR | P02//1MTR/CoilTemp |  |  |  | CDC | 246 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-9A | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2MTR_MW | #2MTR二次側 MW | MTR | P02/69/760/MW |  |  |  | CDC | 247 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P02 | 安南PS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-9B | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | P02/69/760/MVAR |  |  |  | CDC | 248 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 2-A7 |  | 2-08 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | P02//2MTR/TapPosMv |  |  |  | CDC | 249 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 2-A8 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2MTR_OIL | #2MTR 油溫 | MTR | P02//2MTR/OilTemp |  |  |  | CDC | 250 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 2-A9 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2MTR_COIL | #2MTR 線溫 | MTR | P02//2MTR/CoilTemp |  |  |  | CDC | 251 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MW | [17 empty] | 1-9F | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_MW | #1DTR二次側(A) MW | MTR | P02/11/310/MW |  |  |  | CDC | 252 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | MVAR | [17 empty] | 1-A0 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_MVAR | #1DTR二次側(A) MVAR | MTR | P02/11/310/MVAR |  |  |  | CDC | 253 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_R | [17 empty] | 1-9C | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_A1 | #1DTR二次側(A) R相AMP | MTR | P02/11/310/I_R |  |  |  | CDC | 254 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_S | [17 empty] | 1-9D | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_A2 | #1DTR二次側(A) S相AMP | MTR | P02/11/310/I_S |  |  |  | CDC | 255 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR二次側(A) |  | I_T | [17 empty] | 1-9E | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_A3 | #1DTR二次側(A) T相AMP | MTR | P02/11/310/I_T |  |  |  | CDC | 256 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | OilTemp | [17 empty] | 2-AB | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR_OIL | #1DTR 油溫 | MTR | P02//1DTR(A)/OilTemp |  |  |  | CDC | 257 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | CoilTemp | [17 empty] | 2-AC | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_COIL | #1DTR(A) 線溫 | MTR | P02//1DTR(A)/CoilTemp |  |  |  | CDC | 258 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | TapPosMv | [17 empty] | 2-AA |  | 2-10 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_TAP | #1DTR(A) OLTC TAP | MTR | P02//1DTR(A)/TapPosMv |  |  |  | CDC | 259 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MW | [17 empty] | 1-A4 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_MW | #1DTR二次側(B) MW | MTR | P02/11/320/MW |  |  |  | CDC | 260 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | MVAR | [17 empty] | 1-A5 | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_MVAR | #1DTR二次側(B) MVAR | MTR | P02/11/320/MVAR |  |  |  | CDC | 261 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_R | [17 empty] | 1-A1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_A1 | #1DTR二次側(B) R相AMP | MTR | P02/11/320/I_R |  |  |  | CDC | 262 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_S | [17 empty] | 1-A2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_A2 | #1DTR二次側(B) S相AMP | MTR | P02/11/320/I_S |  |  |  | CDC | 263 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR二次側(B) |  | I_T | [17 empty] | 1-A3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_A3 | #1DTR二次側(B) T相AMP | MTR | P02/11/320/I_T |  |  |  | CDC | 264 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR(B) |  | CoilTemp | [17 empty] | 2-AF | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_COIL | #1DTR(B) 線溫 | MTR | P02//1DTR(B)/CoilTemp |  |  |  | CDC | 265 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR(B) |  | TapPosMv | [17 empty] | 2-AD |  | 2-13 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_TAP | #1DTR(B) OLTC TAP | MTR | P02//1DTR(B)/TapPosMv |  |  |  | CDC | 266 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_MW | #2DTR二次側(A) MW | MTR | P02/11/330/MW |  |  |  | CDC | 267 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_MVAR | #2DTR二次側(A) MVAR | MTR | P02/11/330/MVAR |  |  |  | CDC | 268 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.072000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_R | [17 empty] | 1-A6 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_A1 | #2DTR二次側(A) R相AMP | MTR | P02/11/330/I_R |  |  |  | CDC | 269 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_S | [17 empty] | 1-A7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_A2 | #2DTR二次側(A) S相AMP | MTR | P02/11/330/I_S |  |  |  | CDC | 270 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR二次側(A) |  | I_T | [17 empty] | 1-A8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_A3 | #2DTR二次側(A) T相AMP | MTR | P02/11/330/I_T |  |  |  | CDC | 271 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | OilTemp | [17 empty] | 2-B1 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR_OIL | #2DTR 油溫 | MTR | P02//2DTR(A)/OilTemp |  |  |  | CDC | 272 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | CoilTemp | [17 empty] | 2-B2 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_COIL | #2DTR(A) 線溫 | MTR | P02//2DTR(A)/CoilTemp |  |  |  | CDC | 273 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | TapPosMv | [17 empty] | 2-B0 |  | 2-19 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_TAP | #2DTR(A) OLTC TAP | MTR | P02//2DTR(A)/TapPosMv |  |  |  | CDC | 274 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MW | [17 empty] | 1-AE | [5 empty] | MW_-54_54(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_MW | #2DTR二次側(B) MW | MTR | P02/11/340/MW |  |  |  | CDC | 275 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | MVAR | [17 empty] | 1-AF | [5 empty] | MVAR_-36_36(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_MVAR | #2DTR二次側(B) MVAR | MTR | P02/11/340/MVAR |  |  |  | CDC | 276 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.108000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_R | [17 empty] | 1-AB | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_A1 | #2DTR二次側(B) R相AMP | MTR | P02/11/340/I_R |  |  |  | CDC | 277 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_S | [17 empty] | 1-AC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_A2 | #2DTR二次側(B) S相AMP | MTR | P02/11/340/I_S |  |  |  | CDC | 278 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR二次側(B) |  | I_T | [17 empty] | 1-AD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_A3 | #2DTR二次側(B) T相AMP | MTR | P02/11/340/I_T |  |  |  | CDC | 279 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_1450 | 1305.000000 | 1450.000000 | 1813.000000 | 1885.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -15.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR(B) |  | CoilTemp | [17 empty] | 2-B5 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_COIL | #2DTR(B) 線溫 | MTR | P02//2DTR(B)/CoilTemp |  |  |  | CDC | 280 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR(B) |  | TapPosMv | [17 empty] | 2-B3 |  | 2-1C |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_TAP | #2DTR(B) OLTC TAP | MTR | P02//2DTR(B)/TapPosMv |  |  |  | CDC | 281 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MW | [17 empty] | 2-C5 | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_MW | #3DTR二次側(A) MW | MTR | P02/22/350/MW |  |  |  | CDC | 282 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | MVAR | [17 empty] | 2-C6 | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_MVAR | #3DTR二次側(A) MVAR | MTR | P02/22/350/MVAR |  |  |  | CDC | 283 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_R | [17 empty] | 2-C2 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_A1 | #3DTR二次側(A) R相AMP | MTR | P02/22/350/I_R |  |  |  | CDC | 284 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_S | [17 empty] | 2-C3 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_A2 | #3DTR二次側(A) S相AMP | MTR | P02/22/350/I_S |  |  |  | CDC | 285 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR二次側(A) |  | I_T | [17 empty] | 2-C4 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_A3 | #3DTR二次側(A) T相AMP | MTR | P02/22/350/I_T |  |  |  | CDC | 286 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | OilTemp | [17 empty] | 2-D2 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR_OIL | #3DTR 油溫 | MTR | P02//3DTR(A)/OilTemp |  |  |  | CDC | 287 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | CoilTemp | [17 empty] | 2-D3 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_COIL | #3DTR(A) 線溫 | MTR | P02//3DTR(A)/CoilTemp |  |  |  | CDC | 288 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | TapPosMv | [17 empty] | 2-D1 |  | 3-06 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_TAP | #3DTR(A) OLTC TAP | MTR | P02//3DTR(A)/TapPosMv |  |  |  | CDC | 289 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MW | [17 empty] | 2-CA | [5 empty] | MW_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_MW | #3DTR二次側(B) MW | MTR | P02/22/360/MW |  |  |  | CDC | 290 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | MVAR | [17 empty] | 2-CB | [5 empty] | MVAR_-72_72(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_MVAR | #3DTR二次側(B) MVAR | MTR | P02/22/360/MVAR |  |  |  | CDC | 291 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.144000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_R | [17 empty] | 2-C7 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_A1 | #3DTR二次側(B) R相AMP | MTR | P02/22/360/I_R |  |  |  | CDC | 292 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_S | [17 empty] | 2-C8 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_A2 | #3DTR二次側(B) S相AMP | MTR | P02/22/360/I_S |  |  |  | CDC | 293 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR二次側(B) |  | I_T | [17 empty] | 2-C9 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_A3 | #3DTR二次側(B) T相AMP | MTR | P02/22/360/I_T |  |  |  | CDC | 294 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_725 | 653.000000 | 725.000000 | 907.000000 | 943.000000 | 0.100000 | -10.000000 | -10.000000 | -10.000000 | -50.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR(B) |  | CoilTemp | [17 empty] | 2-D6 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_COIL | #3DTR(B) 線溫 | MTR | P02//3DTR(B)/CoilTemp |  |  |  | CDC | 295 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR(B) |  | TapPosMv | [17 empty] | 2-D4 |  | 3-07 |  |  |  | TAP_-8.5_8.5(0_2000) |  | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_TAP | #3DTR(B) OLTC TAP | MTR | P02//3DTR(B)/TapPosMv |  |  |  | CDC | 296 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | TAP8_8 | 7.000000 | 7.000000 | 8.000000 | 8.500000 | 0.000000 | -7.000000 | -7.000000 | -8.000000 | -8.500000 | 0.100000
P02 | 安南PS | 0 |  |  |  |  | DCV_N | [17 empty] | 2-BE | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.直流N電源電壓 | 直流N電源電壓 | OTHER | P02/0/StaDev/DCV_N |  |  |  | CDC | 297 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P02 | 安南PS | 0 |  |  |  |  | DCV_P | [17 empty] | 2-BD | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.直流P電源電壓 | 直流P電源電壓 | OTHER | P02/0/StaDev/DCV_P |  |  |  | CDC | 298 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南21線 | 南21線 |  | 南21線KVAR | [17 empty] | 1-D5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南21線KVAR | 11KV南21線 KVAR | FEEDER | P02/11/KT21/MVAR |  |  |  | CDC | 299 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南21線 | 南21線 |  | 南21線A1 | [17 empty] | 1-D2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南21線A1 | 11KV南21線 R相AMP | FEEDER | P02/11/KT21/I_R |  |  |  | CDC | 300 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南21線 | 南21線 |  | 南21線A2 | [17 empty] | 1-D3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南21線A2 | 11KV南21線 S相AMP | FEEDER | P02/11/KT21/I_S |  |  |  | CDC | 301 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南21線 | 南21線 |  | 南21線A3 | [17 empty] | 1-D4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南21線A3 | 11KV南21線 T相AMP | FEEDER | P02/11/KT21/I_T |  |  |  | CDC | 302 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南22線 | 南22線 |  | 南22線KVAR | [17 empty] | 1-D9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南22線KVAR | 11KV南22線 KVAR | FEEDER | P02/11/KT22/MVAR |  |  |  | CDC | 303 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南22線 | 南22線 |  | 南22線A1 | [17 empty] | 1-D6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南22線A1 | 11KV南22線 R相AMP | FEEDER | P02/11/KT22/I_R |  |  |  | CDC | 304 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南22線 | 南22線 |  | 南22線A2 | [17 empty] | 1-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南22線A2 | 11KV南22線 S相AMP | FEEDER | P02/11/KT22/I_S |  |  |  | CDC | 305 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南22線 | 南22線 |  | 南22線A3 | [17 empty] | 1-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南22線A3 | 11KV南22線 T相AMP | FEEDER | P02/11/KT22/I_T |  |  |  | CDC | 306 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南23線 | 南23線 |  | 南23線KVAR | [17 empty] | 1-DD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南23線KVAR | 11KV南23線 KVAR | FEEDER | P02/11/KT23/MVAR |  |  |  | CDC | 307 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南23線 | 南23線 |  | 南23線A1 | [17 empty] | 1-DA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南23線A1 | 11KV南23線 R相AMP | FEEDER | P02/11/KT23/I_R |  |  |  | CDC | 308 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南23線 | 南23線 |  | 南23線A2 | [17 empty] | 1-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南23線A2 | 11KV南23線 S相AMP | FEEDER | P02/11/KT23/I_S |  |  |  | CDC | 309 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南23線 | 南23線 |  | 南23線A3 | [17 empty] | 1-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南23線A3 | 11KV南23線 T相AMP | FEEDER | P02/11/KT23/I_T |  |  |  | CDC | 310 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南24線 | 南24線 |  | 南24線KVAR | [17 empty] | 1-E1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南24線KVAR | 11KV南24線 KVAR | FEEDER | P02/11/KT24/MVAR |  |  |  | CDC | 311 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南24線 | 南24線 |  | 南24線A1 | [17 empty] | 1-DE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南24線A1 | 11KV南24線 R相AMP | FEEDER | P02/11/KT24/I_R |  |  |  | CDC | 312 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南24線 | 南24線 |  | 南24線A2 | [17 empty] | 1-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南24線A2 | 11KV南24線 S相AMP | FEEDER | P02/11/KT24/I_S |  |  |  | CDC | 313 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南24線 | 南24線 |  | 南24線A3 | [17 empty] | 1-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南24線A3 | 11KV南24線 T相AMP | FEEDER | P02/11/KT24/I_T |  |  |  | CDC | 314 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南25線 | 南25線 |  | 南25線KVAR | [17 empty] | 1-E5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南25線KVAR | 11KV南25線 KVAR | FEEDER | P02/11/KT25/MVAR |  |  |  | CDC | 315 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南25線 | 南25線 |  | 南25線A1 | [17 empty] | 1-E2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南25線A1 | 11KV南25線 R相AMP | FEEDER | P02/11/KT25/I_R |  |  |  | CDC | 316 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南25線 | 南25線 |  | 南25線A2 | [17 empty] | 1-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南25線A2 | 11KV南25線 S相AMP | FEEDER | P02/11/KT25/I_S |  |  |  | CDC | 317 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南25線 | 南25線 |  | 南25線A3 | [17 empty] | 1-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南25線A3 | 11KV南25線 T相AMP | FEEDER | P02/11/KT25/I_T |  |  |  | CDC | 318 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南26線 | 南26線 |  | 南26線KVAR | [17 empty] | 1-E9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南26線KVAR | 11KV南26線 KVAR | FEEDER | P02/11/KT26/MVAR |  |  |  | CDC | 319 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南26線 | 南26線 |  | 南26線A1 | [17 empty] | 1-E6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南26線A1 | 11KV南26線 R相AMP | FEEDER | P02/11/KT26/I_R |  |  |  | CDC | 320 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南26線 | 南26線 |  | 南26線A2 | [17 empty] | 1-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南26線A2 | 11KV南26線 S相AMP | FEEDER | P02/11/KT26/I_S |  |  |  | CDC | 321 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南26線 | 南26線 |  | 南26線A3 | [17 empty] | 1-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南26線A3 | 11KV南26線 T相AMP | FEEDER | P02/11/KT26/I_T |  |  |  | CDC | 322 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南27線 | 南27線 |  | 南27線KVAR | [17 empty] | 1-ED | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南27線KVAR | 11KV南27線 KVAR | FEEDER | P02/11/KT27/MVAR |  |  |  | CDC | 323 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南27線 | 南27線 |  | 南27線A1 | [17 empty] | 1-EA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南27線A1 | 11KV南27線 R相AMP | FEEDER | P02/11/KT27/I_R |  |  |  | CDC | 324 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南27線 | 南27線 |  | 南27線A2 | [17 empty] | 1-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南27線A2 | 11KV南27線 S相AMP | FEEDER | P02/11/KT27/I_S |  |  |  | CDC | 325 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南27線 | 南27線 |  | 南27線A3 | [17 empty] | 1-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南27線A3 | 11KV南27線 T相AMP | FEEDER | P02/11/KT27/I_T |  |  |  | CDC | 326 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南28線 | 南28線 |  | 南28線KVAR | [17 empty] | 1-F1 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南28線KVAR | 11KV南28線 KVAR | FEEDER | P02/11/KT28/MVAR |  |  |  | CDC | 327 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南28線 | 南28線 |  | 南28線A1 | [17 empty] | 1-EE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南28線A1 | 11KV南28線 R相AMP | FEEDER | P02/11/KT28/I_R |  |  |  | CDC | 328 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南28線 | 南28線 |  | 南28線A2 | [17 empty] | 1-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南28線A2 | 11KV南28線 S相AMP | FEEDER | P02/11/KT28/I_S |  |  |  | CDC | 329 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南28線 | 南28線 |  | 南28線A3 | [17 empty] | 1-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南28線A3 | 11KV南28線 T相AMP | FEEDER | P02/11/KT28/I_T |  |  |  | CDC | 330 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南29線 | 南29線 |  | 南29線KVAR | [17 empty] | 1-F5 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南29線KVAR | 11KV南29線 KVAR | FEEDER | P02/11/KT29/MVAR |  |  |  | CDC | 331 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南29線 | 南29線 |  | 南29線A1 | [17 empty] | 1-F2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南29線A1 | 11KV南29線 R相AMP | FEEDER | P02/11/KT29/I_R |  |  |  | CDC | 332 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南29線 | 南29線 |  | 南29線A2 | [17 empty] | 1-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南29線A2 | 11KV南29線 S相AMP | FEEDER | P02/11/KT29/I_S |  |  |  | CDC | 333 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南29線 | 南29線 |  | 南29線A3 | [17 empty] | 1-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南29線A3 | 11KV南29線 T相AMP | FEEDER | P02/11/KT29/I_T |  |  |  | CDC | 334 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南30線 | 南30線 |  | 南30線KVAR | [17 empty] | 1-F9 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南30線KVAR | 11KV南30線 KVAR | FEEDER | P02/11/KT30/MVAR |  |  |  | CDC | 335 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南30線 | 南30線 |  | 南30線A1 | [17 empty] | 1-F6 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南30線A1 | 11KV南30線 R相AMP | FEEDER | P02/11/KT30/I_R |  |  |  | CDC | 336 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南30線 | 南30線 |  | 南30線A2 | [17 empty] | 1-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南30線A2 | 11KV南30線 S相AMP | FEEDER | P02/11/KT30/I_S |  |  |  | CDC | 337 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南30線 | 南30線 |  | 南30線A3 | [17 empty] | 1-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南30線A3 | 11KV南30線 T相AMP | FEEDER | P02/11/KT30/I_T |  |  |  | CDC | 338 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南31線 | 南31線 |  | 南31線KVAR | [17 empty] | 1-FD | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南31線KVAR | 11KV南31線 KVAR | FEEDER | P02/11/KT31/MVAR |  |  |  | CDC | 339 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南31線 | 南31線 |  | 南31線A1 | [17 empty] | 1-FA | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南31線A1 | 11KV南31線 R相AMP | FEEDER | P02/11/KT31/I_R |  |  |  | CDC | 340 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南31線 | 南31線 |  | 南31線A2 | [17 empty] | 1-FB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南31線A2 | 11KV南31線 S相AMP | FEEDER | P02/11/KT31/I_S |  |  |  | CDC | 341 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南31線 | 南31線 |  | 南31線A3 | [17 empty] | 1-FC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南31線A3 | 11KV南31線 T相AMP | FEEDER | P02/11/KT31/I_T |  |  |  | CDC | 342 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南32線 | 南32線 |  | 南32線KVAR | [17 empty] | 2-83 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南32線KVAR | 11KV南32線 KVAR | FEEDER | P02/11/KT32/MVAR |  |  |  | CDC | 343 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南32線 | 南32線 |  | 南32線A1 | [17 empty] | 1-FE | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南32線A1 | 11KV南32線 R相AMP | FEEDER | P02/11/KT32/I_R |  |  |  | CDC | 344 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南32線 | 南32線 |  | 南32線A2 | [17 empty] | 1-FF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南32線A2 | 11KV南32線 S相AMP | FEEDER | P02/11/KT32/I_S |  |  |  | CDC | 345 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南32線 | 南32線 |  | 南32線A3 | [17 empty] | 2-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南32線A3 | 11KV南32線 T相AMP | FEEDER | P02/11/KT32/I_T |  |  |  | CDC | 346 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南33線 | 南33線 |  | 南33線KVAR | [17 empty] | 2-87 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南33線KVAR | 11KV南33線 KVAR | FEEDER | P02/11/KT33/MVAR |  |  |  | CDC | 347 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南33線 | 南33線 |  | 南33線A1 | [17 empty] | 2-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南33線A1 | 11KV南33線 R相AMP | FEEDER | P02/11/KT33/I_R |  |  |  | CDC | 348 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南33線 | 南33線 |  | 南33線A2 | [17 empty] | 2-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南33線A2 | 11KV南33線 S相AMP | FEEDER | P02/11/KT33/I_S |  |  |  | CDC | 349 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南33線 | 南33線 |  | 南33線A3 | [17 empty] | 2-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南33線A3 | 11KV南33線 T相AMP | FEEDER | P02/11/KT33/I_T |  |  |  | CDC | 350 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南34線 | 南34線 |  | 南34線KVAR | [17 empty] | 2-8B | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南34線KVAR | 11KV南34線 KVAR | FEEDER | P02/11/KT34/MVAR |  |  |  | CDC | 351 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南34線 | 南34線 |  | 南34線A1 | [17 empty] | 2-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南34線A1 | 11KV南34線 R相AMP | FEEDER | P02/11/KT34/I_R |  |  |  | CDC | 352 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南34線 | 南34線 |  | 南34線A2 | [17 empty] | 2-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南34線A2 | 11KV南34線 S相AMP | FEEDER | P02/11/KT34/I_S |  |  |  | CDC | 353 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南34線 | 南34線 |  | 南34線A3 | [17 empty] | 2-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南34線A3 | 11KV南34線 T相AMP | FEEDER | P02/11/KT34/I_T |  |  |  | CDC | 354 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南35線 | 南35線 |  | 南35線KVAR | [17 empty] | 2-8F | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南35線KVAR | 11KV南35線 KVAR | FEEDER | P02/11/KT35/MVAR |  |  |  | CDC | 355 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南35線 | 南35線 |  | 南35線A1 | [17 empty] | 2-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南35線A1 | 11KV南35線 R相AMP | FEEDER | P02/11/KT35/I_R |  |  |  | CDC | 356 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南35線 | 南35線 |  | 南35線A2 | [17 empty] | 2-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南35線A2 | 11KV南35線 S相AMP | FEEDER | P02/11/KT35/I_S |  |  |  | CDC | 357 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南35線 | 南35線 |  | 南35線A3 | [17 empty] | 2-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南35線A3 | 11KV南35線 T相AMP | FEEDER | P02/11/KT35/I_T |  |  |  | CDC | 358 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南36線 | 南36線 |  | 南36線KVAR | [17 empty] | 2-93 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南36線KVAR | 11KV南36線 KVAR | FEEDER | P02/11/KT36/MVAR |  |  |  | CDC | 359 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南36線 | 南36線 |  | 南36線A1 | [17 empty] | 2-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南36線A1 | 11KV南36線 R相AMP | FEEDER | P02/11/KT36/I_R |  |  |  | CDC | 360 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南36線 | 南36線 |  | 南36線A2 | [17 empty] | 2-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南36線A2 | 11KV南36線 S相AMP | FEEDER | P02/11/KT36/I_S |  |  |  | CDC | 361 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南36線 | 南36線 |  | 南36線A3 | [17 empty] | 2-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南36線A3 | 11KV南36線 T相AMP | FEEDER | P02/11/KT36/I_T |  |  |  | CDC | 362 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南37線 | 南37線 |  | 南37線KVAR | [17 empty] | 2-97 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南37線KVAR | 11KV南37線 KVAR | FEEDER | P02/11/KT37/MVAR |  |  |  | CDC | 363 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南37線 | 南37線 |  | 南37線A1 | [17 empty] | 2-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南37線A1 | 11KV南37線 R相AMP | FEEDER | P02/11/KT37/I_R |  |  |  | CDC | 364 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南37線 | 南37線 |  | 南37線A2 | [17 empty] | 2-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南37線A2 | 11KV南37線 S相AMP | FEEDER | P02/11/KT37/I_S |  |  |  | CDC | 365 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南37線 | 南37線 |  | 南37線A3 | [17 empty] | 2-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南37線A3 | 11KV南37線 T相AMP | FEEDER | P02/11/KT37/I_T |  |  |  | CDC | 366 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南38線 | 南38線 |  | 南38線KVAR | [17 empty] | 2-9B | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南38線KVAR | 11KV南38線 KVAR | FEEDER | P02/11/KT38/MVAR |  |  |  | CDC | 367 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南38線 | 南38線 |  | 南38線A1 | [17 empty] | 2-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南38線A1 | 11KV南38線 R相AMP | FEEDER | P02/11/KT38/I_R |  |  |  | CDC | 368 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南38線 | 南38線 |  | 南38線A2 | [17 empty] | 2-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南38線A2 | 11KV南38線 S相AMP | FEEDER | P02/11/KT38/I_S |  |  |  | CDC | 369 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南38線 | 南38線 |  | 南38線A3 | [17 empty] | 2-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南38線A3 | 11KV南38線 T相AMP | FEEDER | P02/11/KT38/I_T |  |  |  | CDC | 370 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南39線 | 南39線 |  | 南39線KVAR | [17 empty] | 2-9F | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南39線KVAR | 11KV南39線 KVAR | FEEDER | P02/11/KT39/MVAR |  |  |  | CDC | 371 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南39線 | 南39線 |  | 南39線A1 | [17 empty] | 2-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南39線A1 | 11KV南39線 R相AMP | FEEDER | P02/11/KT39/I_R |  |  |  | CDC | 372 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南39線 | 南39線 |  | 南39線A2 | [17 empty] | 2-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南39線A2 | 11KV南39線 S相AMP | FEEDER | P02/11/KT39/I_S |  |  |  | CDC | 373 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南39線 | 南39線 |  | 南39線A3 | [17 empty] | 2-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南39線A3 | 11KV南39線 T相AMP | FEEDER | P02/11/KT39/I_T |  |  |  | CDC | 374 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南40線 | 南40線 |  | 南40線KVAR | [17 empty] | 2-A3 | [5 empty] | KVAR_-10800_10800(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南40線KVAR | 11KV南40線 KVAR | FEEDER | P02/11/KT40/MVAR |  |  |  | CDC | 375 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 10.800000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南40線 | 南40線 |  | 南40線A1 | [17 empty] | 2-A0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南40線A1 | 11KV南40線 R相AMP | FEEDER | P02/11/KT40/I_R |  |  |  | CDC | 376 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南40線 | 南40線 |  | 南40線A2 | [17 empty] | 2-A1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南40線A2 | 11KV南40線 S相AMP | FEEDER | P02/11/KT40/I_S |  |  |  | CDC | 377 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南40線 | 南40線 |  | 南40線A3 | [17 empty] | 2-A2 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南40線A3 | 11KV南40線 T相AMP | FEEDER | P02/11/KT40/I_T |  |  |  | CDC | 378 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南71線 | 南71線 |  | 南71線KVAR | [17 empty] | 2-DA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南71線KVAR | 23KV南71線 KVAR | FEEDER | P02/22/KT71/MVAR |  |  |  | CDC | 379 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南71線 | 南71線 |  | 南71線A1 | [17 empty] | 2-D7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南71線A1 | 23KV南71線 R相AMP | FEEDER | P02/22/KT71/I_R |  |  |  | CDC | 380 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南71線 | 南71線 |  | 南71線A2 | [17 empty] | 2-D8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南71線A2 | 23KV南71線 S相AMP | FEEDER | P02/22/KT71/I_S |  |  |  | CDC | 381 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南71線 | 南71線 |  | 南71線A3 | [17 empty] | 2-D9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南71線A3 | 23KV南71線 T相AMP | FEEDER | P02/22/KT71/I_T |  |  |  | CDC | 382 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南72線 | 南72線 |  | 南72線KVAR | [17 empty] | 2-DE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南72線KVAR | 23KV南72線 KVAR | FEEDER | P02/22/KT72/MVAR |  |  |  | CDC | 383 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南72線 | 南72線 |  | 南72線A1 | [17 empty] | 2-DB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南72線A1 | 23KV南72線 R相AMP | FEEDER | P02/22/KT72/I_R |  |  |  | CDC | 384 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南72線 | 南72線 |  | 南72線A2 | [17 empty] | 2-DC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南72線A2 | 23KV南72線 S相AMP | FEEDER | P02/22/KT72/I_S |  |  |  | CDC | 385 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南72線 | 南72線 |  | 南72線A3 | [17 empty] | 2-DD | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南72線A3 | 23KV南72線 T相AMP | FEEDER | P02/22/KT72/I_T |  |  |  | CDC | 386 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南73線 | 南73線 |  | 南73線KVAR | [17 empty] | 2-E2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南73線KVAR | 23KV南73線 KVAR | FEEDER | P02/22/KT73/MVAR |  |  |  | CDC | 387 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南73線 | 南73線 |  | 南73線A1 | [17 empty] | 2-DF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南73線A1 | 23KV南73線 R相AMP | FEEDER | P02/22/KT73/I_R |  |  |  | CDC | 388 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南73線 | 南73線 |  | 南73線A2 | [17 empty] | 2-E0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南73線A2 | 23KV南73線 S相AMP | FEEDER | P02/22/KT73/I_S |  |  |  | CDC | 389 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南73線 | 南73線 |  | 南73線A3 | [17 empty] | 2-E1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南73線A3 | 23KV南73線 T相AMP | FEEDER | P02/22/KT73/I_T |  |  |  | CDC | 390 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南74線 | 南74線 |  | 南74線KVAR | [17 empty] | 2-E6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南74線KVAR | 23KV南74線 KVAR | FEEDER | P02/22/KT74/MVAR |  |  |  | CDC | 391 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南74線 | 南74線 |  | 南74線A1 | [17 empty] | 2-E3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南74線A1 | 23KV南74線 R相AMP | FEEDER | P02/22/KT74/I_R |  |  |  | CDC | 392 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南74線 | 南74線 |  | 南74線A2 | [17 empty] | 2-E4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南74線A2 | 23KV南74線 S相AMP | FEEDER | P02/22/KT74/I_S |  |  |  | CDC | 393 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南74線 | 南74線 |  | 南74線A3 | [17 empty] | 2-E5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南74線A3 | 23KV南74線 T相AMP | FEEDER | P02/22/KT74/I_T |  |  |  | CDC | 394 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南75線 | 南75線 |  | 南75線KVAR | [17 empty] | 2-EA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南75線KVAR | 23KV南75線 KVAR | FEEDER | P02/22/KT75/MVAR |  |  |  | CDC | 395 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南75線 | 南75線 |  | 南75線A1 | [17 empty] | 2-E7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南75線A1 | 23KV南75線 R相AMP | FEEDER | P02/22/KT75/I_R |  |  |  | CDC | 396 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南75線 | 南75線 |  | 南75線A2 | [17 empty] | 2-E8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南75線A2 | 23KV南75線 S相AMP | FEEDER | P02/22/KT75/I_S |  |  |  | CDC | 397 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南75線 | 南75線 |  | 南75線A3 | [17 empty] | 2-E9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南75線A3 | 23KV南75線 T相AMP | FEEDER | P02/22/KT75/I_T |  |  |  | CDC | 398 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南76線 | 南76線 |  | 南76線KVAR | [17 empty] | 2-EE | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南76線KVAR | 23KV南76線 KVAR | FEEDER | P02/22/KT76/MVAR |  |  |  | CDC | 399 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南76線 | 南76線 |  | 南76線A1 | [17 empty] | 2-EB | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南76線A1 | 23KV南76線 R相AMP | FEEDER | P02/22/KT76/I_R |  |  |  | CDC | 400 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南76線 | 南76線 |  | 南76線A2 | [17 empty] | 2-EC | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南76線A2 | 23KV南76線 S相AMP | FEEDER | P02/22/KT76/I_S |  |  |  | CDC | 401 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南76線 | 南76線 |  | 南76線A3 | [17 empty] | 2-ED | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南76線A3 | 23KV南76線 T相AMP | FEEDER | P02/22/KT76/I_T |  |  |  | CDC | 402 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南77線 | 南77線 |  | 南77線KVAR | [17 empty] | 2-F2 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南77線KVAR | 23KV南77線 KVAR | FEEDER | P02/22/KT77/MVAR |  |  |  | CDC | 403 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南77線 | 南77線 |  | 南77線A1 | [17 empty] | 2-EF | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南77線A1 | 23KV南77線 R相AMP | FEEDER | P02/22/KT77/I_R |  |  |  | CDC | 404 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南77線 | 南77線 |  | 南77線A2 | [17 empty] | 2-F0 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南77線A2 | 23KV南77線 S相AMP | FEEDER | P02/22/KT77/I_S |  |  |  | CDC | 405 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南77線 | 南77線 |  | 南77線A3 | [17 empty] | 2-F1 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南77線A3 | 23KV南77線 T相AMP | FEEDER | P02/22/KT77/I_T |  |  |  | CDC | 406 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南78線 | 南78線 |  | 南78線KVAR | [17 empty] | 2-F6 | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南78線KVAR | 23KV南78線 KVAR | FEEDER | P02/22/KT78/MVAR |  |  |  | CDC | 407 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南78線 | 南78線 |  | 南78線A1 | [17 empty] | 2-F3 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南78線A1 | 23KV南78線 R相AMP | FEEDER | P02/22/KT78/I_R |  |  |  | CDC | 408 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南78線 | 南78線 |  | 南78線A2 | [17 empty] | 2-F4 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南78線A2 | 23KV南78線 S相AMP | FEEDER | P02/22/KT78/I_S |  |  |  | CDC | 409 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南78線 | 南78線 |  | 南78線A3 | [17 empty] | 2-F5 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南78線A3 | 23KV南78線 T相AMP | FEEDER | P02/22/KT78/I_T |  |  |  | CDC | 410 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南79線 | 南79線 |  | 南79線KVAR | [17 empty] | 2-FA | [5 empty] | KVAR_-21600_21600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南79線KVAR | 23KV南79線 KVAR | FEEDER | P02/22/KT79/MVAR |  |  |  | CDC | 411 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_KVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 21.600000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南79線 | 南79線 |  | 南79線A1 | [17 empty] | 2-F7 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南79線A1 | 23KV南79線 R相AMP | FEEDER | P02/22/KT79/I_R |  |  |  | CDC | 412 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R480R | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | 8.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南79線 | 南79線 |  | 南79線A2 | [17 empty] | 2-F8 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南79線A2 | 23KV南79線 S相AMP | FEEDER | P02/22/KT79/I_S |  |  |  | CDC | 413 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南79線 | 南79線 |  | 南79線A3 | [17 empty] | 2-F9 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南79線A3 | 23KV南79線 T相AMP | FEEDER | P02/22/KT79/I_T |  |  |  | CDC | 414 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C06R0480 | 432.000000 | 432.000000 | 480.000000 | 600.000000 | 1.250000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | MW | [17 empty] | 2-B6 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1550_MW | 安南南濱一路 MW | LINE161 | P02/161/1550/MW |  |  |  | CDC | 415 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | MVAR | [17 empty] | 2-B7 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1550_MVAR | 安南南濱一路 MVAR | LINE161 | P02/161/1550/MVAR |  |  |  | CDC | 416 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | MW | [17 empty] | 2-B8 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1560_MW | 安南南濱二路 MW | LINE161 | P02/161/1560/MW |  |  |  | CDC | 417 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | MVAR | [17 empty] | 2-B9 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1560_MVAR | 安南南濱二路 MVAR | LINE161 | P02/161/1560/MVAR |  |  |  | CDC | 418 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | MW | [17 empty] | 1-BB | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.620_MW | 安南運河線 MW | LINE69 | P02/69/620/MW |  |  |  | CDC | 419 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | MVAR | [17 empty] | 1-BC | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.620_MVAR | 安南運河線 MVAR | LINE69 | P02/69/620/MVAR |  |  |  | CDC | 420 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P02 | 安南PS | 11 | 11kV | _100 | 100 |  | I_R | [17 empty] | 1-CC | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV_100_A1 | 11KV 100 R相AMP | TIE | P02/11/100/I_R |  |  |  | CDC | 421 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | _100 | 100 |  | I_S | [17 empty] | 1-CD | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV_100_A2 | 11KV 100 S相AMP | TIE | P02/11/100/I_S |  |  |  | CDC | 422 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | _100 | 100 |  | I_T | [17 empty] | 1-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV_100_A3 | 11KV 100 T相AMP | TIE | P02/11/100/I_T |  |  |  | CDC | 423 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | _200 | 200 |  | I_R | [17 empty] | 1-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV_200_A1 | 11KV 200 R相AMP | TIE | P02/11/200/I_R |  |  |  | CDC | 424 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | _200 | 200 |  | I_S | [17 empty] | 1-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV_200_A2 | 11KV 200 S相AMP | TIE | P02/11/200/I_S |  |  |  | CDC | 425 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | _200 | 200 |  | I_T | [17 empty] | 1-D1 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.11KV_200_A3 | 11KV 200 T相AMP | TIE | P02/11/200/I_T |  |  |  | CDC | 426 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | C20R1000 | 900.000000 | 900.000000 | 1000.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | _300 | 300 |  | I_R | [17 empty] | 2-CE | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.23KV_300_A1 | 23KV 300 R相AMP | TIE | P02/22/300/I_R |  |  |  | CDC | 427 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | _300 | 300 |  | I_S | [17 empty] | 2-CF | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.23KV_300_A2 | 23KV 300 S相AMP | TIE | P02/22/300/I_S |  |  |  | CDC | 428 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | _300 | 300 |  | I_T | [17 empty] | 2-D0 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.23KV_300_A3 | 23KV 300 T相AMP | TIE | P02/22/300/I_T |  |  |  | CDC | 429 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | C20R0750 | 675.000000 | 675.000000 | 750.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南21線 | 南21線 |  | 南21線A0 | [17 empty] | 3-82 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南21線A0 | 11KV南21線 N相AMP | FEEDER | P02/11/KT21/I_N |  |  |  | CDC | 430 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南22線 | 南22線 |  | 南22線A0 | [17 empty] | 3-83 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南22線A0 | 11KV南22線 N相AMP | FEEDER | P02/11/KT22/I_N |  |  |  | CDC | 431 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南23線 | 南23線 |  | 南23線A0 | [17 empty] | 3-84 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南23線A0 | 11KV南23線 N相AMP | FEEDER | P02/11/KT23/I_N |  |  |  | CDC | 432 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南24線 | 南24線 |  | 南24線A0 | [17 empty] | 3-85 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南24線A0 | 11KV南24線 N相AMP | FEEDER | P02/11/KT24/I_N |  |  |  | CDC | 433 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南25線 | 南25線 |  | 南25線A0 | [17 empty] | 3-86 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南25線A0 | 11KV南25線 N相AMP | FEEDER | P02/11/KT25/I_N |  |  |  | CDC | 434 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南26線 | 南26線 |  | 南26線A0 | [17 empty] | 3-87 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南26線A0 | 11KV南26線 N相AMP | FEEDER | P02/11/KT26/I_N |  |  |  | CDC | 435 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南27線 | 南27線 |  | 南27線A0 | [17 empty] | 3-88 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南27線A0 | 11KV南27線 N相AMP | FEEDER | P02/11/KT27/I_N |  |  |  | CDC | 436 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南28線 | 南28線 |  | 南28線A0 | [17 empty] | 3-89 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南28線A0 | 11KV南28線 N相AMP | FEEDER | P02/11/KT28/I_N |  |  |  | CDC | 437 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南29線 | 南29線 |  | 南29線A0 | [17 empty] | 3-8A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南29線A0 | 11KV南29線 N相AMP | FEEDER | P02/11/KT29/I_N |  |  |  | CDC | 438 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南30線 | 南30線 |  | 南30線A0 | [17 empty] | 3-8B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南30線A0 | 11KV南30線 N相AMP | FEEDER | P02/11/KT30/I_N |  |  |  | CDC | 439 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南31線 | 南31線 |  | 南31線A0 | [17 empty] | 3-8C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南31線A0 | 11KV南31線 N相AMP | FEEDER | P02/11/KT31/I_N |  |  |  | CDC | 440 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南32線 | 南32線 |  | 南32線A0 | [17 empty] | 3-8D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南32線A0 | 11KV南32線 N相AMP | FEEDER | P02/11/KT32/I_N |  |  |  | CDC | 441 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南33線 | 南33線 |  | 南33線A0 | [17 empty] | 3-8E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南33線A0 | 11KV南33線 N相AMP | FEEDER | P02/11/KT33/I_N |  |  |  | CDC | 442 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南34線 | 南34線 |  | 南34線A0 | [17 empty] | 3-8F | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南34線A0 | 11KV南34線 N相AMP | FEEDER | P02/11/KT34/I_N |  |  |  | CDC | 443 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南35線 | 南35線 |  | 南35線A0 | [17 empty] | 3-90 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南35線A0 | 11KV南35線 N相AMP | FEEDER | P02/11/KT35/I_N |  |  |  | CDC | 444 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南36線 | 南36線 |  | 南36線A0 | [17 empty] | 3-91 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南36線A0 | 11KV南36線 N相AMP | FEEDER | P02/11/KT36/I_N |  |  |  | CDC | 445 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南37線 | 南37線 |  | 南37線A0 | [17 empty] | 3-92 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南37線A0 | 11KV南37線 N相AMP | FEEDER | P02/11/KT37/I_N |  |  |  | CDC | 446 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南38線 | 南38線 |  | 南38線A0 | [17 empty] | 3-93 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南38線A0 | 11KV南38線 N相AMP | FEEDER | P02/11/KT38/I_N |  |  |  | CDC | 447 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南39線 | 南39線 |  | 南39線A0 | [17 empty] | 3-94 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南39線A0 | 11KV南39線 N相AMP | FEEDER | P02/11/KT39/I_N |  |  |  | CDC | 448 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 11 | 11kV | 南40線 | 南40線 |  | 南40線A0 | [17 empty] | 3-95 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南40線A0 | 11KV南40線 N相AMP | FEEDER | P02/11/KT40/I_N |  |  |  | CDC | 449 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南71線 | 南71線 |  | 南71線A0 | [17 empty] | 3-96 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南71線A0 | 23KV南71線 N相AMP | FEEDER | P02/22/KT71/I_N |  |  |  | CDC | 450 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南72線 | 南72線 |  | 南72線A0 | [17 empty] | 3-97 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南72線A0 | 23KV南72線 N相AMP | FEEDER | P02/22/KT72/I_N |  |  |  | CDC | 451 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南73線 | 南73線 |  | 南73線A0 | [17 empty] | 3-98 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南73線A0 | 23KV南73線 N相AMP | FEEDER | P02/22/KT73/I_N |  |  |  | CDC | 452 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南74線 | 南74線 |  | 南74線A0 | [17 empty] | 3-99 | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南74線A0 | 23KV南74線 N相AMP | FEEDER | P02/22/KT74/I_N |  |  |  | CDC | 453 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南75線 | 南75線 |  | 南75線A0 | [17 empty] | 3-9A | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南75線A0 | 23KV南75線 N相AMP | FEEDER | P02/22/KT75/I_N |  |  |  | CDC | 454 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南76線 | 南76線 |  | 南76線A0 | [17 empty] | 3-9B | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南76線A0 | 23KV南76線 N相AMP | FEEDER | P02/22/KT76/I_N |  |  |  | CDC | 455 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南77線 | 南77線 |  | 南77線A0 | [17 empty] | 3-9C | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南77線A0 | 23KV南77線 N相AMP | FEEDER | P02/22/KT77/I_N |  |  |  | CDC | 456 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南78線 | 南78線 |  | 南78線A0 | [17 empty] | 3-9D | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南78線A0 | 23KV南78線 N相AMP | FEEDER | P02/22/KT78/I_N |  |  |  | CDC | 457 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 22 | 22kV | 南79線 | 南79線 |  | 南79線A0 | [17 empty] | 3-9E | [5 empty] | A_-600_600(-2000_2000) |  | DDCS4_1 | [8 empty] | 安南PS.南79線A0 | 23KV南79線 N相AMP | FEEDER | P02/22/KT79/I_N |  |  |  | CDC | 458 | GENERICAIPoint | PS013_L3 | CDC2_AI |  | AI | [17 empty] | LGA0_100 | 80.000000 | 90.000000 | 95.000000 | 600.000000 | 0.500000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1510_OF | 安南小北一路 |  | R | [17 empty] | 2-AE | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1510_OF_R | 安南小北一路 R相 油壓 | OTHER | P02/161/1510/OilPreR |  |  |  | CDC | 459 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1510_OF | 安南小北一路 |  | S | [17 empty] | 2-B4 | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1510_OF_S | 安南小北一路 S相 油壓 | OTHER | P02/161/1510/OilPreS |  |  |  | CDC | 460 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1510_OF | 安南小北一路 |  | T | [17 empty] | 2-BF | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1510_OF_T | 安南小北一路 T相 油壓 | OTHER | P02/161/1510/OilPreT |  |  |  | CDC | 461 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1520_OF | 安南小北二路 |  | R | [17 empty] | 2-BA | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1520_OF_R | 安南小北二路 R相 油壓 | OTHER | P02/161/1520/OilPreR |  |  |  | CDC | 462 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1520_OF | 安南小北二路 |  | S | [17 empty] | 2-BB | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1520_OF_S | 安南小北二路 S相 油壓 | OTHER | P02/161/1520/OilPreS |  |  |  | CDC | 463 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 0 |  | 1520_OF | 安南小北二路 |  | T | [17 empty] | 2-BC | [5 empty] | OilPre_-9.3_9.3(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1520_OF_T | 安南小北二路 T相 油壓 | OTHER | P02/161/1520/OilPreT |  |  |  | CDC | 464 | GENERICAIPoint | PS013_L2 | CDC2_AI |  | AI | [17 empty] | KG_10 | 8.000000 | 9.000000 | 10.000000 | 20.000000 | 0.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 1.000000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | MW | [17 empty] | 1-8C | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1740_MW | 安南和順線 MW | LINE161 | P02/161/1740/MW |  |  |  | CDC | 465 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | MVAR | [17 empty] | 1-8D | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_S | [8 empty] | 安南PS.1740_MVAR | 安南和順線 MVAR | LINE161 | P02/161/1740/MVAR |  |  |  | CDC | 466 | GENERICAIPoint | PS013_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | GDA | [17 empty] | 1-11-03 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1510_GDA | 安南小北一路(1510) 接地RY | LINE161 | P02/161/1510/GDA |  |  |  | CDC | 467 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | CB | [17 empty] | 1-11-00 |  | 2-3E | [5 empty] | 161KV_S | [8 empty] | 安南PS.1510_CB | 1510(安南小北一路) CB | LINE161 | P02/161/1510/CB |  |  |  | CDC | 468 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | DS1 | 1511 | [16 empty] | 1-31-00 | 1-31-01 | 1-0F | [5 empty] | ADCS_S | [8 empty] | 安南PS.1511_DS | 1511(安南小北一路) DS | LINE161 | P02/161/1510/DS1 |  |  |  | CDC | 469 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | DS2 | 1512 | [16 empty] | 1-31-02 | 1-31-03 | 1-10 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1512_DS | 1512(安南小北一路) DS | LINE161 | P02/161/1510/DS2 |  |  |  | CDC | 470 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | DS3 | 1513 | [16 empty] | 1-31-04 | 1-31-05 | 1-11 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1513_DS | 1513(安南小北一路) DS | LINE161 | P02/161/1510/DS3 |  |  |  | CDC | 471 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | E3 | 1513E | [16 empty] | 1-31-06 | 1-31-07 | 1-12 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1513E_ES | 1513E(安南小北一路) ES | LINE161 | P02/161/1510/ES3 |  |  |  | CDC | 472 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | GDA | [17 empty] | 1-11-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1520_GDA | 安南小北二路(1520) 接地RY | LINE161 | P02/161/1520/GDA |  |  |  | CDC | 473 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | CB | [17 empty] | 1-11-04 |  | 2-3F | [5 empty] | 161KV_S | [8 empty] | 安南PS.1520_CB | 1520(安南小北二路) CB | LINE161 | P02/161/1520/CB |  |  |  | CDC | 474 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | DS1 | 1521 | [16 empty] | 1-31-08 | 1-31-09 | 1-15 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1521_DS | 1521(安南小北二路) DS | LINE161 | P02/161/1520/DS1 |  |  |  | CDC | 475 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | DS2 | 1522 | [16 empty] | 1-31-10 | 1-31-11 | 1-16 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1522_DS | 1522(安南小北二路) DS | LINE161 | P02/161/1520/DS2 |  |  |  | CDC | 476 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | DS3 | 1523 | [16 empty] | 1-31-12 | 1-31-13 | 1-17 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1523_DS | 1523(安南小北二路) DS | LINE161 | P02/161/1520/DS3 |  |  |  | CDC | 477 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | E3 | 1523E | [16 empty] | 1-31-14 | 1-31-15 | 1-18 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1523E_ES | 1523E(安南小北二路) ES | LINE161 | P02/161/1520/ES3 |  |  |  | CDC | 478 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | GDA | [17 empty] | 1-10-03 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1530_GDA | 安南鹽行線(1530) 接地RY | LINE161 | P02/161/1530/GDA |  |  |  | CDC | 479 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | CB | [17 empty] | 1-10-00 |  | 2-3C | [5 empty] | 161KV_S | [8 empty] | 安南PS.1530_CB | 1530(安南鹽行線) CB | LINE161 | P02/161/1530/CB |  |  |  | CDC | 480 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | 79UL | [17 empty] | 1-39-01 |  | 1-01 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1530_79UL | 安南鹽行線(1530) 79RY U/L | LINE161 | P02/161/1530/79UL |  |  |  | CDC | 481 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | DS1 | 1531 | [16 empty] | 1-32-00 | 1-32-01 | 1-03 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1531_DS | 1531(安南鹽行線) DS | LINE161 | P02/161/1530/DS1 |  |  |  | CDC | 482 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | DS2 | 1532 | [16 empty] | 1-32-02 | 1-32-03 | 1-04 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1532_DS | 1532(安南鹽行線) DS | LINE161 | P02/161/1530/DS2 |  |  |  | CDC | 483 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | DS3 | 1533 | [16 empty] | 1-32-04 | 1-32-05 | 1-05 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1533_DS | 1533(安南鹽行線) DS | LINE161 | P02/161/1530/DS3 |  |  |  | CDC | 484 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | E3 | 1533E | [16 empty] | 1-32-06 | 1-32-07 | 1-06 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1533E_ES | 1533E(安南鹽行線) ES | LINE161 | P02/161/1530/ES3 |  |  |  | CDC | 485 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | GDA | [17 empty] | 1-10-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1710_GDA | 山上豐華紅線(1710) 接地RY | LINE161 | P02/161/1710/GDA |  |  |  | CDC | 486 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | CB | [17 empty] | 1-10-04 |  | 2-3D | [5 empty] | 161KV_S | [8 empty] | 安南PS.1710_CB | 1710(山上豐華紅線) CB | LINE161 | P02/161/1710/CB |  |  |  | CDC | 487 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | 79UL | [17 empty] | 1-39-03 |  | 1-07 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1710_79UL | 山上豐華紅線(1710) 79RY U/L | LINE161 | P02/161/1710/79UL |  |  |  | CDC | 488 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | DS1 | 1711 | [16 empty] | 1-32-08 | 1-32-09 | 1-09 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1711_DS | 1711(山上豐華紅線) DS | LINE161 | P02/161/1710/DS1 |  |  |  | CDC | 489 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | DS2 | 1712 | [16 empty] | 1-32-10 | 1-32-11 | 1-0A | [5 empty] | ADCS_S | [8 empty] | 安南PS.1712_DS | 1712(山上豐華紅線) DS | LINE161 | P02/161/1710/DS2 |  |  |  | CDC | 490 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | DS3 | 1713 | [16 empty] | 1-32-12 | 1-32-13 | 1-0B | [5 empty] | ADCS_S | [8 empty] | 安南PS.1713_DS | 1713(山上豐華紅線) DS | LINE161 | P02/161/1710/DS3 |  |  |  | CDC | 491 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | E3 | 1713E | [16 empty] | 1-32-14 | 1-32-15 | 1-0C | [5 empty] | ADCS_S | [8 empty] | 安南PS.1713E_ES | 1713E(山上豐華紅線) ES | LINE161 | P02/161/1710/ES3 |  |  |  | CDC | 492 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | GDA | [17 empty] | 1-12-03 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1720_GDA | 道爺安南新化線(1720) 接地RY | LINE161 | P02/161/1720/GDA |  |  |  | CDC | 493 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | CB | [17 empty] | 1-12-00 |  | 2-40 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1720_CB | 1720(道爺安南新化線) CB | LINE161 | P02/161/1720/CB |  |  |  | CDC | 494 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | 79UL | [17 empty] | 1-39-09 |  | 1-19 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1720_79UL | 道爺安南新化線(1720) 79RY U/L | LINE161 | P02/161/1720/79UL |  |  |  | CDC | 495 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | DS1 | 1721 | [16 empty] | 1-33-00 | 1-33-01 | 1-1B | [5 empty] | ADCS_S | [8 empty] | 安南PS.1721_DS | 1721(道爺安南新化線) DS | LINE161 | P02/161/1720/DS1 |  |  |  | CDC | 496 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | DS2 | 1722 | [16 empty] | 1-33-02 | 1-33-03 | 1-1C | [5 empty] | ADCS_S | [8 empty] | 安南PS.1722_DS | 1722(道爺安南新化線) DS | LINE161 | P02/161/1720/DS2 |  |  |  | CDC | 497 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | DS3 | 1723 | [16 empty] | 1-33-04 | 1-33-05 | 1-1D | [5 empty] | ADCS_S | [8 empty] | 安南PS.1723_DS | 1723(道爺安南新化線) DS | LINE161 | P02/161/1720/DS3 |  |  |  | CDC | 498 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | E3 | 1723E | [16 empty] | 1-33-06 | 1-33-07 | 1-1E | [5 empty] | ADCS_S | [8 empty] | 安南PS.1723E_ES | 1723E(道爺安南新化線) ES | LINE161 | P02/161/1720/ES3 |  |  |  | CDC | 499 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | PHA | [17 empty] | 1-00-05 | [7 empty] | 69KV_S | [8 empty] | 安南PS.630_PHA | 安順白線(630) 相間RY | LINE69 | P02/69/630/51A |  |  |  | CDC | 500 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | GDA | [17 empty] | 1-00-07 | [7 empty] | 69KV_S | [8 empty] | 安南PS.630_GDA | 安順白線(630) 接地RY | LINE69 | P02/69/630/51NA |  |  |  | CDC | 501 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | CB | [17 empty] | 1-00-04 |  | 1-2B | [5 empty] | 69KV_S | [8 empty] | 安南PS.630_CB | 630(安順白線) CB | LINE69 | P02/69/630/CB |  |  |  | CDC | 502 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | DS1 | 631 | [16 empty] | 1-35-00 | 1-35-01 | 1-2D | [5 empty] | ADCS_S | [8 empty] | 安南PS.631_DS | 631(安順白線) DS | LINE69 | P02/69/630/DS1 |  |  |  | CDC | 503 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | DS2 | 632 | [16 empty] | 1-35-02 | 1-35-03 | 1-2E | [5 empty] | ADCS_S | [8 empty] | 安南PS.632_DS | 632(安順白線) DS | LINE69 | P02/69/630/DS2 |  |  |  | CDC | 504 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | DS3 | 633 | [16 empty] | 1-35-04 | 1-35-05 | 1-2F | [5 empty] | ADCS_S | [8 empty] | 安南PS.633_DS | 633(安順白線) DS | LINE69 | P02/69/630/DS3 |  |  |  | CDC | 505 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | E3 | 633E | [16 empty] | 1-35-06 | 1-35-07 | 1-30 | [5 empty] | ADCS_S | [8 empty] | 安南PS.633E_ES | 633E(安順白線) ES | LINE69 | P02/69/630/ES3 |  |  |  | CDC | 506 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | PHA | [17 empty] | 1-01-02 | [7 empty] | 69KV_S | [8 empty] | 安南PS.640_PHA | 安順紅線(640) 相間RY | LINE69 | P02/69/640/51A |  |  |  | CDC | 507 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | GDA | [17 empty] | 1-01-03 | [7 empty] | 69KV_S | [8 empty] | 安南PS.640_GDA | 安順紅線(640) 接地RY | LINE69 | P02/69/640/51NA |  |  |  | CDC | 508 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | CB | [17 empty] | 1-01-00 |  | 1-31 | [5 empty] | 69KV_S | [8 empty] | 安南PS.640_CB | 640(安順紅線) CB | LINE69 | P02/69/640/CB |  |  |  | CDC | 509 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | DS1 | 641 | [16 empty] | 1-35-08 | 1-35-09 | 1-33 | [5 empty] | ADCS_S | [8 empty] | 安南PS.641_DS | 641(安順紅線) DS | LINE69 | P02/69/640/DS1 |  |  |  | CDC | 510 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | DS2 | 642 | [16 empty] | 1-35-10 | 1-35-11 | 1-34 | [5 empty] | ADCS_S | [8 empty] | 安南PS.642_DS | 642(安順紅線) DS | LINE69 | P02/69/640/DS2 |  |  |  | CDC | 511 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | DS3 | 643 | [16 empty] | 1-35-12 | 1-35-13 | 1-35 | [5 empty] | ADCS_S | [8 empty] | 安南PS.643_DS | 643(安順紅線) DS | LINE69 | P02/69/640/DS3 |  |  |  | CDC | 512 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | E3 | 643E | [16 empty] | 1-35-14 | 1-35-15 | 1-36 | [5 empty] | ADCS_S | [8 empty] | 安南PS.643E_ES | 643E(安順紅線) ES | LINE69 | P02/69/640/ES3 |  |  |  | CDC | 513 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | PHA | [17 empty] | 1-03-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_PHA | 11KV南21線(KT21) 相間RY | FEEDER | P02/11/KT21/51A |  |  |  | CDC | 514 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) |  | GDA | [17 empty] | 1-03-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_GDA | 11KV南21線(KT21) 接地RY | FEEDER | P02/11/KT21/51NA |  |  |  | CDC | 515 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) 79RY |  | 79UL | [17 empty] | 1-3A-10 |  | 1-50 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_79UL | 11KV南21線(KT21) 79RY U/L | FEEDER | P02/11/KT21/79UL |  |  |  | CDC | 516 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT21 | 南21線(KT21) LCO分流器 |  | ADJ | [17 empty] | 2-33-00 |  | 2-50 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_ADJ | 11KV南21線(KT21) LCO分流器 U/L | FEEDER | P02/11/KT21/ADJ |  |  |  | CDC | 517 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT21 | KT21(11KV南21線) |  | CB | [17 empty] | 1-03-00 |  | 1-4F | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_CB | KT21(11KV南21線) CB | FEEDER | P02/11/KT21/CB |  |  |  | CDC | 518 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_PHA | 11KV南22線(KT22) 相間RY | FEEDER | P02/11/KT22/51A |  |  |  | CDC | 519 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_GDA | 11KV南22線(KT22) 接地RY | FEEDER | P02/11/KT22/51NA |  |  |  | CDC | 520 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) 79RY |  | 79UL | [17 empty] | 1-3A-11 |  | 1-52 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_79UL | 11KV南22線(KT22) 79RY U/L | FEEDER | P02/11/KT22/79UL |  |  |  | CDC | 521 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT22 | 南22線(KT22) LCO分流器 |  | ADJ | [17 empty] | 2-33-01 |  | 2-51 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_ADJ | 11KV南22線(KT22) LCO分流器 U/L | FEEDER | P02/11/KT22/ADJ |  |  |  | CDC | 522 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT22 | KT22(11KV南22線) |  | CB | [17 empty] | 1-03-03 |  | 1-51 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_CB | KT22(11KV南22線) CB | FEEDER | P02/11/KT22/CB |  |  |  | CDC | 523 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | PHA | [17 empty] | 1-03-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_PHA | 11KV南23線(KT23) 相間RY | FEEDER | P02/11/KT23/51A |  |  |  | CDC | 524 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) |  | GDA | [17 empty] | 1-04-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_GDA | 11KV南23線(KT23) 接地RY | FEEDER | P02/11/KT23/51NA |  |  |  | CDC | 525 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) 79RY |  | 79UL | [17 empty] | 1-3A-12 |  | 1-54 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_79UL | 11KV南23線(KT23) 79RY U/L | FEEDER | P02/11/KT23/79UL |  |  |  | CDC | 526 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT23 | 南23線(KT23) LCO分流器 |  | ADJ | [17 empty] | 2-33-02 |  | 2-52 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_ADJ | 11KV南23線(KT23) LCO分流器 U/L | FEEDER | P02/11/KT23/ADJ |  |  |  | CDC | 527 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT23 | KT23(11KV南23線) |  | CB | [17 empty] | 1-03-06 |  | 1-53 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_CB | KT23(11KV南23線) CB | FEEDER | P02/11/KT23/CB |  |  |  | CDC | 528 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | PHA | [17 empty] | 1-04-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_PHA | 11KV南24線(KT24) 相間RY | FEEDER | P02/11/KT24/51A |  |  |  | CDC | 529 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) |  | GDA | [17 empty] | 1-04-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_GDA | 11KV南24線(KT24) 接地RY | FEEDER | P02/11/KT24/51NA |  |  |  | CDC | 530 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) 79RY |  | 79UL | [17 empty] | 1-3A-13 |  | 1-56 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_79UL | 11KV南24線(KT24) 79RY U/L | FEEDER | P02/11/KT24/79UL |  |  |  | CDC | 531 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT24 | 南24線(KT24) LCO分流器 |  | ADJ | [17 empty] | 2-33-03 |  | 2-53 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_ADJ | 11KV南24線(KT24) LCO分流器 U/L | FEEDER | P02/11/KT24/ADJ |  |  |  | CDC | 532 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT24 | KT24(11KV南24線) |  | CB | [17 empty] | 1-04-01 |  | 1-55 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_CB | KT24(11KV南24線) CB | FEEDER | P02/11/KT24/CB |  |  |  | CDC | 533 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | PHA | [17 empty] | 1-04-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_PHA | 11KV南25線(KT25) 相間RY | FEEDER | P02/11/KT25/51A |  |  |  | CDC | 534 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) |  | GDA | [17 empty] | 1-04-06 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_GDA | 11KV南25線(KT25) 接地RY | FEEDER | P02/11/KT25/51NA |  |  |  | CDC | 535 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) 79RY |  | 79UL | [17 empty] | 1-3A-14 |  | 1-58 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_79UL | 11KV南25線(KT25) 79RY U/L | FEEDER | P02/11/KT25/79UL |  |  |  | CDC | 536 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT25 | 南25線(KT25) LCO分流器 |  | ADJ | [17 empty] | 2-33-04 |  | 2-54 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_ADJ | 11KV南25線(KT25) LCO分流器 U/L | FEEDER | P02/11/KT25/ADJ |  |  |  | CDC | 537 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT25 | KT25(11KV南25線) |  | CB | [17 empty] | 1-04-04 |  | 1-57 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_CB | KT25(11KV南25線) CB | FEEDER | P02/11/KT25/CB |  |  |  | CDC | 538 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | PHA | [17 empty] | 1-05-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_PHA | 11KV南27線(KT27) 相間RY | FEEDER | P02/11/KT27/51A |  |  |  | CDC | 539 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) |  | GDA | [17 empty] | 1-05-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_GDA | 11KV南27線(KT27) 接地RY | FEEDER | P02/11/KT27/51NA |  |  |  | CDC | 540 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) 79RY |  | 79UL | [17 empty] | 1-3B-04 |  | 1-64 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_79UL | 11KV南27線(KT27) 79RY U/L | FEEDER | P02/11/KT27/79UL |  |  |  | CDC | 541 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT27 | 南27線(KT27) LCO分流器 |  | ADJ | [17 empty] | 2-33-06 |  | 2-56 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_ADJ | 11KV南27線(KT27) LCO分流器 U/L | FEEDER | P02/11/KT31/ADJ |  |  |  | CDC | 542 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT27 | KT27(11KV南27線) |  | CB | [17 empty] | 1-05-02 |  | 1-63 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_CB | KT27(11KV南27線) CB | FEEDER | P02/11/KT27/CB |  |  |  | CDC | 543 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | PHA | [17 empty] | 1-05-06 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_PHA | 11KV南28線(KT28) 相間RY | FEEDER | P02/11/KT28/51A |  |  |  | CDC | 544 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) |  | GDA | [17 empty] | 1-05-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_GDA | 11KV南28線(KT28) 接地RY | FEEDER | P02/11/KT28/51NA |  |  |  | CDC | 545 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) 79RY |  | 79UL | [17 empty] | 1-3B-05 |  | 1-66 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_79UL | 11KV南28線(KT28) 79RY U/L | FEEDER | P02/11/KT28/79UL |  |  |  | CDC | 546 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT28 | 南28線(KT28) LCO分流器 |  | ADJ | [17 empty] | 2-33-07 |  | 2-57 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_ADJ | 11KV南28線(KT28) LCO分流器 U/L | FEEDER | P02/11/KT32/ADJ |  |  |  | CDC | 547 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT28 | KT28(11KV南28線) |  | CB | [17 empty] | 1-05-05 |  | 1-65 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_CB | KT28(11KV南28線) CB | FEEDER | P02/11/KT28/CB |  |  |  | CDC | 548 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | PHA | [17 empty] | 1-06-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_PHA | 11KV南29線(KT29) 相間RY | FEEDER | P02/11/KT29/51A |  |  |  | CDC | 549 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) |  | GDA | [17 empty] | 1-06-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_GDA | 11KV南29線(KT29) 接地RY | FEEDER | P02/11/KT29/51NA |  |  |  | CDC | 550 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) 79RY |  | 79UL | [17 empty] | 1-3B-06 |  | 1-68 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_79UL | 11KV南29線(KT29) 79RY U/L | FEEDER | P02/11/KT29/79UL |  |  |  | CDC | 551 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT29 | 南29線(KT29) LCO分流器 |  | ADJ | [17 empty] | 2-33-08 |  | 2-58 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_ADJ | 11KV南29線(KT29) LCO分流器 U/L | FEEDER | P02/11/KT33/ADJ |  |  |  | CDC | 552 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT29 | KT29(11KV南29線) |  | CB | [17 empty] | 1-06-00 |  | 1-67 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_CB | KT29(11KV南29線) CB | FEEDER | P02/11/KT29/CB |  |  |  | CDC | 553 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | PHA | [17 empty] | 1-06-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_PHA | 11KV南30線(KT30) 相間RY | FEEDER | P02/11/KT30/51A |  |  |  | CDC | 554 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) |  | GDA | [17 empty] | 1-06-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_GDA | 11KV南30線(KT30) 接地RY | FEEDER | P02/11/KT30/51NA |  |  |  | CDC | 555 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) 79RY |  | 79UL | [17 empty] | 1-3B-07 |  | 1-6A | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_79UL | 11KV南30線(KT30) 79RY U/L | FEEDER | P02/11/KT30/79UL |  |  |  | CDC | 556 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT30 | 南30線(KT30) LCO分流器 |  | ADJ | [17 empty] | 2-33-09 |  | 2-59 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_ADJ | 11KV南30線(KT30) LCO分流器 U/L | FEEDER | P02/11/KT34/ADJ |  |  |  | CDC | 557 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT30 | KT30(11KV南30線) |  | CB | [17 empty] | 1-06-03 |  | 1-69 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_CB | KT30(11KV南30線) CB | FEEDER | P02/11/KT30/CB |  |  |  | CDC | 558 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | PHA | [17 empty] | 1-06-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_PHA | 11KV南31線(KT31) 相間RY | FEEDER | P02/11/KT31/51A |  |  |  | CDC | 559 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) |  | GDA | [17 empty] | 1-07-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_GDA | 11KV南31線(KT31) 接地RY | FEEDER | P02/11/KT31/51NA |  |  |  | CDC | 560 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) 79RY |  | 79UL | [17 empty] | 1-3B-00 |  | 1-5C | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_79UL | 11KV南31線(KT31) 79RY U/L | FEEDER | P02/11/KT31/79UL |  |  |  | CDC | 561 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT31 | 南31線(KT31) LCO分流器 |  | ADJ | [17 empty] | 2-33-10 |  | 2-5A | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_ADJ | 11KV南31線(KT31) LCO分流器 U/L | FEEDER | P02/11/KT27/ADJ |  |  |  | CDC | 562 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT31 | KT31(11KV南31線) |  | CB | [17 empty] | 1-06-06 |  | 1-5B | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_CB | KT31(11KV南31線) CB | FEEDER | P02/11/KT31/CB |  |  |  | CDC | 563 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | PHA | [17 empty] | 1-07-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_PHA | 11KV南32線(KT32) 相間RY | FEEDER | P02/11/KT32/51A |  |  |  | CDC | 564 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) |  | GDA | [17 empty] | 1-07-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_GDA | 11KV南32線(KT32) 接地RY | FEEDER | P02/11/KT32/51NA |  |  |  | CDC | 565 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) 79RY |  | 79UL | [17 empty] | 1-3B-01 |  | 1-5E | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_79UL | 11KV南32線(KT32) 79RY U/L | FEEDER | P02/11/KT32/79UL |  |  |  | CDC | 566 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT32 | 南32線(KT32) LCO分流器 |  | ADJ | [17 empty] | 2-33-11 |  | 2-5B | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_ADJ | 11KV南32線(KT32) LCO分流器 U/L | FEEDER | P02/11/KT28/ADJ |  |  |  | CDC | 567 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT32 | KT32(11KV南32線) |  | CB | [17 empty] | 1-07-01 |  | 1-5D | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_CB | KT32(11KV南32線) CB | FEEDER | P02/11/KT32/CB |  |  |  | CDC | 568 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | PHA | [17 empty] | 1-07-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_PHA | 11KV南33線(KT33) 相間RY | FEEDER | P02/11/KT33/51A |  |  |  | CDC | 569 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) |  | GDA | [17 empty] | 1-07-06 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_GDA | 11KV南33線(KT33) 接地RY | FEEDER | P02/11/KT33/51NA |  |  |  | CDC | 570 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) 79RY |  | 79UL | [17 empty] | 1-3B-02 |  | 1-60 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_79UL | 11KV南33線(KT33) 79RY U/L | FEEDER | P02/11/KT33/79UL |  |  |  | CDC | 571 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT33 | 南33線(KT33) LCO分流器 |  | ADJ | [17 empty] | 2-33-12 |  | 2-5C | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_ADJ | 11KV南33線(KT33) LCO分流器 U/L | FEEDER | P02/11/KT29/ADJ |  |  |  | CDC | 572 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT33 | KT33(11KV南33線) |  | CB | [17 empty] | 1-07-04 |  | 1-5F | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_CB | KT33(11KV南33線) CB | FEEDER | P02/11/KT33/CB |  |  |  | CDC | 573 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | PHA | [17 empty] | 1-08-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_PHA | 11KV南34線(KT34) 相間RY | FEEDER | P02/11/KT34/51A |  |  |  | CDC | 574 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) |  | GDA | [17 empty] | 1-08-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_GDA | 11KV南34線(KT34) 接地RY | FEEDER | P02/11/KT34/51NA |  |  |  | CDC | 575 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) 79RY |  | 79UL | [17 empty] | 1-3B-03 |  | 1-62 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_79UL | 11KV南34線(KT34) 79RY U/L | FEEDER | P02/11/KT34/79UL |  |  |  | CDC | 576 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT34 | 南34線(KT34) LCO分流器 |  | ADJ | [17 empty] | 2-33-13 |  | 2-5D | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_ADJ | 11KV南34線(KT34) LCO分流器 U/L | FEEDER | P02/11/KT30/ADJ |  |  |  | CDC | 577 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT34 | KT34(11KV南34線) |  | CB | [17 empty] | 1-07-07 |  | 1-61 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_CB | KT34(11KV南34線) CB | FEEDER | P02/11/KT34/CB |  |  |  | CDC | 578 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | PHA | [17 empty] | 1-08-06 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_PHA | 11KV南36線(KT36) 相間RY | FEEDER | P02/11/KT36/51A |  |  |  | CDC | 579 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) |  | GDA | [17 empty] | 1-08-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_GDA | 11KV南36線(KT36) 接地RY | FEEDER | P02/11/KT36/51NA |  |  |  | CDC | 580 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) 79RY |  | 79UL | [17 empty] | 1-3B-09 |  | 1-6E | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_79UL | 11KV南36線(KT36) 79RY U/L | FEEDER | P02/11/KT36/79UL |  |  |  | CDC | 581 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT36 | 南36線(KT36) LCO分流器 |  | ADJ | [17 empty] | 2-33-15 |  | 2-5F | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_ADJ | 11KV南36線(KT36) LCO分流器 U/L | FEEDER | P02/11/KT36/ADJ |  |  |  | CDC | 582 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT36 | KT36(11KV南36線) |  | CB | [17 empty] | 1-08-05 |  | 1-6D | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_CB | KT36(11KV南36線) CB | FEEDER | P02/11/KT36/CB |  |  |  | CDC | 583 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | PHA | [17 empty] | 1-09-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_PHA | 11KV南37線(KT37) 相間RY | FEEDER | P02/11/KT37/51A |  |  |  | CDC | 584 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) |  | GDA | [17 empty] | 1-09-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_GDA | 11KV南37線(KT37) 接地RY | FEEDER | P02/11/KT37/51NA |  |  |  | CDC | 585 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) 79RY |  | 79UL | [17 empty] | 1-3B-10 |  | 1-70 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_79UL | 11KV南37線(KT37) 79RY U/L | FEEDER | P02/11/KT37/79UL |  |  |  | CDC | 586 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT37 | 南37線(KT37) LCO分流器 |  | ADJ | [17 empty] | 2-34-00 |  | 2-60 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_ADJ | 11KV南37線(KT37) LCO分流器 U/L | FEEDER | P02/11/KT37/ADJ |  |  |  | CDC | 587 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT37 | KT37(11KV南37線) |  | CB | [17 empty] | 1-09-00 |  | 1-6F | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_CB | KT37(11KV南37線) CB | FEEDER | P02/11/KT37/CB |  |  |  | CDC | 588 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | PHA | [17 empty] | 1-09-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_PHA | 11KV南38線(KT38) 相間RY | FEEDER | P02/11/KT38/51A |  |  |  | CDC | 589 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) |  | GDA | [17 empty] | 1-09-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_GDA | 11KV南38線(KT38) 接地RY | FEEDER | P02/11/KT38/51NA |  |  |  | CDC | 590 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) 79RY |  | 79UL | [17 empty] | 1-3B-11 |  | 1-72 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_79UL | 11KV南38線(KT38) 79RY U/L | FEEDER | P02/11/KT38/79UL |  |  |  | CDC | 591 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT38 | 南38線(KT38) LCO分流器 |  | ADJ | [17 empty] | 2-34-01 |  | 2-61 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_ADJ | 11KV南38線(KT38) LCO分流器 U/L | FEEDER | P02/11/KT38/ADJ |  |  |  | CDC | 592 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT38 | KT38(11KV南38線) |  | CB | [17 empty] | 1-09-03 |  | 1-71 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_CB | KT38(11KV南38線) CB | FEEDER | P02/11/KT38/CB |  |  |  | CDC | 593 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | PHA | [17 empty] | 1-09-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_PHA | 11KV南39線(KT39) 相間RY | FEEDER | P02/11/KT39/51A |  |  |  | CDC | 594 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) |  | GDA | [17 empty] | 1-0A-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_GDA | 11KV南39線(KT39) 接地RY | FEEDER |  |  |  |  | CDC | 595 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) 79RY |  | 79UL | [17 empty] | 1-3B-12 |  | 1-74 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_79UL | 11KV南39線(KT39) 79RY U/L | FEEDER | P02/11/KT39/79UL |  |  |  | CDC | 596 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT39 | 南39線(KT39) LCO分流器 |  | ADJ | [17 empty] | 2-34-02 |  | 2-62 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_ADJ | 11KV南39線(KT39) LCO分流器 U/L | FEEDER | P02/11/KT39/ADJ |  |  |  | CDC | 597 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT39 | KT39(11KV南39線) |  | CB | [17 empty] | 1-09-06 |  | 1-73 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_CB | KT39(11KV南39線) CB | FEEDER | P02/11/KT39/CB |  |  |  | CDC | 598 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | PHA | [17 empty] | 1-0A-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_PHA | 11KV南40線(KT40) 相間RY | FEEDER |  |  |  |  | CDC | 599 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) |  | GDA | [17 empty] | 1-0A-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_GDA | 11KV南40線(KT40) 接地RY | FEEDER |  |  |  |  | CDC | 600 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) 79RY |  | 79UL | [17 empty] | 1-3B-13 |  | 1-76 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_79UL | 11KV南40線(KT40) 79RY U/L | FEEDER | P02/11/KT40/79UL |  |  |  | CDC | 601 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT40 | 南40線(KT40) LCO分流器 |  | ADJ | [17 empty] | 2-34-03 |  | 2-63 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_ADJ | 11KV南40線(KT40) LCO分流器 U/L | FEEDER | P02/11/KT40/ADJ |  |  |  | CDC | 602 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT40 | KT40(11KV南40線) |  | CB | [17 empty] | 1-0A-01 |  | 1-75 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_CB | KT40(11KV南40線) CB | FEEDER | P02/11/KT40/CB |  |  |  | CDC | 603 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | PHA | [17 empty] | 1-1B-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_PHA | 23KV南71線(KT71) 相間RY | FEEDER | P02/22/KT71/51A |  |  |  | CDC | 604 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) |  | GDA | [17 empty] | 1-1B-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_GDA | 23KV南71線(KT71) 接地RY | FEEDER | P02/22/KT71/51NA |  |  |  | CDC | 605 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) 79RY |  | 79UL | [17 empty] | 2-37-04 |  | 3-16 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_79UL | 23KV南71線(KT71) 79RY U/L | FEEDER | P02/22/KT71/79UL |  |  |  | CDC | 606 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT71 | 南71線(KT71) LCO分流器 |  | ADJ | [17 empty] | 2-38-00 |  | 3-14 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_ADJ | 23KV南71線(KT71) LCO分流器 U/L | FEEDER | P02/22/KT71/ADJ |  |  |  | CDC | 607 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT71 | KT71(23KV南71線) |  | CB | [17 empty] | 1-1B-02 |  | 2-76 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_CB | KT71(23KV南71線) CB | FEEDER | P02/22/KT71/CB |  |  |  | CDC | 608 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | PHA | [17 empty] | 1-1B-06 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_PHA | 23KV南72線(KT72) 相間RY | FEEDER | P02/22/KT72/51A |  |  |  | CDC | 609 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) |  | GDA | [17 empty] | 1-1B-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_GDA | 23KV南72線(KT72) 接地RY | FEEDER | P02/22/KT72/51NA |  |  |  | CDC | 610 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) 79RY |  | 79UL | [17 empty] | 2-37-05 |  | 3-17 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_79UL | 23KV南72線(KT72) 79RY U/L | FEEDER | P02/22/KT72/79UL |  |  |  | CDC | 611 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT72 | 南72線(KT72) LCO分流器 |  | ADJ | [17 empty] | 2-38-01 |  | 3-15 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_ADJ | 23KV南72線(KT72) LCO分流器 U/L | FEEDER | P02/22/KT72/ADJ |  |  |  | CDC | 612 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT72 | KT72(23KV南72線) |  | CB | [17 empty] | 1-1B-05 |  | 2-77 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_CB | KT72(23KV南72線) CB | FEEDER | P02/22/KT72/CB |  |  |  | CDC | 613 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | PHA | [17 empty] | 1-1C-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_PHA | 23KV南73線(KT73) 相間RY | FEEDER | P02/22/KT73/51A |  |  |  | CDC | 614 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) |  | GDA | [17 empty] | 1-1C-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_GDA | 23KV南73線(KT73) 接地RY | FEEDER | P02/22/KT73/51NA |  |  |  | CDC | 615 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) 79RY |  | 79UL | [17 empty] | 2-37-06 |  | 3-18 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_79UL | 23KV南73線(KT73) 79RY U/L | FEEDER | P02/22/KT73/79UL |  |  |  | CDC | 616 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT73 | 南73線(KT73) LCO分流器 |  | ADJ | [17 empty] | 2-38-02 |  | 3-20 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_ADJ | 23KV南73線(KT73) LCO分流器 U/L | FEEDER | P02/22/KT73/ADJ |  |  |  | CDC | 617 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT73 | KT73(23KV南73線) |  | CB | [17 empty] | 1-1C-00 |  | 2-78 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_CB | KT73(23KV南73線) CB | FEEDER | P02/22/KT73/CB |  |  |  | CDC | 618 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | PHA | [17 empty] | 1-1C-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_PHA | 23KV南74線(KT74) 相間RY | FEEDER | P02/22/KT74/51A |  |  |  | CDC | 619 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) |  | GDA | [17 empty] | 1-1C-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_GDA | 23KV南74線(KT74) 接地RY | FEEDER | P02/22/KT74/51NA |  |  |  | CDC | 620 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) 79RY |  | 79UL | [17 empty] | 2-37-07 |  | 3-19 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_79UL | 23KV南74線(KT74) 79RY U/L | FEEDER | P02/22/KT74/79UL |  |  |  | CDC | 621 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT74 | 南74線(KT74) LCO分流器 |  | ADJ | [17 empty] | 2-38-03 |  | 3-21 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_ADJ | 23KV南74線(KT74) LCO分流器 U/L | FEEDER | P02/22/KT74/ADJ |  |  |  | CDC | 622 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT74 | KT74(23KV南74線) |  | CB | [17 empty] | 1-1C-03 |  | 2-79 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_CB | KT74(23KV南74線) CB | FEEDER | P02/22/KT74/CB |  |  |  | CDC | 623 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | PHA | [17 empty] | 1-1D-02 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_PHA | 23KV南76線(KT76) 相間RY | FEEDER | P02/22/KT76/51A |  |  |  | CDC | 624 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) |  | GDA | [17 empty] | 1-1D-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_GDA | 23KV南76線(KT76) 接地RY | FEEDER | P02/22/KT76/51NA |  |  |  | CDC | 625 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) 79RY |  | 79UL | [17 empty] | 2-37-09 |  | 3-1B | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_79UL | 23KV南76線(KT76) 79RY U/L | FEEDER | P02/22/KT76/79UL |  |  |  | CDC | 626 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT76 | 南76線(KT76) LCO分流器 |  | ADJ | [17 empty] | 2-38-05 |  | 3-23 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_ADJ | 23KV南76線(KT76) LCO分流器 U/L | FEEDER | P02/22/KT76/ADJ |  |  |  | CDC | 627 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT76 | KT76(23KV南76線) |  | CB | [17 empty] | 1-1D-01 |  | 2-7B | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_CB | KT76(23KV南76線) CB | FEEDER | P02/22/KT76/CB |  |  |  | CDC | 628 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | PHA | [17 empty] | 1-1D-05 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_PHA | 23KV南77線(KT77) 相間RY | FEEDER | P02/22/KT77/51A |  |  |  | CDC | 629 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) |  | GDA | [17 empty] | 1-1D-06 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_GDA | 23KV南77線(KT77) 接地RY | FEEDER | P02/22/KT77/51NA |  |  |  | CDC | 630 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) 79RY |  | 79UL | [17 empty] | 2-37-10 |  | 3-1C | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_79UL | 23KV南77線(KT77) 79RY U/L | FEEDER | P02/22/KT77/79UL |  |  |  | CDC | 631 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT77 | 南77線(KT77) LCO分流器 |  | ADJ | [17 empty] | 2-38-06 |  | 3-24 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_ADJ | 23KV南77線(KT77) LCO分流器 U/L | FEEDER | P02/22/KT77/ADJ |  |  |  | CDC | 632 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT77 | KT77(23KV南77線) |  | CB | [17 empty] | 1-1D-04 |  | 2-7C | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_CB | KT77(23KV南77線) CB | FEEDER | P02/22/KT77/CB |  |  |  | CDC | 633 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | PHA | [17 empty] | 1-1E-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_PHA | 23KV南78線(KT78) 相間RY | FEEDER | P02/22/KT78/51A |  |  |  | CDC | 634 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) |  | GDA | [17 empty] | 1-1E-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_GDA | 23KV南78線(KT78) 接地RY | FEEDER | P02/22/KT78/51NA |  |  |  | CDC | 635 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) 79RY |  | 79UL | [17 empty] | 2-37-11 |  | 3-1D | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_79UL | 23KV南78線(KT78) 79RY U/L | FEEDER | P02/22/KT78/79UL |  |  |  | CDC | 636 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT78 | 南78線(KT78) LCO分流器 |  | ADJ | [17 empty] | 2-38-07 |  | 3-25 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_ADJ | 23KV南78線(KT78) LCO分流器 U/L | FEEDER | P02/22/KT78/ADJ |  |  |  | CDC | 637 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT78 | KT78(23KV南78線) |  | CB | [17 empty] | 1-1D-07 |  | 2-7D | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_CB | KT78(23KV南78線) CB | FEEDER | P02/22/KT78/CB |  |  |  | CDC | 638 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | PHA | [17 empty] | 1-1E-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_PHA | 23KV南79線(KT79) 相間RY | FEEDER | P02/22/KT79/51A |  |  |  | CDC | 639 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) |  | GDA | [17 empty] | 1-1E-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_GDA | 23KV南79線(KT79) 接地RY | FEEDER | P02/22/KT79/51NA |  |  |  | CDC | 640 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) 79RY |  | 79UL | [17 empty] | 2-37-12 |  | 3-1E | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_79UL | 23KV南79線(KT79) 79RY U/L | FEEDER | P02/22/KT79/79UL |  |  |  | CDC | 641 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT79 | 南79線(KT79) LCO分流器 |  | ADJ | [17 empty] | 2-38-08 |  | 3-26 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_ADJ | 23KV南79線(KT79) LCO分流器 U/L | FEEDER | P02/22/KT79/ADJ |  |  |  | CDC | 642 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT79 | KT79(23KV南79線) |  | CB | [17 empty] | 1-1E-02 |  | 2-7E | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_CB | KT79(23KV南79線) CB | FEEDER | P02/22/KT79/CB |  |  |  | CDC | 643 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-16-06 |  | 2-2F | [5 empty] | 161KV_S | [8 empty] | 安南PS.1500_CB | 1500(TIE) CB | TIE | P02/161/1500/CB |  |  |  | CDC | 644 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-16-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1500_50A | 161KV TIE(1500) 50RY | TIE | P02/161/1500/50A |  |  |  | CDC | 645 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS1 | 1501 | [16 empty] | 1-38-00 | 1-38-01 | 2-30 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1501_DS | 1501(TIE) DS | TIE | P02/161/1500/DS1 |  |  |  | CDC | 646 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | DS2 | 1502 | [16 empty] | 1-38-02 | 1-38-03 | 2-31 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1502_DS | 1502(TIE) DS | TIE | P02/161/1500/DS2 |  |  |  | CDC | 647 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-17-00 |  | 2-32 | [5 empty] | 69KV_S | [8 empty] | 安南PS.600_CB | 600(TIE) CB | TIE | P02/69/600/CB |  |  |  | CDC | 648 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | DS1 | 601 | [16 empty] | 1-38-04 | 1-38-05 | 2-33 | [5 empty] | ADCS_S | [8 empty] | 安南PS.601_DS | 601(TIE) DS | TIE | P02/69/600/DS1 |  |  |  | CDC | 649 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | DS2 | 602 | [16 empty] | 1-38-06 | 1-38-07 | 2-34 | [5 empty] | ADCS_S | [8 empty] | 安南PS.602_DS | 602(TIE) DS | TIE | P02/69/600/DS2 |  |  |  | CDC | 650 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | CB | [17 empty] | 1-14-00 |  | 1-79 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1650_CB | 1650(#1MTR) CB | MTR | P02/161/1650/CB |  |  |  | CDC | 651 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | CB | [17 empty] | 1-14-01 |  | 1-7A | [5 empty] | 69KV_S | [8 empty] | 安南PS.750_CB | 750(#1MTR) CB | MTR | P02/69/750/CB |  |  |  | CDC | 652 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 51ZA | [17 empty] | 1-14-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#1MTR_51ZA | #1MTR 51Z RY | MTR | P02//1MTR/51ZA |  |  |  | CDC | 653 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 87A | [17 empty] | 1-13-04 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#1MTR_87A | #1MTR 87RY | MTR | P02//1MTR/87A |  |  |  | CDC | 654 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 96PA | [17 empty] | 1-13-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#1MTR_96PA | #1MTR 機械保護動作 | MTR | P02//1MTR/96PA |  |  |  | CDC | 655 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 96D | [17 empty] | 2-38-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_96D | #1MTR 96D RY | MTR | P02//1MTR/96D |  |  |  | CDC | 656 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 96P | [17 empty] | 2-38-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_96P | #1MTR 96P RY | MTR | P02//1MTR/96P |  |  |  | CDC | 657 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 63Q | [17 empty] | 2-38-12 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_63Q | #1MTR 63Q RY | MTR | P02//1MTR/63Q |  |  |  | CDC | 658 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 96B1 | [17 empty] | 2-38-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_96B1 | #1MTR 96B1 RY | MTR | P02//1MTR/96B1 |  |  |  | CDC | 659 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 96B2 | [17 empty] | 2-38-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_96B2 | #1MTR 96B2 RY | MTR | P02//1MTR/96B2 |  |  |  | CDC | 660 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | TRA | [17 empty] | 1-3C-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_TRA | #1MTR 重故障 | MTR | P02//1MTR/TRA |  |  |  | CDC | 661 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | TRF | [17 empty] | 1-3C-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_TRF | #1MTR 輕故障 | MTR | P02//1MTR/TRF |  |  |  | CDC | 662 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | SupLocal | [17 empty] | 1-3C-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_S/L | #1MTR OLTC S/L | MTR | P02//1MTR/SupLocal |  |  |  | CDC | 663 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | A_M | [17 empty] | 1-3C-12 |  | 1-7D | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_A/M | #1MTR OLTC A/M | MTR | P02//1MTR/Tap Chan |  |  |  | CDC | 664 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | M/F/I | [17 empty] | 1-3C-08 | 1-3C-09 | 1-77 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_M/F/I | #1MTR M/F/I | MTR | P02//1MTR/M_F_I |  |  |  | CDC | 665 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS1 | 1651 | [16 empty] | 1-3C-00 | 1-3C-01 | 1-7B | [5 empty] | ADCS_S | [8 empty] | 安南PS.1651_DS | 1651(#1MTR) DS | MTR | P02/161/1650/DS1 |  |  |  | CDC | 666 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | DS2 | 1652 | [16 empty] | 1-3C-02 | 1-3C-03 | 1-7C | [5 empty] | ADCS_S | [8 empty] | 安南PS.1652_DS | 1652(#1MTR) DS | MTR | P02/161/1650/DS2 |  |  |  | CDC | 667 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | DS1 | 751 | [16 empty] | 1-3C-04 | 1-3C-05 | 1-7F | [5 empty] | ADCS_S | [8 empty] | 安南PS.751_DS | 751(#1MTR) DS | MTR | P02/69/750/DS1 |  |  |  | CDC | 668 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | DS2 | 752 | [16 empty] | 1-3C-06 | 1-3C-07 | 2-00 | [5 empty] | ADCS_S | [8 empty] | 安南PS.752_DS | 752(#1MTR) DS | MTR | P02/69/750/DS2 |  |  |  | CDC | 669 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | [17 empty] | 1-14-07 |  | 2-03 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1660_CB | 1660(#2MTR) CB | MTR | P02/161/1660/CB |  |  |  | CDC | 670 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-15-00 |  | 2-04 | [5 empty] | 69KV_S | [8 empty] | 安南PS.760_CB | 760(#2MTR) CB | MTR | P02/69/760/CB |  |  |  | CDC | 671 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-15-01 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | P02//2MTR/51ZA |  |  |  | CDC | 672 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-14-03 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#2MTR_87A | #2MTR 87RY | MTR | P02//2MTR/87A |  |  |  | CDC | 673 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-14-06 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | P02//2MTR/96PA |  |  |  | CDC | 674 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 2-38-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_96D | #2MTR 96D RY | MTR | P02//2MTR/96D |  |  |  | CDC | 675 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 2-39-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_96P | #2MTR 96P RY | MTR | P02//2MTR/96P |  |  |  | CDC | 676 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 2-39-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_63Q | #2MTR 63Q RY | MTR | P02//2MTR/63Q |  |  |  | CDC | 677 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 2-39-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | P02//2MTR/96B1 |  |  |  | CDC | 678 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 2-39-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | P02//2MTR/96B2 |  |  |  | CDC | 679 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-3D-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_TRA | #2MTR 重故障 | MTR | P02//2MTR/TRA |  |  |  | CDC | 680 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-3D-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_TRF | #2MTR 輕故障 | MTR | P02//2MTR/TRF |  |  |  | CDC | 681 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-3D-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | P02//2MTR/SupLocal |  |  |  | CDC | 682 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-3D-12 |  | 2-07 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | P02//2MTR/Tap Chan |  |  |  | CDC | 683 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | M/F/I | [17 empty] | 1-3D-08 | 1-3D-09 | 2-01 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | P02//2MTR/M_F_I |  |  |  | CDC | 684 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS1 | 1661 | [16 empty] | 1-3D-00 | 1-3D-01 | 2-05 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1661_DS | 1661(#2MTR) DS | MTR | P02/161/1660/DS1 |  |  |  | CDC | 685 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | DS2 | 1662 | [16 empty] | 1-3D-02 | 1-3D-03 | 2-06 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1662_DS | 1662(#2MTR) DS | MTR | P02/161/1660/DS2 |  |  |  | CDC | 686 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | DS1 | 761 | [16 empty] | 1-3D-04 | 1-3D-05 | 2-09 | [5 empty] | ADCS_S | [8 empty] | 安南PS.761_DS | 761(#2MTR) DS | MTR | P02/69/760/DS1 |  |  |  | CDC | 687 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | DS2 | 762 | [16 empty] | 1-3D-06 | 1-3D-07 | 2-0A | [5 empty] | ADCS_S | [8 empty] | 安南PS.762_DS | 762(#2MTR) DS | MTR | P02/69/760/DS2 |  |  |  | CDC | 688 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | CB | [17 empty] | 1-15-05 |  | 2-0B | [5 empty] | 161KV_S | [8 empty] | 安南PS.1750_CB | 1750(#1DTR) CB | MTR | P02/161/1750/CB |  |  |  | CDC | 689 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 310 | #1DTR(310) |  | CB | [17 empty] | 1-0A-04 |  | 2-0C | [5 empty] | ADCS_S | [8 empty] | 安南PS.310_CB | 310(#1DTR) CB | MTR |  |  |  |  | CDC | 690 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 320 | #1DTR(320) |  | CB | [17 empty] | 1-0A-05 |  | 2-11 | [5 empty] | ADCS_S | [8 empty] | 安南PS.320_CB | 320(#1DTR) CB | MTR |  |  |  |  | CDC | 691 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 51ZA | [17 empty] | 1-15-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#1DTR_51ZA | #1DTR 51Z RY | MTR | P02//1DTR/51ZA |  |  |  | CDC | 692 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 87A | [17 empty] | 1-15-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#1DTR_87A | #1DTR 87RY | MTR | P02//1DTR/87A |  |  |  | CDC | 693 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 310 | #1DTR(310) |  | 51A | [17 empty] | 1-0A-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.310_51A | #1DTR二次側(310) 51RY | MTR |  |  |  |  | CDC | 694 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 320 | #1DTR(320) |  | 51A | [17 empty] | 1-0A-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.320_51A | #1DTR二次側(320) 51RY | MTR |  |  |  |  | CDC | 695 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 96PA | [17 empty] | 1-15-04 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#1DTR_96PA | #1DTR 機械保護動作 | MTR | P02//1DTR/96PA |  |  |  | CDC | 696 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 96D | [17 empty] | 1-38-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_96D | #1DTR 96D RY | MTR | P02//1DTR/96D |  |  |  | CDC | 697 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 96P | [17 empty] | 1-38-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_96P | #1DTR 96P RY | MTR | P02//1DTR/96P |  |  |  | CDC | 698 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 63Q | [17 empty] | 1-38-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_63Q | #1DTR 63Q RY | MTR | P02//1DTR/63Q |  |  |  | CDC | 699 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 96B1 | [17 empty] | 1-38-12 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_96B1 | #1DTR 96B1 RY | MTR | P02//1DTR/96B1 |  |  |  | CDC | 700 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 96B2 | [17 empty] | 1-38-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_96B2 | #1DTR 96B2 RY | MTR | P02//1DTR/96B2 |  |  |  | CDC | 701 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | TRA | [17 empty] | 1-3E-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_TRA | #1DTR 重故障 | MTR | P02//1DTR/TRA |  |  |  | CDC | 702 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | TRF | [17 empty] | 1-3E-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_TRF | #1DTR 輕故障 | MTR | P02//1DTR/TRF |  |  |  | CDC | 703 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | SupLocal | [17 empty] | 1-3E-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_S/L | #1DTR(A) OLTC S/L | MTR | P02//1DTR(A)/SupLocal |  |  |  | CDC | 704 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 1DTR(A) | #1DTR(A) |  | A_M | [17 empty] | 1-3E-06 |  | 2-0F | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(A)_A/M | #1DTR(A) OLTC A/M | MTR | P02//1DTR(A)/Tap Chan |  |  |  | CDC | 705 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR(B) |  | SupLocal | [17 empty] | 1-3E-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_S/L | #1DTR(B) OLTC S/L | MTR | P02//1DTR(B)/SupLocal |  |  |  | CDC | 706 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 1DTR(B) | #1DTR(B) |  | A_M | [17 empty] | 1-3E-07 |  | 2-12 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR(B)_A/M | #1DTR(B) OLTC A/M | MTR | P02//1DTR(B)/Tap Chan |  |  |  | CDC | 707 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS1 | 1751 | [16 empty] | 1-3E-00 | 1-3E-01 | 2-0D | [5 empty] | ADCS_S | [8 empty] | 安南PS.1751_DS | 1751(#1DTR) DS | MTR | P02/161/1750/DS1 |  |  |  | CDC | 708 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | DS2 | 1752 | [16 empty] | 1-3E-02 | 1-3E-03 | 2-0E | [5 empty] | ADCS_S | [8 empty] | 安南PS.1752_DS | 1752(#1DTR) DS | MTR | P02/161/1750/DS2 |  |  |  | CDC | 709 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | CB | [17 empty] | 1-16-03 |  | 2-14 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1760_CB | 1760(#2DTR) CB | MTR | P02/161/1760/CB |  |  |  | CDC | 710 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 330 | #2DTR(330) |  | CB | [17 empty] | 1-0B-00 |  | 2-15 | [5 empty] | ADCS_S | [8 empty] | 安南PS.330_CB | 330(#2DTR) CB | MTR |  |  |  |  | CDC | 711 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 340 | #2DTR(340) |  | CB | [17 empty] | 1-0B-01 |  | 2-1A | [5 empty] | ADCS_S | [8 empty] | 安南PS.340_CB | 340(#2DTR) CB | MTR |  |  |  |  | CDC | 712 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 51ZA | [17 empty] | 1-16-05 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#2DTR_51ZA | #2DTR 51Z RY | MTR | P02//2DTR/51ZA |  |  |  | CDC | 713 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 87A | [17 empty] | 1-16-00 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#2DTR_87A | #2DTR 87RY | MTR | P02//2DTR/87A |  |  |  | CDC | 714 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 330 | #2DTR(330) |  | 51A | [17 empty] | 1-0C-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.330_51A | #2DTR二次側(330) 51RY | MTR |  |  |  |  | CDC | 715 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 340 | #2DTR(340) |  | 51A | [17 empty] | 1-0C-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.340_51A | #2DTR二次側(340) 51RY | MTR |  |  |  |  | CDC | 716 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 96PA | [17 empty] | 1-16-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#2DTR_96PA | #2DTR 機械保護動作 | MTR | P02//2DTR/96PA |  |  |  | CDC | 717 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 96D | [17 empty] | 2-39-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_96D | #2DTR 96D RY | MTR | P02//2DTR/96D |  |  |  | CDC | 718 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 96P | [17 empty] | 2-39-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_96P | #2DTR 96P RY | MTR | P02//2DTR/96P |  |  |  | CDC | 719 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 63Q | [17 empty] | 2-39-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_63Q | #2DTR 63Q RY | MTR | P02//2DTR/63Q |  |  |  | CDC | 720 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 96B1 | [17 empty] | 2-39-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_96B1 | #2DTR 96B1 RY | MTR | P02//2DTR/96B1 |  |  |  | CDC | 721 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 96B2 | [17 empty] | 2-39-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_96B2 | #2DTR 96B2 RY | MTR | P02//2DTR/96B2 |  |  |  | CDC | 722 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | TRA | [17 empty] | 1-3F-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_TRA | #2DTR 重故障 | MTR | P02//2DTR/TRA |  |  |  | CDC | 723 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | TRF | [17 empty] | 1-3F-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_TRF | #2DTR 輕故障 | MTR | P02//2DTR/TRF |  |  |  | CDC | 724 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | SupLocal | [17 empty] | 1-3F-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_S/L | #2DTR(A) OLTC S/L | MTR | P02//2DTR(A)/SupLocal |  |  |  | CDC | 725 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 2DTR(A) | #2DTR(A) |  | A_M | [17 empty] | 1-3F-02 |  | 2-18 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(A)_A/M | #2DTR(A) OLTC A/M | MTR | P02//2DTR(A)/Tap Chan |  |  |  | CDC | 726 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR(B) |  | SupLocal | [17 empty] | 1-3F-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_S/L | #2DTR(B) OLTC S/L | MTR | P02//2DTR(B)/SupLocal |  |  |  | CDC | 727 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 2DTR(B) | #2DTR(B) |  | A_M | [17 empty] | 1-3F-03 |  | 2-1B | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR(B)_A/M | #2DTR(B) OLTC A/M | MTR | P02//2DTR(B)/Tap Chan |  |  |  | CDC | 728 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS1 | 1761 | [16 empty] | 1-3E-12 | 1-3E-13 | 2-16 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1761_DS | 1761(#2DTR) DS | MTR | P02/161/1760/DS1 |  |  |  | CDC | 729 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | DS2 | 1762 | [16 empty] | 1-3E-14 | 1-3E-15 | 2-17 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1762_DS | 1762(#2DTR) DS | MTR | P02/161/1760/DS2 |  |  |  | CDC | 730 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | CB | [17 empty] | 2-0A-03 |  | 2-68 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1770_CB | 1770(#3DTR) CB | MTR |  |  |  |  | CDC | 731 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 350 | #3DTR(350) |  | CB | [17 empty] | 1-1A-00 |  | 2-69 | [5 empty] | ADCS_S | [8 empty] | 安南PS.350_CB | 350(#3DTR) CB | MTR | P02/22/350/CB |  |  |  | CDC | 732 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 360 | #3DTR(360) |  | CB | [17 empty] | 1-1A-01 |  | 2-6A | [5 empty] | ADCS_S | [8 empty] | 安南PS.360_CB | 360(#3DTR) CB | MTR | P02/22/360/CB |  |  |  | CDC | 733 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 51ZA | [17 empty] | 2-0A-05 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#3DTR_51ZA | #3DTR 51Z RY | MTR |  |  |  |  | CDC | 734 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 87A | [17 empty] | 2-0A-00 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#3DTR_87A | #3DTR 87RY | MTR |  |  |  |  | CDC | 735 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 350 | #3DTR(350) |  | 51A | [17 empty] | 1-1A-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.350_51A | #3DTR二次側(350) 51RY | MTR | P02/22/350/51A |  |  |  | CDC | 736 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 360 | #3DTR(360) |  | 51A | [17 empty] | 1-1A-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.360_51A | #3DTR二次側(360) 51RY | MTR | P02/22/360/51A |  |  |  | CDC | 737 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 96PA | [17 empty] | 2-0A-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.#3DTR_96PA | #3DTR 機械保護動作 | MTR |  |  |  |  | CDC | 738 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 96D | [17 empty] | 2-39-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_96D | #3DTR 96D RY | MTR | P02//3DTR/96D |  |  |  | CDC | 739 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 96P | [17 empty] | 2-39-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_96P | #3DTR 96P RY | MTR | P02//3DTR/96P |  |  |  | CDC | 740 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 63Q | [17 empty] | 2-39-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_63Q | #3DTR 63Q RY | MTR | P02//3DTR/63Q |  |  |  | CDC | 741 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 96B1 | [17 empty] | 2-39-12 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_96B1 | #3DTR 96B1 RY | MTR | P02//3DTR/96B1 |  |  |  | CDC | 742 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 96B2 | [17 empty] | 2-39-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_96B2 | #3DTR 96B2 RY | MTR | P02//3DTR/96B2 |  |  |  | CDC | 743 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | TRA | [17 empty] | 2-35-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_TRA | #3DTR 重故障 | MTR | P02//3DTR/TRA |  |  |  | CDC | 744 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | TRF | [17 empty] | 2-35-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_TRF | #3DTR 輕故障 | MTR | P02//3DTR/TRF |  |  |  | CDC | 745 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | SupLocal | [17 empty] | 2-35-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_S/L | #3DTR(A) OLTC S/L | MTR | P02//3DTR(A)/SupLocal |  |  |  | CDC | 746 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 3DTR(A) | #3DTR(A) |  | A_M | [17 empty] | 2-35-11 |  | 3-04 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(A)_A/M | #3DTR(A) OLTC A/M | MTR | P02//3DTR(A)/Tap Chan |  |  |  | CDC | 747 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR(B) |  | SupLocal | [17 empty] | 2-35-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_S/L | #3DTR(B) OLTC S/L | MTR | P02//3DTR(B)/SupLocal |  |  |  | CDC | 748 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P02 | 安南PS | 0 |  | 3DTR(B) | #3DTR(B) |  | A_M | [17 empty] | 2-35-12 |  | 3-05 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR(B)_A/M | #3DTR(B) OLTC A/M | MTR | P02//3DTR(B)/Tap Chan |  |  |  | CDC | 749 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS1 | 1771 | [16 empty] | 2-36-00 | 2-36-01 | 3-00 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1771_DS | 1771(#3DTR) DS | MTR | P02/161/1770/DS1 |  |  |  | CDC | 750 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | DS2 | 1772 | [16 empty] | 2-36-02 | 2-36-03 | 3-01 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1772_DS | 1772(#3DTR) DS | MTR | P02/161/1770/DS2 |  |  |  | CDC | 751 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | CB | [17 empty] | 1-0C-04 |  | 2-23 | [5 empty] | ADCS_S | [8 empty] | 安南PS.210_CB | 210(11KV #1SC) CB | SC |  |  |  |  | CDC | 752 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | SC_A_M | [17 empty] | 1-30-03 |  | 2-24 | [5 empty] | ADCS_S | [8 empty] | 安南PS.210_A/M | 11KV #1SC 乏控器 A/M | SC | P02/11/210/SC_A_M |  |  |  | CDC | 753 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | SCA | [17 empty] | 1-0C-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.210_SCA | 11KV #1SC 51,51N RY | SC | P02/11/210/SCA |  |  |  | CDC | 754 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 210 | #1SC(210) |  | UVA | [17 empty] | 1-0C-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.210_UVA | 11KV #1SC 27RY(欠壓) | SC | P02/11/210/UVA |  |  |  | CDC | 755 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | CB | [17 empty] | 1-0C-07 |  | 2-25 | [5 empty] | ADCS_S | [8 empty] | 安南PS.220_CB | 220(11KV #2SC) CB | SC |  |  |  |  | CDC | 756 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | SC_A_M | [17 empty] | 1-30-05 |  | 2-26 | [5 empty] | ADCS_S | [8 empty] | 安南PS.220_A/M | 11KV #2SC 乏控器 A/M | SC | P02/11/220/SC_A_M |  |  |  | CDC | 757 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | SCA | [17 empty] | 1-0C-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.220_SCA | 11KV #2SC 51,51N RY | SC | P02/11/220/SCA |  |  |  | CDC | 758 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 220 | #2SC(220) |  | UVA | [17 empty] | 1-0C-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.220_UVA | 11KV #2SC 27RY(欠壓) | SC | P02/11/220/UVA |  |  |  | CDC | 759 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | CB | [17 empty] | 1-0D-05 |  | 2-29 | [5 empty] | ADCS_S | [8 empty] | 安南PS.230_CB | 230(11KV #3SC) CB | SC |  |  |  |  | CDC | 760 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | SC_A_M | [17 empty] | 1-30-09 |  | 2-2A | [5 empty] | ADCS_S | [8 empty] | 安南PS.230_A/M | 11KV #3SC 乏控器 A/M | SC | P02/11/230/SC_A_M |  |  |  | CDC | 761 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | SCA | [17 empty] | 1-0D-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.230_SCA | 11KV #3SC 51,51N RY | SC | P02/11/230/SCA |  |  |  | CDC | 762 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 230 | #3SC(230) |  | UVA | [17 empty] | 1-0D-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.230_UVA | 11KV #3SC 27RY(欠壓) | SC | P02/11/230/UVA |  |  |  | CDC | 763 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | CB | [17 empty] | 1-0D-02 |  | 2-27 | [5 empty] | ADCS_S | [8 empty] | 安南PS.240_CB | 240(11KV #4SC) CB | SC |  |  |  |  | CDC | 764 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | SC_A_M | [17 empty] | 1-30-07 |  | 2-28 | [5 empty] | ADCS_S | [8 empty] | 安南PS.240_A/M | 11KV #4SC 乏控器 A/M | SC | P02/11/240/SC_A_M |  |  |  | CDC | 765 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | SCA | [17 empty] | 1-0D-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.240_SCA | 11KV #4SC 51,51N RY | SC | P02/11/240/SCA |  |  |  | CDC | 766 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 240 | #4SC(240) |  | UVA | [17 empty] | 1-0D-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.240_UVA | 11KV #4SC 27RY(欠壓) | SC | P02/11/240/UVA |  |  |  | CDC | 767 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | CB | [17 empty] | 1-0E-04 |  | 2-2D | [5 empty] | ADCS_S | [8 empty] | 安南PS.250_CB | 250(11KV #5SC) CB | SC |  |  |  |  | CDC | 768 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | SC_A_M | [17 empty] | 1-30-13 |  | 2-2E | [5 empty] | ADCS_S | [8 empty] | 安南PS.250_A/M | 11KV #5SC 乏控器 A/M | SC | P02/11/250/SC_A_M |  |  |  | CDC | 769 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | SCA | [17 empty] | 1-0E-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.250_SCA | 11KV #5SC 51,51N RY | SC | P02/11/250/SCA |  |  |  | CDC | 770 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 250 | #5SC(250) |  | UVA | [17 empty] | 1-0E-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.250_UVA | 11KV #5SC 27RY(欠壓) | SC | P02/11/250/UVA |  |  |  | CDC | 771 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | CB | [17 empty] | 1-0E-00 |  | 2-2B | [5 empty] | ADCS_S | [8 empty] | 安南PS.260_CB | 260(11KV #6SC) CB | SC |  |  |  |  | CDC | 772 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | SC_A_M | [17 empty] | 1-30-11 |  | 2-2C | [5 empty] | ADCS_S | [8 empty] | 安南PS.260_A/M | 11KV #6SC 乏控器 A/M | SC | P02/11/260/SC_A_M |  |  |  | CDC | 773 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | SCA | [17 empty] | 1-0D-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.260_SCA | 11KV #6SC 51,51N RY | SC | P02/11/260/SCA |  |  |  | CDC | 774 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 260 | #6SC(260) |  | UVA | [17 empty] | 1-0D-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.260_UVA | 11KV #6SC 27RY(欠壓) | SC | P02/11/260/UVA |  |  |  | CDC | 775 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | CB | [17 empty] | 1-1A-06 |  | 2-6B | [5 empty] | ADCS_S | [8 empty] | 安南PS.270_CB | 270(23KV #7SC) CB | SC | P02/22/270/CB |  |  |  | CDC | 776 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | SC_A_M | [17 empty] | 2-35-00 |  | 3-08 | [5 empty] | ADCS_S | [8 empty] | 安南PS.270_A/M | 23KV #7SC 乏控器 A/M | SC | P02/22/270/SC_A_M |  |  |  | CDC | 777 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | SCA | [17 empty] | 1-1A-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.270_SCA | 23KV #7SC 51,51N RY | SC | P02/22/270/SCA |  |  |  | CDC | 778 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 270 | #7SC(270) |  | UVA | [17 empty] | 1-1A-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.270_UVA | 23KV #7SC 27RY(欠壓) | SC | P02/22/270/UVA |  |  |  | CDC | 779 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | CB | [17 empty] | 1-1B-01 |  | 2-6C | [5 empty] | ADCS_S | [8 empty] | 安南PS.280_CB | 280(23KV #8SC) CB | SC | P02/22/280/CB |  |  |  | CDC | 780 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | SC_A_M | [17 empty] | 2-35-02 |  | 3-09 | [5 empty] | ADCS_S | [8 empty] | 安南PS.280_A/M | 23KV #8SC 乏控器 A/M | SC | P02/22/280/SC_A_M |  |  |  | CDC | 781 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | MANUAL
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | SCA | [17 empty] | 1-1A-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.280_SCA | 23KV #8SC 51,51N RY | SC | P02/22/280/SCA |  |  |  | CDC | 782 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | 280 | #8SC(280) |  | UVA | [17 empty] | 1-1B-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.280_UVA | 23KV #8SC 27RY(欠壓) | SC | P02/22/280/UVA |  |  |  | CDC | 783 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | CB | [17 empty] | 1-0B-06 |  | 2-1D | [5 empty] | 69KV_S | [8 empty] | 安南PS.810_CB | 810(69KV #1SC) CB | SC | P02/69/810/CB |  |  |  | CDC | 784 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | DS1 | 811 | [16 empty] | 1-37-08 | 1-37-09 | 2-1E | [5 empty] | ADCS_S | [8 empty] | 安南PS.811_DS | 811(69KV #1SC) DS | SC | P02/69/810/DS1 |  |  |  | CDC | 785 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | DS2 | 812 | [16 empty] | 1-37-10 | 1-37-11 | 2-1F | [5 empty] | ADCS_S | [8 empty] | 安南PS.812_DS | 812(69KV #1SC) DS | SC | P02/69/810/DS2 |  |  |  | CDC | 786 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | SCA | [17 empty] | 1-0B-04 | [7 empty] | 69KV_S | [8 empty] | 安南PS.810_SCA | 69KV #1SC 51,51N RY | SC | P02/69/810/SCA |  |  |  | CDC | 787 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 810 | #1SC(810) |  | UVA | [17 empty] | 1-0B-05 | [7 empty] | 69KV_S | [8 empty] | 安南PS.810_OUVA | 69KV #1SC 27,59RY | SC | P02/69/810/UVA |  |  |  | CDC | 788 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | CB | [17 empty] | 1-0B-03 |  | 2-20 | [5 empty] | 69KV_S | [8 empty] | 安南PS.820_CB | 820(69KV #2SC) CB | SC | P02/69/820/CB |  |  |  | CDC | 789 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | DS1 | 821 | [16 empty] | 1-37-12 | 1-37-13 | 2-21 | [5 empty] | ADCS_S | [8 empty] | 安南PS.821_DS | 821(69KV #2SC) DS | SC | P02/69/820/DS1 |  |  |  | CDC | 790 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | DS2 | 822 | [16 empty] | 1-37-14 | 1-37-15 | 2-22 | [5 empty] | ADCS_S | [8 empty] | 安南PS.822_DS | 822(69KV #2SC) DS | SC | P02/69/820/DS2 |  |  |  | CDC | 791 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | SCA | [17 empty] | 1-0B-07 | [7 empty] | 69KV_S | [8 empty] | 安南PS.820_SCA | 69KV #2SC 51,51N RY | SC | P02/69/820/SCA |  |  |  | CDC | 792 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 820 | #2SC(820) |  | UVA | [17 empty] | 1-0B-02 | [7 empty] | 69KV_S | [8 empty] | 安南PS.820_OUVA | 69KV #2SC 27,59RY | SC | P02/69/820/UVA |  |  |  | CDC | 793 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | CB | [17 empty] | 1-02-04 |  | 1-49 | [5 empty] | 69KV_S | [8 empty] | 安南PS.830_CB | 830(69KV #3SC) CB | SC | P02/69/830/CB |  |  |  | CDC | 794 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | DS1 | 831 | [16 empty] | 1-37-00 | 1-37-01 | 1-4B | [5 empty] | ADCS_S | [8 empty] | 安南PS.831_DS | 831(69KV #3SC) DS | SC | P02/69/830/DS1 |  |  |  | CDC | 795 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | DS2 | 832 | [16 empty] | 1-37-02 | 1-37-03 | 1-4C | [5 empty] | ADCS_S | [8 empty] | 安南PS.832_DS | 832(69KV #3SC) DS | SC | P02/69/830/DS2 |  |  |  | CDC | 796 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | SCA | [17 empty] | 1-02-06 | [7 empty] | 69KV_S | [8 empty] | 安南PS.830_SCA | 69KV #3SC 51,51N RY | SC | P02/69/830/SCA |  |  |  | CDC | 797 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | UVA | [17 empty] | 1-02-07 | [7 empty] | 69KV_S | [8 empty] | 安南PS.830_OUVA | 69KV #3SC 27,59RY | SC | P02/69/830/UVA |  |  |  | CDC | 798 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-3F-12 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | P02/161/1BUS/BUS_VUA |  |  |  | CDC | 799 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-17-03 | [7 empty] | 161KV_S | [8 empty] | 安南PS.161#1BUS_87A | 161KV #1BUS 87RY | BUS | P02/161/1BUS/87A |  |  |  | CDC | 800 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-3F-08 |  | 3-32 | [5 empty] | ADCS_S | [8 empty] | 安南PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | P02/161/1BUS/87UL |  |  |  | CDC | 801 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-3F-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | P02/161/2BUS/BUS_VUA |  |  |  | CDC | 802 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-17-04 | [7 empty] | 161KV_S | [8 empty] | 安南PS.161#2BUS_87A | 161KV #2BUS 87RY | BUS | P02/161/2BUS/87A |  |  |  | CDC | 803 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-3F-09 |  | 3-33 | [5 empty] | ADCS_S | [8 empty] | 安南PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | P02/161/2BUS/87UL |  |  |  | CDC | 804 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-3F-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | P02/69/1BUS/BUS_VUA |  |  |  | CDC | 805 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-17-06 | [7 empty] | 69KV_S | [8 empty] | 安南PS.69#1BUS_87A | 69KV #1BUS 87RY | BUS | P02/69/1BUS/87A |  |  |  | CDC | 806 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 691BUS | #1BUS |  | 87UL | [17 empty] | 1-3F-10 |  | 3-34 | [5 empty] | ADCS_S | [8 empty] | 安南PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | P02/69/1BUS/87UL |  |  |  | CDC | 807 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-3F-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | P02/69/2BUS/BUS_VUA |  |  |  | CDC | 808 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-17-07 | [7 empty] | 69KV_S | [8 empty] | 安南PS.69#2BUS_87A | 69KV #2BUS 87RY | BUS | P02/69/2BUS/87A |  |  |  | CDC | 809 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 692BUS | #2BUS |  | 87UL | [17 empty] | 1-3F-11 |  | 3-35 | [5 empty] | ADCS_S | [8 empty] | 安南PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | P02/69/2BUS/87UL |  |  |  | CDC | 810 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV |  |  |  | CBA | [17 empty] | 2-31-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.11KV_CBA | 11KV斷路器重故障 | OTHER | P02/11/ComPoint/CBA |  |  |  | CDC | 811 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV |  |  |  | CBF | [17 empty] | 2-31-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.11KV_CBF | 11KV斷路器輕故障 | OTHER | P02/11/ComPoint/CBF |  |  |  | CDC | 812 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | _ABS | ABS |  | ABS_89A | [17 empty] | 2-31-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | P02/161/ComPoint/ABS_89A |  |  |  | CDC | 813 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV |  |  |  | CBA | [17 empty] | 2-30-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_CBA | 161KV斷路器重故障 | OTHER | P02/161/ComPoint/CBA |  |  |  | CDC | 814 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV |  |  |  | CBF | [17 empty] | 2-30-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | P02/161/ComPoint/CBF |  |  |  | CDC | 815 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-18-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | P02/0/ComPoint/RCA |  |  |  | CDC | 816 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV |  |  |  | CBA | [17 empty] | 2-35-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.23KV_CBA | 23KV斷路器重故障 | OTHER | P02//3DTR/CBA |  |  |  | CDC | 817 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV |  |  |  | CBF | [17 empty] | 2-35-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.23KV_CBF | 23KV斷路器輕故障 | OTHER | P02//3DTR/CBF |  |  |  | CDC | 818 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 2-31-12 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | P02/69/ComPoint/ABS_89A |  |  |  | CDC | 819 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV |  |  |  | CBA | [17 empty] | 2-31-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_CBA | 69KV斷路器重故障 | OTHER | P02/69/ComPoint/CBA |  |  |  | CDC | 820 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV |  |  |  | CBF | [17 empty] | 2-31-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | P02/69/ComPoint/CBF |  |  |  | CDC | 821 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV |  |  |  | COMT | [17 empty] | 2-31-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69空壓機COMT | 69KV空壓機運轉超時警報 | OTHER | P02/69/ComPoint/COMT |  |  |  | CDC | 822 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | OSCA | [17 empty] | 1-18-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.OSC啟動 | 示波器啟動警報 | OTHER | P02/161/ComPoint/OSCA |  |  |  | CDC | 823 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | P02/0/RTU/RTU_R_L |  |  |  | CDC | 824 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P02 | 安南PS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_S | [8 empty] | 安南PS.TEST_CB | TEST CB | OTHER | P02/0/RTU/Test_CB |  |  |  | CDC | 825 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  |  |  |  | Fire1 | [17 empty] | 2-31-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | P02/0/StaDev/Fire1 |  |  |  | CDC | 826 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | Fire3 | [17 empty] | 2-32-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.火災警報(3) | 火災警報(3) | OTHER | P02/0/StaDev/Fire3 |  |  |  | CDC | 827 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | OPA | [17 empty] | 2-31-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.充油電纜OPA | 充油電纜低油壓警報 | OTHER | P02/0/ComPoint/OPA |  |  |  | CDC | 828 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 25PFA | [17 empty] | 2-30-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | P02/0/ComPoint/25PFA |  |  |  | CDC | 829 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 25TA | [17 empty] | 2-30-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | P02/0/ComPoint/25TA |  |  |  | CDC | 830 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | ACB1 | [17 empty] | 2-30-00 |  | 2-37 | [5 empty] | ADCS_S | [8 empty] | 安南PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | P02/0/StaDev/ACB1 |  |  |  | CDC | 831 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P02 | 安南PS | 0 |  |  |  |  | ACB2 | [17 empty] | 2-30-01 |  | 2-38 | [5 empty] | ADCS_S | [8 empty] | 安南PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | P02/0/StaDev/ACB2 |  |  |  | CDC | 832 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P02 | 安南PS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 2-30-02 |  | 2-39 | [5 empty] | ADCS_S | [8 empty] | 安南PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | P02/0/StaDev/ACB3 |  |  |  | CDC | 833 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P02 | 安南PS | 0 |  |  |  |  | DCA | [17 empty] | 2-32-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.直流電源DCA | 直流電源故障警報 | OTHER | P02/0/StaDev/DCA |  |  |  | CDC | 834 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | DCE | [17 empty] | 2-30-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.直流電源DCE | 直流電源接地故障警報 | OTHER | P02/0/StaDev/DCE |  |  |  | CDC | 835 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | CHG2 | [17 empty] | 2-30-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | P02/0/StaDev/CHG2 |  |  |  | CDC | 836 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | Burglar1 | [17 empty] | 2-32-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.無人化防盜(1) | 無人化防盜(1)保全系統 | OTHER | P02/0/StaDev/Door |  |  |  | CDC | 837 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | Door1 | [17 empty] | 2-30-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.無人化門禁(1) | 無人化門禁(1)控制室門 | OTHER | P02/0/StaDev/Door1 |  |  |  | CDC | 838 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  |  |  |  | Lights1 | [17 empty] | 2-30-11 |  | 2-3A | [5 empty] | ADCS_S | [8 empty] | 安南PS.開關場照明(A) | 開關場照明 | OTHER | P02/0/StaDev/Lights1 |  |  |  | CDC | 839 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P02 | 安南PS | 0 |  |  |  |  | Lights2 | [17 empty] | 2-30-12 |  | 2-3B | [5 empty] | ADCS_S | [8 empty] | 安南PS.開關場照明(B) | 涵洞照明 | OTHER | P02/0/StaDev/Lights2 |  |  |  | CDC | 840 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P02 | 安南PS | 0 |  |  |  |  | 載波機故障警報 | [17 empty] | 2-32-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.載波機故障警報 | 載波機故障警報 | OTHER |  |  |  |  | CDC | 841 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 161#1空壓機 | [17 empty] | 2-31-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161#1空壓機 | 161KV#1空壓機 | OTHER | P02/161/StaDev/1A5Other |  |  |  | CDC | 842 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 161#2空壓機 | [17 empty] | 2-31-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161#2空壓機 | 161KV#2空壓機 | OTHER | P02/161/StaDev/2A5Other |  |  |  | CDC | 843 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | M1A_51Z | #1A |  | U/L | [17 empty] | 1-39-04 |  | 1-0D | [5 empty] | ADCS_S | [8 empty] | 安南PS.M1A_51Z_U/L | #1A DTR中性點51Z RY閉瑣 | OTHER | P02/11/310/51Z_UL |  |  |  | CDC | 844 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | M1B_51Z | #1B |  | U/L | [17 empty] | 1-39-05 |  | 1-0E | [5 empty] | ADCS_S | [8 empty] | 安南PS.M1B_51Z_U/L | #1B DTR中性點51Z RY閉瑣 | OTHER | P02/11/320/51Z_UL |  |  |  | CDC | 845 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | M2A_51Z | #2A |  | U/L | [17 empty] | 1-39-06 |  | 1-13 | [5 empty] | ADCS_S | [8 empty] | 安南PS.M2A_51Z_U/L | #2A DTR中性點51Z RY閉瑣 | OTHER | P02/11/330/51Z_UL |  |  |  | CDC | 846 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | M2B_51Z | #2B |  | U/L | [17 empty] | 1-39-07 |  | 1-14 | [5 empty] | ADCS_S | [8 empty] | 安南PS.M2B_51Z_U/L | #2B DTR中性點51Z RY閉瑣 | OTHER | P02/11/340/51Z_UL |  |  |  | CDC | 847 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | 23_ | 23/ |  | MCSGA | [17 empty] | 2-31-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.MCSGA | 23/11KV MCSG電源跳脫 | OTHER | P02/0/ComPoint/MCSG_89A |  |  |  | CDC | 848 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 2-32-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | P02/0/StaDev/AIRCON |  |  |  | CDC | 849 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
P02 | 安南PS | 22 | 22kV | _SC | 23/ SC |  | 60A | [17 empty] | 2-32-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.23KV_SC_60A | 23/11KV SC 60A | OTHER | P02/0/ComPoint/FDR_60A |  |  |  | CDC | 850 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | PHA | [17 empty] | 1-12-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1720_PHA | 道爺安南新化線(1720) 相間RY | LINE161 | P02/161/1720/PHA |  |  |  | CDC | 851 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 81RY | #2DTR |  | A/S(1) | [17 empty] | 2-0C-00 |  | 2-4D | [5 empty] | ADCS_S | [8 empty] | 安南PS.81RY_A/S(1) | #2DTR 330/340低頻電驛動作 | OTHER |  |  |  |  | CDC | 852 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
P02 | 安南PS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 2-34-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.水位警報(1) | 地下室水位警報(1) | OTHER | P02/0/StaDev/Water1 |  |  |  | CDC | 853 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 2-34-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.水位警報(2) | 地下室水位警報(2) | OTHER | P02/0/StaDev/Water2 |  |  |  | CDC | 854 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | PHA | [17 empty] | 1-05-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_PHA | 11KV南26線(KT26) 相間RY | FEEDER | P02/11/KT26/51A |  |  |  | CDC | 855 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) |  | GDA | [17 empty] | 1-05-01 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_GDA | 11KV南26線(KT26) 接地RY | FEEDER | P02/11/KT26/51NA |  |  |  | CDC | 856 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) 79RY |  | 79UL | [17 empty] | 1-3A-15 |  | 1-5A | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_79UL | 11KV南26線(KT26) 79RY U/L | FEEDER | P02/11/KT26/79UL |  |  |  | CDC | 857 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT26 | 南26線(KT26) LCO分流器 |  | ADJ | [17 empty] | 2-33-05 |  | 2-55 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_ADJ | 11KV南26線(KT26) LCO分流器 U/L | FEEDER | P02/11/KT26/ADJ |  |  |  | CDC | 858 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT26 | KT26(11KV南26線) |  | CB | [17 empty] | 1-04-07 |  | 1-59 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_CB | KT26(11KV南26線) CB | FEEDER | P02/11/KT26/CB |  |  |  | CDC | 859 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | PHA | [17 empty] | 1-08-03 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_PHA | 11KV南35線(KT35) 相間RY | FEEDER | P02/11/KT35/51A |  |  |  | CDC | 860 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) |  | GDA | [17 empty] | 1-08-04 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_GDA | 11KV南35線(KT35) 接地RY | FEEDER | P02/11/KT35/51NA |  |  |  | CDC | 861 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) 79RY |  | 79UL | [17 empty] | 1-3B-08 |  | 1-6C | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_79UL | 11KV南35線(KT35) 79RY U/L | FEEDER | P02/11/KT35/79UL |  |  |  | CDC | 862 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 11 | 11kV | KT35 | 南35線(KT35) LCO分流器 |  | ADJ | [17 empty] | 2-33-14 |  | 2-5E | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_ADJ | 11KV南35線(KT35) LCO分流器 U/L | FEEDER | P02/11/KT35/ADJ |  |  |  | CDC | 863 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 11 | 11kV | KT35 | KT35(11KV南35線) |  | CB | [17 empty] | 1-08-02 |  | 1-6B | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_CB | KT35(11KV南35線) CB | FEEDER | P02/11/KT35/CB |  |  |  | CDC | 864 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | PHA | [17 empty] | 1-1C-07 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_PHA | 23KV南75線(KT75) 相間RY | FEEDER | P02/22/KT75/51A |  |  |  | CDC | 865 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) |  | GDA | [17 empty] | 1-1D-00 | [7 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_GDA | 23KV南75線(KT75) 接地RY | FEEDER | P02/22/KT75/51NA |  |  |  | CDC | 866 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) 79RY |  | 79UL | [17 empty] | 2-37-08 |  | 3-1A | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_79UL | 23KV南75線(KT75) 79RY U/L | FEEDER | P02/22/KT75/79UL |  |  |  | CDC | 867 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 22 | 22kV | KT75 | 南75線(KT75) LCO分流器 |  | ADJ | [17 empty] | 2-38-04 |  | 3-22 | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_ADJ | 23KV南75線(KT75) LCO分流器 U/L | FEEDER | P02/22/KT75/ADJ |  |  |  | CDC | 868 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | LOCK
P02 | 安南PS | 22 | 22kV | KT75 | KT75(23KV南75線) |  | CB | [17 empty] | 1-1C-06 |  | 2-7A | [5 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_CB | KT75(23KV南75線) CB | FEEDER | P02/22/KT75/CB |  |  |  | CDC | 869 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  |  |  |  | CommACF | [17 empty] | 2-39-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | P02/0/StaDev/CommACF |  |  |  | CDC | 870 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | CHG1 | [17 empty] | 2-30-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | P02/0/StaDev/CHG1 |  |  |  | CDC | 871 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | PHA | [17 empty] | 1-18-03 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1550_PHA | 安南南濱一路(1550) 相間RY | LINE161 | P02/161/1550/PHA |  |  |  | CDC | 872 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | GDA | [17 empty] | 1-18-04 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1550_GDA | 安南南濱一路(1550) 接地RY | LINE161 | P02/161/1550/GDA |  |  |  | CDC | 873 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | 87A | [17 empty] | 1-18-05 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1550_87A | 安南南濱一路(1550) 87RY | LINE161 | P02/161/1550/87A |  |  |  | CDC | 874 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | 87UL | [17 empty] | 1-30-14 |  | 1-4D | [5 empty] | ADCS_S | [8 empty] | 安南PS.1550_87UL | 安南南濱一路(1550) 87RY U/L | LINE161 | P02/161/1550/87UL |  |  |  | CDC | 875 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | CB | [17 empty] | 2-0A-06 |  | 2-72 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1550_CB | 1550(安南南濱一路) CB | LINE161 | P02/161/1550/CB |  |  |  | CDC | 876 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | 79UL | [17 empty] | 2-30-10 |  | 2-45 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1550_79UL | 安南南濱一路(1550) 79RY U/L | LINE161 | P02/161/1550/79UL |  |  |  | CDC | 877 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | DS1 | 1551 | [16 empty] | 1-34-00 | 1-34-01 | 1-27 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1551_DS | 1551(安南南濱一路) DS | LINE161 | P02/161/1550/DS1 |  |  |  | CDC | 878 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | DS2 | 1552 | [16 empty] | 1-34-02 | 1-34-03 | 1-28 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1552_DS | 1552(安南南濱一路) DS | LINE161 | P02/161/1550/DS2 |  |  |  | CDC | 879 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | DS3 | 1553 | [16 empty] | 1-34-04 | 1-34-05 | 1-29 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1553_DS | 1553(安南南濱一路) DS | LINE161 | P02/161/1550/DS3 |  |  |  | CDC | 880 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | E3 | 1553E | [16 empty] | 1-34-06 | 1-34-07 | 1-2A | [5 empty] | ADCS_S | [8 empty] | 安南PS.1553E_ES | 1553E(安南南濱一路) ES | LINE161 | P02/161/1550/ES3 |  |  |  | CDC | 881 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | PHA | [17 empty] | 1-18-06 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1560_PHA | 安南南濱二路(1560) 相間RY | LINE161 | P02/161/1560/PHA |  |  |  | CDC | 882 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | GDA | [17 empty] | 1-18-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1560_GDA | 安南南濱二路(1560) 接地RY | LINE161 | P02/161/1560/GDA |  |  |  | CDC | 883 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | 87A | [17 empty] | 1-19-00 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1560_87A | 安南南濱二路(1560) 87RY | LINE161 | P02/161/1560/87A |  |  |  | CDC | 884 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | 87UL | [17 empty] | 1-30-15 |  | 1-4E | [5 empty] | ADCS_S | [8 empty] | 安南PS.1560_87UL | 安南南濱二路(1560) 87RY U/L | LINE161 | P02/161/1560/87UL |  |  |  | CDC | 885 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | CB | [17 empty] | 2-0A-07 |  | 2-73 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1560_CB | 1560(安南南濱二路) CB | LINE161 | P02/161/1560/CB |  |  |  | CDC | 886 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | 79UL | [17 empty] | 2-30-13 |  | 2-46 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1560_79UL | 安南南濱二路(1560) 79RY U/L | LINE161 | P02/161/1560/79UL |  |  |  | CDC | 887 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | DS1 | 1561 | [16 empty] | 2-34-08 | 2-34-09 | 2-47 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1561_DS | 1561(安南南濱二路) DS | LINE161 | P02/161/1560/DS1 |  |  |  | CDC | 888 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | DS2 | 1562 | [16 empty] | 2-34-10 | 2-34-11 | 2-48 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1562_DS | 1562(安南南濱二路) DS | LINE161 | P02/161/1560/DS2 |  |  |  | CDC | 889 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | DS3 | 1563 | [16 empty] | 2-34-12 | 2-34-13 | 2-49 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1563_DS | 1563(安南南濱二路) DS | LINE161 | P02/161/1560/DS3 |  |  |  | CDC | 890 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | E3 | 1563E | [16 empty] | 2-34-14 | 2-34-15 | 2-4A | [5 empty] | ADCS_S | [8 empty] | 安南PS.1563E_ES | 1563E(安南南濱二路) ES | LINE161 | P02/161/1560/ES3 |  |  |  | CDC | 891 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-30-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | P02/161/1500/50SA |  |  |  | CDC | 892 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-3A-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.通信機房溫度 | 通信機房溫度警報 | OTHER | P02/0/StaDev/R_Temp |  |  |  | CDC | 893 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-31-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | P02/161/ComPoint/OSCF |  |  |  | CDC | 894 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV |  |  |  | OSCA | [17 empty] | 1-19-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_OSCA | 69KV示波器啟動 | OTHER | P02/69/ComPoint/OSCA |  |  |  | CDC | 895 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV |  |  |  | OSCF | [17 empty] | 1-38-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | P02/69/ComPoint/OSCF |  |  |  | CDC | 896 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | PHA | [17 empty] | 1-00-02 | [7 empty] | 69KV_S | [8 empty] | 安南PS.620_PHA | 安南運河線(620) 相間RY | LINE69 | P02/69/620/PHA |  |  |  | CDC | 897 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | GDA | [17 empty] | 1-00-03 | [7 empty] | 69KV_S | [8 empty] | 安南PS.620_GDA | 安南運河線(620) 接地RY | LINE69 | P02/69/620/GDA |  |  |  | CDC | 898 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | CB | [17 empty] | 1-00-00 |  | 1-37 | [5 empty] | 69KV_S | [8 empty] | 安南PS.620_CB | 620(安南運河線) CB | LINE69 | P02/69/620/CB |  |  |  | CDC | 899 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | DS1 | 621 | [16 empty] | 1-34-08 | 1-34-09 | 1-39 | [5 empty] | ADCS_S | [8 empty] | 安南PS.621_DS | 621(安南運河線) DS | LINE69 | P02/69/620/DS1 |  |  |  | CDC | 900 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | DS2 | 622 | [16 empty] | 1-34-10 | 1-34-11 | 1-3A | [5 empty] | ADCS_S | [8 empty] | 安南PS.622_DS | 622(安南運河線) DS | LINE69 | P02/69/620/DS2 |  |  |  | CDC | 901 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | DS3 | 623 | [16 empty] | 1-34-12 | 1-34-13 | 1-3B | [5 empty] | ADCS_S | [8 empty] | 安南PS.623_DS | 623(安南運河線) DS | LINE69 | P02/69/620/DS3 |  |  |  | CDC | 902 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | E3 | 623E | [16 empty] | 1-34-14 | 1-34-15 | 1-3C | [5 empty] | ADCS_S | [8 empty] | 安南PS.623E_ES | 623E(安南運河線) ES | LINE69 | P02/69/620/ES3 |  |  |  | CDC | 903 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 0 |  | 100 | TIE(100) |  | CB | [17 empty] | 1-0E-05 |  | 2-35 | [5 empty] | ADCS_S | [8 empty] | 安南PS.100_CB | 100(TIE) CB | TIE |  |  |  |  | CDC | 904 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 100 | TIE(100) |  | 51A | [17 empty] | 1-0E-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.100_51A | 11KV TIE(100) 51RY | TIE |  |  |  |  | CDC | 905 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 100 | TIE(100) |  | 51NA | [17 empty] | 1-0E-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.100_51NA | 11KV TIE(100) 51N RY | TIE |  |  |  |  | CDC | 906 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 200 | TIE(200) |  | CB | [17 empty] | 1-0F-00 |  | 2-36 | [5 empty] | ADCS_S | [8 empty] | 安南PS.200_CB | 200(TIE) CB | TIE |  |  |  |  | CDC | 907 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 200 | TIE(200) |  | 51A | [17 empty] | 1-0F-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.200_51A | 11KV TIE(200) 51RY | TIE |  |  |  |  | CDC | 908 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 200 | TIE(200) |  | 51NA | [17 empty] | 1-0F-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.200_51NA | 11KV TIE(200) 51N RY | TIE |  |  |  |  | CDC | 909 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 300 | TIE(300) |  | CB | [17 empty] | 1-1F-00 |  | 2-6E | [5 empty] | ADCS_S | [8 empty] | 安南PS.300_CB | 300(TIE) CB | TIE | P02/22/300/CB |  |  |  | CDC | 910 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 300 | TIE(300) |  | 51A | [17 empty] | 1-1F-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.300_51A | 23KV TIE(300) 51RY | TIE | P02/22/300/51A |  |  |  | CDC | 911 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 300 | TIE(300) |  | 51NA | [17 empty] | 1-1F-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.300_51NA | 23KV TIE(300) 51N RY | TIE | P02/22/300/51NA |  |  |  | CDC | 912 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | 87A | [17 empty] | 1-11-01 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1510_87A | 安南小北一路(1510) 87RY | LINE161 | P02/161/1510/87A |  |  |  | CDC | 913 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | 87UL | [17 empty] | 1-38-14 |  | 2-43 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1510_87UL | 安南小北一路(1510) 87RY U/L | LINE161 | P02/161/1510/87UL |  |  |  | CDC | 914 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | 79UL | [17 empty] | 1-39-12 |  | 2-4B | [5 empty] | ADCS_S | [8 empty] | 安南PS.1510_79UL | 安南小北一路(1510) 79RY U/L | LINE161 | P02/161/1510/79UL |  |  |  | CDC | 915 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1510 | 安南小北一路(1510) |  | 87CFA | [17 empty] | 2-32-13 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1510_87CFA | 安南小北一路(1510)87RY通訊故障 | OTHER | P02/161/1510/87CFA |  |  |  | CDC | 916 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1510 | 安南小北一路(1510) |  | RYFA | [17 empty] | 2-32-12 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1510_RYFA | 安南小北一路(1510)數位電驛故障 | OTHER | P02/161/1510/RYFA |  |  |  | CDC | 917 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | PHA | [17 empty] | 1-11-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1510_PHA | 安南小北一路(1510) 相間RY | LINE161 | P02/161/1510/PHA |  |  |  | CDC | 918 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | PHA | [17 empty] | 1-11-06 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1520_PHA | 安南小北二路(1520) 相間RY | LINE161 | P02/161/1520/PHA |  |  |  | CDC | 919 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | 87A | [17 empty] | 1-11-05 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1520_87A | 安南小北二路(1520) 87RY | LINE161 | P02/161/1520/87A |  |  |  | CDC | 920 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | 87UL | [17 empty] | 1-38-15 |  | 2-44 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1520_87UL | 安南小北二路(1520) 87RY U/L | LINE161 | P02/161/1520/87UL |  |  |  | CDC | 921 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | 79UL | [17 empty] | 1-39-13 |  | 2-4C | [5 empty] | ADCS_S | [8 empty] | 安南PS.1520_79UL | 安南小北二路(1520) 79RY U/L | LINE161 | P02/161/1520/79UL |  |  |  | CDC | 922 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1520 | 安南小北二路(1520) |  | 87CFA | [17 empty] | 2-32-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1520_87CFA | 安南小北二路(1520)87RY通訊故障 | OTHER | P02/161/1520/87CFA |  |  |  | CDC | 923 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1520 | 安南小北二路(1520) |  | RYFA | [17 empty] | 2-32-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1520_RYFA | 安南小北二路(1520)數位電驛故障 | OTHER | P02/161/1520/RYFA |  |  |  | CDC | 924 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | PHA | [17 empty] | 1-10-02 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1530_PHA | 安南鹽行線(1530) 相間RY | LINE161 | P02/161/1530/PHA |  |  |  | CDC | 925 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | 87A | [17 empty] | 1-10-01 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1530_87A | 安南鹽行線(1530) 87RY | LINE161 | P02/161/1530/87A |  |  |  | CDC | 926 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | 87UL | [17 empty] | 1-39-00 |  | 1-02 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1530_87UL | 安南鹽行線(1530) 87RY U/L | LINE161 | P02/161/1530/87UL |  |  |  | CDC | 927 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1530 | 安南鹽行線(1530) |  | 87CFA | [17 empty] | 2-34-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1530_87CFA | 安南鹽行線(1530)87RY通訊故障 | OTHER | P02/161/1530/87CFA |  |  |  | CDC | 928 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1530 | 安南鹽行線(1530) |  | RYFA | [17 empty] | 2-34-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1530_RYFA | 安南鹽行線(1530)數位電驛故障 | OTHER | P02/161/1530/RYFA |  |  |  | CDC | 929 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1550 | 安南南濱一路(1550) |  | 87CFA | [17 empty] | 1-3A-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1550_87CFA | 安南南濱一路(1550)87RY通訊故障 | OTHER | P02/161/1550/87CFA |  |  |  | CDC | 930 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1550 | 安南南濱一路(1550) |  | RYFA | [17 empty] | 1-3A-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1550_RYFA | 安南南濱一路(1550)數位電驛故障 | OTHER | P02/161/1550/RYFA |  |  |  | CDC | 931 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1560 | 安南南濱二路(1560) |  | 87CFA | [17 empty] | 1-3B-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1560_87CFA | 安南南濱二路(1560)87RY通訊故障 | OTHER | P02/161/1560/87CFA |  |  |  | CDC | 932 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1560 | 安南南濱二路(1560) |  | RYFA | [17 empty] | 1-3B-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1560_RYFA | 安南南濱二路(1560)數位電驛故障 | OTHER | P02/161/1560/RYFA |  |  |  | CDC | 933 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1710 | 山上豐華紅線(1710) |  | RYFA | [17 empty] | 2-32-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1710_RYFA | 山上豐華紅線(1710)數位電驛故障 | OTHER | P02/161/1710/RYFA |  |  |  | CDC | 934 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1720 | 道爺安南新化線(1720) |  | RYFA | [17 empty] | 1-30-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1720_RYFA | 道爺安南新化(1720)數位電驛故障 | OTHER | P02/161/1720/RYFA |  |  |  | CDC | 935 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | PHA | [17 empty] | 1-10-06 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1710_PHA | 山上豐華紅線(1710) 相間RY | LINE161 | P02/161/1710/PHA |  |  |  | CDC | 936 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | 87A | [17 empty] | 1-12-01 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1720_87A | 道爺安南新化線(1720) 87RY | LINE161 | P02/161/1720/87A |  |  |  | CDC | 937 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | 87UL | [17 empty] | 1-39-08 |  | 1-1A | [5 empty] | ADCS_S | [8 empty] | 安南PS.1720_87UL | 道爺安南新化線(1720) 87RY U/L | LINE161 | P02/161/1720/87UL |  |  |  | CDC | 938 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1720 | 道爺安南新化線(1720) |  | 87CFA | [17 empty] | 1-30-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1720_87CFA | 道爺安南新化(1720)87RY通訊故障 | OTHER | P02/161/1720/87CFA |  |  |  | CDC | 939 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | 87A | [17 empty] | 1-00-01 | [7 empty] | 69KV_S | [8 empty] | 安南PS.620_87A | 安南運河線(620) 87RY | LINE69 | P02/69/620/87A |  |  |  | CDC | 940 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | 87UL | [17 empty] | 1-3A-02 |  | 1-38 | [5 empty] | ADCS_S | [8 empty] | 安南PS.620_87UL | 安南運河線(620) 87RY U/L | LINE69 | P02/69/620/87UL |  |  |  | CDC | 941 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 620 | 安南運河線(620) |  | 87CFA | [17 empty] | 1-3A-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.620_87CFA | 安南運河線(620)87RY通訊故障 | OTHER | P02/69/620/87CFA |  |  |  | CDC | 942 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 620 | 安南運河線(620) |  | RYFA | [17 empty] | 1-3C-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.620_RYFA | 安南運河線(620)數位電驛故障 | OTHER | P02/69/620/RYFA |  |  |  | CDC | 943 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | 81RYFA | [17 empty] | 2-3A-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.81RYFA | 低頻電驛故障 | OTHER | P02/0/ComPoint/RYFA |  |  |  | CDC | 944 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | BVS | BVS |  | RY | [17 empty] | 2-3A-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.BVS_RY | BVS GRZ100 RY U/L | OTHER | P02/0/ComPoint/GRZ100 |  |  |  | CDC | 945 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | LOCK/USE | USE
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | 87A1 | [17 empty] | 1-10-05 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1710_87A1 | 山上豐華紅線(1710) #1 87RY | LINE161 | P02/161/1710/87A1 |  |  |  | CDC | 946 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | 87A2 | [17 empty] | 1-13-00 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1710_87A2 | 山上豐華紅線(1710) #2 87RY | LINE161 | P02/161/1710/87A2 |  |  |  | CDC | 947 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | 1_87UL1 | [17 empty] | 1-39-02 |  | 1-08 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1710_87UL1 | 山上豐華紅線(1710) #1 87RY U/L | LINE161 | P02/161/1710/1_87UL1 |  |  |  | CDC | 948 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | 1_87UL2 | [17 empty] | 2-3A-04 |  | 2-4E | [5 empty] | ADCS_S | [8 empty] | 安南PS.1710_87UL2 | 山上豐華紅線(1710) #2 87RY U/L | LINE161 | P02/161/1710/1_87UL2 |  |  |  | CDC | 949 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1710 | 山上豐華紅線(1710) |  | 87CFA | [17 empty] | 2-32-10 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1710_87CFA | 山上豐華紅線(1710)87RY通訊故障 | OTHER | P02/161/1710/87CFA |  |  |  | CDC | 950 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | Fire4 | [17 empty] | 2-32-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.火災警報(4) | 火災警報(4)-主(配)變火警 | OTHER | P02/0/StaDev/Fire4 |  |  |  | CDC | 951 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | 87A | [17 empty] | 1-00-06 | [7 empty] | 69KV_S | [8 empty] | 安南PS.630_87A | 安順白線(630) 87RY | LINE69 | P02/69/630/87A |  |  |  | CDC | 952 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | 87UL | [17 empty] | 1-39-14 |  | 1-2C | [5 empty] | ADCS_S | [8 empty] | 安南PS.630_87UL | 安順白線(630) 87RY U/L | LINE69 | P02/69/630/87UL |  |  |  | CDC | 953 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 630 | 安順白線(630) |  | 87CFA | [17 empty] | 1-39-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.630_87CFA | 安南安順白線(630)87RY通訊故障 | OTHER | P02/69/630/87CFA |  |  |  | CDC | 954 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 630 | 安順白線(630) |  | RYFA | [17 empty] | 2-35-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.630_RYFA | 安南安順白線(630)數位電驛故障 | OTHER | P02/69/630/RYFA |  |  |  | CDC | 955 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | 87A | [17 empty] | 1-01-01 | [7 empty] | 69KV_S | [8 empty] | 安南PS.640_87A | 安順紅線(640) 87RY | LINE69 | P02/69/640/87A |  |  |  | CDC | 956 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | 87UL | [17 empty] | 1-3A-00 |  | 1-32 | [5 empty] | ADCS_S | [8 empty] | 安南PS.640_87UL | 安順紅線(640) 87RY U/L | LINE69 | P02/69/640/87UL |  |  |  | CDC | 957 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 640 | 安順紅線(640) |  | 87CFA | [17 empty] | 1-3A-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.640_87CFA | 安南安順紅線(640)87RY通訊故障 | OTHER | P02/69/640/87CFA |  |  |  | CDC | 958 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 640 | 安順紅線(640) |  | RYFA | [17 empty] | 2-35-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.640_RYFA | 安南安順紅線(640)數位電驛故障 | OTHER | P02/69/640/RYFA |  |  |  | CDC | 959 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  |  |  |  | GEN | [17 empty] | 2-3A-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.GEN | 緊急發電機運轉 | OTHER | P02/0/StaDev/3A5Other |  |  |  | CDC | 960 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P02 | 安南PS | 0 |  |  |  |  | STUV | [17 empty] | 2-3A-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | P02/0/StaDev/STUV |  |  |  | CDC | 961 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 2-3A-12 |  | 3-0A | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | P02//2MTR/51Z_UL |  |  |  | CDC | 962 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 2-0B-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_86A | #2MTR 86RY | OTHER |  |  |  |  | CDC | 963 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-3D-14 |  | 3-02 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | P02//2MTR/87UL |  |  |  | CDC | 964 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 2-3A-10 |  | 3-03 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | P02//2MTR/1_87UL2 |  |  |  | CDC | 965 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | GDA | [17 empty] | 2-0B-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_GDA | #2MTR GDA | OTHER |  |  |  |  | CDC | 966 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 2-3A-11 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | P02//2MTR/RYFA |  |  |  | CDC | 967 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 51Z_UL | [17 empty] | 2-3A-14 |  | 3-2A | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_51ZUL | #1DTR 51ZRY U/L | OTHER | P02//1DTR/51Z_UL |  |  |  | CDC | 968 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | DTR_86A | [17 empty] | 2-0B-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_86A | #1DTR 86RY | OTHER |  |  |  |  | CDC | 969 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 1_87UL1 | [17 empty] | 1-3E-10 |  | 3-28 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_87UL1 | #1DTR #1 87RY U/L | OTHER | P02//1DTR/1_87UL1 |  |  |  | CDC | 970 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | 1_87UL2 | [17 empty] | 2-3A-13 |  | 3-29 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_87UL2 | #1DTR #2 87RY U/L | OTHER | P02//1DTR/87UL |  |  |  | CDC | 971 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | GDA | [17 empty] | 2-0B-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_GDA | #1DTR GDA | OTHER |  |  |  |  | CDC | 972 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | PHA | [17 empty] | 1-15-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_PHA | #1DTR PHA | OTHER | P02//1DTR/PHA |  |  |  | CDC | 973 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1DTR | #1DTR |  | RYFA | [17 empty] | 2-3B-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1DTR_RYFA | #1DTR數位電驛故障 | OTHER | P02//1DTR/RYFA |  |  |  | CDC | 974 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2MTR | #2MTR |  | PHA | [17 empty] | 1-14-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2MTR_PHA | #2MTR PHA | OTHER | P02//2MTR/PHA |  |  |  | CDC | 975 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 51Z_UL | [17 empty] | 2-3A-09 |  | 2-66 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_51ZUL | #1MTR 51ZRY U/L | OTHER | P02//1MTR/51Z_UL |  |  |  | CDC | 976 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | MTR_86A | [17 empty] | 2-0B-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_86A | #1MTR 86RY | OTHER |  |  |  |  | CDC | 977 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 1_87UL1 | [17 empty] | 1-3C-14 |  | 2-64 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_87UL1 | #1MTR #1 87RY U/L | OTHER | P02//1MTR/87UL |  |  |  | CDC | 978 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | 1_87UL2 | [17 empty] | 2-3A-07 |  | 2-65 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_87UL2 | #1MTR #2 87RY U/L | OTHER | P02//1MTR/1_87UL2 |  |  |  | CDC | 979 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | GDA | [17 empty] | 2-0B-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_GDA | #1MTR GDA | OTHER |  |  |  |  | CDC | 980 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | PHA | [17 empty] | 1-13-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_PHA | #1MTR PHA | OTHER | P02//1MTR/PHA |  |  |  | CDC | 981 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1MTR | #1MTR |  | RYFA | [17 empty] | 2-3A-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#1MTR_RYFA | #1MTR數位電驛故障 | OTHER | P02//1MTR/RYFA |  |  |  | CDC | 982 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 51Z_UL | [17 empty] | 2-3B-03 |  | 3-31 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_51ZUL | #3DTR 51ZRY U/L | OTHER | P02//3DTR/51Z_UL |  |  |  | CDC | 983 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | DTR_86A | [17 empty] | 2-0C-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_86A | #3DTR 86RY | OTHER |  |  |  |  | CDC | 984 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 1_87UL1 | [17 empty] | 2-35-15 |  | 3-2F | [5 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_87UL1 | #3DTR #1 87RY U/L | OTHER | P02//3DTR/1_87UL1 |  |  |  | CDC | 985 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | 1_87UL2 | [17 empty] | 2-3B-02 |  | 3-30 | [5 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_87UL2 | #3DTR #2 87RY U/L | OTHER | P02//3DTR/87UL |  |  |  | CDC | 986 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | GDA | [17 empty] | 2-0C-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_GDA | #3DTR GDA | OTHER |  |  |  |  | CDC | 987 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | PHA | [17 empty] | 2-0A-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_PHA | #3DTR PHA | OTHER |  |  |  |  | CDC | 988 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 3DTR | #3DTR |  | RYFA | [17 empty] | 2-3B-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#3DTR_RYFA | #3DTR數位電驛故障 | OTHER | P02//3DTR/RYFA |  |  |  | CDC | 989 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 350 | #3DTR(350) |  | 51NA | [17 empty] | 1-0F-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.350_51N | #3DTR 350 51NRY | OTHER |  |  |  |  | CDC | 990 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 360 | #3DTR(360) |  | 51NA | [17 empty] | 1-0F-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.360_51N | #3DTR 360 51NRY | OTHER |  |  |  |  | CDC | 991 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 81RY | #2DTR |  | U/L(1) | [17 empty] | 2-3B-01 |  | 3-2E | [5 empty] | ADCS_S | [8 empty] | 安南PS.81RY_U/L(1) | #2DTR 81RY U/L | OTHER | P02//2MTR/81A |  |  |  | CDC | 992 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 51Z_UL | [17 empty] | 2-3B-00 |  | 3-2D | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_51ZUL | #2DTR 51ZRY U/L | OTHER | P02//2DTR/51Z_UL |  |  |  | CDC | 993 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | DTR_86A | [17 empty] | 2-0B-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_86A | #2DTR 86RY | OTHER |  |  |  |  | CDC | 994 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 1_87UL1 | [17 empty] | 1-3F-06 |  | 3-2B | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_87UL1 | #2DTR #1 87RY U/L | OTHER | P02//2DTR/1_87UL1 |  |  |  | CDC | 995 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | 1_87UL2 | [17 empty] | 2-3A-15 |  | 3-2C | [5 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_87UL2 | #2DTR #2 87RY U/L | OTHER | P02//2DTR/87UL |  |  |  | CDC | 996 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | GDA | [17 empty] | 2-0B-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_GDA | #2DTR GDA | OTHER |  |  |  |  | CDC | 997 | GENERICDIPoint | PS013_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | PHA | [17 empty] | 1-16-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_PHA | #2DTR PHA | OTHER | P02//2DTR/PHA |  |  |  | CDC | 998 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 2DTR | #2DTR |  | RYFA | [17 empty] | 2-3B-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.#2DTR_RYFA | #2DTR數位電驛故障 | OTHER | P02//2DTR/RYFA |  |  |  | CDC | 999 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 | [17 empty] | 1-17-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | P02/69/600/GDA1 |  |  |  | CDC | 1000 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 | [17 empty] | 1-19-03 | [7 empty] | ADCS_S | [8 empty] | 安南PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | P02/69/600/GDA2 |  |  |  | CDC | 1001 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 | [17 empty] | 1-17-01 | [7 empty] | ADCS_S | [8 empty] | 安南PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | P02/69/600/PHA1 |  |  |  | CDC | 1002 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 | [17 empty] | 1-19-02 | [7 empty] | ADCS_S | [8 empty] | 安南PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | P02/69/600/PHA2 |  |  |  | CDC | 1003 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | RYFA | [17 empty] | 2-3B-07 | [7 empty] | ADCS_S | [8 empty] | 安南PS.600_RYFA | 69KV 600 TIE 數位電驛故障 | OTHER | P02/69/600/RYFA |  |  |  | CDC | 1004 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | PHA | [17 empty] | 1-12-06 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1740_PHA | 安南和順線(1740) 相間RY | LINE161 | P02/161/1740/PHA |  |  |  | CDC | 1005 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | GDA | [17 empty] | 1-12-07 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1740_GDA | 安南和順線(1740) 接地RY | LINE161 | P02/161/1740/GDA |  |  |  | CDC | 1006 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | 87A | [17 empty] | 1-12-05 | [7 empty] | 161KV_S | [8 empty] | 安南PS.1740_87A | 安南和順線(1740) 87RY | LINE161 | P02/161/1740/87A |  |  |  | CDC | 1007 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | 87UL | [17 empty] | 1-39-10 |  | 1-20 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1740_87UL | 安南和順線(1740) 87RY U/L | LINE161 | P02/161/1740/87UL |  |  |  | CDC | 1008 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | CB | [17 empty] | 1-12-04 |  | 2-41 | [5 empty] | 161KV_S | [8 empty] | 安南PS.1740_CB | 1740(安南和順線) CB | LINE161 | P02/161/1740/CB |  |  |  | CDC | 1009 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | 79UL | [17 empty] | 1-39-11 |  | 1-1F | [5 empty] | ADCS_S | [8 empty] | 安南PS.1740_79UL | 安南和順線(1740) 79RY U/L | LINE161 | P02/161/1740/79UL |  |  |  | CDC | 1010 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | DS1 | 1741 | [16 empty] | 1-33-08 | 1-33-09 | 1-21 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1741_DS | 1741(安南和順線) DS | LINE161 | P02/161/1740/DS1 |  |  |  | CDC | 1011 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | DS2 | 1742 | [16 empty] | 1-33-10 | 1-33-11 | 1-22 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1742_DS | 1742(安南和順線) DS | LINE161 | P02/161/1740/DS2 |  |  |  | CDC | 1012 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | DS3 | 1743 | [16 empty] | 1-33-12 | 1-33-13 | 1-23 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1743_DS | 1743(安南和順線) DS | LINE161 | P02/161/1740/DS3 |  |  |  | CDC | 1013 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | E3 | 1743E | [16 empty] | 1-33-14 | 1-33-15 | 1-24 | [5 empty] | ADCS_S | [8 empty] | 安南PS.1743E_ES | 1743E(安南和順線) ES | LINE161 | P02/161/1740/ES3 |  |  |  | CDC | 1014 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P02 | 安南PS | 0 |  | 1740 | 安南和順線(1740) |  | 87CFA | [17 empty] | 2-31-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1740_87CFA | 安南和順線(1740)87RY通訊故障 | OTHER | P02/161/1740/87CFA |  |  |  | CDC | 1015 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 1740 | 安南和順線(1740) |  | RYFA | [17 empty] | 2-31-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.1740_RYFA | 安南和順線(1740)數位電驛故障 | OTHER | P02/161/1740/RYFA |  |  |  | CDC | 1016 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-37-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_BUS_CTFA | 161KV BUS CT迴路故障 | OTHER | P02/161/BUS/87CTFA |  |  |  | CDC | 1017 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 2-37-14 | [7 empty] | ADCS_S | [8 empty] | 安南PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | P02/161/BUS/RYFA |  |  |  | CDC | 1018 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-3B-09 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_BUS_CTFA | 69KV BUS CT迴路故障 | OTHER | P02/69/BUS/87CTFA |  |  |  | CDC | 1019 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 2-3B-08 | [7 empty] | ADCS_S | [8 empty] | 安南PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | P02/69/BUS/RYFA |  |  |  | CDC | 1020 | GENERICDIPoint | PS013_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P02 | 安南PS | 0 |  | OLTC | OLTC |  | OLTCA | [17 empty] | 1-3D-15 | [7 empty] | ADCS_S | [8 empty] | 安南PS.OLTCA | OLTC 15分鐘連動3次 | OTHER | P02/0/ComPoint/OLTC_A |  |  |  | CDC | 1021 | GENERICDIPoint | PS013_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 310 | #1DTR(310) |  | GDA | [17 empty] | 1-15-06 | [7 empty] | ADCS_S | [8 empty] | 安南PS.310_GDA | 11KV M1A(310) 51N RY | OTHER |  |  |  |  | CDC | 1022 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 320 | #1DTR(320) |  | GDA | [17 empty] | 1-16-04 | [7 empty] | ADCS_S | [8 empty] | 安南PS.320_GDA | 11KV M1B(320) 51N RY | OTHER |  |  |  |  | CDC | 1023 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 330 | #2DTR(330) |  | GDA | [17 empty] | 1-17-05 | [7 empty] | ADCS_S | [8 empty] | 安南PS.330_GDA | 11KV M2A(330) 51N RY | OTHER |  |  |  |  | CDC | 1024 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 0 |  | 340 | #2DTR(340) |  | GDA | [17 empty] | 1-18-00 | [7 empty] | ADCS_S | [8 empty] | 安南PS.340_GDA | 11KV M2B(340) 51N RY | OTHER |  |  |  |  | CDC | 1025 | GENERICDIPoint | PS013_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P02 | 安南PS | 11 | 11kV | 210_SC | #1SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.210_SC_CAP | 11KV#1SC 容量 | SC | [5 empty] | 1026 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 220_SC | #2SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.220_SC_CAP | 11KV#2SC 容量 | SC | [5 empty] | 1027 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 230_SC | #3SC | 3 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.230_SC_CAP | 11KV#3SC 容量 | SC | [5 empty] | 1028 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 240_SC | #4SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.240_SC_CAP | 11KV#4SC 容量 | SC | [5 empty] | 1029 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 250_SC | #5SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.250_SC_CAP | 11KV#5SC 容量 | SC | [5 empty] | 1030 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 11 | 11kV | 260_SC | #6SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.260_SC_CAP | 11KV#6SC 容量 | SC | [5 empty] | 1031 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 22 | 22kV | 270_SC | #7SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.270_SC_CAP | 23KV#7SC 容量 | SC | [5 empty] | 1032 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 22 | 22kV | 280_SC | #8SC | 6 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.280_SC_CAP | 23KV#8SC 容量 | SC | [5 empty] | 1033 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 810_SC | #1SC | 28.799999 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.810_SC_CAP | 69KV#1SC 容量 | SC | [5 empty] | 1034 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 820_SC | #2SC | 28.799999 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.820_SC_CAP | 69KV#2SC 容量 | SC | [5 empty] | 1035 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 69 | 69kV | 830_SC | #3SC | 43.200001 | CAP | [25 empty] | ADCS_S | [8 empty] | 安南PS.830_SC_CAP | 69KV#3SC 容量 | SC | [5 empty] | 1036 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 079 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_079 | 安南PS NT 69KV_Hi_Limit | [6 empty] | 1037 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 080 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_080 | 安南PS NT 69KV_Lo_Limit | [6 empty] | 1038 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 081 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_081 | 安南PS NT #1ADTR 11KV_Hi_Limit | [6 empty] | 1039 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 082 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_082 | 安南PS NT #1ADTR 11KV_Lo_Limit | [6 empty] | 1040 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 083 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_083 | 安南PS NT #2ADTR 11KV_Hi_Limit | [6 empty] | 1041 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 084 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_084 | 安南PS NT #2ADTR 11KV_Lo_Limit | [6 empty] | 1042 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 085 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_085 | 安南PS NT #2BDTR 11KV_Hi_Limit | [6 empty] | 1043 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 086 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_086 | 安南PS NT #2BDTR 11KV_Lo_Limit | [6 empty] | 1044 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 087 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_087 | 安南PS NT #1BDTR 11KV_Hi_Limit | [6 empty] | 1045 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 088 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_088 | 安南PS NT #1BDTR 11KV_Lo_Limit | [6 empty] | 1046 | NotelAIPoint | [21 empty] | LG_11 | 7.200000 | 7.200000 | 7.600000 | 9.000000 | 0.200000 | 6.500000 | 6.500000 | 6.200000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 089 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_089 | 安南PS NT #3ADTR 23KV_Hi_Limit | [6 empty] | 1047 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 090 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_090 | 安南PS NT #3ADTR 23KV_Lo_Limit | [6 empty] | 1048 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 091 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_091 | 安南PS NT #3BDTR 23KV_Hi_Limit | [6 empty] | 1049 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P02 | 安南PS | 0 |  | TRD | 安南PS |  | 092 | [25 empty] | TRAIN_AD | [8 empty] | 安南PS.TRD_092 | 安南PS NT #3BDTR 23KV_Lo_Limit | [6 empty] | 1050 | NotelAIPoint | [21 empty] | LG_23 | 14.200000 | 14.200000 | 15.200000 | 18.000000 | 0.200000 | 12.360000 | 12.360000 | 12.360000 | 0.000000
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1510LE | 1510LE (非取樣點) | LINE161 | P02/161/1510/LE0 |  |  |  |  | 1051 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1510 | 安南小北一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1510BE | 1510BE (非取樣點) | LINE161 | P02/161/1510/BE0 |  |  |  |  | 1052 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1520LE | 1520LE (非取樣點) | LINE161 | P02/161/1520/LE0 |  |  |  |  | 1053 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1520 | 安南小北二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1520BE | 1520BE (非取樣點) | LINE161 | P02/161/1520/BE0 |  |  |  |  | 1054 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | LE0 | 1530LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1530LE | 1530LE (非取樣點) | LINE161 | P02/161/1530/LE0 |  |  |  |  | 1055 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1530 | 安南鹽行線(1530) |  | BE0 | 1530BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1530BE | 1530BE (非取樣點) | LINE161 | P02/161/1530/BE0 |  |  |  |  | 1056 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | LE0 | 1710LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1710LE | 1710LE (非取樣點) | LINE161 | P02/161/1710/LE0 |  |  |  |  | 1057 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1710 | 山上豐華紅線(1710) |  | BE0 | 1710BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1710BE | 1710BE (非取樣點) | LINE161 | P02/161/1710/BE0 |  |  |  |  | 1058 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | LE0 | 1720LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1720LE | 1720LE (非取樣點) | LINE161 | P02/161/1720/LE0 |  |  |  |  | 1059 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1720 | 道爺安南新化線(1720) |  | BE0 | 1720BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1720BE | 1720BE (非取樣點) | LINE161 | P02/161/1720/BE0 |  |  |  |  | 1060 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | LE0 | 630LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.630LE | 630LE (非取樣點) | LINE69 | P02/69/630/LE0 |  |  |  |  | 1061 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | BE0 | 630BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.630BE | 630BE (非取樣點) | LINE69 | P02/69/630/BE0 |  |  |  |  | 1062 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | LE0 | 640LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.640LE | 640LE (非取樣點) | LINE69 | P02/69/640/LE0 |  |  |  |  | 1063 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | BE0 | 640BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.640BE | 640BE (非取樣點) | LINE69 | P02/69/640/BE0 |  |  |  |  | 1064 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT21 | KT21_DS |  | DS1 | KT21_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_DS | KT21_DS (非取樣點) | FEEDER | P02/11/KT21/DS |  |  |  |  | 1065 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT21 | KT21_ES |  | LE0 | KT21_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT21_ES | KT21_ES (非取樣點) | FEEDER | P02/11/KT21/ES |  |  |  |  | 1066 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT22 | KT22_DS |  | DS1 | KT22_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_DS | KT22_DS (非取樣點) | FEEDER | P02/11/KT22/DS |  |  |  |  | 1067 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT22 | KT22_ES |  | LE0 | KT22_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT22_ES | KT22_ES (非取樣點) | FEEDER | P02/11/KT22/ES |  |  |  |  | 1068 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT23 | KT23_DS |  | DS1 | KT23_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_DS | KT23_DS (非取樣點) | FEEDER | P02/11/KT23/DS |  |  |  |  | 1069 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT23 | KT23_ES |  | LE0 | KT23_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT23_ES | KT23_ES (非取樣點) | FEEDER | P02/11/KT23/ES |  |  |  |  | 1070 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT24 | KT24_DS |  | DS1 | KT24_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_DS | KT24_DS (非取樣點) | FEEDER | P02/11/KT24/DS |  |  |  |  | 1071 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT24 | KT24_ES |  | LE0 | KT24_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT24_ES | KT24_ES (非取樣點) | FEEDER | P02/11/KT24/ES |  |  |  |  | 1072 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT25 | KT25_DS |  | DS1 | KT25_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_DS | KT25_DS (非取樣點) | FEEDER | P02/11/KT25/DS |  |  |  |  | 1073 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT25 | KT25_ES |  | LE0 | KT25_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT25_ES | KT25_ES (非取樣點) | FEEDER | P02/11/KT25/ES |  |  |  |  | 1074 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT27 | KT27_DS |  | DS1 | KT27_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_DS | KT27_DS (非取樣點) | FEEDER | P02/11/KT27/DS |  |  |  |  | 1075 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT27 | KT27_ES |  | LE0 | KT27_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT27_ES | KT27_ES (非取樣點) | FEEDER | P02/11/KT27/ES |  |  |  |  | 1076 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT28 | KT28_DS |  | DS1 | KT28_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_DS | KT28_DS (非取樣點) | FEEDER | P02/11/KT28/DS |  |  |  |  | 1077 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT28 | KT28_ES |  | LE0 | KT28_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT28_ES | KT28_ES (非取樣點) | FEEDER | P02/11/KT28/ES |  |  |  |  | 1078 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT29 | KT29_DS |  | DS1 | KT29_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_DS | KT29_DS (非取樣點) | FEEDER | P02/11/KT29/DS |  |  |  |  | 1079 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT29 | KT29_ES |  | LE0 | KT29_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT29_ES | KT29_ES (非取樣點) | FEEDER | P02/11/KT29/ES |  |  |  |  | 1080 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT30 | KT30_DS |  | DS1 | KT30_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_DS | KT30_DS (非取樣點) | FEEDER | P02/11/KT30/DS |  |  |  |  | 1081 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT30 | KT30_ES |  | LE0 | KT30_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT30_ES | KT30_ES (非取樣點) | FEEDER | P02/11/KT30/ES |  |  |  |  | 1082 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT31 | KT31_DS |  | DS1 | KT31_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_DS | KT31_DS (非取樣點) | FEEDER | P02/11/KT31/DS |  |  |  |  | 1083 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT31 | KT31_ES |  | LE0 | KT31_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT31_ES | KT31_ES (非取樣點) | FEEDER | P02/11/KT31/ES |  |  |  |  | 1084 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT32 | KT32_DS |  | DS1 | KT32_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_DS | KT32_DS (非取樣點) | FEEDER | P02/11/KT32/DS |  |  |  |  | 1085 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT32 | KT32_ES |  | LE0 | KT32_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT32_ES | KT32_ES (非取樣點) | FEEDER | P02/11/KT32/ES |  |  |  |  | 1086 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT33 | KT33_DS |  | DS1 | KT33_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_DS | KT33_DS (非取樣點) | FEEDER | P02/11/KT33/DS |  |  |  |  | 1087 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT33 | KT33_ES |  | LE0 | KT33_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT33_ES | KT33_ES (非取樣點) | FEEDER | P02/11/KT33/ES |  |  |  |  | 1088 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT34 | KT34_DS |  | DS1 | KT34_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_DS | KT34_DS (非取樣點) | FEEDER | P02/11/KT34/DS |  |  |  |  | 1089 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT34 | KT34_ES |  | LE0 | KT34_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT34_ES | KT34_ES (非取樣點) | FEEDER | P02/11/KT34/ES |  |  |  |  | 1090 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT36 | KT36_DS |  | DS1 | KT36_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_DS | KT36_DS (非取樣點) | FEEDER | P02/11/KT36/DS |  |  |  |  | 1091 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT36 | KT36_ES |  | LE0 | KT36_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT36_ES | KT36_ES (非取樣點) | FEEDER | P02/11/KT36/ES |  |  |  |  | 1092 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT37 | KT37_DS |  | DS1 | KT37_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_DS | KT37_DS (非取樣點) | FEEDER | P02/11/KT37/DS |  |  |  |  | 1093 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT37 | KT37_ES |  | LE0 | KT37_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT37_ES | KT37_ES (非取樣點) | FEEDER | P02/11/KT37/ES |  |  |  |  | 1094 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT38 | KT38_DS |  | DS1 | KT38_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_DS | KT38_DS (非取樣點) | FEEDER | P02/11/KT38/DS |  |  |  |  | 1095 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT38 | KT38_ES |  | LE0 | KT38_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT38_ES | KT38_ES (非取樣點) | FEEDER | P02/11/KT38/ES |  |  |  |  | 1096 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT39 | KT39_DS |  | DS1 | KT39_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_DS | KT39_DS (非取樣點) | FEEDER | P02/11/KT39/DS |  |  |  |  | 1097 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT39 | KT39_ES |  | LE0 | KT39_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT39_ES | KT39_ES (非取樣點) | FEEDER | P02/11/KT39/ES |  |  |  |  | 1098 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT40 | KT40_DS |  | DS1 | KT40_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_DS | KT40_DS (非取樣點) | FEEDER | P02/11/KT40/DS |  |  |  |  | 1099 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT40 | KT40_ES |  | LE0 | KT40_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT40_ES | KT40_ES (非取樣點) | FEEDER | P02/11/KT40/ES |  |  |  |  | 1100 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT71 | KT71_DS |  | DS1 | KT71_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_DS | KT71_DS (非取樣點) | FEEDER | P02/22/KT71/DS |  |  |  |  | 1101 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT71 | KT71_ES |  | LE0 | KT71_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT71_ES | KT71_ES (非取樣點) | FEEDER | P02/22/KT71/ES |  |  |  |  | 1102 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT72 | KT72_DS |  | DS1 | KT72_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_DS | KT72_DS (非取樣點) | FEEDER | P02/22/KT72/DS |  |  |  |  | 1103 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT72 | KT72_ES |  | LE0 | KT72_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT72_ES | KT72_ES (非取樣點) | FEEDER | P02/22/KT72/ES |  |  |  |  | 1104 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT73 | KT73_DS |  | DS1 | KT73_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_DS | KT73_DS (非取樣點) | FEEDER | P02/22/KT73/DS |  |  |  |  | 1105 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT73 | KT73_ES |  | LE0 | KT73_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT73_ES | KT73_ES (非取樣點) | FEEDER | P02/22/KT73/ES |  |  |  |  | 1106 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT74 | KT74_DS |  | DS1 | KT74_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_DS | KT74_DS (非取樣點) | FEEDER | P02/22/KT74/DS |  |  |  |  | 1107 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT74 | KT74_ES |  | LE0 | KT74_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT74_ES | KT74_ES (非取樣點) | FEEDER | P02/22/KT74/ES |  |  |  |  | 1108 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT76 | KT76_DS |  | DS1 | KT76_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_DS | KT76_DS (非取樣點) | FEEDER | P02/22/KT76/DS |  |  |  |  | 1109 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT76 | KT76_ES |  | LE0 | KT76_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT76_ES | KT76_ES (非取樣點) | FEEDER | P02/22/KT76/ES |  |  |  |  | 1110 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT77 | KT77_DS |  | DS1 | KT77_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_DS | KT77_DS (非取樣點) | FEEDER | P02/22/KT77/DS |  |  |  |  | 1111 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT77 | KT77_ES |  | LE0 | KT77_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT77_ES | KT77_ES (非取樣點) | FEEDER | P02/22/KT77/ES |  |  |  |  | 1112 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT78 | KT78_DS |  | DS1 | KT78_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_DS | KT78_DS (非取樣點) | FEEDER | P02/22/KT78/DS |  |  |  |  | 1113 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT78 | KT78_ES |  | LE0 | KT78_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT78_ES | KT78_ES (非取樣點) | FEEDER | P02/22/KT78/ES |  |  |  |  | 1114 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT79 | KT79_DS |  | DS1 | KT79_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_DS | KT79_DS (非取樣點) | FEEDER | P02/22/KT79/DS |  |  |  |  | 1115 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT79 | KT79_ES |  | LE0 | KT79_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT79_ES | KT79_ES (非取樣點) | FEEDER | P02/22/KT79/ES |  |  |  |  | 1116 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_S | [8 empty] | 安南PS.1501E | 1501E (非取樣點) | TIE | P02/161/1500/E1 |  |  |  |  | 1117 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_S | [8 empty] | 安南PS.1502E | 1502E (非取樣點) | TIE | P02/161/1500/E2 |  |  |  |  | 1118 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_S | [8 empty] | 安南PS.601E | 601E (非取樣點) | TIE | P02/69/600/E1 |  |  |  |  | 1119 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_S | [8 empty] | 安南PS.602E | 602E (非取樣點) | TIE | P02/69/600/E2 |  |  |  |  | 1120 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | TE0 | 1650TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1650TE | 1650TE (非取樣點) | MTR | P02/161/1650/TE0 |  |  |  |  | 1121 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | TE0 | 750TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.750TE | 750TE (非取樣點) | MTR | P02/69/750/TE0 |  |  |  |  | 1122 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | NE0 | 1651N | [24 empty] | ADCS_S | [8 empty] | 安南PS.1651N | 1651N (非取樣點) | MTR | P02/161/1650/NE0 |  |  |  |  | 1123 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 161 | 161kV | 1650 | #1MTR(1650) |  | BE0 | 1650BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1650BE | 1650BE (非取樣點) | MTR | P02/161/1650/BE0 |  |  |  |  | 1124 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 750 | #1MTR(750) |  | BE0 | 750BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.750BE | 750BE (非取樣點) | MTR | P02/69/750/BE0 |  |  |  |  | 1125 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1660TE | 1660TE (非取樣點) | MTR | P02/161/1660/TE0 |  |  |  |  | 1126 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.760TE | 760TE (非取樣點) | MTR | P02/69/760/TE0 |  |  |  |  | 1127 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | NE0 | 1661N | [24 empty] | ADCS_S | [8 empty] | 安南PS.1661N | 1661N (非取樣點) | MTR | P02/161/1660/NE0 |  |  |  |  | 1128 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1660BE | 1660BE (非取樣點) | MTR | P02/161/1660/BE0 |  |  |  |  | 1129 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.760BE | 760BE (非取樣點) | MTR | P02/69/760/BE0 |  |  |  |  | 1130 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | TE0 | 1750TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1750TE | 1750TE (非取樣點) | MTR | P02/161/1750/TE0 |  |  |  |  | 1131 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1750 | #1DTR(1750) |  | BE0 | 1750BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1750BE | 1750BE (非取樣點) | MTR | P02/161/1750/BE0 |  |  |  |  | 1132 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 310 | #1DTR(310) |  | DS1 | 310_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.310_DS | 310_DS (非取樣點) | MTR | P02/11/310/DS |  |  |  |  | 1133 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 310 | #1DTR(310) |  | LE0 | 310_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.310_ES | 310_ES (非取樣點) | MTR | P02/11/310/ES |  |  |  |  | 1134 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 320 | #1DTR(320) |  | DS1 | 320_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.320_DS | 320_DS (非取樣點) | MTR | P02/11/320/DS |  |  |  |  | 1135 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 320 | #1DTR(320) |  | LE0 | 320_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.320_ES | 320_ES (非取樣點) | MTR | P02/11/320/ES |  |  |  |  | 1136 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | TE0 | 1760TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1760TE | 1760TE (非取樣點) | MTR | P02/161/1760/TE0 |  |  |  |  | 1137 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1760 | #2DTR(1760) |  | BE0 | 1760BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1760BE | 1760BE (非取樣點) | MTR | P02/161/1760/BE0 |  |  |  |  | 1138 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 330 | #2DTR(330) |  | DS1 | 330_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.330_DS | 330_DS (非取樣點) | MTR | P02/11/330/DS |  |  |  |  | 1139 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 330 | #2DTR(330) |  | LE0 | 330_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.330_ES | 330_ES (非取樣點) | MTR | P02/11/330/ES |  |  |  |  | 1140 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 340 | #2DTR(340) |  | DS1 | 340_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.340_DS | 340_DS (非取樣點) | MTR | P02/11/340/DS |  |  |  |  | 1141 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 340 | #2DTR(340) |  | LE0 | 340_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.340_ES | 340_ES (非取樣點) | MTR | P02/11/340/ES |  |  |  |  | 1142 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | TE0 | 1770TE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1770TE | 1770TE (非取樣點) | MTR | [5 empty] | 1143 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1770 | #3DTR(1770) |  | BE0 | 1770BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1770BE | 1770BE (非取樣點) | MTR | [5 empty] | 1144 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 350 | #3DTR(350) |  | DS1 | 350_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.350_DS | 350_DS (非取樣點) | MTR | P02/22/350/DS |  |  |  |  | 1145 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 350 | #3DTR(350) |  | LE0 | 350_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.350_ES | 350_ES (非取樣點) | MTR | P02/22/350/ES |  |  |  |  | 1146 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 360 | #3DTR(360) |  | DS1 | 360_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.360_DS | 360_DS (非取樣點) | MTR | P02/22/360/DS |  |  |  |  | 1147 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 360 | #3DTR(360) |  | LE0 | 360_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.360_ES | 360_ES (非取樣點) | MTR | P02/22/360/ES |  |  |  |  | 1148 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 210 | #1SC(210) |  | LE0 | 210_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.210_ES | 210_ES (非取樣點) | SC | P02/11/210/ES |  |  |  |  | 1149 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 210 | #1SC(210) |  | DS1 | 210_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.210_DS | 210_DS (非取樣點) | SC | P02/11/210/DS |  |  |  |  | 1150 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 220 | #2SC(220) |  | LE0 | 220_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.220_ES | 220_ES (非取樣點) | SC | P02/11/220/ES |  |  |  |  | 1151 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 220 | #2SC(220) |  | DS1 | 220_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.220_DS | 220_DS (非取樣點) | SC | P02/11/220/DS |  |  |  |  | 1152 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 230 | #3SC(230) |  | LE0 | 230_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.230_ES | 230_ES (非取樣點) | SC | P02/11/230/ES |  |  |  |  | 1153 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 230 | #3SC(230) |  | DS1 | 230_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.230_DS | 230_DS (非取樣點) | SC | P02/11/230/DS |  |  |  |  | 1154 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 240 | #4SC(240) |  | LE0 | 240_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.240_ES | 240_ES (非取樣點) | SC | P02/11/240/ES |  |  |  |  | 1155 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 240 | #4SC(240) |  | DS1 | 240_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.240_DS | 240_DS (非取樣點) | SC | P02/11/240/DS |  |  |  |  | 1156 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 250 | #5SC(250) |  | LE0 | 250_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.250_ES | 250_ES (非取樣點) | SC | P02/11/250/ES |  |  |  |  | 1157 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 250 | #5SC(250) |  | DS1 | 250_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.250_DS | 250_DS (非取樣點) | SC | P02/11/250/DS |  |  |  |  | 1158 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 260 | #6SC(260) |  | LE0 | 260_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.260_ES | 260_ES (非取樣點) | SC | P02/11/260/ES |  |  |  |  | 1159 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 260 | #6SC(260) |  | DS1 | 260_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.260_DS | 260_DS (非取樣點) | SC | P02/11/260/DS |  |  |  |  | 1160 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 270 | #7SC(270) |  | LE0 | 270_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.270_ES | 270_ES (非取樣點) | SC | P02/22/270/ES |  |  |  |  | 1161 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 270 | #7SC(270) |  | DS1 | 270_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.270_DS | 270_DS (非取樣點) | SC | P02/22/270/DS |  |  |  |  | 1162 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 280 | #8SC(280) |  | LE0 | 280_ES | [24 empty] | ADCS_S | [8 empty] | 安南PS.280_ES | 280_ES (非取樣點) | SC | P02/22/280/ES |  |  |  |  | 1163 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 280 | #8SC(280) |  | DS1 | 280_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.280_DS | 280_DS (非取樣點) | SC | P02/22/280/DS |  |  |  |  | 1164 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 810BE | 810BE |  | 810BE | 810BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.810BE | 810BE (非取樣點) | SC | P02/69/810/BE0 |  |  |  |  | 1165 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 810CE | 810CE |  | 810CE | 810CE | [24 empty] | ADCS_S | [8 empty] | 安南PS.810CE | 810CE (非取樣點) | SC | P02/69/810/CE0 |  |  |  |  | 1166 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 820BE | 820BE |  | 820BE | 820BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.820BE | 820BE (非取樣點) | SC | P02/69/820/BE0 |  |  |  |  | 1167 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 820CE | 820CE |  | 820CE | 820CE | [24 empty] | ADCS_S | [8 empty] | 安南PS.820CE | 820CE (非取樣點) | SC | P02/69/820/CE0 |  |  |  |  | 1168 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 830BE | 830BE |  | 830BE | 830BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.830BE | 830BE (非取樣點) | SC | P02/69/830/BE0 |  |  |  |  | 1169 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_S | [8 empty] | 安南PS.161B1E | 161B1E (非取樣點) | BUS | P02/161/161B1E/BE1 |  |  |  |  | 1170 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_S | [8 empty] | 安南PS.161B2E | 161B2E (非取樣點) | BUS | P02/161/161B2E/BE2 |  |  |  |  | 1171 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_S | [8 empty] | 安南PS.69B1E | 69B1E (非取樣點) | BUS | P02/69/69B1E/BE1 |  |  |  |  | 1172 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_S | [8 empty] | 安南PS.69B2E | 69B2E (非取樣點) | BUS | P02/69/69B2E/BE2 |  |  |  |  | 1173 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_S | [8 empty] | 安南PS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 1174 | NotelDIPoint | [38 empty] | START/STOP | STOP
P02 | 安南PS | 69 | 69kV | 830 | #3SC(830) |  | DS3 | 833 | [24 empty] | ADCS_S | [8 empty] | 安南PS.833_DS | 833_DS (非取樣點) | SC | P02/69/830/DS3 |  |  |  |  | 1175 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | PW1UL | 630_PW1UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.630_PW1UL | 安順白線(630)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1176 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | PW2UL | 630_PW2UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.630_PW2UL | 安順白線(630)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1177 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P02 | 安南PS | 69 | 69kV | 630 | 安順白線(630) |  | HCBUL | 630_HCBUL | [24 empty] | ADCS_S | [8 empty] | 安南PS.630_HCBUL | 安順白線(630)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1178 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | PW1UL | 640_PW1UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.640_PW1UL | 安順紅線(640)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1179 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | PW2UL | 640_PW2UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.640_PW2UL | 安順紅線(640)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1180 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P02 | 安南PS | 69 | 69kV | 640 | 安順紅線(640) |  | HCBUL | 640_HCBUL | [24 empty] | ADCS_S | [8 empty] | 安南PS.640_HCBUL | 安順紅線(640)HCB_UL (非取樣點) | LINE69 | [5 empty] | 1181 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 670 | 運河臨時(670)PW1_UL |  | PW1UL | 670_PW1UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.670_PW1UL | 運河臨時(670)PW1_UL (非取樣點) | LINE69 | [5 empty] | 1182 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 670 | 運河臨時(670)PW2_UL |  | PW2UL | 670_PW2UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.670_PW2UL | 運河臨時(670)PW2_UL (非取樣點) | LINE69 | [5 empty] | 1183 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P02 | 安南PS | 69 | 69kV | 670 | 運河臨時(670)HCB_UL |  | HCBUL | 670_HCBUL | [24 empty] | ADCS_S | [8 empty] | 安南PS.670_HCBUL | 運河臨時(670)HCB_UL (非取樣點) | LINE69 | [5 empty] | 1184 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 1730 | 1730 |  | PW1UL | 1730_PW1UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.1730_PW1UL | 新化一路(1730)PW1_UL(非取樣點) | LINE69 | [5 empty] | 1185 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 1730 | 1730 |  | PW2UL | 1730_PW2UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.1730_PW2UL | 新化一路(1730)PW2_UL(非取樣點) | LINE69 | [5 empty] | 1186 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P02 | 安南PS | 69 | 69kV | 1730 | 1730 |  | HCBUL | 1730_HCBUL | [24 empty] | ADCS_S | [8 empty] | 安南PS.1730_HCBUL | 新化一路(1730)HCB_UL(非取樣點) | LINE69 | [5 empty] | 1187 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 0 |  | KT26 | KT26_DS |  | DS1 | KT26_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_DS | KT26_DS (非取樣點) | FEEDER | P02/11/KT26/DS |  |  |  |  | 1188 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT26 | KT26_ES |  | LE0 | KT26_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT26_ES | KT26_ES (非取樣點) | FEEDER | P02/11/KT26/ES |  |  |  |  | 1189 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | KT35 | KT35_DS |  | DS1 | KT35_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_DS | KT35_DS (非取樣點) | FEEDER | P02/11/KT35/DS |  |  |  |  | 1190 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT35 | KT35_ES |  | LE0 | KT35_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT35_ES | KT35_ES (非取樣點) | FEEDER | P02/11/KT35/ES |  |  |  |  | 1191 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 安南PS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 1192 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 安南PS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 1193 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_S | [8 empty] | 安南PS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 1194 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_S | [8 empty] | 安南PS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 1195 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT75 | KT75_DS |  | DS1 | KT75_DS | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_DS | KT75_DS (非取樣點) | FEEDER | P02/22/KT75/DS |  |  |  |  | 1196 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | KT75 | KT75_ES |  | LE0 | KT75_ES | [24 empty] | DDCS4_1 | [8 empty] | 安南PS.KT75_ES | KT75_ES (非取樣點) | FEEDER | P02/22/KT75/ES |  |  |  |  | 1197 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | LE0 | 1550LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1550LE | 1550LE (非取樣點) | LINE161 | P02/161/1550/LE0 |  |  |  |  | 1198 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1550 | 安南南濱一路(1550) |  | BE0 | 1550BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1550BE | 1550BE (非取樣點) | LINE161 | P02/161/1550/BE0 |  |  |  |  | 1199 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1560LE | 1560LE (非取樣點) | LINE161 | P02/161/1560/LE0 |  |  |  |  | 1200 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1560 | 安南南濱二路(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1560BE | 1560BE (非取樣點) | LINE161 | P02/161/1560/BE0 |  |  |  |  | 1201 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | LE0 | 620LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.620LE | 620LE (非取樣點) | LINE69 | P02/69/620/LE0 |  |  |  |  | 1202 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | BE0 | 620BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.620BE | 620BE (非取樣點) | LINE69 | P02/69/620/BE0 |  |  |  |  | 1203 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 100 | TIE(100) |  | DS1 | 100_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.100_DS | 100_DS (非取樣點) | TIE | P02/11/100/DS |  |  |  |  | 1204 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 200 | TIE(200) |  | DS1 | 200_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.200_DS | 200_DS (非取樣點) | TIE | P02/11/200/DS |  |  |  |  | 1205 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 300 | TIE(300) |  | DS1 | 300_DS | [24 empty] | ADCS_S | [8 empty] | 安南PS.300_DS | 300_DS (非取樣點) | TIE | P02/22/300/DS |  |  |  |  | 1206 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | PW1UL | 620_PW1UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.620_PW1UL | 運河線(620)PW1_UL (非取樣點) | LINE69 | [5 empty] | 1207 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P02 | 安南PS | 69 | 69kV | 620 | 安南運河線(620) |  | PW2UL | 620_PW2UL | [24 empty] | ADCS_S | [8 empty] | 安南PS.620_PW2UL | 運河線(620)PW2_UL (非取樣點) | LINE69 | [5 empty] | 1208 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P02 | 安南PS | 0 |  | 210E | 210E |  | 210E | 210E | [24 empty] | ADCS_S | [8 empty] | 安南PS.210E | 210E (非取樣點) | SC | P02/11/210/CE0 |  |  |  |  | 1209 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 220E | 220E |  | 220E | 220E | [24 empty] | ADCS_S | [8 empty] | 安南PS.220E | 220E (非取樣點) | SC | P02/11/220/CE0 |  |  |  |  | 1210 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 230E | 230E |  | 230E | 230E | [24 empty] | ADCS_S | [8 empty] | 安南PS.230E | 230E (非取樣點) | SC | P02/11/230/CE0 |  |  |  |  | 1211 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 240E | 240E |  | 240E | 240E | [24 empty] | ADCS_S | [8 empty] | 安南PS.240E | 240E (非取樣點) | SC | P02/11/240/CE0 |  |  |  |  | 1212 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 250E | 250E |  | 250E | 250E | [24 empty] | ADCS_S | [8 empty] | 安南PS.250E | 250E (非取樣點) | SC | P02/11/250/CE0 |  |  |  |  | 1213 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 260E | 260E |  | 260E | 260E | [24 empty] | ADCS_S | [8 empty] | 安南PS.260E | 260E (非取樣點) | SC | P02/11/260/CE0 |  |  |  |  | 1214 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 270E | 270E |  | 270E | 270E | [24 empty] | ADCS_S | [8 empty] | 安南PS.270E | 270E (非取樣點) | SC | [5 empty] | 1215 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 280E | 280E |  | 280E | 280E | [24 empty] | ADCS_S | [8 empty] | 安南PS.280E | 280E (非取樣點) | SC | [5 empty] | 1216 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | LE0 | 1740LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1740LE | 1740LE (非取樣點) | LINE161 | P02/161/1740/LE0 |  |  |  |  | 1217 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 161 | 161kV | 1740 | 安南和順線(1740) |  | BE0 | 1740BE | [24 empty] | ADCS_S | [8 empty] | 安南PS.1740BE | 1740BE (非取樣點) | LINE161 | P02/161/1740/BE0 |  |  |  |  | 1218 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 830LE | 830LE |  | 830LE | 830LE | [24 empty] | ADCS_S | [8 empty] | 安南PS.830LE | 830LE (非取樣點) | SC | P02/69/830/LE0 |  |  |  |  | 1219 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  |  |  |  | 833CE | 833CE | [24 empty] | ADCS_S | [8 empty] | 安南PS.833CE | 833CE(非取樣點) | OTHER | P02/69/830/CE3 |  |  |  |  | 1220 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P02 | 安南PS | 0 |  | 1ABUS | 1ABUS |  | PTD | 1ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 安南PS.1ABUS_PTD | #1ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1221 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 1BBUS | 1BBUS |  | PTD | 1BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 安南PS.1BBUS_PTD | #1BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1222 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 2ABUS | 2ABUS |  | PTD | 2ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 安南PS.2ABUS_PTD | #2ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1223 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 2BBUS | 2BBUS |  | PTD | 2BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 安南PS.2BBUS_PTD | #2BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1224 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 3ABUS | 3ABUS |  | PTD | 3ABUS_PTD | [24 empty] | ADCS_S | [8 empty] | 安南PS.3ABUS_PTD | #3ABUS_PTD(非取樣點) | OTHER | [5 empty] | 1225 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P02 | 安南PS | 0 |  | 3BBUS | 3BBUS |  | PTD | 3BBUS_PTD | [24 empty] | ADCS_S | [8 empty] | 安南PS.3BBUS_PTD | #3BBUS_PTD(非取樣點) | OTHER | [5 empty] | 1226 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo