## 版本
版本 | 20181205 | 欄位 | 說明
|  | B1 Name | TA
B1 Text
日期 | 說明 | B2 Name
B2 Text
B3 Name
B3 Text
Element Instance
Element Name
Element Text
|  | Manual Adjustment | 手動調整
|  | Info Name | TA
Info Text
ValueName
GenSUM
AL1/3/5/7
AI/DI Type
Info Order
|  | Topo_Type | Topology Type
Topo_ExtN1
Topo_ExtN2
Topo_ExtN3
Topo_ExtN4
|  | DNP Mon1 | DNP Index
DNP Mon2
DNP Cmd
|  | CDC Mon1 | CDC Index
CDC Mon2
CDC Cmd
|  | DEV locate | Point List Descript
Unit_Status
Descript
CharacteristicCurve
Postion
AoR
Spu
Qpu
CT
MVA
V-FS
A-FS
P-FS
Q-FS
|  | PointName | DBSave 或 健格 或 Spectrum3 資料
PointDesc
GraphicDesc
Point Ref
Point Memo
Limit Group Name
|  | Point Area | RTU名稱
|  | Point Class | DNP 或 CDC
|  | OldRow | 原資料Row
|  | Tag | DBSave 或 健格 或 Spectrum3 資料註記
Tag Mon1
Tag Mon2
Tag Cmd
Tag Info
|  | Compare Memo | 比對註記
|  | Element Name | Spectrum 3 原資訊
Element Text
Info Name
Info Text
|  | MvLimName | Analog Limitation
MvLim01U
MvLim02U
MvLim03U
MvLim04U
MvLim05U
MvLim01L
MvLim02L
MvLim03L
MvLim04L
MvLim05L

## 資料
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P04 | 北港PS | 0 |  | RTU | RTU |  | Test_CB |  |  | Status | TEST CB | Open/Close | Y | 7 | DI-SP | [6 empty] | 0512 |  | 0000 | 1-30-00 |  | 1-00 | TEST CB | ON/OFF | TEST CB |  |  | ELEM/ALL | [8 empty] | 北港PS.TEST_CB | TEST CB | OTHER | [5 empty] | 2 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/備用線/T1 |  | 0098 |  | 0002 | 1-0C-02 |  | 1-02 | 1560 | ON/OFF | 北港台西二路 1560 CB |  | aaha | B2/P04_A1 | [8 empty] | 北港PS.1560_CB | 1560(台西二路) CB | LINE161 | [5 empty] | 3 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0516 |  | 0146 | 1-30-04 |  | 2-12 | 1560 | USE/LOCK | 北港台西二 路 1560 79S U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_79UL | 台西二路(1560) 79RY U/L | LINE161 | [5 empty] | 138 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | 85UL |  |  | Status | 85RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0517 |  | 0147 | 1-30-05 |  | 2-13 | 1560 | USE/LOCK | 北港台西二路 1560 85S U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_85UL | 台西二路(1560) 85RY U/L | LINE161 | [5 empty] | 139 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | ABS1 | 1561 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0760 | 761 | 0152 | 1-3F-08 | 1-3F-09 | 2-18 | 1561 | ON | 北港台西二路 1561 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1561_ABS | 1561(台西二路) ABS | LINE161 | [5 empty] | 140 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | ABS2 | 1562 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0762 | 763 | 0153 | 1-3F-10 | 1-3F-11 | 2-19 | 1562 | ON | 北港台西二路 1562 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1562_ABS | 1562(台西二路) ABS | LINE161 | [5 empty] | 141 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ABS1 | 1641 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0544 | 545 | 0009 | 1-32-00 | 1-32-01 | 1-09 | 1641 | ON | 嘉民北港北線 1641 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1641_ABS | 1641(嘉民北線) ABS | LINE161 | [5 empty] | 8 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ABS2 | 1642 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0546 | 547 | 0010 | 1-32-02 | 1-32-03 | 1-0A | 1642 | ON | 嘉民北港北線 1642 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1642_ABS | 1642(嘉民北線) ABS | LINE161 | [5 empty] | 9 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ABS3 | 1643 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0548 | 549 | 0011 | 1-32-04 | 1-32-05 | 1-0B | 1643 | ON | 嘉民北港北線 1643 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1643_ABS | 1643(嘉民北線) ABS | LINE161 | [5 empty] | 10 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | ES3 | 1643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0550 | 551 | 0012 | 1-32-06 | 1-32-07 | 1-0C | 1643E | ON | 嘉民北港北線 1643E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1643E_ES | 1643E(嘉民北線) ES | LINE161 | [5 empty] | 11 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0124 |  |  | 1-0F-04 |  |  | 640 | 87A | 北港朴子線 640 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.640_87A | 北港朴子線(640) 87RY | LINE69 | [5 empty] | 380 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0168 |  |  | 1-15-00 |  |  | 670 | 87A | 北港新港一路 670 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.670_87A | 北港新港一路(670) 87RY | LINE69 | [5 empty] | 413 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ABS1 | 1631 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0536 | 537 | 0015 | 1-31-08 | 1-31-09 | 1-0F | 1631 | ON | 嘉民北港南線 1631 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1631_ABS | 1631(嘉民南線) ABS | LINE161 | [5 empty] | 14 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ABS2 | 1632 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0538 | 539 | 0016 | 1-31-10 | 1-31-11 | 1-10 | 1632 | ON | 嘉民北港南線 1632 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1632_ABS | 1632(嘉民南線) ABS | LINE161 | [5 empty] | 15 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ABS3 | 1633 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0540 | 541 | 0017 | 1-31-12 | 1-31-13 | 1-11 | 1633 | ON | 嘉民北港南線 1633 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1633_ABS | 1633(嘉民南線) ABS | LINE161 | [5 empty] | 16 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | ES3 | 1633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0542 | 543 | 0018 | 1-31-14 | 1-31-15 | 1-12 | 1633E | ON | 嘉民北港南線 1633E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1633E_ES | 1633E(嘉民南線) ES | LINE161 | [5 empty] | 17 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0169 |  |  | 1-15-01 |  |  | 680 | 87A | 北港新港二路 680 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.680_87A | 北港新港二路(680) 87RY | LINE69 | [5 empty] | 414 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | LE0 | 1550LE(非取樣點) | B3 | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1550LE | 1550LE (非取樣點) | LINE161 | [5 empty] | 216 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0171 |  |  | 1-15-03 |  |  | 620 | 87A | 北港水林二路 620 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.620_87A | 北港水林二路(620) 87RY | LINE69 | [5 empty] | 416 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0172 |  |  | 1-15-04 |  |  | 630 | 87A | 北港水林一路 630 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.630_87A | 北港水林一路(630) 87RY | LINE69 | [5 empty] | 417 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0842 |  |  | 2-34-10 |  |  | 670 | 87CFA | 北港新港一路 670 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.670_87CFA | 北港新港ㄧ路(670)87RY通訊故障 | OTHER | [5 empty] | 511 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0845 |  |  | 2-34-13 |  |  | 680 | 87CFA | 北港新港二路 680 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.680_87CFA | 北港新港二路(680)87RY通訊故障 | OTHER | [5 empty] | 513 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | BE0 | 1550BE(非取樣點) | B3 | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1550BE | 1550BE (非取樣點) | LINE161 | [5 empty] | 217 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0871 |  |  | 2-36-07 |  |  | 640 | 87CFA | 北港朴子線 640 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.640_87CFA | 北港朴子線(640)87RY通訊故障 | OTHER | [5 empty] | 526 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0883 |  |  | 2-37-03 |  |  | 620 | 87CFA | 北港水林二路 620 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.620_87CFA | 北港水林二路(620)87RY通訊故障 | OTHER | [5 empty] | 532 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0886 |  |  | 2-37-06 |  |  | 630 | 87CFA | 北港水林一路 630 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.630_87CFA | 北港水林一路(630)87RY通訊故障 | OTHER | [5 empty] | 534 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0885 |  | 0013 | 2-37-05 |  | 1-0D | 620 | USE/LOCK | 北港水林二路 620 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.620_87UL | 北港水林二路(620) 87RY U/L | LINE69 | [5 empty] | 12 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0888 |  | 0014 | 2-37-08 |  | 1-0E | 630 | USE/LOCK | 北港水林一路 630 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.630_87UL | 北港水林一路(630) 87RY U/L | LINE69 | [5 empty] | 13 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0844 |  | 0176 | 2-34-12 |  | 2-30 | 670 | USE/LOCK | 北港新港一路 670 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.670_87UL | 北港新港一路(670) 87RY U/L | LINE69 | [5 empty] | 147 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0847 |  | 0177 | 2-34-15 |  | 2-31 | 680 | USE/LOCK | 北港新港二路 680 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.680_87UL | 北港新港二路(680) 87RY U/L | LINE69 | [5 empty] | 148 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | MW |  | INSERT | MvMoment | MW |  | Y |  | AI | [6 empty] | 0084 |  |  | 1-C3 |  |  | 1510 | MW | 備用線 | MW_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1510_MW | 北港四湖一路 MW | LINE161 | [5 empty] | 582 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0870 |  | 0185 | 2-36-06 |  | 2-39 | 640 | USE/LOCK | 北港朴子線 640 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.640_87UL | 北港朴子線(640) 87RY U/L | LINE69 | [5 empty] | 154 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | MVAR |  | INSERT | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0085 |  |  | 1-C4 |  |  | 1510 | MVAR | 備用線 | MVAR_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1510_MVAR | 北港四湖一路 MVAR | LINE161 | [5 empty] | 583 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | ABS1 | 621 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0568 | 569 | 0025 | 1-33-08 | 1-33-09 | 1-19 | 621 | ON | 北港水林二路 621 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.621_ABS | 621(北港水林二路) ABS | LINE69 | [5 empty] | 24 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | ABS1 | 671 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0576 | 577 | 0030 | 1-34-00 | 1-34-01 | 1-28 | 671 | ON | 北港新港一路 671 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.671_ABS | 671(北港新港一路) ABS | LINE69 | [5 empty] | 29 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | ABS1 | 681 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0584 | 585 | 0035 | 1-34-08 | 1-34-09 | 1-2D | 681 | ON | 北港新港二路 681 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.681_ABS | 681(北港新港二路) ABS | LINE69 | [5 empty] | 34 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S011/T1 |  | 0018 |  | 0039 | 1-02-02 |  | 1-27 | 710 | ON/OFF | 北港雲港一路 710 CB |  | aajb | B2/P04_A1 | [8 empty] | 北港PS.710_CB | 710(雲港一路) CB | LINE69 | [5 empty] | 38 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | ABS1 | 711 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0592 | 593 | 0040 | 1-35-00 | 1-35-01 | 1-32 | 711 | ON | 北港雲港一路 711 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.711_ABS | 711(雲港一路) ABS | LINE69 | [5 empty] | 39 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | ABS2 | 712 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0594 | 595 | 0041 | 1-35-02 | 1-35-03 | 1-33 | 712 | ON | 北港雲港一路 712 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.712_ABS | 712(雲港一路) ABS | LINE69 | [5 empty] | 40 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | ABS3 | 713 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0596 | 597 | 0042 | 1-35-04 | 1-35-05 | 1-34 | 713 | ON | 北港雲港一路 713 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.713_ABS | 713(雲港一路) ABS | LINE69 | [5 empty] | 41 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | ES3 | 713E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0598 | 599 | 0043 | 1-35-06 | 1-35-07 | 1-35 | 713E | ON | 北港雲港一路 713E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.713E_ES | 713E(雲港一路) ES | LINE69 | [5 empty] | 42 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S012/T1 |  | 0021 |  | 0044 | 1-02-05 |  | 1-2C | 720 | ON/OFF | 北港雲港二路 720 CB |  | aakb | B2/P04_A1 | [8 empty] | 北港PS.720_CB | 720(雲港二路) CB | LINE69 | [5 empty] | 43 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | ABS1 | 721 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0600 | 601 | 0045 | 1-35-08 | 1-35-09 | 1-46 | 721 | ON | 北港雲港二路 721 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.721_ABS | 721(雲港二路) ABS | LINE69 | [5 empty] | 44 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | ABS2 | 722 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0602 | 603 | 0046 | 1-35-10 | 1-35-11 | 1-47 | 722 | ON | 北港雲港二路 722 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.722_ABS | 722(雲港二路) ABS | LINE69 | [5 empty] | 45 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | ABS3 | 723 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0604 | 605 | 0047 | 1-35-12 | 1-35-13 | 1-48 | 723 | ON | 北港雲港二路 723 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.723_ABS | 723(雲港二路) ABS | LINE69 | [5 empty] | 46 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | ES3 | 723E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0606 | 607 | 0048 | 1-35-14 | 1-35-15 | 1-49 | 723E | ON | 北港雲港二路 723E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.723E_ES | 723E(雲港二路) ES | LINE69 | [5 empty] | 47 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0117 |  |  | 1-0E-05 |  |  | 920 | 87A | 北港元長線 920 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.920_87A | 元長線(920) 87RY | LINE69 | [5 empty] | 375 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0118 |  |  | 1-0E-06 |  |  | 940 | 87A | 北港東北線 940 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.940_87A | 北港東北線(940) 87RY | LINE69 | [5 empty] | 376 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0119 |  |  | 1-0E-07 |  |  | 910 | 87A | 北港土庫線 910 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.910_87A | 北港土庫線(910) 87RY | LINE69 | [5 empty] | 377 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0745 |  |  | 1-3E-09 |  |  | 920 | 87CFA | 北港元長線 920 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.920_87CFA | 北港元長線(920)87RY通訊故障 | OTHER | [5 empty] | 471 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0852 |  |  | 2-35-04 |  |  | 910 | 87CFA | 北港土庫線 910 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.910_87CFA | 北港土庫線(910)87RY通訊故障 | OTHER | [5 empty] | 515 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0859 |  |  | 2-35-11 |  |  | 940 | 87CFA | 北港東北線 940 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.940_87CFA | 北港東北線(940)87RY通訊故障 | OTHER | [5 empty] | 520 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0744 |  | 0141 | 1-3E-08 |  | 2-0D | 920 | USE/LOCE | 北港元長線 920 87RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.920_87UL | 元長線(920) 87RY U/L | LINE69 | [5 empty] | 135 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0861 |  | 0179 | 2-35-13 |  | 2-33 | 940 | USE/LOCK | 北港東北線 940 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.940_87UL | 北港東北線(940) 87RY U/L | LINE69 | [5 empty] | 150 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0854 |  | 0180 | 2-35-06 |  | 2-34 | 910 | USE/LOCK | 北港土庫線 910 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.910_87UL | 北港土庫線(910) 87RY U/L | LINE69 | [5 empty] | 151 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | ABS1 | 911 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0608 | 609 | 0050 | 1-36-00 | 1-36-01 | 1-3C | 911 | ON | 北港土庫線 911 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.911_ABS | 911(北港土庫線) ABS | LINE69 | [5 empty] | 49 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | ABS1 | 631 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0624 | 625 | 0060 | 1-37-00 | 1-37-01 | 1-1E | 631 | ON | 北港水林一路 631 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.631_ABS | 631(北港水林一路) ABS | LINE69 | [5 empty] | 59 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ABS1 | 641 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0632 | 633 | 0065 | 1-37-08 | 1-37-09 | 1-23 | 641 | ON | 北港朴子線 641 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.641_ABS | 641(北港朴子線) ABS | LINE69 | [5 empty] | 64 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | ABS2 | 622 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0570 | 571 | 0026 | 1-33-10 | 1-33-11 | 1-1A | 622 | ON | 北港水林二路 622 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.622_ABS | 622(北港水林二路) ABS | LINE69 | [5 empty] | 25 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | ABS2 | 672 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0578 | 579 | 0031 | 1-34-02 | 1-34-03 | 1-29 | 672 | ON | 北港新港一路 672 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.672_ABS | 672(北港新港一路) ABS | LINE69 | [5 empty] | 30 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | ABS2 | 682 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0586 | 587 | 0036 | 1-34-10 | 1-34-11 | 1-2E | 682 | ON | 北港新港二路 682 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.682_ABS | 682(北港新港二路) ABS | LINE69 | [5 empty] | 35 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | ABS2 | 632 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0626 | 627 | 0061 | 1-37-02 | 1-37-03 | 1-1F | 632 | ON | 北港水林一路 632 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.632_ABS | 632(北港水林一路) ABS | LINE69 | [5 empty] | 60 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ABS2 | 642 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0634 | 635 | 0066 | 1-37-10 | 1-37-11 | 1-24 | 642 | ON | 北港朴子線 642 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.642_ABS | 642(北港朴子線) ABS | LINE69 | [5 empty] | 65 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 87A1 |  | INSERT | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0257 |  |  | 2-00-01 |  |  | 1510 | 87A1 | 備用線 1510 87A1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_87A1 | 北港四湖一路(1510)第一套87RY | OTHER | [5 empty] | 584 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | ABS3 | 623 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0572 | 573 | 0027 | 1-33-12 | 1-33-13 | 1-1B | 623 | ON | 北港水林二路 623 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.623_ABS | 623(北港水林二路) ABS | LINE69 | [5 empty] | 26 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | ABS1 | 941 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0640 | 641 | 0055 | 1-38-00 | 1-38-01 | 1-37 | 941 | ON | 北港東北線 941 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.941_ABS | 941(北港東北線) ABS | LINE69 | [5 empty] | 54 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | ABS1 | 921 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0616 | 617 | 0070 | 1-36-08 | 1-36-09 | 1-41 | 921 | ON | 北港元長線 921 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.921_ABS | 921(元長線) ABS | LINE69 | [5 empty] | 69 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | ABS2 | 912 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0610 | 611 | 0051 | 1-36-02 | 1-36-03 | 1-3D | 912 | ON | 北港土庫線 912 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.912_ABS | 912(北港土庫線) ABS | LINE69 | [5 empty] | 50 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | ABS2 | 942 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0642 | 643 | 0056 | 1-38-02 | 1-38-03 | 1-38 | 942 | ON | 北港東北線 942 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.942_ABS | 942(北港東北線) ABS | LINE69 | [5 empty] | 55 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | ABS2 | 922 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0618 | 619 | 0071 | 1-36-10 | 1-36-11 | 1-42 | 922 | ON | 北港元長線 922 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.922_ABS | 922(元長線) ABS | LINE69 | [5 empty] | 70 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [5 empty] | v | 0694 | 695 | 0074 | 1-3B-06 | 1-3B-07 | 1-54 | #2MTR | M/I | #2MTR M/I |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | [5 empty] | 73 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR | v | 0057 |  | 0076 | 1-07-01 |  | 1-4C | #2MTR | ON/OFF | #2MTR 760 CB |  | aaea | B2/P04_A1 | [8 empty] | 北港PS.760_CB | 760(#2MTR) CB | MTR | [5 empty] | 74 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/2MTR | v | 0056 |  | 0077 | 1-07-00 |  | 1-4D | #2MTR | ON/OFF | #2MTR 1660 CB |  | aaeb | B2/P04_A1 | [8 empty] | 北港PS.1660_CB | 1660(#2MTR) CB | MTR | [5 empty] | 75 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS1 | 1661 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0700 | 701 | 0078 | 1-3B-12 | 1-3B-13 | 1-5C | 1661 | ON | #2MTR 1661 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1661_ABS | 1661(#2MTR) ABS | MTR | [5 empty] | 76 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS2 | 1662 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0702 | 703 | 0079 | 1-3B-14 | 1-3B-15 | 1-5D | 1662 | ON | #2MTR 1662 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1662_ABS | 1662(#2MTR) ABS | MTR | [5 empty] | 77 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0658 |  | 0080 | 1-39-02 |  |  | #2MTR | A/M | #2MTR OLTC A/M |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | [5 empty] | 78 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P04 | 北港PS |  |  | 2MTR | #2MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [5 empty] | v | 0062 |  | 0081 | 1-AD |  | 1-51 | #2MTR | 升/降 | #2MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | [5 empty] | 79 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0696 | 697 | 0082 | 1-3B-08 | 1-3B-09 | 1-58 | 761 | ON | #2MTR 761 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.761_ABS | 761(#2MTR) ABS | MTR | [5 empty] | 80 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS2 | 762 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0698 | 699 | 0083 | 1-3B-10 | 1-3B-11 | 1-59 | 762 | ON | #2MTR 762 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.762_ABS | 762(#2MTR) ABS | MTR | [5 empty] | 81 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 3MTR | #3MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [5 empty] | v | 0662 | 663 | 0084 | 1-39-06 | 1-39-07 | 1-62 | #3MTR | M/I | #3MTR M/I |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | [5 empty] | 82 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0063 |  | 0086 | 1-07-07 |  | 1-56 | #3MTR | ON/OFF | #3MTR 1670 CB |  | aalb | B2/P04_A1 | [8 empty] | 北港PS.1670_CB | 1670(#3MTR) CB | MTR | [5 empty] | 83 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/3MTR |  | 0064 |  | 0087 | 1-08-00 |  | 1-57 | #3MTR | ON/OFF | #3MTR 770 CB |  | aala | B2/P04_A1 | [8 empty] | 北港PS.770_CB | 770(#3MTR) CB | MTR | [5 empty] | 84 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS1 | 1671 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0664 | 665 | 0088 | 1-39-08 | 1-39-09 | 1-63 | 1671 | ON | #3MTR 1671 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1671_ABS | 1671(#3MTR) ABS | MTR | [5 empty] | 85 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS2 | 1672 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0666 | 667 | 0089 | 1-39-10 | 1-39-11 | 1-66 | 1672 | ON | #3MTR 1672 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1672_ABS | 1672(#3MTR) ABS | MTR | [5 empty] | 86 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0657 |  | 0090 | 1-39-01 |  | 1-5A | #2MTR | TRF | #2MTR 輕故障 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_TRF | #2MTR 輕故障 | MTR | [5 empty] | 87 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0067 |  | 0091 | 1-B0 |  | 1-5B | #3MTR | 升/降 | #3MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | [5 empty] | 88 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0668 | 669 | 0092 | 1-39-12 | 1-39-13 | 1-67 | 771 | ON | #3MTR 771 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.771_ABS | 771(#3MTR) ABS | MTR | [5 empty] | 89 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0660 |  | 0094 | 1-39-04 |  | 1-5E | #2MTR | USE/LOCE | #2MTR #1 87RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | [5 empty] | 90 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4MTR |  | 0070 |  | 0096 | 1-08-06 |  | 1-60 | #4MTR | ON/OFF | #4MTR 1680 CB |  | aaob | B2/P04_A1 | [8 empty] | 北港PS.1680_CB | 1680(#4MTR) CB | MTR | [5 empty] | 91 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | T/4MTR |  | 0071 |  | 0097 | 1-08-07 |  | 1-61 | #4MTR | ON/OFF | #4MTR 780 CB |  | aaqa | B2/P04_A1 | [8 empty] | 北港PS.780_CB | 780(#4MTR) CB | MTR | [5 empty] | 92 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | ABS1 | 1681 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0678 | 679 | 0098 | 1-3A-06 | 1-3A-07 | 1-4A | 1681 | ON | #4MTR 1681 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1681_ABS | 1681(#4MTR) ABS | MTR | [5 empty] | 93 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | ABS2 | 1682 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0680 | 681 | 0099 | 1-3A-08 | 1-3A-09 | 1-52 | 1682 | ON | #4MTR 1682 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1682_ABS | 1682(#4MTR) ABS | MTR | [5 empty] | 94 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS |  |  | 4MTR | #4MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0704 |  | 0100 | 1-3C-00 |  | 1-64 | #4MTR | A/M | #4MTR OLTC A/M |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_A/M | #4MTR OLTC A/M | MTR | [5 empty] | 95 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P04 | 北港PS |  |  | 4MTR | #4MTR |  | TapPosMv |  |  | MvMoment | OLTC TAP |  | Y |  | AI | [6 empty] | 0070 |  | 0101 | 1-B5 |  | 1-65 | #4MTR | 升/降 | #4MTR TAP | TAP_-6.5_6.5(0_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_TAP | #4MTR OLTC TAP | MTR | [5 empty] | 96 |  |  |  |  | AI | [5 empty] | TAP6_6 | 5 | 6 | 7 | 7.5 | 0 | -5 | -6 | -7 | -7.5 | 0.1 |  | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0682 | 683 | 0102 | 1-3A-10 | 1-3A-11 | 1-53 | 781 | ON | #4MTR 781 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.781_ABS | 781(#4MTR) ABS | MTR | [5 empty] | 97 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | ABS2 | 782 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0684 | 685 | 0103 | 1-3A-12 | 1-3A-13 | 1-4E | 782 | ON | #4MTR 782 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.782_ABS | 782(#4MTR) ABS | MTR | [5 empty] | 98 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/2SC |  | 0035 |  | 0104 | 1-04-03 |  | 1-68 | 820 | ON/OFF | 69KV #2SC 820 CB |  | aamb | B2/P04_A1 | [8 empty] | 北港PS.820_CB | 820(69KV #2SC) CB | SC | [5 empty] | 99 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | ABS1 | 821 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0648 | 649 | 0105 | 1-38-08 | 1-38-09 | 1-69 | 821 | ON | 69KV #2SC 821 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.821_ABS | 821(69KV #2SC) ABS | SC | [5 empty] | 100 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | ABS2 | 822 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0650 | 651 | 0106 | 1-38-10 | 1-38-11 | 1-6A | 822 | ON | 69KV #2SC 822 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.822_ABS | 822(69KV #2SC) ABS | SC | [5 empty] | 101 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | C/3SC |  | 0038 |  | 0107 | 1-04-06 |  | 1-6B | 830 | ON/OFF | 69KV #3SC 830 CB |  | aarb | B2/P04_A1 | [8 empty] | 北港PS.830_CB | 830(69KV #3SC) CB | SC | [5 empty] | 102 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | ABS1 | 831 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0652 | 653 | 0108 | 1-38-12 | 1-38-13 | 1-6C | 831 | ON | 69KV #3SC 831 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.831_ABS | 831(69KV #3SC) ABS | SC | [5 empty] | 103 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | ABS2 | 832 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0654 | 655 | 0109 | 1-38-14 | 1-38-15 | 1-6D | 832 | ON | 69KV #3SC 832 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.832_ABS | 832(69KV #3SC) ABS | SC | [5 empty] | 104 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0073 |  | 0110 | 1-09-01 |  | 1-6E | 1500 | ON/OFF | 1500 TIE CB |  | aagz | B2/P04_A1 | [8 empty] | 北港PS.1500_CB | 1500(TIE) CB | TIE | [5 empty] | 105 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS1 | 1501 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0552 | 553 | 0111 | 1-32-08 | 1-32-09 | 1-6F | 1501 | ON | 161KV TIE 1501 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1501_ABS | 1501(TIE) ABS | TIE | [5 empty] | 106 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS2 | 1502 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0554 | 555 | 0112 | 1-32-10 | 1-32-11 | 1-70 | 1502 | ON | 161KV TIE 1502 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1502_ABS | 1502(TIE) ABS | TIE | [5 empty] | 107 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Coupler | B/1Bus | B/2Bus |  |  | 0075 |  | 0114 | 1-09-03 |  | 1-72 | 600 | ON/OFF | 600 TIE CB |  | aagz | B2/P04_A1 | [8 empty] | 北港PS.600_CB | 600(TIE) CB | TIE | [5 empty] | 108 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | ABS1 | 601 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0556 | 557 | 0115 | 1-32-12 | 1-32-13 | 1-73 | 601 | ON | 69KV TIE 601 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.601_ABS | 601(TIE) ABS | TIE | [5 empty] | 109 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | ABS2 | 602 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0558 | 559 | 0116 | 1-32-14 | 1-32-15 | 1-74 | 602 | ON | 69KV TIE 602 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.602_ABS | 602(TIE) ABS | TIE | [5 empty] | 110 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | ABS3 | 1563 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0764 | 765 | 0154 | 1-3F-12 | 1-3F-13 | 2-1A | 1563 | ON | 北港台西二路 1563 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1563_ABS | 1563(台西二路) ABS | LINE161 | [5 empty] | 142 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | ES3 | 1563E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0766 | 767 | 0155 | 1-3F-14 | 1-3F-15 | 2-1B | 1563E | ON | 北港台西二路 1563E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1563E_ES | 1563E(台西二路) ES | LINE161 | [5 empty] | 143 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1560BE | 1560BE (非取樣點) | LINE161 | [5 empty] | 219 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | 81A |  |  | Status | 81RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0087 |  | 0121 | 1-0A-07 |  | 1-79 | 720 | 81A | 北港雲港二路 81A |  |  | B3/P04_A1 | [8 empty] | 北港PS.720_81A/S | (720) 81RY A/S | LINE69 | [5 empty] | 115 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/RESET | RESET
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0692 |  | 0122 | 1-3B-04 |  | 1-7A | 1630 | USE/LOCE | 嘉民北港南線 1630 87RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_87UL | 嘉民南線(1630) 87RY U/L | LINE161 | [5 empty] | 116 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0873 |  | 0123 | 2-36-09 |  | 1-7B | #2MTR | U/L | #2MTR #2 87RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | [5 empty] | 117 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0080 |  |  | 1-BF |  |  | 1560 | MW | 北港台西二路 1560 瓦 | MW_-448_448(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1560_MW | 台西二路 MW | LINE161 | [5 empty] | 317 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P05N/T2 |  | 0048 |  | 0125 | 1-06-00 |  | 1-7D | 1640 | ON/OFF | 嘉民北港北線 1640 CB |  | aama | B2/P04_A1 | [8 empty] | 北港PS.1640_CB | 1640(嘉民北線) CB | LINE161 | [5 empty] | 119 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/E03P04S/T2 |  | 0044 |  | 0126 | 1-05-04 |  | 1-7E | 1630 | ON/OFF | 嘉民北港南線 1630 CB |  | aana | B2/P04_A1 | [8 empty] | 北港PS.1630_CB | 1630(嘉民南線) CB | LINE161 | [5 empty] | 120 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0081 |  |  | 1-B2 |  |  | 1560 | MVAR | 北港台西二路 1560 乏 | MVAR_-448_448(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1560_MVAR | 台西二路 MVAR | LINE161 | [5 empty] | 318 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.896 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P04 | 北港PS |  |  | 3MTR | #3MTR |  | Tap Chan |  | Element | TapPos |  | Rise/Low | Y | 3 | DI-SP | [6 empty] | 0673 |  | 0128 | 1-3A-01 |  | 2-00 | #3MTR | A/M | #3MTR OLTC A/M |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | [5 empty] | 122 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rise/Low | Rise | 0 |  |  | AUTO/MANUAL | AUTO
P04 | 北港PS |  |  | 3MTR | #3MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0672 |  | 0129 | 1-3A-00 |  | 2-01 | #3MTR | TRF | #3MTR 輕故障 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_TRF | #3MTR 輕故障 | MTR | [5 empty] | 123 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0675 |  | 0130 | 1-3A-03 |  | 2-02 | #3MTR | USE/LOCE | #3MTR #1 87RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | [5 empty] | 124 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0690 |  | 0131 | 1-3B-02 |  | 1-50 | 1640 | USE/LOCE | 嘉民北港北線 1640 87RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_87UL | 嘉民北線(1640) 87RY U/L | LINE161 | [5 empty] | 125 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 3MTR | #3MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0674 |  | 0131 | 1-3A-02 |  | 2-03 | #3MTR | 遙控/現場 | #3MTR S/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | [5 empty] | 126 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P04 | 北港PS |  |  | 4MTR | #4MTR |  | M_F_I |  |  | Status/Intermed | Mas/Fol/Ind | Mas/Fol/Ind | Y | 5 | DI-DP | [6 empty] | 0676 | 677 | 0133 | 1-3A-04 | 1-3A-05 | 2-05 | #4MTR | M/I | #4MTR M/I |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_M/F/I | #4MTR M/F/I | MTR | [5 empty] | 127 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Mas/Fol/Ind | Ind | 2 |  |  | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | ACB1 |  |  | Status | 所內電源ACB1 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0715 |  | 0134 | 1-3C-11 |  | 2-06 | ACB1 | ON/OFF | 所內電源 ACB1 |  |  | B3/P04_A1 | [8 empty] | 北港PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | [5 empty] | 128 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | ACB2 |  |  | Status | 所內電源ACB2 | Close/Open | Y | 3 | DI-SP | [6 empty] | 0716 |  | 0135 | 1-3C-12 |  | 2-07 | ACB2 | ON/OFF | 所內電源 ACB2 |  |  | B3/P04_A1 | [8 empty] | 北港PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | [5 empty] | 129 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | ON/OFF | ON
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | ACBT |  |  | Status | 所內電源ACB TIE | Close/Open | Y | 3 | DI-SP | [6 empty] | 0717 |  | 0136 | 1-3C-13 |  | 2-08 | ACB TIE | ON/OFF | 所內電源 ACB TIE |  |  | B3/P04_A1 | [8 empty] | 北港PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | [5 empty] | 130 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Open | 1 |  |  | ON/OFF | OFF
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Lights1 | 開關場161 |  | Status | 照明1 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0725 |  | 0137 | 1-3D-05 |  | 2-09 | FLA-161 | ON/OFF | 開關場照明 FLA-161 |  |  | B3/P04_A1 | [8 empty] | 北港PS.開關場照明(A) | 161KV開關場照明(1) | OTHER | [5 empty] | 131 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Lights2 | 開關場161 |  | Status | 照明2 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0726 |  | 0138 | 1-3D-06 |  | 2-0A | FLB-161 | ON/OFF | 開關場照明 FLB-161 |  |  | B3/P04_A1 | [8 empty] | 北港PS.開關場照明(B) | 161KV開關場照明(2) | OTHER | [5 empty] | 132 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Lights3 | 開關場69 |  | Status | 照明3 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0727 |  | 0139 | 1-3D-07 |  | 2-0B | FLA-69 | ON/OFF | 開關場照明 FLA-69 |  |  | B3/P04_A1 | [8 empty] | 北港PS.開關場照明(C) | 69KV開關場照明(1) | OTHER | [5 empty] | 133 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Lights4 | 開關場69 |  | Status | 照明4 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0728 |  | 0140 | 1-3D-08 |  | 2-0C | FLB-69 | ON/OFF | 開關場照明 FLB-69 |  |  | B3/P04_A1 | [8 empty] | 北港PS.開關場照明(D) | 69KV開關場照明(2) | OTHER | [5 empty] | 134 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | ABS3 | 913 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0612 | 613 | 0052 | 1-36-04 | 1-36-05 | 1-3E | 913 | ON | 北港土庫線 913 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.913_ABS | 913(北港土庫線) ABS | LINE69 | [5 empty] | 51 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | 85A |  |  | Status | 85RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0099 |  |  | 1-0C-03 |  |  | 1560 | 85A | 北港台西二路 1560 85A |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_85A | 台西二路(1560) 85RY | LINE161 | [5 empty] | 370 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0100 |  |  | 1-0C-04 |  |  | 1560 | PHA | 北港台西二路 1560 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_PHA | 台西二路(1560) 相間RY | LINE161 | [5 empty] | 371 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0101 |  |  | 1-0C-05 |  |  | 1560 | GDA | 北港台西二路 1560 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_GDA | 台西二路(1560) 接地RY | LINE161 | [5 empty] | 372 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0774 |  |  | 2-30-06 |  |  | 1560 | ON/OFF | 北港台西二路 1560 TONE |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_TONEF | 1560 TONE訊號不良 | OTHER | [5 empty] | 482 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | 1A5Other | MDAR | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0775 |  |  | 2-30-07 |  |  | 1560 | ON/OFF | 北港台西二路 1560 MDAR |  |  | B2/P04_A1 | [8 empty] | 北港PS.1560_MDARF | 1560 MDAR RY故障 | OTHER | [5 empty] | 483 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | ABS1 | 1571 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0528 | 529 | 0003 | 1-31-00 | 1-31-01 | 1-03 | 1571 | ON | 雲林北港雲高線1571 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1571_ABS | 1571(雲林北港雲高線) ABS | LINE161 | [5 empty] | 4 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | ABS2 | 1572 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0530 | 531 | 0004 | 1-31-02 | 1-31-03 | 1-04 | 1572 | ON | 雲林北港雲高線1572 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1572_ABS | 1572(雲林北港雲高線) ABS | LINE161 | [5 empty] | 5 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | ABS3 | 1573 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0532 | 533 | 0005 | 1-31-04 | 1-31-05 | 1-05 | 1573 | ON | 雲林北港雲高線1573 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1573_ABS | 1573(雲林北港雲高線) ABS | LINE161 | [5 empty] | 6 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0875 |  | 0158 | 2-36-11 |  | 2-1E | #2MTR | U/L | #2MTR 51Z RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | [5 empty] | 144 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | ES3 | 1573E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [5 empty] | v | 0534 | 535 | 0006 | 1-31-06 | 1-31-07 | 1-06 | 1573E | ON | 雲林北港雲高線1573E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1573E_ES | 1573E(雲林北港雲高線) ES | LINE161 | [5 empty] | 7 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04TN05/T2 |  | 0040 |  | 0124 | 1-05-00 |  | 1-7C | 1570 | ON/OFF | 雲林北港雲高線 1570 CB |  | aaka | B2/P04_A1 | [8 empty] | 北港PS.1570_CB | 1570(雲林北港雲高線) CB | LINE161 | [5 empty] | 118 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | ABS3 | 673 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0580 | 581 | 0032 | 1-34-04 | 1-34-05 | 1-2A | 673 | ON | 北港新港一路 673 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.673_ABS | 673(北港新港一路) ABS | LINE69 | [5 empty] | 31 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | ABS3 | 683 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0588 | 589 | 0037 | 1-34-12 | 1-34-13 | 1-2F | 683 | ON | 北港新港二路 683 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.683_ABS | 683(北港新港二路) ABS | LINE69 | [5 empty] | 36 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | ABS3 | 633 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0628 | 629 | 0062 | 1-37-04 | 1-37-05 | 1-20 | 633 | ON | 北港水林一路 633 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.633_ABS | 633(北港水林一路) ABS | LINE69 | [5 empty] | 61 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | ABS3 | 943 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0644 | 645 | 0057 | 1-38-04 | 1-38-05 | 1-39 | 943 | ON | 北港東北線 943 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.943_ABS | 943(北港東北線) ABS | LINE69 | [5 empty] | 56 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | ABS3 | 923 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0620 | 621 | 0072 | 1-36-12 | 1-36-13 | 1-43 | 923 | ON | 北港元長線 923 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.923_ABS | 923(元長線) ABS | LINE69 | [5 empty] | 71 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0864 |  | 0181 | 2-36-00 |  | 2-35 | 710 | USE/LOCK | 北港雲港一路 710 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.710_87UL | 雲港一路(710) 87RY U/L | LINE69 | [5 empty] | 152 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0867 |  | 0182 | 2-36-03 |  | 2-36 | 720 | USE/LOCK | 北港雲港二路 720 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.720_87UL | 雲港二路(720) 87RY U/L | LINE69 | [5 empty] | 153 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ABS3 | 643 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0636 | 637 | 0067 | 1-37-12 | 1-37-13 | 1-25 | 643 | ON | 北港朴子線 643 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.643_ABS | 643(北港朴子線) ABS | LINE69 | [5 empty] | 66 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0659 |  | 0186 | 1-39-03 |  | 2-3A | #2MTR | 遙控/現場 | #2MTR S/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | [5 empty] | 155 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0876 |  | 0187 | 2-36-12 |  | 2-3B | #3MTR | U/L | #3MTR #2 87RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER | [5 empty] | 156 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0878 |  | 0188 | 2-36-14 |  | 2-3C | #3MTR | U/L | #3MTR 51Z RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER | [5 empty] | 157 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0706 |  | 0189 | 1-3C-02 |  | 2-3D | #4MTR | USE/LOCE | #4MTR #1 87RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_87UL1 | #4MTR #1 87RY U/L | OTHER | [5 empty] | 158 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0879 |  | 0190 | 2-36-15 |  | 2-3E | #4MTR | U/L | #4MTR #2 87RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_87UL2 | #4MTR #2 87RY U/L | OTHER | [5 empty] | 159 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 51Z_UL |  |  | Status | 51Z RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0881 |  | 0191 | 2-37-01 |  | 2-3F | #4MTR | U/L | #4MTR 51Z RY U/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_51ZUL | #4MTR 51ZRY U/L | OTHER | [5 empty] | 160 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0192 |  | 0192 | 1-18-00 |  | 2-40 | #2 MTR | ON/OFF | #2 MTR OLTC TAP連動 |  |  | B1/P04_A1 | [8 empty] | 北港PS.2MOLTC_TAP連動 | #2MTR OLTC TAP連動,請確認處理 | OTHER | [5 empty] | 161 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0193 |  | 0193 | 1-18-01 |  | 2-41 | #3 MTR | ON/OFF | #3 MTR OLTC TAP連動 |  |  | B1/P04_A1 | [8 empty] | 北港PS.3MOLTC_TAP連動 | #3MTR OLTC TAP連動,請確認處理 | OTHER | [5 empty] | 162 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | OLTC_A |  |  | Status | OLTC連動3次 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0194 |  | 0194 | 1-18-02 |  | 2-42 | #4 MTR | ON/OFF | #4 MTR OLTC TAP連動 |  |  | B1/P04_A1 | [8 empty] | 北港PS.4MOLTC_TAP連動 | #4MTR OLTC TAP連動,請確認處理 | OTHER | [5 empty] | 163 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0713 |  | 0195 | 1-3C-09 |  | 2-43 | 69KV | USE/LOCE | 69KV #1 BUS╴87UL |  |  | B2/P04_A1 | [8 empty] | 北港PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | [5 empty] | 164 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0714 |  | 0196 | 1-3C-10 |  | 2-44 | 69KV | USE/LOCE | 69KV #2 BUS╴87UL |  |  | B2/P04_A1 | [8 empty] | 北港PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | [5 empty] | 165 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1BUS | #1BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0711 |  | 0197 | 1-3C-07 |  | 2-45 | 161KV | USE/LOCE | 161KV #1 BUS╴87UL |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | [5 empty] | 166 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 2BUS | #2BUS |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0712 |  | 0198 | 1-3C-08 |  | 2-46 | 161KV | USE/LOCE | 161KV #2 BUS╴87UL |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | [5 empty] | 167 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 87A2 |  | INSERT | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0258 |  |  | 2-00-02 |  |  | 1510 | 87A2 | 備用線 1510 87A2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_87A2 | 北港四湖一路(1510)第二套87RY | OTHER | [5 empty] | 585 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/1SHR |  | 0266 |  | 0202 | 2-01-02 |  | 2-4A | 1950 | ON/OFF | #1並聯電抗器 1950 CB |  | aaab | B2/P04_A1 | [8 empty] | 北港PS.1950_CB | 1950(161KV #1SHR) CB | OTHER | [5 empty] | 169 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS1 | 1951 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1008 | 1009 | 0224 | 2-3F-00 | 2-3F-01 | 2-60 | 1951 | ON | #1並聯電抗器 1951 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1951_ABS | 1951(161KV #1SHR) ABS | OTHER | [5 empty] | 177 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS2 | 1952 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1010 | 1011 | 0225 | 2-3F-02 | 2-3F-03 | 2-61 | 1952 | ON | #1並聯電抗器 1952 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1952_ABS | 1952(161KV #1SHR) ABS | OTHER | [5 empty] | 178 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1950 | #1SSR(1950) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1950BE | 1950BE(非取樣點) | OTHER | [5 empty] | 248 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | GDA |  | INSERT | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0259 |  |  | 2-00-03 |  |  | 1510 | GDA | 備用線 1510 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_GDA | 北港四湖一路(1510)GDA | OTHER | [5 empty] | 586 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | PHA |  | INSERT | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0260 |  |  | 2-00-04 |  |  | 1510 | PHA | 備用線 1510 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_PHA | 北港四湖一路(1510)PHA | OTHER | [5 empty] | 587 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | 87CFA |  | INSERT | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0896 |  |  | 2-38-00 |  |  | 1510 | 87CFA | 備用線 1510 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_87CFA | 北港四湖一路(1510)87RY通訊故障 | OTHER | [5 empty] | 588 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | RYFA |  | INSERT | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0897 |  |  | 2-38-01 |  |  | 1510 | RYFA | 備用線 1510 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_RYFA | 北港四湖一路(1510)數位電驛故障 | OTHER | [5 empty] | 589 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | DTTA |  | INSERT | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0898 |  |  | 2-38-02 |  |  | 1510 | DTTA | 備用線 1510 遠方遙跳 DTTA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_DTTA | 北港四湖一路(1510) 遠方遙跳 | OTHER | [5 empty] | 590 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SSR(1950) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1950RE | 1950RE(非取樣點) | OTHER | [5 empty] | 249 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0267 |  |  | 2-01-03 |  |  | 1950 | 87RA | #1並聯電抗器 87RA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | [5 empty] | 422 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | MTR_86A |  | B3 | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0268 |  |  | 2-01-04 |  |  | 1950 | 86A | #1並聯電抗器 86A |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | [5 empty] | 423 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0269 |  |  | 2-01-05 |  |  | 1950 | 51A | #1並聯電抗器 51A(51、51N) |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | [5 empty] | 424 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96PA | 1SSR | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0270 |  |  | 2-01-06 |  |  | 1950 | 96A | #1並聯電抗器 機械保護動作96PA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | [5 empty] | 425 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0910 |  |  | 2-38-14 |  |  | 1950 | 87R1S | #1並聯電抗器 1950 87Ry U/L1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_87UL1 | 161KV #1SHR #187RY U/L | OTHER | [5 empty] | 545 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | LPDA |  | INSERT | Status | LPD電壓偵測 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0899 |  |  | 2-38-03 |  |  | 1510 | LPTA | 備用線 1510 LPTA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1510_LPDA | 北港四湖一路(1510) LPD電壓偵測 | OTHER | [5 empty] | 591 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | ABS1 | 1511 | INSERT | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0992 | 993 |  | 2-3E-00 | 2-3E-01 |  | 1511 | ON | 備用線 1511 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1511_ABS | 1511(北港四湖一路) ABS | LINE161 | [5 empty] | 592 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | ABS2 | 1512 | INSERT | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0994 | 995 |  | 2-3E-02 | 2-3E-03 |  | 1512 | ON | 備用線 1512 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1512_ABS | 1512(北港四湖一路) ABS | LINE161 | [5 empty] | 593 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Lights | ABS夜間監視照明 |  | Status | 開關場照明 | OFF/ON | Y | 7 | DI-SP | [6 empty] | 0947 |  | 0238 | 2-3B-03 |  | 2-6E | 1573 | ON/OFF | 雲林北港雲高線ABS夜間監視照明開關 |  |  | B3/P04_A1 | [8 empty] | 北港PS.開關場照明(E) | 雲林北港雲高線ABS夜間照明 | OTHER | [5 empty] | 186 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | OFF/ON | OFF | 0 | Y |  | ON/OFF | OFF
P04 | 北港PS |  |  | 4MTR | #4MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0686 |  |  | 1-3A-14 |  | 1-4F | #4MTR | TRA | #4MTR 重故障 |  | a | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_TRA | #4MTR 重故障 | MTR | [5 empty] | 187 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0661 |  |  | 1-39-05 |  | 1-5F | #3MTR | TRA | #3MTR 重故障 |  | a | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_TRA | #3MTR 重故障 | MTR | [5 empty] | 188 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0828 |  | 0172 | 2-33-12 |  | 2-2C | 1570 | USE/LOCE | 雲林北港雲高線 87RY UL1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_87UL1 | 雲林北港雲高線(1570)#187RY U/L | LINE161 | [5 empty] | 145 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1630BE | 1630BE (非取樣點) | LINE161 | [5 empty] | 192 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1640BE | 1640BE (非取樣點) | LINE161 | [5 empty] | 194 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1660TE | 1660TE (非取樣點) | MTR | [5 empty] | 195 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1660BE | 1660BE (非取樣點) | MTR | [5 empty] | 197 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.760TE | 760TE (非取樣點) | MTR | [5 empty] | 198 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.760BE | 760BE (非取樣點) | MTR | [5 empty] | 199 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1670TE | 1670TE (非取樣點) | MTR | [5 empty] | 200 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1670BE | 1670BE (非取樣點) | MTR | [5 empty] | 202 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.770TE | 770TE (非取樣點) | MTR | [5 empty] | 203 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.770BE | 770BE (非取樣點) | MTR | [5 empty] | 204 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1680TE | 1680TE (非取樣點) | MTR | [5 empty] | 205 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1680BE | 1680BE (非取樣點) | MTR | [5 empty] | 207 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.780TE | 780TE (非取樣點) | MTR | [5 empty] | 208 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.780BE | 780BE (非取樣點) | MTR | [5 empty] | 209 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1501E | 1501E (非取樣點) | TIE | [5 empty] | 210 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1502E | 1502E (非取樣點) | TIE | [5 empty] | 211 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.601E | 601E (非取樣點) | TIE | [5 empty] | 212 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.602E | 602E (非取樣點) | TIE | [5 empty] | 213 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1570BE | 1570BE (非取樣點) | LINE161 | [5 empty] | 190 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0003 |  |  | 1-82 |  |  | 1570 | MW | 雲林北港雲高線1570 瓦 | MW_-336_336(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1570_MW | 雲林北港雲高線 MW | LINE161 | [5 empty] | 262 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | ABS3 | 1513 | INSERT | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0996 | 997 |  | 2-3E-04 | 2-3E-05 |  | 1513 | ON | 備用線 1513 DS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1513_ABS | 1513(北港四湖一路) ABS | LINE161 | [5 empty] | 594 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | ES3 | 1513E | INSERT | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0998 | 999 |  | 2-3E-06 | 2-3E-07 |  | 1513E | ON | 備用線 1513 ES |  |  | B2/P04_A1 | [8 empty] | 北港PS.1513E_ES | 1513E(北港四湖一路) ES | LINE161 | [5 empty] | 595 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0004 |  |  | 1-83 |  |  | 1570 | MVAR | 雲林北港雲高線1570 乏 | MVAR_-336_336(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1570_MVAR | 雲林北港雲高線 MVAR | LINE161 | [5 empty] | 263 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0041 |  |  | 1-05-01 |  |  | 1570 | 87A1 | 雲林北港雲高線1570 87A1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_87A1 | 雲林北港雲高線(1570) #1 87RY | LINE161 | [5 empty] | 331 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0170 |  |  | 1-15-02 |  |  | 610 | 87A | 北港口湖線 610 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.610_87A | 北港口湖線(610) 87RY | LINE69 | [5 empty] | 415 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.620BE | 620BE (非取樣點) | LINE69 | [5 empty] | 223 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.630BE | 630BE (非取樣點) | LINE69 | [5 empty] | 225 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.640BE | 640BE (非取樣點) | LINE69 | [5 empty] | 227 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.670BE | 670BE (非取樣點) | LINE69 | [5 empty] | 229 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.680BE | 680BE (非取樣點) | LINE69 | [5 empty] | 231 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0856 |  |  | 2-35-08 |  |  | 610 | 87CFA | 北港口湖線 610 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.610_87CFA | 北港口湖線(610)87RY通訊故障 | OTHER | [5 empty] | 518 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S132/T1 |  | 0003 |  | 0024 | 1-00-03 |  | 1-18 | 620 | ON/OFF | 北港水林二路 620 CB |  | aabb | B2/P04_A1 | [8 empty] | 北港PS.620_CB | 620(北港水林二路) CB | LINE69 | [5 empty] | 23 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S361/T1 |  | 0012 |  | 0029 | 1-01-04 |  | 1-1D | 670 | ON/OFF | 北港新港一路 670 CB |  | aahb | B2/P04_A1 | [8 empty] | 北港PS.670_CB | 670(北港新港一路) CB | LINE69 | [5 empty] | 28 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S362/T1 |  | 0015 |  | 0034 | 1-01-07 |  | 1-22 | 680 | ON/OFF | 北港新港二路 680 CB |  | aaib | B2/P04_A1 | [8 empty] | 北港PS.680_CB | 680(北港新港二路) CB | LINE69 | [5 empty] | 33 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S131/T1 |  | 0006 |  | 0059 | 1-00-06 |  | 1-3B | 630 | ON/OFF | 北港水林一路 630 CB |  | aacb | B2/P04_A1 | [8 empty] | 北港PS.630_CB | 630(北港水林一路) CB | LINE69 | [5 empty] | 58 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S31/T1 |  | 0009 |  | 0064 | 1-01-01 |  | 1-40 | 640 | ON/OFF | 北港朴子線 640 CB |  | aadb | B2/P04_A1 | [8 empty] | 北港PS.640_CB | 640(北港朴子線) CB | LINE69 | [5 empty] | 63 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.710BE | 710BE (非取樣點) | LINE69 | [5 empty] | 233 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.720BE | 720BE (非取樣點) | LINE69 | [5 empty] | 235 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.910BE | 910BE (非取樣點) | LINE69 | [5 empty] | 237 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.920BE | 920BE (非取樣點) | LINE69 | [5 empty] | 239 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.940BE | 940BE (非取樣點) | LINE69 | [5 empty] | 241 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S06/T1 |  | 0024 |  | 0049 | 1-03-00 |  | 1-31 | 910 | ON/OFF | 北港土庫線 910 CB |  | aanb | B2/P04_A1 | [8 empty] | 北港PS.910_CB | 910(北港土庫線) CB | LINE69 | [5 empty] | 48 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S03/T1 |  | 0030 |  | 0054 | 1-03-06 |  | 1-36 | 940 | ON/OFF | 北港東北線 940 CB |  | aapb | B2/P04_A1 | [8 empty] | 北港PS.940_CB | 940(北港東北線) CB | LINE69 | [5 empty] | 53 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S05/T1 |  | 0027 |  | 0069 | 1-03-03 |  | 1-45 | 920 | ON/OFF | 北港元長線 920 CB |  | aaob | B2/P04_A1 | [8 empty] | 北港PS.920_CB | 920(元長線) CB | LINE69 | [5 empty] | 68 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.820BE | 820BE (非取樣點) | SC | [5 empty] | 242 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.820CE | 820CE (非取樣點) | SC | [5 empty] | 243 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.830BE | 830BE (非取樣點) | SC | [5 empty] | 244 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | CE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.830CE | 830CE (非取樣點) | SC | [5 empty] | 245 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0858 |  | 0178 | 2-35-10 |  | 2-32 | 610 | USE/LOCK | 北港口湖線 610 87 RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.610_87UL | 北港口湖線(610) 87RY U/L | LINE69 | [5 empty] | 149 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | ABS1 | 611 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0560 | 561 | 0020 | 1-33-00 | 1-33-01 | 1-14 | 611 | ON | 北港口湖線 611 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.611_ABS | 611(北港口湖線) ABS | LINE69 | [5 empty] | 19 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0911 |  |  | 2-38-15 |  |  | 1950 | 87R2S | #1並聯電抗器 1950 87Ry U/L2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_87UL2 | 161KV #1SHR #287RY U/L | OTHER | [5 empty] | 546 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0912 |  |  | 2-39-00 |  |  | 1950 | RYFA | #1並聯電抗器 1950 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | [5 empty] | 547 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0913 |  |  | 2-39-01 |  |  | 1950 | 96B1 | #1並聯電抗器96B1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | [5 empty] | 548 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0914 |  |  | 2-39-02 |  |  | 1950 | 96B2 | #1並聯電抗器96B2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | [5 empty] | 549 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0915 |  |  | 2-39-03 |  |  | 1950 | 96D | #1並聯電抗器96D |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | [5 empty] | 550 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0916 |  |  | 2-39-04 |  |  | 1950 | 96P | #1並聯電抗器96P |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | [5 empty] | 551 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SSR(1950) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0917 |  |  | 2-39-05 |  |  | 1950 | SRF | #1並聯電抗器 SRF 輕故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | [5 empty] | 552 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SSR(1950) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0918 |  |  | 2-39-06 |  |  | 1950 | SRA | #1並聯電抗器 SRA 重故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | [5 empty] | 553 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 161B1E | #1BUS(161B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aafz | B2/P04_A1 | [8 empty] | 北港PS.161B1E | 161B1E (非取樣點) | BUS | [5 empty] | 256 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 161B2E | #2BUS(161B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aafz | B2/P04_A1 | [8 empty] | 北港PS.161B2E | 161B2E (非取樣點) | BUS | [5 empty] | 257 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 69B1E | #1BUS(69B1E) |  | BE1 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth1 | B/1Bus | [13 empty] | aafz | B2/P04_A1 | [8 empty] | 北港PS.69B1E | 69B1E (非取樣點) | BUS | [5 empty] | 258 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 69B2E | #2BUS(69B2E) |  | BE2 | (非取樣點) | B2,B3,Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | Bb2Eth2 | B/2Bus | [13 empty] | aafz | B2/P04_A1 | [8 empty] | 北港PS.69B2E | 69B2E (非取樣點) | BUS | [5 empty] | 259 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | RTU | RTU |  | ADCL1 |  |  | MvMoment | No1 AI參考點 10% |  | Y |  | AI | [6 empty] | 0000 |  |  | 1-80 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.1 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P04_A1 | [8 empty] | 北港PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | [5 empty] | 260 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | RTU | RTU |  | ADCH1 |  |  | MvMoment | No1 AI參考點 90% |  | Y |  | AI | [6 empty] | 0001 |  |  | 1-81 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.1 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P04_A1 | [8 empty] | 北港PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | [5 empty] | 261 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0042 |  |  | 1-05-02 |  |  | 1570 | PHA | 雲林北港雲高線1570 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_PHA | 雲林北港雲高線(1570) 相間RY | LINE161 | [5 empty] | 332 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0043 |  |  | 1-05-03 |  |  | 1570 | GDA | 雲林北港雲高線1570 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_GDA | 雲林北港雲高線(1570) 接地RY | LINE161 | [5 empty] | 333 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0006 |  |  | 1-84 |  |  | 1640 | MW | 嘉民北港北線 1640 瓦 | MW_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1640_MW | 嘉民北線 MW | LINE161 | [5 empty] | 264 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0007 |  |  | 1-85 |  |  | 1640 | MVAR | 嘉民北港北線 1640 乏 | MVAR_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1640_MVAR | 嘉民北線 MVAR | LINE161 | [5 empty] | 265 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0009 |  |  | 1-86 |  |  | 1630 | MW | 嘉民北港南線 1630 瓦 | MW_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1630_MW | 嘉民南線 MW | LINE161 | [5 empty] | 266 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0010 |  |  | 1-87 |  |  | 1630 | MVAR | 嘉民北港南線 1630 乏 | MVAR_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1630_MVAR | 嘉民南線 MVAR | LINE161 | [5 empty] | 267 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0011 |  |  | 1-88 |  |  | 161KV #1BUS | KV | 161KV #1BUS 電壓 | kV_-210_210(-2000_2000) | aaa | B2/P04_A1 | [8 empty] | 北港PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | [5 empty] | 268 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P04 | 北港PS | 161 | 161kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0012 |  |  | 1-89 |  |  | 161KV #2BUS | KV | 161KV #2BUS 電壓 | kV_-210_210(-2000_2000) | aab | B2/P04_A1 | [8 empty] | 北港PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | [5 empty] | 269 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 4 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0013 |  |  | 1-8A |  |  | 1500 | A | 1500 TIE 電流 | A_-1600_1600(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1500TIE_AMP | 1500TIE AMP | TIE | [5 empty] | 270 |  |  |  |  | AI | [5 empty] | C16R1600 | 1520 | 1600 | 1601 | 1602 | 0 | -1520 | -1600 | -1601 | -1602 | 1 | 0.01 | C16R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 1600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0014 |  |  | 1-8B |  |  | 1660 | A | #2MTR 1660 電流 |  |  | B2/P04_A1 | [16 empty] | 271 | [10 empty] | LG_1670 | 1503 | 1670 | 1837 | 2087.5 |  | -1503 | -1670 | -1837 | -2087.5
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0015 |  |  | 1-8C |  |  | 1670 | A | #3MTR 1670 電流 |  |  | B2/P04_A1 | [16 empty] | 272 | [10 empty] | LG_1670 | 1503 | 1670 | 1837 | 2087.5 |  | -1503 | -1670 | -1837 | -2087.5
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0016 |  |  | 1-8D |  |  | 1680 | A | #4MTR 1680 電流 |  |  | B2/P04_A1 | [16 empty] | 273 | [10 empty] | LG_1670 | 1503 | 1670 | 1837 | 2087.5 |  | -1503 | -1670 | -1837 | -2087.5
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0018 |  |  | 1-8E |  |  | 760 | MW | #2MTR 760 瓦 | MW_-360_360(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.#2MTR_MW | #2MTR二次側 MW | MTR | [5 empty] | 274 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0019 |  |  | 1-8F |  |  | 760 | MVAR | #2MTR 760 乏 | MVAR_-240_240(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | [5 empty] | 275 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0021 |  |  | 1-90 |  |  | 770 | MW | #3MTR 770 瓦 | MW_-360_360(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.#3MTR_MW | #3MTR二次側 MW | MTR | [5 empty] | 276 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0022 |  |  | 1-91 |  |  | 770 | MVAR | #3MTR 770 乏 | MVAR_-240_240(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | [5 empty] | 277 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0024 |  |  | 1-92 |  |  | 780 | MW | #4MTR 780 瓦 | MW_-360_360(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.#4MTR_MW | #4MTR二次側 MW | MTR | [5 empty] | 278 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.72 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0025 |  |  | 1-93 |  |  | 780 | MVAR | #4MTR 780 乏 | MVAR_-240_240(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.#4MTR_MVAR | #4MTR二次側 MVAR | MTR | [5 empty] | 279 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 1BUS | #1BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS1 |  |  |  |  | 0026 |  |  | 1-94 |  |  | 69KV #1BUS | KV | 69KV #1BUS 電壓 | kV_-90_90(-2000_2000) | aaa | B2/P04_A1 | [8 empty] | 北港PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | [5 empty] | 280 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P04 | 北港PS | 69 | 69kV | 2BUS | #2BUS |  | V |  |  | MvMoment | kV |  | Y |  | AI |  | BUS2 |  |  |  |  | 0027 |  |  | 1-95 |  |  | 69KV #1BUS | KV | 69KV #2BUS 電壓 | kV_-90_90(-2000_2000) | aab | B2/P04_A1 | [8 empty] | 北港PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | [5 empty] | 281 |  |  |  |  | AI | [5 empty] | LG_69 | 70.3 | 71.3 | 72.5 | 90 | 0.2 | 65 | 64 | 63 | 0 | 4 | 5 | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | I |  |  | MvMoment | AMP |  | Y |  | AI | [6 empty] | 0028 |  |  | 1-96 |  |  | 600 | A | 600 TIE 電流 | A_-2000_2000(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.600TIE_AMP | 600TIE AMP | TIE | [5 empty] | 282 |  |  |  |  | AI | [5 empty] | C20R2000 | 1900 | 2000 | 2001 | 2002 | 0.3 | -1900 | -2000 | -2001 | -2002 | 1 | 0.01 | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | ABS2 | 612 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0562 | 563 | 0021 | 1-33-02 | 1-33-03 | 1-15 | 612 | ON | 北港口湖線 612 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.612_ABS | 612(北港口湖線) ABS | LINE69 | [5 empty] | 20 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | ES3 | 623E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0574 | 575 | 0028 | 1-33-14 | 1-33-15 | 1-1C | 623E | ON | 北港水林二路 623E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.623E_ES | 623E(北港水林二路) ES | LINE69 | [5 empty] | 27 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | ES3 | 673E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0582 | 583 | 0033 | 1-34-06 | 1-34-07 | 1-2B | 673E | ON | 北港新港一路 673E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.673E_ES | 673E(北港新港一路) ES | LINE69 | [5 empty] | 32 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | ES3 | 683E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0590 | 591 | 0038 | 1-34-14 | 1-34-15 | 1-30 | 683E | ON | 北港新港二路 683E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.683E_ES | 683E(北港新港二路) ES | LINE69 | [5 empty] | 37 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | ES3 | 633E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0630 | 631 | 0063 | 1-37-06 | 1-37-07 | 1-21 | 633E | ON | 北港水林一路 633E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.633E_ES | 633E(北港水林一路) ES | LINE69 | [5 empty] | 62 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | ES3 | 643E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0638 | 639 | 0068 | 1-37-14 | 1-37-15 | 1-26 | 643E | ON | 北港朴子線 643E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.643E_ES | 643E(北港朴子線) ES | LINE69 | [5 empty] | 67 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | ABS3 | 613 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0564 | 565 | 0022 | 1-33-04 | 1-33-05 | 1-16 | 613 | ON | 北港口湖線 613 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.613_ABS | 613(北港口湖線) ABS | LINE69 | [5 empty] | 21 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0005 |  |  | 1-00-05 |  |  | 620 | GDA | 北港水林二路 620 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.620_GDA | 北港水林二路(620) 接地RY | LINE69 | [5 empty] | 390 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0008 |  |  | 1-01-00 |  |  | 630 | GDA | 北港水林一路 630 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.630_GDA | 北港水林一路(630) 接地RY | LINE69 | [5 empty] | 392 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0011 |  |  | 1-01-03 |  |  | 640 | GDA | 北港朴子線 640 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.640_GDA | 北港朴子線(640) 接地RY | LINE69 | [5 empty] | 394 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0014 |  |  | 1-01-06 |  |  | 670 | GDA | 北港新港一路 670 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.670_GDA | 北港新港一路(670) 接地RY | LINE69 | [5 empty] | 396 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0017 |  |  | 1-02-01 |  |  | 680 | GDA | 北港新港二路 680 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.680_GDA | 北港新港二路(680) 接地RY | LINE69 | [5 empty] | 398 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0048 |  |  | 1-A3 |  |  | 710 | MW | 北港雲港一路 710 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.710_MW | 雲港一路 MW | LINE69 | [5 empty] | 295 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0049 |  |  | 1-A4 |  |  | 710 | MVAR | 北港雲港一路 710 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.710_MVAR | 雲港一路 MVAR | LINE69 | [5 empty] | 296 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0051 |  |  | 1-A5 |  |  | 720 | MW | 北港雲港二路 720 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.720_MW | 雲港二路 MW | LINE69 | [5 empty] | 297 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0052 |  |  | 1-A6 |  |  | 720 | MVAR | 北港雲港二路 720 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.720_MVAR | 雲港二路 MVAR | LINE69 | [5 empty] | 298 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | ES3 | 913E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0614 | 615 | 0053 | 1-36-06 | 1-36-07 | 1-3F | 913E | ON | 北港土庫線 913E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.913E_ES | 913E(北港土庫線) ES | LINE69 | [5 empty] | 52 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | ES3 | 943E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0646 | 647 | 0058 | 1-38-06 | 1-38-07 | 1-3A | 943E | ON | 北港東北線 943E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.943E_ES | 943E(北港東北線) ES | LINE69 | [5 empty] | 57 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | ES3 | 923E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0622 | 623 | 0073 | 1-36-14 | 1-36-15 | 1-44 | 923E | ON | 北港元長線 923E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.923E_ES | 923E(元長線) ES | LINE69 | [5 empty] | 72 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0026 |  |  | 1-03-02 |  |  | 910 | GDA | 北港土庫線 910 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.910_GDA | 北港土庫線(910) 接地RY | LINE69 | [5 empty] | 404 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | GDA |  | B3 | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0029 |  |  | 1-03-05 |  |  | 920 | GDA | 北港元長線 920 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.920_GDA | 元長線(920) 接地RY | LINE69 | [5 empty] | 406 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0032 |  |  | 1-04-00 |  |  | 940 | GDA | 北港東北線 940 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.940_GDA | 北港東北線(940) 接地RY | LINE69 | [5 empty] | 408 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0063 |  |  | 1-AE |  |  | #2MTR | ℃ | #2MTR 油溫 | OIL_-160_160(-2000_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_OIL | #2MTR 油溫 | MTR | [5 empty] | 305 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.32 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.320000
P04 | 北港PS | 0 |  | RTU | RTU |  | ADCL2 |  |  | MvMoment | No2 AI參考點 10% |  | Y |  | AI | [6 empty] | 0064 |  |  | 1-C0 |  |  | 10% ＡＩ轉換卡檢查參考點 200 ± 2 COUNTS (For No.2 AI Card) |  |  | ADCL_-2000_2000(-2000_2000) |  | B3/P04_A1 | [8 empty] | 北港PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | [5 empty] | 306 |  |  |  |  | AI | [5 empty] | LG_ADCL | 210 | 211 | 212 | 213 | 10 | 190 | 189 | 188 | 187 | 1 | 0.01 | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | RTU | RTU |  | ADCH2 |  |  | MvMoment | No2 AI參考點 90% |  | Y |  | AI | [6 empty] | 0065 |  |  | 1-C1 |  |  | 90% ＡＩ轉換卡檢查參考點 1800 ±2 COUNTS (For No.2 AI Card) |  |  | ADCH_-2000_2000(-2000_2000) |  | B3/P04_A1 | [8 empty] | 北港PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | [5 empty] | 307 |  |  |  |  | AI | [5 empty] | LG_ADCH | 1810 | 1811 | 1812 | 1813 | 10 | 1790 | 1789 | 1788 | 1787 | 1 | 0.01 | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P04 | 北港PS |  |  | 2MTR | #2MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0066 |  |  | 1-AF |  |  | #2MTR | ℃ | #2MTR 二次線溫 | COIL_-160_160(-2000_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_COIL | #2MTR 線溫 | MTR | [5 empty] | 308 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.32 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.320000
P04 | 北港PS |  |  | 3MTR | #3MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0068 |  |  | 1-B1 |  |  | #3MTR | ℃ | #3MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_OIL | #3MTR 油溫 | MTR | [5 empty] | 309 |  |  |  |  | AI | [5 empty] | LG_TMP3M | 67 | 68 | 83 | 90 | 2.6 | 20 | -10 | -11 | -12 | 0.24 |  | LG_TMP3M | 67.000000 | 67.000000 | 83.000000 | 90.000000 | 2.600000 | 20.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 3MTR | #3MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0069 |  |  | 1-B4 |  |  | #3MTR | ℃ | #3MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_COIL | #3MTR 線溫 | MTR | [5 empty] | 310 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 4MTR | #4MTR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0071 |  |  | 1-B6 |  |  | #4MTR | ℃ | #4MTR 油溫 | OIL_-120_120(-2000_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_OIL | #4MTR 油溫 | MTR | [5 empty] | 311 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 4MTR | #4MTR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0072 |  |  | 1-B7 |  |  | #4MTR | ℃ | #4MTR 二次線溫 | COIL_-120_120(-2000_2000) |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_COIL | #4MTR 線溫 | MTR | [5 empty] | 312 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | DCV_P |  |  | MvMoment | 直流P電源電壓 |  | Y |  | AI | [6 empty] | 0073 |  |  | 1-B8 |  |  | DCV | 65 | DC-P 電壓 | kV_-150_150(-2000_2000) |  | B3/P04_A1 | [8 empty] | 北港PS.直流P電源電壓 | 直流P電源電壓 | OTHER | [5 empty] | 313 |  |  |  |  | AI | [5 empty] | LG_125P | 70 | 71 | 75 | 150 | 0.2 | 60 | 59 | 55 | -150 | 0.1 | 0.01 | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | DCV_N |  |  | MvMoment | 直流N電源電壓 |  | Y |  | AI | [6 empty] | 0074 |  |  | 1-B9 |  |  | DCV | -65.5 | DC-N 電壓 | kV_-150_150(-2000_2000) |  | B3/P04_A1 | [8 empty] | 北港PS.直流N電源電壓 | 直流N電源電壓 | OTHER | [5 empty] | 314 |  |  |  |  | AI | [5 empty] | LG_125N | -60 | -59 | -55 | 150 | 0.2 | -70 | -71 | -75 | -150 | 0.1 | 0.01 | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0102 |  |  | 1-0C-06 |  |  | 1570 | 87A2 | 雲林北港雲高線1570 87A2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_87A2 | 雲林北港雲高線(1570) #2 87RY | LINE161 | [5 empty] | 373 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0688 |  |  | 1-3B-00 |  |  | 1570 | USE/LOCE | 雲林北港雲高線 87RY UL2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_87UL2 | 雲林北港雲高線(1570)#287RY U/L | LINE161 | [5 empty] | 439 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0689 |  |  | 1-3B-01 |  |  | 1570 | USE/LOCE | 雲林北港雲高線 79RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_79UL | 雲林北港雲高線(1570) 79RY U/L | LINE161 | [5 empty] | 440 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0768 |  |  | 2-30-00 |  |  | 1570 | ON/OFF | 雲林北港雲高線 TONE |  |  | B2/P04_A1 | [16 empty] | 478 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0082 |  |  | 1-B3 |  |  | 1630 | KV | 北港嘉民南線 1630 LPD | kV_-210_210(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1630LPD_KV | 嘉民南線(1630) LPD KV | LINE161 | [5 empty] | 319 |  |  |  |  | AI | [5 empty] | LG_16LPD | 169 | 170 | 172 | 210 | 0.5 | 153 | 152 | 151 | 0 | 5 | 10 | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | V |  |  | MvMoment | kV |  | Y |  | AI | [6 empty] | 0083 |  |  | 1-C2 |  |  | 1640 | KV | 北港嘉民北線 1640 LPD | kV_-210_210(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1640LPD_KV | 嘉民北線(1640) LPD KV | LINE161 | [5 empty] | 320 |  |  |  |  | AI | [5 empty] | LG_161 | 167 | 168 | 169 | 210 | 0.5 | 155 | 154 | 153 | 0 | 5 | 10 | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.610BE | 610BE (非取樣點) | LINE69 | [5 empty] | 221 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04S02/T1 |  | 0000 |  | 0019 | 1-00-00 |  | 1-13 | 610 | ON/OFF | 北港口湖線 610 CB |  | aaab | B2/P04_A1 | [8 empty] | 北港PS.610_CB | 610(北港口湖線) CB | LINE69 | [5 empty] | 18 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS |  |  | 1SHR | #1SHR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0088 |  |  | 1-C7 |  |  | 1950 | ℃ | #1並聯電抗器 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | [5 empty] | 323 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 1SHR | #1SHR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0089 |  |  | 1-C8 |  |  | 1950 | ℃ | #1並聯電抗器 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | [5 empty] | 324 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 2SHR | #2SHR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0090 |  |  | 1-C9 |  |  | 1960 | ℃ | #2並聯電抗器 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#2SHR_OIL | 161KV #2SHR 油溫 | OTHER | [5 empty] | 325 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 2SHR | #2SHR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0091 |  |  | 1-CA |  |  | 1960 | ℃ | #2並聯電抗器 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#2SHR_COIL | 161KV #2SHR 線溫 | OTHER | [5 empty] | 326 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 3SHR | #3SHR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0092 |  |  | 1-CB |  |  | 1970 | ℃ | #3並聯電抗器 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#3SHR_OIL | 161KV #3SHR 油溫 | OTHER | [5 empty] | 327 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 3SHR | #3SHR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0093 |  |  | 1-CC |  |  | 1970 | ℃ | #3並聯電抗器 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#3SHR_COIL | 161KV #3SHR 線溫 | OTHER | [5 empty] | 328 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 4SHR | #4SHR |  | OilTemp |  |  | MvMoment | 油溫 |  | Y |  | AI | [6 empty] | 0094 |  |  | 1-CD |  |  | 1980 | ℃ | #4並聯電抗器 油溫 | OIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#4SHR_OIL | 161KV #4SHR 油溫 | OTHER | [5 empty] | 329 |  |  |  |  | AI | [5 empty] | LG_TMP1 | 75 | 76 | 83 | 90 | 2 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS |  |  | 4SHR | #4SHR |  | CoilTemp |  |  | MvMoment | 線溫 |  | Y |  | AI | [6 empty] | 0095 |  |  | 1-CE |  |  | 1980 | ℃ | #4並聯電抗器 線溫 | COIL_-120_120(-2000_2000) | [10 empty] | 北港PS.161#4SHR_COIL | 161KV #4SHR 線溫 | OTHER | [5 empty] | 330 |  |  |  |  | AI | [5 empty] | LG_TMP2 | 90 | 100 | 101 | 110 | 1.7 | -10 | -11 | -12 | -13 | 0.24 |  | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 1A5Other | MDAR | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0769 |  |  | 2-30-01 |  |  | 1570 | ON/OFF | 雲林北港雲高線 MDAR |  |  | B2/P04_A1 | [16 empty] | 479 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0824 |  |  | 2-33-08 |  |  | 1570 | 87CFA | 雲林北港雲高線87RY通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_87CFA | 雲林北港雲高線(1570)RY通訊故障 | OTHER | [5 empty] | 506 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0825 |  |  | 2-33-09 |  |  | 1570 | RYFA | 雲林北港雲高線數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1570_RYFA | 雲林北港雲高線(1570)數位RY故障 | OTHER | [5 empty] | 507 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0045 |  |  | 1-05-05 |  |  | 1630 | 87A | 嘉民北港南線 1630 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_87A | 嘉民南線(1630) 87RY | LINE161 | [5 empty] | 334 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0046 |  |  | 1-05-06 |  |  | 1630 | PHA | 嘉民北港南線 1630 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_PHA | 嘉民南線(1630) 相間RY | LINE161 | [5 empty] | 335 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0047 |  |  | 1-05-07 |  |  | 1630 | GDA | 嘉民北港南線 1630 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_GDA | 嘉民南線(1630) 接地RY | LINE161 | [5 empty] | 336 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0049 |  |  | 1-06-01 |  |  | 1640 | 87A | 嘉民北港北線 1640 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_87A | 嘉民北線(1640) 87RY | LINE161 | [5 empty] | 337 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0050 |  |  | 1-06-02 |  |  | 1640 | PHA | 嘉民北港北線 1640 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_PHA | 嘉民北線(1640) 相間RY | LINE161 | [5 empty] | 338 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0051 |  |  | 1-06-03 |  |  | 1640 | GDA | 嘉民北港北線 1640 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_GDA | 嘉民北線(1640) 接地RY | LINE161 | [5 empty] | 339 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0052 |  |  | 1-06-04 |  |  | #2MTR | 87A | #2MTR 87A |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_87A | #2MTR 87RY | MTR | [5 empty] | 340 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0053 |  |  | 1-06-05 |  |  | #2MTR | PHA | #2MTR_ PHA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_PHA | #2MTR PHA | OTHER | [5 empty] | 341 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0054 |  |  | 1-06-06 |  |  | #2MTR | GDA | #2MTR_GDA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_GDA | #2MTR GDA | OTHER | [5 empty] | 342 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0055 |  |  | 1-06-07 |  |  | #2MTR | 96PA | #2MTR 機械保護動作(96PA) |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | [5 empty] | 343 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0058 |  |  | 1-07-02 |  |  | #2MTR | 51ZA | #2MTR 51ZA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | [5 empty] | 344 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0059 |  |  | 1-07-03 |  |  | #3MTR | 87A | #3MTR 87A |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_87A | #3MTR 87RY | MTR | [5 empty] | 345 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0060 |  |  | 1-07-04 |  |  | #3MTR | PHA | #3MTR_PHA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_PHA | #3MTR PHA | OTHER | [5 empty] | 346 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0061 |  |  | 1-07-05 |  |  | #3MTR | GDA | #3MTR_GDA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_GDA | #3MTR GDA | OTHER | [5 empty] | 347 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0062 |  |  | 1-07-06 |  |  | #3MTR | 96PA | #3MTR 機械保護動作(96PA) |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | [5 empty] | 348 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0065 |  |  | 1-08-01 |  |  | #3MTR | 51ZA | #3MTR 51ZA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | [5 empty] | 349 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0066 |  |  | 1-08-02 |  |  | #4MTR | 87A | #4MTR 87A |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_87A | #4MTR 87RY | MTR | [5 empty] | 350 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0067 |  |  | 1-08-03 |  |  | #4MTR | PHA | #4MTR_PHA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_PHA | #4MTR PHA | OTHER | [5 empty] | 351 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0068 |  |  | 1-08-04 |  |  | #4MTR | GDA | #4MTR_GDA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_GDA | #4MTR GDA | OTHER | [5 empty] | 352 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 96PA |  |  | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0069 |  |  | 1-08-05 |  |  | #4MTR | 96PA | #4MTR 機械保護動作(96PA) |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_96PA | #4MTR 機械保護動作 | MTR | [5 empty] | 353 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 51ZA |  |  | Status | 51Z RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0072 |  |  | 1-09-00 |  |  | #4MTR | 51ZA | #4MTR 51ZA |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_51ZA | #4MTR 51Z RY | MTR | [5 empty] | 354 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | 50A |  |  | Status | 50RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0074 |  |  | 1-09-02 |  |  | 1500 | 50A | 1500 TIE 50 RY |  |  | B2/P04_A1 | [8 empty] | 北港PS.1500_50A | 161KV TIE(1500) 50RY | TIE | [5 empty] | 355 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 |  |  | Status | 第1具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0076 |  |  | 1-09-04 |  |  | 600 | #1PHA | 600 TIE #1 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | [5 empty] | 356 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 |  |  | Status | 第1具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0077 |  |  | 1-09-05 |  |  | 600 | #1GDA | 600 TIE #1 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | [5 empty] | 357 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0078 |  |  | 1-09-06 |  |  | 161KVBUS | 87B1A | 161KVBUS 87B1A |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1BUS_87A | 161KV #1BUS 87A | BUS | [5 empty] | 358 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0079 |  |  | 1-09-07 |  |  | 161KVBUS | 87B2A | 161KVBUS 87B2A |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2BUS_87A | 161KV #2BUS 87A | BUS | [5 empty] | 359 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 1BUS | #1BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0081 |  |  | 1-0A-01 |  |  | 69KVBUS | 87B1A | 69KVBUS 87B1A |  |  | B2/P04_A1 | [8 empty] | 北港PS.69#1BUS_87A | 69KV #1BUS 87A | BUS | [5 empty] | 360 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 2BUS | #2BUS |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0082 |  |  | 1-0A-02 |  |  | 69KVBUS | 87B2A | 69KVBUS 87B2A |  |  | B2/P04_A1 | [8 empty] | 北港PS.69#2BUS_87A | 69KV #2BUS 87A | BUS | [5 empty] | 361 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | RCA |  |  | Status | 79RY動作 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0084 |  |  | 1-0A-04 |  |  | 161KV | 79RY | 161KV 79RY動作 |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | [5 empty] | 362 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0085 |  |  | 1-0A-05 |  |  | OSCA | A/N | 161KV示波器啟動警報OSCA |  |  | B3/P04_A1 | [8 empty] | 北港PS.OSC啟動 | 示波器啟動警報 | OTHER | [5 empty] | 363 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | OSCA |  |  | Status | 示波器起動警報 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0086 |  |  | 1-0A-06 |  |  | OSCA | A/N | 69KV示波器啟動警報OSCA |  |  | B3/P04_A1 | [8 empty] | 北港PS.69KV_OSCA | 69KV示波器啟動 | OTHER | [5 empty] | 364 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | ABS1 | 1581 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0520 | 521 | 0117 | 1-30-08 | 1-30-09 | 1-75 | 1581 | ON | 北港台西線1581 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1581_ABS | 1581(北港台西線) ABS | LINE161 | [5 empty] | 111 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | ABS2 | 1582 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0522 | 523 | 0118 | 1-30-10 | 1-30-11 | 1-76 | 1582 | ON | 北港台西線1582 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1582_ABS | 1582(北港台西線) ABS | LINE161 | [5 empty] | 112 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | ABS3 | 1583 | Element | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0524 | 525 | 0119 | 1-30-12 | 1-30-13 | 1-77 | 1583 | ON | 北港台西線1583 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1583_ABS | 1583(北港台西線) ABS | LINE161 | [5 empty] | 113 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0092 |  |  | 1-0B-04 |  |  | 1630 | A/N | 嘉民北港南線 1630 遠方遙跳 DTTA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_DTTA | 北港嘉民南線(1630)遠方遙跳 | OTHER | [5 empty] | 368 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0093 |  |  | 1-0B-05 |  |  | 1640 | A/N | 嘉民北港北線 1640 遠方遙跳 DTTA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_DTTA | 北港嘉民北線(1640)遠方遙跳 | OTHER | [5 empty] | 369 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | ES3 | 1583E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0526 | 527 | 0120 | 1-30-14 | 1-30-15 | 1-78 | 1583E | ON | 北港台西線1583 EABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1583E_ES | 1583E(北港台西線) ES | LINE161 | [5 empty] | 114 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04D21/T1 |  | 0088 |  | 0127 | 1-0B-00 |  | 1-7F | 1580 | ON/OFF | 北港台西線1580 CB |  | aaja | B2/P04_A1 | [8 empty] | 北港PS.1580_CB | 1580(北港台西線) CB | LINE161 | [5 empty] | 121 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0519 |  | 0142 | 1-30-07 |  | 2-0E | 1580 | USE/LOCK | 北港台西線 79RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_79UL | 北港台西線(1580) 79RY U/L | LINE161 | [5 empty] | 136 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 87UL |  |  | Status | 87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0518 |  | 0143 | 1-30-06 |  | 2-0F | 1580 | USE/LOCK | 北港台西線 87RY UL2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_87UL2 | 北港台西線(1580) #2 87RY U/L | LINE161 | [5 empty] | 137 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0829 |  | 0173 | 2-33-13 |  | 2-2D | 1580 | USE/LOCK | 北港台西線 87RY UL1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_87UL1 | 北港台西線(1580) #1 87RY U/L | LINE161 | [5 empty] | 146 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0120 |  |  | 1-0F-00 |  |  | 710 | 87A | 北港雲港一路 710 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.710_87A | 雲港一路(710) 87RY | LINE69 | [5 empty] | 378 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | 87A |  |  | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0121 |  |  | 1-0F-01 |  |  | 720 | 87A | 北港雲港二路 720 87A |  |  | B2/P04_A1 | [8 empty] | 北港PS.720_87A | 雲港二路(720) 87RY | LINE69 | [5 empty] | 379 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | ES3 | 613E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 0566 | 567 | 0023 | 1-33-06 | 1-33-07 | 1-17 | 613E | ON | 北港口湖線 613E ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.613E_ES | 613E(北港口湖線) ES | LINE69 | [5 empty] | 22 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS |  |  | 2MTR | #2MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0125 |  |  | 1-0F-05 |  |  | #2MTR | 86A | #2MTR_ 86A |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_86A | #2MTR 86RY | OTHER | [5 empty] | 381 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0126 |  |  | 1-0F-06 |  |  | #3MTR | 86A | #3MTR_ 86A |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_86A | #3MTR 86RY | OTHER | [5 empty] | 382 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | MTR_86A |  |  | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0127 |  |  | 1-0F-07 |  |  | #4MTR | 86A | #4MTR_ 86A |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_86A | #4MTR 86RY | OTHER | [5 empty] | 383 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 |  |  | Status | 第2具PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0128 |  |  | 1-10-00 |  |  | 600 | #2PHA | 600 TIE #2 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | [5 empty] | 384 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 |  |  | Status | 第2具GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0129 |  |  | 1-10-01 |  |  | 600 | #2GDA | 600 TIE #2 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | [5 empty] | 385 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | RTU | RTU |  | RTU_MCT |  |  | Status | RTU Master Ry | Open/Close | Y | E | DI-SP | [6 empty] | 0130 |  |  | 1-10-02 |  |  | RTU | MCT_ SOE | RTU MASTER RY SOE |  |  | B3/P04_A1 | [16 empty] | 386 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0002 |  |  | 1-00-02 |  |  | 610 | GDA | 北港口湖線 610 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.610_GDA | 北港口湖線(610) 接地RY | LINE69 | [5 empty] | 388 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0034 |  |  | 1-9A |  |  | 620 | MVAR | 北港水林二路 620 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.620_MVAR | 北港水林二路 MVAR | LINE69 | [5 empty] | 286 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0037 |  |  | 1-9C |  |  | 630 | MVAR | 北港水林一路 630 乏 | MVAR_-240_240(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.630_MVAR | 北港水林一路 MVAR | LINE69 | [5 empty] | 288 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0040 |  |  | 1-9E |  |  | 640 | MVAR | 北港朴子線 640 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.640_MVAR | 北港朴子線 MVAR | LINE69 | [5 empty] | 290 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0043 |  |  | 1-A0 |  |  | 670 | MVAR | 北港新港一路 670 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.670_MVAR | 北港新港一路 MVAR | LINE69 | [5 empty] | 292 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0046 |  |  | 1-A2 |  |  | 680 | MVAR | 北港新港二路 680 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.680_MVAR | 北港新港二路 MVAR | LINE69 | [5 empty] | 294 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0019 |  |  | 1-02-03 |  |  | 710 | PHA | 北港雲港一路 710 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.710_PHA | 雲港一路(710) 相間RY | LINE69 | [5 empty] | 399 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0020 |  |  | 1-02-04 |  |  | 710 | GDA | 北港雲港一路 710 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.710_GDA | 雲港一路(710) 接地RY | LINE69 | [5 empty] | 400 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0022 |  |  | 1-02-06 |  |  | 720 | PHA | 北港雲港二路 720 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.720_PHA | 雲港二路(720) 相間RY | LINE69 | [5 empty] | 401 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0023 |  |  | 1-02-07 |  |  | 720 | GDA | 北港雲港二路 720 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.720_GDA | 雲港二路(720) 接地RY | LINE69 | [5 empty] | 402 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0055 |  |  | 1-A8 |  |  | 910 | MVAR | 北港土庫線 910 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.910_MVAR | 北港土庫線 MVAR | LINE69 | [5 empty] | 300 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0058 |  |  | 1-AA |  |  | 920 | MVAR | 北港元長線 920 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.920_MVAR | 元長線 MVAR | LINE69 | [5 empty] | 302 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0061 |  |  | 1-AC |  |  | 940 | MVAR | 北港東北線 940 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.940_MVAR | 北港東北線 MVAR | LINE69 | [5 empty] | 304 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0054 |  |  | 1-A7 |  |  | 910 | MW | 北港土庫線 910 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.910_MW | 北港土庫線 MW | LINE69 | [5 empty] | 299 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0057 |  |  | 1-A9 |  |  | 920 | MW | 北港元長線 920 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.920_MW | 元長線 MW | LINE69 | [5 empty] | 301 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0060 |  |  | 1-AB |  |  | 940 | MW | 北港東北線 940 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.940_MW | 北港東北線 MW | LINE69 | [5 empty] | 303 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0033 |  |  | 1-04-01 |  |  | 820 | SCA | 69KV #2SC 820 SCA |  |  | B2/P04_A1 | [8 empty] | 北港PS.820_SCA | 69KV #2SC 51,51N RY | SC | [5 empty] | 409 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0034 |  |  | 1-04-02 |  |  | 820 | UVA | 69KV #2SC 820 UVA |  |  | B2/P04_A1 | [8 empty] | 北港PS.820_OUVA | 69KV #2SC 27,59RY | SC | [5 empty] | 410 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | SCA |  |  | Status | 51/51N RY | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0036 |  |  | 1-04-04 |  |  | 830 | SCA | 69KV #3SC 830 SCA |  |  | B2/P04_A1 | [8 empty] | 北港PS.830_SCA | 69KV #3SC 51,51N RY | SC | [5 empty] | 411 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | UVA |  |  | Status | 27/59 RY(欠壓或過壓) | Normal/Trip | Y | 3 | DI-SP | [6 empty] | 0037 |  |  | 1-04-05 |  |  | 830 | UVA | 69KV #3SC 830 UVA |  |  | B2/P04_A1 | [8 empty] | 北港PS.830_OUVA | 69KV #3SC 27,59RY | SC | [5 empty] | 412 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0033 |  |  | 1-99 |  |  | 620 | MW | 北港水林二路 620 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.620_MW | 北港水林二路 MW | LINE69 | [5 empty] | 285 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0036 |  |  | 1-9B |  |  | 630 | MW | 北港水林一路 630 瓦 | MW_-240_240(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.630_MW | 北港水林一路 MW | LINE69 | [5 empty] | 287 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.48 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0039 |  |  | 1-9D |  |  | 640 | MW | 北港朴子線 640 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.640_MW | 北港朴子線 MW | LINE69 | [5 empty] | 289 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0042 |  |  | 1-9F |  |  | 670 | MW | 北港新港一路 670 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.670_MW | 北港新港一路 MW | LINE69 | [5 empty] | 291 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0045 |  |  | 1-A1 |  |  | 680 | MW | 北港新港二路 680 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.680_MW | 北港新港二路 MW | LINE69 | [5 empty] | 293 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0031 |  |  | 1-98 |  |  | 610 | MVAR | 北港口湖線 610 乏 | MVAR_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.610_MVAR | 北港口湖線 MVAR | LINE69 | [5 empty] | 284 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0030 |  |  | 1-97 |  |  | 610 | MW | 北港口湖線 610 瓦 | MW_-144_144(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.610_MW | 北港口湖線 MW | LINE69 | [5 empty] | 283 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.288 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | CB |  |  | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04D222/T1 |  | 0261 |  | 0201 | 2-00-05 |  | 2-49 | 1520 | ON/OFF | 北港四湖二路1520 CB |  | aaca | B2/P04_A1 | [8 empty] | 北港PS.1520_CB | 1520(北港四湖二路) CB | LINE161 | [5 empty] | 168 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | ABS1 | 1521 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1000 | 1001 | 0220 | 2-3E-08 | 2-3E-09 | 2-5C | 1521 | ON | 北港四湖二路 1521 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1521_ABS | 1521(北港四湖二路) ABS | LINE161 | [5 empty] | 173 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbA | B/1Bus | B/2Bus | R/2SHR |  | 0271 |  | 0203 | 2-01-07 |  | 2-4B | 1960 | ON/OFF | #2並聯電抗器 1960 CB |  | aabb | B2/P04_A1 | [8 empty] | 北港PS.1960_CB | 1960(161KV #2SHR) CB | OTHER | [5 empty] | 170 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | ABS1 | 1961 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1012 | 1013 | 0226 | 2-3F-04 | 2-3F-05 | 2-62 | 1961 | ON | #2並聯電抗器 1961 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1961_ABS | 1961(161KV #2SHR) ABS | OTHER | [5 empty] | 179 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | ABS2 | 1962 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1014 | 1015 | 0227 | 2-3F-06 | 2-3F-07 | 2-63 | 1962 | ON | #2並聯電抗器 1962 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1962_ABS | 1962(161KV #2SHR) ABS | OTHER | [5 empty] | 180 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1960BE | 1960BE(非取樣點) | OTHER | [5 empty] | 250 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1960RE | 1960RE(非取樣點) | OTHER | [5 empty] | 251 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0272 |  |  | 2-02-00 |  |  | 1960 | 87RA | #2並聯電抗器 87RA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_87A | 161KV #2SHR 87RY | OTHER | [5 empty] | 426 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | MTR_86A |  | B3 | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0273 |  |  | 2-02-01 |  |  | 1960 | 86A | #2並聯電抗器 86A |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_86A | 161KV #2SHR 86RY | OTHER | [5 empty] | 427 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0274 |  |  | 2-02-02 |  |  | 1960 | 51A | #2並聯電抗器 51A(51、51N) |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_51A | 161KV #2SHR 51RY | OTHER | [5 empty] | 428 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96PA | 2SSR | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0275 |  |  | 2-02-03 |  |  | 1960 | 96A | #2並聯電抗器 機械保護動作96PA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR96PA | 161KV #2SHR 機械保護動作 | OTHER | [5 empty] | 429 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | 1_87UL1 |  | B3 | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0919 |  |  | 2-39-07 |  |  | 1960 | USE/LOCK | #2並聯電抗器 #1 87RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_87UL1 | 161KV #2SHR #187RY U/L | OTHER | [5 empty] | 554 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | 1_87UL2 |  | B3 | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0920 |  |  | 2-39-08 |  |  | 1960 | USE/LOCK | #2並聯電抗器 #2 87RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_87UL2 | 161KV #2SHR #287RY U/L | OTHER | [5 empty] | 555 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0921 |  |  | 2-39-09 |  |  | 1960 | RYFA | #2並聯電抗器數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161_2SHR_RYFA | 161KV 2SHR(1960)數位電驛故障 | OTHER | [5 empty] | 556 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0922 |  |  | 2-39-10 |  |  | 1960 | 96B1 | #2並聯電抗器96B1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_96B1 | 161KV #2SHR 96B1 RY | OTHER | [5 empty] | 557 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0923 |  |  | 2-39-11 |  |  | 1960 | 96B2 | #2並聯電抗器96B2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_96B2 | 161KV #2SHR 96B2 RY | OTHER | [5 empty] | 558 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0924 |  |  | 2-39-12 |  |  | 1960 | 96D | #2並聯電抗器96D |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_96D | 161KV #2SHR 96D RY | OTHER | [5 empty] | 559 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0925 |  |  | 2-39-13 |  |  | 1960 | 96P | #2並聯電抗器96P |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_96P | 161KV #2SHR 96P RY | OTHER | [5 empty] | 560 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | RTU | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP | [6 empty] | 0513 |  |  | 1-30-01 |  |  | RTU | L/R | L/R STATUS |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | [5 empty] | 438 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Rem/Loc | Loc | 1 |  |  | LOCAL/SUPERVISORY | SUPERVISORY
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1580BE | 1580BE (非取樣點) | LINE161 | [5 empty] | 215 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0691 |  |  | 1-3B-03 |  |  | 1640 | USE/LOCE | 嘉民北港北線 1640 79RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_79UL | 嘉民北線(1640) 79RY U/L | LINE161 | [5 empty] | 441 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0693 |  |  | 1-3B-05 |  |  | 1630 | USE/LOCE | 嘉民北港南線 1630 79RY U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_79UL | 嘉民南線(1630) 79RY U/L | LINE161 | [5 empty] | 442 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS |  |  | 2MTR | #2MTR |  | TRA |  |  | Status | 變壓器重故障 | Normal/Fault | Y | 3 | DI-SP |  | MTR |  |  |  |  | 0656 |  |  | 1-39-00 |  |  | #2MTR | TRA | #2MTR 重故障 |  | a | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_TRA | #2MTR 重故障 | MTR | [5 empty] | 443 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS2 | 772 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 0670 | 671 |  | 1-39-14 | 1-39-15 |  | 772 | ON | #3MTR 772 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.772_ABS | 772(#3MTR) ABS | MTR | [5 empty] | 444 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS |  |  | 4MTR | #4MTR |  | TRF |  |  | Status | 變壓器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0687 |  |  | 1-3A-15 |  |  | #4MTR | TRF | #4MTR 輕故障 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_TRF | #4MTR 輕故障 | MTR | [5 empty] | 445 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | SupLocal |  |  | Status | OLTC S/L | Sup/Loc | Y | 3 | DI-SP | [6 empty] | 0705 |  |  | 1-3C-01 |  |  | #4MTR | 遙控/現場 | #4MTR S/L |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_S/L | #4MTR OLTC S/L | MTR | [5 empty] | 446 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Sup/Loc | Sup | 0 |  |  | SUPERVISORY/LOCAL | SUPERVISORY
P04 | 北港PS | 161 | 161kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0707 |  |  | 1-3C-03 |  |  | 161KV | ON/OFF | 161KV #1BUS VUA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | [5 empty] | 447 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0708 |  |  | 1-3C-04 |  |  | 161KV | ON/OFF | 161KV #2BUS VUA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | [5 empty] | 448 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 1BUS | #1BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0709 |  |  | 1-3C-05 |  |  | 69KV | ON/OFF | 69KV #1BUS VUA |  |  | B2/P04_A1 | [8 empty] | 北港PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | [5 empty] | 449 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 2BUS | #2BUS |  | BUS_VUA |  |  | Status | 衡相RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0710 |  |  | 1-3C-06 |  |  | 69KV | ON/OFF | 69KV #2BUS VUA |  |  | B2/P04_A1 | [8 empty] | 北港PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | [5 empty] | 450 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | ComPoint |  |  | 25TA |  |  | Status | 同步校核電驛超時 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0718 |  |  | 1-3C-14 |  |  | 25RY | 25TA | 同步校核裝置 超時警報 |  |  | B3/P04_A1 | [8 empty] | 北港PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | [5 empty] | 451 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | ComPoint |  |  | 25PFA |  |  | Status | 同步校核電驛電源 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0719 |  |  | 1-3C-15 |  |  | 25RY | 25PFA | 同步校核裝置 電源故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | [5 empty] | 452 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | CHG1 |  |  | Status | 直流充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0720 |  |  | 1-3D-00 |  |  | CHG1 | ON/OFF | 變電充電機故障 CHG1 |  |  | B3/P04_A1 | [8 empty] | 北港PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | [5 empty] | 453 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | CHG2 |  |  | Status | 通訊充電機 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0721 |  |  | 1-3D-01 |  |  | CHG2 | ON/OFF | 通訊充電機故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | [5 empty] | 454 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0722 |  |  | 1-3D-02 |  |  | DCE | ON/OFF | 直流接地故障 DCE |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.直流電源DCE | 直流電源接地故障警報 | OTHER | [5 empty] | 455 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Door1 | 圍牆大小門 |  | Status | 無人化門禁1 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0723 |  |  | 1-3D-03 |  |  | DOOR#1 | ON/OFF | 圍牆大小門 DOOR#1 |  |  | B3/P04_A1 | [8 empty] | 北港PS.無人化門禁(1) | 無人化門禁(1)變電所大門 | OTHER | [5 empty] | 456 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Door2 | 控制室 |  | Status | 無人化門禁2 | Close/Open | Y | 5 | DI-SP | [6 empty] | 0724 |  |  | 1-3D-04 |  |  | DOOR#2 | ON/OFF | 控制室 DOOR#2 |  |  | B3/P04_A1 | [8 empty] | 北港PS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | [5 empty] | 457 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0729 |  |  | 1-3D-09 |  |  | 161KV | CBF | 161KV CB 輕故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | [5 empty] | 458 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0730 |  |  | 1-3D-10 |  |  | 161KV | CBA | 161KV CB 重故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_CBA | 161KV斷路器重故障 | OTHER | [5 empty] | 459 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | CBF |  |  | Status | 斷路器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0731 |  |  | 1-3D-11 |  |  | 69KV | CBF | 69KV CB 輕故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | [5 empty] | 460 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | CBA |  |  | Status | 斷路器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0732 |  |  | 1-3D-12 |  |  | 69KV | CBA | 69KV CB 重故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.69KV_CBA | 69KV斷路器重故障 | OTHER | [5 empty] | 461 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Fire1 | 受信總機 |  | Status | 火災警報1 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0733 |  |  | 1-3D-13 |  |  | 火災警報(1) | ON/OFF | 火災警報(1)受信總機 |  |  | B3/P04_A1 | [8 empty] | 北港PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | [5 empty] | 462 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Fire4 | #4MTR |  | Status | 火災警報4 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0734 |  |  | 1-3D-14 |  |  | 火災警報(4) | ON/OFF | 火災警報(4) -#4MTR |  |  | B3/P04_A1 | [8 empty] | 北港PS.火災警報(4) | 火災警報(4)#4MTR | OTHER | [5 empty] | 463 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | 50SA |  |  | Status | 50RY 測試/正常 | Normal/Test | Y | 3 | DI-SP | [6 empty] | 0735 |  |  | 1-3D-15 |  |  | 161KV TIE | 測試/正常 | 161KV TIE (1500)50RY 測試/正常 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | [5 empty] | 464 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Test | Test | 1 |  |  | TEST/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Fire2 | 控制大樓CO2 |  | Status | 火災警報2 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0737 |  |  | 1-3E-01 |  |  | 火災警報(2) | ON/OFF | 火災警報(2)建物-控制大樓CO2 |  |  | B3/P04_A1 | [8 empty] | 北港PS.火災警報(2) | 火災警報(2)建物-控制大樓CO2 | OTHER | [5 empty] | 465 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0738 |  |  | 1-3E-02 |  |  | DC之NFB | ON/OFF | DC之NFB DCA |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.直流電源DCA | 直流電源故障警報 | OTHER | [5 empty] | 466 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0740 |  |  | 1-3E-04 |  |  | 69KV | ON/OFF | 69KV ABS 電源警報 |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 467 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0741 |  |  | 1-3E-05 |  |  | STUV | ON/OFF | 所內電源欠壓 STUV |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | [5 empty] | 468 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0742 |  |  | 1-3E-06 |  |  | 161KV ABS | ON/OFF | 161KV ABS 電源警報 |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | [5 empty] | 469 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | AIRCON |  |  | Status | 冷氣跳脫 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0743 |  |  | 1-3E-07 |  |  | 空調機 | ON/OFF | 空調機 運轉跳脫警報 |  |  | B3/P04_A1 | [8 empty] | 北港PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | [5 empty] | 470 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Normal | 0 |  |  | NORMAL/FAULT | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0025 |  |  | 1-03-01 |  |  | 910 | PHA | 北港土庫線 910 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.910_PHA | 北港土庫線(910) 相間RY | LINE69 | [5 empty] | 403 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Burglar1 | 控制室 |  | Status | 無人化防盜1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0746 |  |  | 1-3E-10 |  |  | 保全(1) | ON/OFF | 控制室保全(1) |  |  | B3/P04_A1 | [8 empty] | 北港PS.無人化防盜(1) | 無人化防盜(1)控制室保全 | OTHER | [5 empty] | 472 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Burglar2 | 圍牆 |  | Status | 無人化防盜2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0747 |  |  | 1-3E-11 |  |  | 保全(2) | ON/OFF | 圍牆保全(2) |  |  | B3/P04_A1 | [8 empty] | 北港PS.無人化防盜(2) | 無人化防盜(2)圍牆保全 | OTHER | [5 empty] | 473 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0748 |  |  | 1-3E-12 |  |  | 1630 | A/N | 嘉民北港南線 1630 87CFA(87L通訊故障) |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_87CFA | 北港嘉民南線(1630)87RY通訊故障 | OTHER | [5 empty] | 474 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0749 |  |  | 1-3E-13 |  |  | 1640 | A/N | 嘉民北港北線 1640 87CFA(87L通訊故障) |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_87CFA | 北港嘉民北線(1640)87RY通訊故障 | OTHER | [5 empty] | 475 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Water1 | 0.5M |  | Status | 地下室淹水1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0750 |  |  | 1-3E-14 |  |  | 地下室 | A/N | 地下室 0.5M 水位警報 |  |  | B3/P04_A1 | [8 empty] | 北港PS.水位警報(1) | 地下室水位警報(1) | OTHER | [5 empty] | 476 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | Water2 | 1M |  | Status | 地下室淹水2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0751 |  |  | 1-3E-15 |  |  | 地下室 | A/N | 地下室 1M 水位警報 |  |  | B3/P04_A1 | [8 empty] | 北港PS.水位警報(2) | 地下室水位警報(2) | OTHER | [5 empty] | 477 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0075 |  |  | 1-BA |  |  | 1580 | MW | 北港台西線1580 瓦 | MW_-336_336(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1580_MW | 北港台西線 MW | LINE161 | [5 empty] | 315 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0076 |  |  | 1-BB |  |  | 1580 | MVAR | 北港台西線 1580 乏 | MVAR_-336_336(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1580_MVAR | 北港台西線 MVAR | LINE161 | [5 empty] | 316 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 0.672 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0089 |  |  | 1-0B-01 |  |  | 1580 | 87A1 | 北港台西線1580 87A1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_87A1 | 北港台西線(1580) #1 87RY | LINE161 | [5 empty] | 365 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0090 |  |  | 1-0B-02 |  |  | 1580 | PHA | 北港台西線1580 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_PHA | 北港台西線(1580) 相間RY | LINE161 | [5 empty] | 366 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0091 |  |  | 1-0B-03 |  |  | 1580 | GDA | 北港台西線1580 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_GDA | 北港台西線(1580) 接地RY | LINE161 | [5 empty] | 367 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0103 |  |  | 1-0C-07 |  |  | 1580 | 87A2 | 北港台西線1580 87A2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_87A2 | 北港台西線(1580) #2 87RY | LINE161 | [5 empty] | 374 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0784 |  |  | 2-31-00 |  |  | #2MTR | ON/OFF | #2MTR 96P |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_96P | #2MTR 96P RY | MTR | [5 empty] | 484 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0785 |  |  | 2-31-01 |  |  | #2MTR | ON/OFF | #2MTR 96D |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_96D | #2MTR 96D RY | MTR | [5 empty] | 485 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0786 |  |  | 2-31-02 |  |  | #2MTR | ON/OFF | #2MTR 96B1 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | [5 empty] | 486 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0787 |  |  | 2-31-03 |  |  | #2MTR | ON/OFF | #2MTR 96B2 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | [5 empty] | 487 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0788 |  |  | 2-31-04 |  |  | #2MTR | ON/OFF | #2MTR 63Q |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_63Q | #2MTR 63Q RY | MTR | [5 empty] | 488 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0789 |  |  | 2-31-05 |  |  | #3MTR | ON/OFF | #3MTR 96P |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_96P | #3MTR 96P RY | MTR | [5 empty] | 489 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0790 |  |  | 2-31-06 |  |  | #3MTR | ON/OFF | #3MTR 96D |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_96D | #3MTR 96D RY | MTR | [5 empty] | 490 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0791 |  |  | 2-31-07 |  |  | #3MTR | ON/OFF | #3MTR 96B1 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | [5 empty] | 491 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0792 |  |  | 2-31-08 |  |  | #3MTR | ON/OFF | #3MTR 96B2 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_96B2 | #3MTR 96B2 RY | MTR | [5 empty] | 492 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0793 |  |  | 2-31-09 |  |  | #3MTR | ON/OFF | #3MTR 63Q |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_63Q | #3MTR 63Q RY | MTR | [5 empty] | 493 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 96P |  |  | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0794 |  |  | 2-31-10 |  |  | #4MTR | ON/OFF | #4MTR 96P |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_96P | #4MTR 96P RY | MTR | [5 empty] | 494 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 96D |  |  | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0795 |  |  | 2-31-11 |  |  | #4MTR | ON/OFF | #4MTR 96D |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_96D | #4MTR 96D RY | MTR | [5 empty] | 495 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 96B1 |  |  | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0796 |  |  | 2-31-12 |  |  | #4MTR | ON/OFF | #4MTR 96B1 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_96B1 | #4MTR 96B1 RY | MTR | [5 empty] | 496 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 96B2 |  |  | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0797 |  |  | 2-31-13 |  |  | #4MTR | ON/OFF | #4MTR 96B2 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_96B2 | #4MTR 96B2 RY | MTR | [5 empty] | 497 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | 63Q |  |  | Status | 63Q RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0798 |  |  | 2-31-14 |  |  | #4MTR | ON/OFF | #4MTR 63Q |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_63Q | #4MTR 63Q RY | MTR | [5 empty] | 498 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | GEN | 緊急發電機運轉 | Element | Status | 警報等級5動作2 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0799 |  |  | 2-31-15 |  |  | Locate Empty | ON/OFF | 緊急發電機運轉 |  |  | B3/P04_A1 | [8 empty] | 北港PS.GEN | 緊急發電機運轉 | OTHER | [5 empty] | 499 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ON/OFF | OFF
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0816 |  |  | 2-33-00 |  |  | 1640 | A/N | 嘉民北港北線 1640 RYFA(電驛故障) |  |  | B2/P04_A1 | [8 empty] | 北港PS.1640_RYFA | 北港嘉民北線(1640)數位電驛故障 | OTHER | [5 empty] | 500 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0817 |  |  | 2-33-01 |  |  | 1630 | A/N | 嘉民北港南線 1630 RYFA(電驛故障) |  |  | B2/P04_A1 | [8 empty] | 北港PS.1630_RYFA | 北港嘉民南線(1630)數位電驛故障 | OTHER | [5 empty] | 501 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | CommACF |  |  | Status | 通訊設備AC | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0818 |  |  | 2-33-02 |  |  | Locate Empty | A/N | 通訊設備 AC故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | [5 empty] | 502 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | R_Temp |  |  | Status | 溫度警報 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0821 |  |  | 2-33-05 |  |  | Locate Empty | A/N | 通信室溫控警報 |  |  | B3/P04_A1 | [8 empty] | 北港PS.通信機房溫度 | 通信機房溫度警報 | OTHER | [5 empty] | 503 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0822 |  |  | 2-33-06 |  |  | OSCF | A/N | 161KV示波器缺紙或故障警報OSCF |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 504 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | OSCF |  |  | Status | 示波器故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0823 |  |  | 2-33-07 |  |  | OSCF | A/N | 69KV示波器缺紙或故障警報OSCF |  |  | B3/P04_A1 | [8 empty] | 北港PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | [5 empty] | 505 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 85CFA |  |  | Status | 85CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0770 |  |  | 2-30-02 |  |  | 1580 | ON/OFF | 北港台西線 TONE |  |  | B2/P04_A1 | [16 empty] | 480 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 1A5Other | MDAR | Element | Status | 警報等級5動作1 | Normal/Alarm | Y | 5 | DI-SP | [6 empty] | 0771 |  |  | 2-30-03 |  |  | 1580 | ON/OFF | 北港台西線 MDAR |  |  | B2/P04_A1 | [16 empty] | 481 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0826 |  |  | 2-33-10 |  |  | 1580 | 87CFA | 北港台西線 87RY通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_87CFA | 北港台西線(1580)87RY通訊故障 | OTHER | [5 empty] | 508 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0827 |  |  | 2-33-11 |  |  | 1580 | RYFA | 北港台西線 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1580_RYFA | 北港台西線(1580)數位電驛故障 | OTHER | [5 empty] | 509 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | LPDA |  |  | Status | LPD電壓偵測 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0841 |  |  | 2-34-09 |  |  | Locate Empty | LPDA | 161kV LPD電壓偵測 |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_LPDA | 161KV LPD電壓偵測 | OTHER | [5 empty] | 510 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0001 |  |  | 1-00-01 |  |  | 610 | PHA | 北港口湖線 610 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.610_PHA | 北港口湖線(610) 相間RY | LINE69 | [5 empty] | 387 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0004 |  |  | 1-00-04 |  |  | 620 | PHA | 北港水林二路 620 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.620_PHA | 北港水林二路(620) 相間RY | LINE69 | [5 empty] | 389 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0007 |  |  | 1-00-07 |  |  | 630 | PHA | 北港水林一路 630 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.630_PHA | 北港水林一路(630) 相間RY | LINE69 | [5 empty] | 391 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0010 |  |  | 1-01-02 |  |  | 640 | PHA | 北港朴子線 640 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.640_PHA | 北港朴子線(640) 相間RY | LINE69 | [5 empty] | 393 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | PHA |  | B3 | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0028 |  |  | 1-03-04 |  |  | 920 | PHA | 北港元長線 920 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.920_PHA | 元長線(920) 相間RY | LINE69 | [5 empty] | 405 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0031 |  |  | 1-03-07 |  |  | 940 | PHA | 北港東北線 940 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.940_PHA | 北港東北線(940) 相間RY | LINE69 | [5 empty] | 407 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0853 |  |  | 2-35-05 |  |  | 910 | RYFA | 北港土庫線 910 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.910_RYFA | 北港土庫線(910)數位電驛故障 | OTHER | [5 empty] | 516 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0013 |  |  | 1-01-05 |  |  | 670 | PHA | 北港新港一路 670 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.670_PHA | 北港新港一路(670) 相間RY | LINE69 | [5 empty] | 395 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0016 |  |  | 1-02-00 |  |  | 680 | PHA | 北港新港二路 680 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.680_PHA | 北港新港二路(680) 相間RY | LINE69 | [5 empty] | 397 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0855 |  |  | 2-35-07 |  |  | 920 | RYFA | 北港元長線 920 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.920_RYFA | 北港元長線(920)數位電驛故障 | OTHER | [5 empty] | 517 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0860 |  |  | 2-35-12 |  |  | 940 | RYFA | 北港東北線 940 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.940_RYFA | 北港東北線(940)數位電驛故障 | OTHER | [5 empty] | 521 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0862 |  |  | 2-35-14 |  |  | 710 | 87CFA | 北港雲港一路 710 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.710_87CFA | 北港雲港ㄧ路(710)87RY通訊故障 | OTHER | [5 empty] | 522 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0863 |  |  | 2-35-15 |  |  | 710 | RYFA | 北港雲港一路 710 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.710_RYFA | 北港雲港ㄧ路(710)數位電驛故障 | OTHER | [5 empty] | 523 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0865 |  |  | 2-36-01 |  |  | 720 | 87CFA | 北港雲港二路 720 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.720_87CFA | 北港雲港二路(720)87RY通訊故障 | OTHER | [5 empty] | 524 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0866 |  |  | 2-36-02 |  |  | 720 | RYFA | 北港雲港二路 720 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.720_RYFA | 北港雲港二路(720)數位電驛故障 | OTHER | [5 empty] | 525 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0843 |  |  | 2-34-11 |  |  | 670 | RYFA | 北港新港一路 670 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.670_RYFA | 北港新港ㄧ路(670)數位電驛故障 | OTHER | [5 empty] | 512 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0846 |  |  | 2-34-14 |  |  | 680 | RYFA | 北港新港二路 680 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.680_RYFA | 北港新港二路(680)數位電驛故障 | OTHER | [5 empty] | 514 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 2MTR | #2MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0874 |  |  | 2-36-10 |  |  | #2MTR | RYFA | #2MTR 數位電驛故障 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | [5 empty] | 528 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 3MTR | #3MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0877 |  |  | 2-36-13 |  |  | #3MTR | RYFA | #3MTR 數位電驛故障 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER | [5 empty] | 529 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS |  |  | 4MTR | #4MTR |  | RYFA |  |  | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0880 |  |  | 2-37-00 |  |  | #4MTR | RYFA | #4MTR 數位電驛故障 |  |  | B1/P04_A1 | [8 empty] | 北港PS.#4MTR_RYFA | #4MTR數位電驛故障 | OTHER | [5 empty] | 530 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | ACBA |  |  | Status | 所內電源故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0882 |  |  | 2-37-02 |  |  | ACB TIE | A/N | 所內電源警報 TIE ACBA |  |  | B3/P04_A1 | [8 empty] | 北港PS.所內電源ACBA | 所內電源故障警報 | OTHER | [5 empty] | 531 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0857 |  |  | 2-35-09 |  |  | 610 | RYFA | 北港口湖線 610 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.610_RYFA | 北港口湖線(610)數位電驛故障 | OTHER | [5 empty] | 519 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0872 |  |  | 2-36-08 |  |  | 640 | RYFA | 北港朴子線 640 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.640_RYFA | 北港朴子線(640)數位電驛故障 | OTHER | [5 empty] | 527 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0884 |  |  | 2-37-04 |  |  | 620 | RYFA | 北港水林二路 620 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.620_RYFA | 北港水林二路(620)數位電驛故障 | OTHER | [5 empty] | 533 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0887 |  |  | 2-37-07 |  |  | 630 | RYFA | 北港水林一路 630 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.630_RYFA | 北港水林一路(630)數位電驛故障 | OTHER | [5 empty] | 535 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0889 |  |  | 2-37-09 |  |  | 600 | RYFA | 69KV TIE 600數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.600_RYFA | 600 TIE 數位電驛故障 | OTHER | [5 empty] | 536 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0890 |  |  | 2-37-10 |  |  | BUS | A/N | 69KV BUS數位電驛故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | [5 empty] | 537 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0891 |  |  | 2-37-11 |  |  | BUS | A/N | 69KV BUS 87RY CT 迴路故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | [5 empty] | 538 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | BUS_RYFA |  |  | Status | BUS 數位電驛故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0892 |  |  | 2-37-12 |  |  | BUS | A/N | 161KV BUS數位電驛故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | [5 empty] | 539 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | ComPoint |  |  | 12B_CTFA | BUS_87CTFA | Element | Status | #1#2 BUS CT迴路故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0893 |  |  | 2-37-13 |  |  | BUS | A/N | 161KV BUS 87RY CT 迴路故障 |  |  | B3/P04_A1 | [8 empty] | 北港PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | [5 empty] | 540 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | ABS2 | 1522 | Element | Status | ABS2 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1002 | 1003 | 0221 | 2-3E-10 | 2-3E-11 | 2-5D | 1522 | ON | 北港四湖二路 1522 ABS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1522_ABS | 1522(北港四湖二路) ABS | LINE161 | [5 empty] | 174 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | ABS3 | 1523 |  | Status | ABS3 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1004 | 1005 | 0222 | 2-3E-12 | 2-3E-13 | 2-5E | 1523 | ON | 北港四湖二路 1523 DS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1523_ABS | 1523(北港四湖二路) ABS | LINE161 | [5 empty] | 175 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | ES3 | 1523E | Element | Status | ES(接地開關) | Open/Close/Transit/Error | Y | 5 | DI-DP | [6 empty] | 1006 | 1007 | 0223 | 2-3E-14 | 2-3E-15 | 2-5F | 1523E | ON | 北港四湖二路 1523 ES |  |  | B2/P04_A1 | [8 empty] | 北港PS.1523E_ES | 1523E(北港四湖二路) ES | LINE161 | [5 empty] | 176 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Open | 0 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0907 |  | 0235 | 2-38-11 |  | 2-6B | 1520 | 187S | 北港四湖二路 1520 87Ry U/L1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_87UL1 | 北港四湖二路(1520)#1 87RY U/L | OTHER | [5 empty] | 183 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0926 |  |  | 2-39-14 |  |  | 1960 | SRF | #2並聯電抗器 SRF 輕故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_SRF | 161KV #2SHR 輕故障 | OTHER | [5 empty] | 561 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SSR(1960) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0927 |  |  | 2-39-15 |  |  | 1960 | SRA | #2並聯電抗器 SRA 重故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#2SHR_SRA | 161KV #2SHR 重故障 | OTHER | [5 empty] | 562 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | DS1 | 1971 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1016 | 1017 | 0228 | 2-3F-08 | 2-3F-09 | 2-64 | 1971 | ON | #3並聯電抗器 1971 DS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1971_ABS | 1971(161KV #3SHR) DS | OTHER | [5 empty] | 181 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1970 | #3SSR(1970) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1970LE | 1970LE(非取樣點) | OTHER | [5 empty] | 252 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1970 | #3SSR(1970) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1970RE | 1970RE(非取樣點) | OTHER | [5 empty] | 253 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0277 |  |  | 2-02-05 |  |  | 1970 | 87RA | #3並聯電抗器 87RA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_87A | 161KV #3SHR 87RY | OTHER | [5 empty] | 430 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | MTR_86A |  | B3 | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0278 |  |  | 2-02-06 |  |  | 1970 | 86A | #3並聯電抗器 86A |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_86A | 161KV #3SHR 86RY | OTHER | [5 empty] | 431 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0279 |  |  | 2-02-07 |  |  | 1970 | 51A | #3並聯電抗器 51A(51、51N) |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_51A | 161KV #3SHR 51RY | OTHER | [5 empty] | 432 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 96PA | 3SSR | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0280 |  |  | 2-03-00 |  |  | 1970 | 96A | #3並聯電抗器 機械保護動作96PA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR96PA | 161KV #3SHR 機械保護動作 | OTHER | [5 empty] | 433 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0928 |  |  | 2-3A-00 |  |  | 1970 | 87R1S | #3並聯電抗器 1970 87Ry U/L1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_87UL1 | 161KV #3SHR #187RY U/L | OTHER | [5 empty] | 563 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0929 |  |  | 2-3A-01 |  |  | 1970 | 87R2S | #3並聯電抗器 1970 87Ry U/L2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_87UL2 | 161KV #3SHR #287RY U/L | OTHER | [5 empty] | 564 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0930 |  |  | 2-3A-02 |  |  | 1970 | RYFA | #3並聯電抗器 1970 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161_3SHR_RYFA | 161KV 3SHR(1970)數位電驛故障 | OTHER | [5 empty] | 565 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0931 |  |  | 2-3A-03 |  |  | 1970 | 96B1 | #3並聯電抗器96B1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_96B1 | 161KV #3SHR 96B1 RY | OTHER | [5 empty] | 566 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0932 |  |  | 2-3A-04 |  |  | 1970 | 96B2 | #3並聯電抗器96B2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_96B2 | 161KV #3SHR 96B2 RY | OTHER | [5 empty] | 567 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0933 |  |  | 2-3A-05 |  |  | 1970 | 96D | #3並聯電抗器96D |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_96D | 161KV #3SHR 96D RY | OTHER | [5 empty] | 568 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0934 |  |  | 2-3A-06 |  |  | 1970 | 96P | #3並聯電抗器96P |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_96P | 161KV #3SHR 96P RY | OTHER | [5 empty] | 569 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0935 |  |  | 2-3A-07 |  |  | 1970 | SRF | #3並聯電抗器 SRF 輕故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_SRF | 161KV #3SHR 輕故障 | OTHER | [5 empty] | 570 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0936 |  |  | 2-3A-08 |  |  | 1970 | SRA | #3並聯電抗器 SRA 重故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#3SHR_SRA | 161KV #3SHR 重故障 | OTHER | [5 empty] | 571 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | DS1 | 1981 | Element | Status | ABS1 | Open/Close/Transit/Error | Y | 7 | DI-DP | [6 empty] | 1018 | 1019 | 0229 | 2-3F-10 | 2-3F-11 | 2-65 | 1981 | ON | #4並聯電抗器 1981DS |  |  | B2/P04_A1 | [8 empty] | 北港PS.1981_ABS | 1981(161KV #4SHR) ABS | OTHER | [5 empty] | 182 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close/Transit/Error | Close | 1 |  |  | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1980 | #4SSR(1980) |  | TE0 | (非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1980LE | 1980LE(非取樣點) | OTHER | [5 empty] | 254 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1980 | #4SSR(1980) |  | RE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1980RE | 1980RE(非取樣點) | OTHER | [5 empty] | 255 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 87A |  | B3 | Status | 87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0282 |  |  | 2-03-02 |  |  | 1980 | 87RA | #4並聯電抗器 87RA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_87A | 161KV #4SHR 87RY | OTHER | [5 empty] | 434 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | MTR_86A |  | B3 | Status | 86(51Z/21/87/96)RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0283 |  |  | 2-03-03 |  |  | 1980 | 86A | #4並聯電抗器 86A |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_86A | 161KV #4SHR 86RY | OTHER | [5 empty] | 435 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 51A |  | B3 | Status | 51RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0284 |  |  | 2-03-04 |  |  | 1980 | 51A | #4並聯電抗器 51A(51、51N) |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_51A | 161KV #4SHR 51RY | OTHER | [5 empty] | 436 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 96PA | 4SSR | B3 | Status | 機械保護動作 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0285 |  |  | 2-03-05 |  |  | 1980 | 96A | #4並聯電抗器 機械保護動作96PA |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR96PA | 161KV #4SHR 機械保護動作 | OTHER | [5 empty] | 437 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 1_87UL1 |  |  | Status | 第1套第1具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0937 |  |  | 2-3A-09 |  |  | 1980 | 87R1S | #4並聯電抗器 1980 87Ry U/L1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_87UL1 | 161KV #4SHR #187RY U/L | OTHER | [5 empty] | 572 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0938 |  |  | 2-3A-10 |  |  | 1980 | 87R2S | #4並聯電抗器 1980 87Ry U/L2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_87UL2 | 161KV #4SHR #287RY U/L | OTHER | [5 empty] | 573 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0939 |  |  | 2-3A-11 |  |  | 1980 | RYFA | #4並聯電抗器 1980 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161_4SHR_RYFA | 161KV 4SHR(1980)數位電驛故障 | OTHER | [5 empty] | 574 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 96B1 |  | B3 | Status | 96B1 RY | Normal/Alarm | Y | 3 | DI-SP | [6 empty] | 0940 |  |  | 2-3A-12 |  |  | 1980 | 96B1 | #4並聯電抗器96B1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_96B1 | 161KV #4SHR 96B1 RY | OTHER | [5 empty] | 575 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 96B2 |  | B3 | Status | 96B2 RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0941 |  |  | 2-3A-13 |  |  | 1980 | 96B2 | #4並聯電抗器96B2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_96B2 | 161KV #4SHR 96B2 RY | OTHER | [5 empty] | 576 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 96D |  | B3 | Status | 96D RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0942 |  |  | 2-3A-14 |  |  | 1980 | 96D | #4並聯電抗器96D |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_96D | 161KV #4SHR 96D RY | OTHER | [5 empty] | 577 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | 96P |  | B3 | Status | 96P RY | Normal/Alarm | Y | 1 | DI-SP | [6 empty] | 0943 |  |  | 2-3A-15 |  |  | 1980 | 96P | #4並聯電抗器96P |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_96P | 161KV #4SHR 96P RY | OTHER | [5 empty] | 578 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Alarm | Alarm | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | SHRF |  | B3 | Status | 電抗器輕故障 | Normal/Fault | Y | 5 | DI-SP | [6 empty] | 0944 |  |  | 2-3B-00 |  |  | 1980 | SRF | #4並聯電抗器 SRF 輕故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_SRF | 161KV #4SHR 輕故障 | OTHER | [5 empty] | 579 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | SHRA |  | B3 | Status | 電抗器重故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0945 |  |  | 2-3B-01 |  |  | 1980 | SRA | #4並聯電抗器 SRA 重故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.161#4SHR_SRA | 161KV #4SHR 重故障 | OTHER | [5 empty] | 580 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | StaDev | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0946 |  |  | 2-3B-02 |  |  | PMA | A/N | 電力量測表計故障 |  |  | ELEM/P04_A1 | [8 empty] | 北港PS.PMA | 電力量測表計故障 | OTHER | [5 empty] | 581 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 1_87UL2 |  |  | Status | 第1套第2具87RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0908 |  | 0236 | 2-38-12 |  | 2-6C | 1520 | 287S | 北港四湖二路 1520 87Ry U/L2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_87UL2 | 北港四湖二路(1520)#2 87RY U/L | OTHER | [5 empty] | 184 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 79UL |  |  | Status | 79RY U/L | Use/Lock | Y | 3 | DI-SP | [6 empty] | 0909 |  | 0237 | 2-38-13 |  | 2-6D | 1520 | 79S | 北港四湖二路 1520 79Ry U/L |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_79UL | 北港四湖二路(1520) 79RY U/L | LINE161 | [5 empty] | 185 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Use/Lock | Use | 0 |  |  | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1520LE | 1520LE (非取樣點) | LINE161 | [5 empty] | 246 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | BE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1520BE | 1520BE (非取樣點) | LINE161 | [5 empty] | 247 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | MW |  |  | MvMoment | MW |  | Y |  | AI | [6 empty] | 0086 |  |  | 1-C5 |  |  | 1520 | MW | 北港四湖二路 1520 乏 | MW_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1520_MW | 北港四湖二路 MW | LINE161 | [5 empty] | 321 |  |  |  |  | AI | [5 empty] | LG_MW | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI | [6 empty] | 0087 |  |  | 1-C6 |  |  | 1520 | MVAR | 北港四湖二路 1520 乏 | MVAR_-560_560(-2000_2000) |  | B2/P04_A1 | [8 empty] | 北港PS.1520_MVAR | 北港四湖二路 MVAR | LINE161 | [5 empty] | 322 |  |  |  |  | AI | [5 empty] | LG_MVAR | 20000 | 20001 | 20002 | 20003 | 1 | -20000 | -20001 | -20002 | -20003 | 1.12 | 0.01 | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 87A1 |  |  | Status | 第1具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0262 |  |  | 2-00-06 |  |  | 1520 | 87A1 | 北港四湖二路 1520 87A1 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_87A1 | 北港四湖二路(1520) #1 87RY | OTHER | [5 empty] | 418 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 87A2 |  |  | Status | 第2具87RY | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0263 |  |  | 2-00-07 |  |  | 1520 | 87A2 | 北港四湖二路 1520 87A2 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_87A2 | 北港四湖二路(1520) #2 87RY | OTHER | [5 empty] | 419 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | GDA |  |  | Status | GDA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0264 |  |  | 2-01-00 |  |  | 1520 | GDA | 北港四湖二路 1520 GDA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_GDA | 北港四湖二路(1520) 接地RY | LINE161 | [5 empty] | 420 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | PHA |  |  | Status | PHA | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0265 |  |  | 2-01-01 |  |  | 1520 | PHA | 北港四湖二路 1520 PHA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_PHA | 北港四湖二路(1520) 相間RY | LINE161 | [5 empty] | 421 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | 87CFA |  |  | Status | 87CFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0903 |  |  | 2-38-07 |  |  | 1520 | 87CFA | 北港四湖二路 1520 87Ry 通訊故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_87CFA | 北港四湖二路(1520)87RY通訊故障 | OTHER | [5 empty] | 541 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | RYFA |  | B3 | Status | RYFA | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0904 |  |  | 2-38-08 |  |  | 1520 | RYFA | 北港四湖二路 1520 數位電驛故障 |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_RYFA | 北港四湖二路(1520)數位電驛故障 | OTHER | [5 empty] | 542 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | DTTA |  |  | Status | 遠方遙跳 | Normal/Trip | Y | 1 | DI-SP | [6 empty] | 0905 |  |  | 2-38-09 |  |  | 1520 | DTTA | 北港四湖二路 1520 遠方遙跳 DTTA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_DTTA | 北港四湖二路(1520) 遠方遙跳 | OTHER | [5 empty] | 543 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Trip | Trip | 1 |  |  | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | LPDA |  |  | Status | LPD電壓偵測 | Normal/Fault | Y | 3 | DI-SP | [6 empty] | 0906 |  |  | 2-38-10 |  |  | 1520 | LPTA | 北港四湖二路 1520 LPTA |  |  | B2/P04_A1 | [8 empty] | 北港PS.1520_LPDA | 北港四湖二路(1520) LPD電壓偵測 | OTHER | [5 empty] | 544 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Normal/Fault | Fault | 1 |  |  | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | CB |  | ADD | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay2BbN | B/1Bus | B/2Bus | L/P04D221/T1 |  | 0261 |  | 0201 | 2-00-05 |  | 2-49 | 1520 | ON/OFF | 北港四湖二路1520 CB |  | aaca | B2/P04_A1 | [8 empty] | 北港PS.1520_CB | 1520(北港四湖二路) CB | LINE161 | [5 empty] | 168 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1560LE | 1560LE (非取樣點) | LINE161 | [5 empty] | 218 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1570LE | 1570LE (非取樣點) | LINE161 | [5 empty] | 189 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1630LE | 1630LE (非取樣點) | LINE161 | [5 empty] | 191 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1640LE | 1640LE (非取樣點) | LINE161 | [5 empty] | 193 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1660NE | #2MTR(1660) |  | NE0 | 1661N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/2MTR | [13 empty] | no rule | B2/P04_A1 | [8 empty] | 北港PS.1661N | 1661N (非取樣點) | MTR | [5 empty] | 196 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1670NE | #3MTR(1670) |  | NE0 | 1671N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/3MTR | [13 empty] | no rule | B2/P04_A1 | [8 empty] | 北港PS.1671N | 1671N (非取樣點) | MTR | [5 empty] | 201 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Close | 1 | Y |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1680NE | #4MTR(1680) |  | NE0 | 1681N(非取樣點) | Element | Status | ES | Open/Close | Y | 7 | DI-SP |  | StarEth | T/4MTR | [13 empty] | no rule | B2/P04_A1 | [8 empty] | 北港PS.1681N | 1681N (非取樣點) | MTR | [5 empty] | 206 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.710LE | 710LE (非取樣點) | LINE69 | [5 empty] | 232 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.720LE | 720LE (非取樣點) | LINE69 | [5 empty] | 234 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.910LE | 910LE (非取樣點) | LINE69 | [5 empty] | 236 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.920LE | 920LE (非取樣點) | LINE69 | [5 empty] | 238 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.940LE | 940LE (非取樣點) | LINE69 | [5 empty] | 240 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.620LE | 620LE (非取樣點) | LINE69 | [5 empty] | 222 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.630LE | 630LE (非取樣點) | LINE69 | [5 empty] | 224 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.640LE | 640LE (非取樣點) | LINE69 | [5 empty] | 226 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.670LE | 670LE (非取樣點) | LINE69 | [5 empty] | 228 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.680LE | 680LE (非取樣點) | LINE69 | [5 empty] | 230 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.610LE | 610LE (非取樣點) | LINE69 | [5 empty] | 220 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | LE0 | (非取樣點) |  | Status | ES | Open/Close | Y | 7 | DI-SP | [17 empty] | B2/P04_A1 | [8 empty] | 北港PS.1580LE | 1580LE (非取樣點) | LINE161 | [5 empty] | 214 | [11 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Open/Close | Open | 0 | Y |  | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | L/P04D221/T1 | R/3SHR |  |  | 0276 |  | 0204 | 2-02-04 |  | 2-4C | 1970 | ON/OFF | #3並聯電抗器 1970 CB |  | aada | B2/P04_A1 | [8 empty] | 北港PS.1970_CB | 1970(161KV #3SHR) CB | OTHER | [5 empty] | 171 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | CB |  | B3 | Status | CB | Close/Open | Y | 1 | DI-SP |  | Bay1TrB | L/P04D222/T1 | R/4SHR |  |  | 0281 |  | 0205 | 2-03-01 |  | 2-4D | 1980 | ON/OFF | #4並聯電抗器 1980 CB |  | aaca | B2/P04_A1 | [8 empty] | 北港PS.1980_CB | 1980(161KV #4SHR) CB | OTHER | [5 empty] | 172 |  |  |  |  | DI | [6 empty] | 0 | 1 | 2 | 3 |  | 0 | -1 | -2 | -3 | [14 empty] | Close/Open | Close | 0 |  |  | CLOSE/OPEN | CLOSE

## 計算點
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | AoR | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | PointName | PointDesc | GraphicDesc | CalculateName | MvLimName | FormulaName | OPRD1 | OPRD2 | OPRD3 | OPRD4 | OPRD5 | OPRD6 | OPRD7 | OPRD8 | OPRD9 | OPRD10 | OPRD11 | OPRD12 | OPRD13 | OPRD14 | OPRD15 | OPRD16 | OPRD17 | OPRD18 | OPRD19 | OPRD20 | OPRD21 | OPRD22 | OPRD23 | OPRD24 | OPRD25 | OPRD26 | OPRD27 | OPRD28 | OPRD29 | OPRD30 | OPRD31 | OPRD32 | OPRD33 | OPRD34 | OPRD35 | OPRD36 | OPRD37 | OPRD38 | OPRD39 | OPRD40 | OPRD41 | OPRD42 | OPRD43 | OPRD44 | OPRD45 | OPRD46 | OPRD47 | OPRD48 | OPRD49 | OPRD50
P04 | 北港PS | 0 |  | CalcPoint |  |  | Vbs4 | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | BEST_SOURCE_161KV_2 | LG_161 | v_best_161_12 | OPRD1: P04/161/1BUS/V; OPRD2: P04/161/2BUS/V
P04 | 北港PS | 0 |  | CalcPoint |  |  | Vbs2 | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | BEST_SOURCE_69KV_2 | LG_69 | v_best_69_12 | OPRD1: P04/69/1BUS/V; OPRD2: P04/69/2BUS/V
P04 | 北港PS | 0 |  | CalcPoint |  |  | OPRN1 | [9 empty] | B1/P04_A1 | [15 empty] | BEST_SOURCE_1 |  | pwr_cnd1 | OPRD1: NULL; OPRD2: P04/0/CalcPoint/Vbs2; OPRD3: NULL; OPRD4: P04/0/CalcPoint/Vbs4; OPRD5: NULL; OPRD6: NULL; OPRD7: NULL; OPRD8: NULL; OPRD9: NULL
P04 | 北港PS | 0 |  | CalcPoint |  |  | OPRN2_MW | [9 empty] | B1/P04_A1 | [15 empty] | TOT_1MTR_CAL |  | p_sum_21 | OPRD1: P04/161/1510/MW; OPRD2: P04/161/1520/MW; OPRD3: P04/161/1560/MW; OPRD4: P04/161/1570/MW; OPRD5: P04/161/1580/MW; OPRD6: P04/161/1630/MW; OPRD7: P04/161/1640/MW; OPRD8: P04/69/610/MW; OPRD9: P04/69/620/MW; OPRD10: P04/69/630/MW; OPRD11: P04/69/640/MW; OPRD12: P04/69/670/MW; OPRD13: P04/69/680/MW; OPRD14: P04/69/710/MW; OPRD15: P04/69/720/MW; OPRD16: P04/69/760/MW; OPRD17: P04/69/770/MW; OPRD18: P04/69/780/MW; OPRD19: P04/69/910/MW; OPRD20: P04/69/920/MW; OPRD21: P04/69/940/MW
P04 | 北港PS | 0 |  | CalcPoint |  |  | OPRN2 | [9 empty] | B1/P04_A1 | [15 empty] | PWRFAIL_CND2_1 |  | pwr_cnd2 | OPRD1: P04/0/CalcPoint/OPRN2_MW
P04 | 北港PS | 0 |  | CalcPoint |  |  | PRFL_UL | [9 empty] | B1/P04_A1 | [17 empty] | none
P04 | 北港PS | 0 |  | CalcPoint |  |  | PWR_FAIL | [9 empty] | B1/P04_A1 | [15 empty] | PWR_FAIL_CAL |  | pwr_fail | OPRD1: P04/0/CalcPoint/OPRN1; OPRD2: P04/0/CalcPoint/OPRN2; OPRD3: P04/0/CalcPoint/PRFL_UL
P04 | 北港PS |  |  | 2MTR | 2MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P04_A1 | [12 empty] | 北港PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P04/69/760/MW; OPRD2: P04/69/760/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS |  |  | 3MTR | 3MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P04_A1 | [12 empty] | 北港PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P04/69/770/MW; OPRD2: P04/69/770/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS |  |  | 4MTR | 4MTR |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B1/P04_A1 | [12 empty] | 北港PS.#4MTR_AMP | #4MTR 二次側 AMP | MTR | AMP_CAL | LG_1673 | amp_cal | OPRD1: P04/69/780/MW; OPRD2: P04/69/780/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 161 | 161kV | 1510 | 北港～四湖一路(1510) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1510_AMP | 北港四湖一路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P04/161/1510/MW; OPRD2: P04/161/1510/MVAR; OPRD3: NULL
P04 | 北港PS | 161 | 161kV | 1520 | 北港～四湖二路(1520) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1520_AMP | 北港四湖二路 AMP | LINE161 | AMP_CAL | C20R1790 | amp_cal | OPRD1: P04/161/1520/MW; OPRD2: P04/161/1520/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 161 | 161kV | 1560 | 北港台西二路(1560) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1560_AMP | 台西二路 AMP | LINE161 | AMP_CAL | C16R1200 | amp_cal | OPRD1: P04/161/1560/MW; OPRD2: P04/161/1560/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 161 | 161kV | 1570 | 雲林~北港~雲高線(1570) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1570_AMP | 雲林北港雲高線 AMP | LINE161 | AMP_CAL | C12R1000 | amp_cal | OPRD1: P04/161/1570/MW; OPRD2: P04/161/1570/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 161 | 161kV | 1580 | 北港～台西線(1580) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1580_AMP | 北港台西線 AMP | LINE161 | AMP_CAL | C12R0600 | amp_cal | OPRD1: P04/161/1580/MW; OPRD2: P04/161/1580/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民～北港南線(1630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1630_AMP | 嘉民南線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: P04/161/1630/MW; OPRD2: P04/161/1630/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民～北港北線(1640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.1640_AMP | 嘉民北線 AMP | LINE161 | AMP_CAL | C20R1792 | amp_cal | OPRD1: P04/161/1640/MW; OPRD2: P04/161/1640/MVAR; OPRD3: P04/0/CalcPoint/Vbs4
P04 | 北港PS | 69 | 69kV | 610 | 北港～口湖線(610) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.610_AMP | 北港口湖線 AMP | LINE69 | AMP_CAL | C12R0879 | amp_cal | OPRD1: P04/69/610/MW; OPRD2: P04/69/610/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 620 | 北港～水林二路(620) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.620_AMP | 北港水林二路 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: P04/69/620/MW; OPRD2: P04/69/620/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 630 | 北港～水林一路(630) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.630_AMP | 北港水林一路 AMP | LINE69 | AMP_CAL | C20R1001 | amp_cal | OPRD1: P04/69/630/MW; OPRD2: P04/69/630/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 640 | 北港～朴子線(640) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.640_AMP | 北港朴子線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: P04/69/640/MW; OPRD2: P04/69/640/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 670 | 北港～新港一路(670) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.670_AMP | 北港新港一路 AMP | LINE69 | AMP_CAL | C12R1000 | amp_cal | OPRD1: P04/69/670/MW; OPRD2: P04/69/670/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 680 | 北港～新港二路(680) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.680_AMP | 北港新港二路 AMP | LINE69 | AMP_CAL | C12R1000 | amp_cal | OPRD1: P04/69/680/MW; OPRD2: P04/69/680/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 710 | 北港～雲港一路(710) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.710_AMP | 雲港一路 AMP | LINE69 | AMP_CAL | C12R0945 | amp_cal | OPRD1: P04/69/710/MW; OPRD2: P04/69/710/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 720 | 北港～雲港二路(720) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.720_AMP | 雲港二路 AMP | LINE69 | AMP_CAL | C12R0945 | amp_cal | OPRD1: P04/69/720/MW; OPRD2: P04/69/720/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 910 | 北港～土庫線(910) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.910_AMP | 北港土庫線 AMP | LINE69 | AMP_CAL | C12R0896 | amp_cal | OPRD1: P04/69/910/MW; OPRD2: P04/69/910/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 920 | 北港～元長線(920) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.920_AMP | 元長線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: P04/69/920/MW; OPRD2: P04/69/920/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS | 69 | 69kV | 940 | 北港～東北線(940) |  | I |  |  | MvMoment | AMP |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.940_AMP | 北港東北線 AMP | LINE69 | AMP_CAL | C12R1001 | amp_cal | OPRD1: P04/69/940/MW; OPRD2: P04/69/940/MVAR; OPRD3: P04/0/CalcPoint/Vbs2
P04 | 北港PS |  |  | 2MTR | #2MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P04_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 北港PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P04/69/760/MW; OPRD2: P04/69/760/MVAR
P04 | 北港PS |  |  | 3MTR | #3MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P04_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 北港PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P04/69/770/MW; OPRD2: P04/69/770/MVAR
P04 | 北港PS |  |  | 4MTR | #4MTR |  | MVA |  |  | MvMoment | 二次測MVA |  | Y |  | AI |  | B1/P04_A1 | LG_200 | 190 | 220 | 250 | 396 | 1 | -190 | -220 | -250 | -396 |  |  | 北港PS.#4MTR_MVA | #4MTR二次側 MVA | MTR | MVA_CAL | LG_200 | va_million | OPRD1: P04/69/780/MW; OPRD2: P04/69/780/MVAR
P04 | 北港PS |  |  | 2MTR | #2MTR |  | LOAD | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#2MTR_LOAD | #2MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P04//2MTR/MVA; OPRD2: 0
P04 | 北港PS |  |  | 3MTR | #3MTR |  | LOAD | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#3MTR_LOAD | #3MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P04//3MTR/MVA; OPRD2: 0
P04 | 北港PS |  |  | 4MTR | #4MTR |  | LOAD | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#4MTR_LOAD | #4MTR 負載率 | MTR | TR_LOAD_200 | LG_LOAD | tr_loading | OPRD1: P04//4MTR/MVA; OPRD2: 0
P04 | 北港PS |  |  | 2MTR | #2MTR |  | PF | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#2MTR_PF | #2MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P04/69/760/MW; OPRD2: P04/69/760/MVAR
P04 | 北港PS |  |  | 3MTR | #3MTR |  | PF | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#3MTR_PF | #3MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P04/69/770/MW; OPRD2: P04/69/770/MVAR
P04 | 北港PS |  |  | 4MTR | #4MTR |  | PF | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#4MTR_PF | #4MTR 功率因素 | MTR | RPDC_PF_CAL | LG_PF | pf_cal | OPRD1: P04/69/780/MW; OPRD2: P04/69/780/MVAR
P04 | 北港PS |  |  | 2MTR | 2MTR |  | TR_PERM | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P04//2MTR/SupLocal; OPRD2: P04//2MTR/Tap Chan; OPRD3: P04//2MTR/M_F_I
P04 | 北港PS |  |  | 3MTR | 3MTR |  | TR_PERM | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P04//3MTR/SupLocal; OPRD2: P04//3MTR/Tap Chan; OPRD3: P04//3MTR/M_F_I
P04 | 北港PS |  |  | 4MTR | 4MTR |  | TR_PERM | [9 empty] | B1/P04_A1 | [12 empty] | 北港PS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | MTR | MTR_PERM |  | mtr_perm | OPRD1: P04//4MTR/SupLocal; OPRD2: P04//4MTR/Tap Chan; OPRD3: P04//4MTR/M_F_I
P04 | 北港PS | 0 |  | CalcPoint |  |  | MTR_MW | [9 empty] | B1/P04_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: P04/69/760/MW; OPRD2: P04/69/770/MW; OPRD3: P04/69/780/MW
P04 | 北港PS | 0 |  | CalcPoint |  |  | MTR_MVAR | [9 empty] | B1/P04_A1 | [15 empty] | TOT_1MTR_CAL |  | tot_tr_3 | OPRD1: P04/69/760/MVAR; OPRD2: P04/69/770/MVAR; OPRD3: P04/69/780/MVAR
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.820_SC_MVAR | 69KV#2SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P04/69/820/CB; OPRD2: 69; OPRD3: 0
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | MVAR |  |  | MvMoment | MVAR |  | Y |  | AI |  | B2/P04_A1 | [12 empty] | 北港PS.830_SC_MVAR | 69KV#3SC MVAR | SC | SC_CAL_69 | LG_MVAR | sc_mvar | OPRD1: P04/69/830/CB; OPRD2: 69; OPRD3: 0
P04 | 北港PS | 0 |  | CalcPoint |  |  | SUBA |  |  | Status | 變電所重故障 | Normal/Alarm | Y | 3 | DI-SP |  | B1/P04_A1 | [12 empty] | 北港PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | STATION_FAULT_16 |  | com_alarm_34 | P04//2MTR/51ZA | P04//2MTR/96PA | P04//2MTR/TRA | P04//2MTR/63Q | P04//2MTR/96B2 | P04//2MTR/96D | P04//2MTR/96B1 | P04//2MTR/87A | P04//2MTR/GDA | P04//2MTR/PHA | P04//3MTR/96B2 | P04//3MTR/63Q | P04//3MTR/96D | P04//3MTR/96B1 | P04//3MTR/PHA | P04//3MTR/GDA | P04//3MTR/TRA | P04//3MTR/87A | P04//3MTR/96PA | P04//3MTR/51ZA | P04//4MTR/96D | P04//4MTR/63Q | P04//4MTR/96B2 | P04//4MTR/96B1 | P04//4MTR/GDA | P04//4MTR/96PA | P04//4MTR/PHA | P04//4MTR/TRA | P04//4MTR/87A | P04//4MTR/51ZA | P04/161/1BUS/87A | P04/161/2BUS/87A | P04/69/1BUS/87A | P04/69/2BUS/87A
P04 | 北港PS | 0 |  | CalcPoint |  |  | SUBF |  |  | Status | 變電所輕故障 | Normal/Alarm | Y | 5 | DI-SP |  | B1/P04_A1 | [12 empty] | 北港PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | STATION_FAULT_3 |  | com_alarm_3 | OPRD1: P04//2MTR/TRF; OPRD2: P04//3MTR/TRF; OPRD3: P04//4MTR/TRF
P04 | 北港PS | 0 |  | RTU_D1 | RTU |  | RTU_R_L |  |  | Status | Remote/Local | Rem/Loc | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/0/RTU/RTU_R_L
P04 | 北港PS | 0 |  | StaDev_D1 | 所內設施 |  | DCE |  |  | Status | 直流電源接地故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/0/StaDev/DCE
P04 | 北港PS | 0 |  | StaDev_D1 | 所內設施 |  | DCA |  |  | Status | 直流電源故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/0/StaDev/DCA
P04 | 北港PS | 69 | 69kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/69/ComPoint/ABS_89A
P04 | 北港PS | 0 |  | StaDev_D1 | 所內設施 |  | STUV |  |  | Status | 所內電源欠壓 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/0/StaDev/STUV
P04 | 北港PS | 161 | 161kV | ComPoint_D1 |  |  | ABS_89A |  |  | Status | ABS NFB跳脫 | Normal/Alarm | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/161/ComPoint/ABS_89A
P04 | 北港PS | 0 |  | StaDev_D1 | 所內設施 |  | PMA |  |  | Status | 電力量測表計故障 | Normal/Fault | Y | 3 | DI-SP |  | ELEM/P04_D1 | [17 empty] | lamp2CC | OPRD1: P04/0/StaDev/PMA

## 比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | CalculateName | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo | Element Name | Element Text | Info Name | Info Text | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | MvLimName | MvLim01U | MvLim02U | MvLim03U | MvLim04U | AlarmDeadband | MvLim01L | MvLim02L | MvLim03L | MvLim04L | Deadband | ZeroDeadband | StatusDesc | NormStatDesc | NormStat | Mon1 Inv | Mon2 Inv | StatusDesc1 | NormStatDesc1 | StatusDesc2 | NormStatDesc2
P04 | 北港PS | 161 | 161kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 北港PS.161KV_BUS_KV | 161KV BUS BEST SOURCE | BUS | P04/0/CalcPoint/Vbs4 |  | BEST_SOURCE_161KV_2 |  |  | 2 | CalcAIPoint | [21 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000
P04 | 北港PS | 69 | 69kV | _BUS | BUS |  | V | [25 empty] | ADCS_N | [8 empty] | 北港PS.69KV_BUS_KV | 69KV BUS BEST SOURCE | BUS | P04/0/CalcPoint/Vbs2 |  | BEST_SOURCE_69KV_2 |  |  | 3 | CalcAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1510_AMP | 北港四湖一路 AMP | LINE161 | P04/161/1510/I |  | AMP_CAL |  |  | 4 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1520_AMP | 北港四湖二路 AMP | LINE161 | P04/161/1520/I |  | AMP_CAL |  |  | 5 | CalcAIPoint | [21 empty] | C20R1790 | 1612.800049 | 1612.800049 | 1790.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1560_AMP | 台西二路 AMP | LINE161 | P04/161/1560/I |  | AMP_CAL |  |  | 6 | CalcAIPoint | [21 empty] | C16R1200 | 1080.000000 | 1080.000000 | 1200.000000 | 1600.000000 | 2.780000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1570_AMP | 雲林北港雲高線 AMP | LINE161 | P04/161/1570/I |  | AMP_CAL |  |  | 7 | CalcAIPoint | [21 empty] | C12R1000 | 900.000000 | 900.000000 | 1000.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1580_AMP | 北港台西線 AMP | LINE161 | P04/161/1580/I |  | AMP_CAL |  |  | 8 | CalcAIPoint | [21 empty] | C12R0600 | 500.000000 | 550.000000 | 600.000000 | 720.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1630_AMP | 嘉民南線 AMP | LINE161 | P04/161/1630/I |  | AMP_CAL |  |  | 9 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.1640_AMP | 嘉民北線 AMP | LINE161 | P04/161/1640/I |  | AMP_CAL |  |  | 10 | CalcAIPoint | [21 empty] | C20R1792 | 1612.800049 | 1612.800049 | 1792.000000 | 2000.000000 | 2.270000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.610_AMP | 北港口湖線 AMP | LINE69 | P04/69/610/I |  | AMP_CAL |  |  | 11 | CalcAIPoint | [21 empty] | C12R0879 | 791.099976 | 791.099976 | 879.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.630_AMP | 北港水林一路 AMP | LINE69 | P04/69/630/I |  | AMP_CAL |  |  | 12 | CalcAIPoint | [21 empty] | C20R1001 | 900.000000 | 900.000000 | 1001.000000 | 2000.000000 | 0.450000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.640_AMP | 北港朴子線 AMP | LINE69 | P04/69/640/I |  | AMP_CAL |  |  | 13 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.670_AMP | 北港新港一路 AMP | LINE69 | P04/69/670/I |  | AMP_CAL |  |  | 14 | CalcAIPoint | [21 empty] | C12R1000 | 900.000000 | 900.000000 | 1000.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.680_AMP | 北港新港二路 AMP | LINE69 | P04/69/680/I |  | AMP_CAL |  |  | 15 | CalcAIPoint | [21 empty] | C12R1000 | 900.000000 | 900.000000 | 1000.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.710_AMP | 雲港一路 AMP | LINE69 | P04/69/710/I |  | AMP_CAL |  |  | 16 | CalcAIPoint | [21 empty] | C12R0945 | 850.500000 | 850.500000 | 945.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.720_AMP | 雲港二路 AMP | LINE69 | P04/69/720/I |  | AMP_CAL |  |  | 17 | CalcAIPoint | [21 empty] | C12R0945 | 850.500000 | 850.500000 | 945.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.910_AMP | 北港土庫線 AMP | LINE69 | P04/69/910/I |  | AMP_CAL |  |  | 18 | CalcAIPoint | [21 empty] | C12R0896 | 806.400024 | 806.400024 | 896.000000 | 1200.000000 | 0.710000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.920_AMP | 元長線 AMP | LINE69 | P04/69/920/I |  | AMP_CAL |  |  | 19 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.940_AMP | 北港東北線 AMP | LINE69 | P04/69/940/I |  | AMP_CAL |  |  | 20 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 0 |  | 2MTR | #2MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_MVA | #2MTR二次側 MVA | MTR | P04//2MTR/MVA |  | MVA_CAL |  |  | 21 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_LOAD | #2MTR 負載率 | MTR | P04//2MTR/Loading |  | TR_LOAD_200 |  |  | 22 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_PF | #2MTR 功率因素 | MTR | P04//2MTR/PF |  | RPDC_PF_CAL |  |  | 23 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_AMP | #2MTR 二次側 AMP | MTR | P04//2MTR/I |  | AMP_CAL |  |  | 24 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P04 | 北港PS | 0 |  | 3MTR | #3MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_MVA | #3MTR二次側 MVA | MTR | P04//3MTR/MVA |  | MVA_CAL |  |  | 25 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_LOAD | #3MTR 負載率 | MTR | P04//3MTR/Loading |  | TR_LOAD_200 |  |  | 26 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_PF | #3MTR 功率因素 | MTR | P04//3MTR/PF |  | RPDC_PF_CAL |  |  | 27 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_AMP | #3MTR 二次側 AMP | MTR | P04//3MTR/I |  | AMP_CAL |  |  | 28 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P04 | 北港PS | 0 |  | 4MTR | #4MTR二次側 |  | MVA | [25 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_MVA | #4MTR二次側 MVA | MTR | P04//4MTR/MVA |  | MVA_CAL |  |  | 29 | CalcAIPoint | [21 empty] | LG_200 | 180.000000 | 200.000000 | 250.000000 | 260.000000 | 1.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | LOAD | [25 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_LOAD | #4MTR 負載率 | MTR | P04//4MTR/Loading |  | TR_LOAD_200 |  |  | 30 | CalcAIPoint | [21 empty] | LG_LOAD | 100.000000 | 110.000000 | 125.000000 | 130.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | PF | [25 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_PF | #4MTR 功率因素 | MTR | P04//4MTR/PF |  | RPDC_PF_CAL |  |  | 31 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_AMP | #4MTR 二次側 AMP | MTR | P04//4MTR/I |  | AMP_CAL |  |  | 32 | CalcAIPoint | [21 empty] | LG_1673 | 1505.699951 | 1673.400024 | 2091.250000 | 2174.899902 | 0.100000 | -20.000000 | -20.000000 | -20.000000 | -25.100000
P04 | 北港PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MW) |  | MW | [25 empty] | ADCS_N | [8 empty] | 北港PS.RPDC_MTR_MW | SUM(161/69KV MTR MW) | MTR |  |  | RPDC_3MTR_MW_CAL |  |  | 33 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 69 | 69kV | RPDC_MTR | SUM(161/69KV MTR MVAR) |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.RPDC_MTR_MVAR | SUM(161/69KV MTR MVAR) | MTR |  |  | RPDC_3MTR_MVAR_CAL |  |  | 34 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 0 |  | RPDC_MTR | RPDC |  | PF | [25 empty] | ADCS_N | [8 empty] | 北港PS.RPDC_MTR_PF | RPDC MTR 功率因素 | MTR |  |  | RPDC_PF_CAL |  |  | 35 | CalcAIPoint | [21 empty] | LG_PF | 1.000000 | 1.000000 | 1.000000 | 1.000000 | 0.000000 | -1.000000 | -1.000000 | -1.000000 | -1.000000
P04 | 北港PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.820_SC_MVAR | 69KV#2SC MVAR | SC | P04/69/820/MVAR |  | SC_CAL_69 |  |  | 36 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 69 | 69kV | 830_SC | #3SC | 28.799999 | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.830_SC_MVAR | 69KV#3SC MVAR | SC | P04/69/830/MVAR |  | SC_CAL_69 |  |  | 37 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 0 |  | TRTOT | 北港主變瞬時供電量 |  | MW | [25 empty] | CDCS | [8 empty] | 北港PS.TRTOT_MW | 北港主變瞬時供電量 MW |  |  |  | TOTAL_PQ_CAL_3 |  |  | 38 | CalcAIPoint | [21 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 0 |  | TRTOT | 北港主變瞬時供電量 |  | MVAR | [25 empty] | CDCS | [8 empty] | 北港PS.TRTOT_MVAR | 北港主變瞬時供電量 MVAR |  |  |  | TOTAL_PQ_CAL_3 |  |  | 39 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | I | [25 empty] | ADCS_N | [8 empty] | 北港PS.620_AMP | 北港水林二路 AMP | LINE69 | P04/69/620/I |  | AMP_CAL |  |  | 40 | CalcAIPoint | [21 empty] | C12R1001 | 900.900024 | 900.900024 | 1001.000000 | 1200.000000 | 3.570000 | -200.000000 | -200.000000 | -200.000000 | -200.000000
P04 | 北港PS | 161 | 161kV | 1950_SHR | #1SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.1950_SHR_MVAR | 161KV#1SHR MVAR | SC |  |  | SHR_CAL_648_5 |  |  | 41 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 161 | 161kV | 1960_SHR | #2SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.1960_SHR_MVAR | 161KV#2SHR MVAR | SC |  |  | SHR_CAL_324_5 |  |  | 42 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 161 | 161kV | 1970_SHR | #3SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.1970_SHR_MVAR | 161KV#3SHR MVAR | SC |  |  | SHR_CAL_648_5 |  |  | 43 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 161 | 161kV | 1980_SHR | #4SHR |  | MVAR | [25 empty] | ADCS_N | [8 empty] | 北港PS.1980_SHR_MVAR | 161KV#4SHR MVAR | SC |  |  | SHR_CAL_648_5 |  |  | 44 | CalcAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 69 | 69kV | 610_CB | 北港口湖線(610_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.610_CB_1 | 610(北港口湖線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 45 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 630_CB | 北港水林一路(630_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.630_CB_1 | 630(北港水林一路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 46 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 640_CB | 北港朴子線(640_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.640_CB_1 | 640(北港朴子線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 47 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 670_CB | 北港新港一路(670_CB) | [27 empty] | DDCS2_2 | [8 empty] | 北港PS.670_CB_2 | 670(北港新港一路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 48 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 680_CB | 北港新港二路(680_CB) | [27 empty] | DDCS2_2 | [8 empty] | 北港PS.680_CB_2 | 680(北港新港二路) CB (D2) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 49 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 710_CB | 雲港一路(710_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.710_CB_1 | 710(雲港一路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 50 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 720_CB | 雲港二路(720_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.720_CB_1 | 720(雲港二路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 51 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 910_CB | 北港土庫線(910_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.910_CB_1 | 910(北港土庫線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 52 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 920_CB | 元長線(920_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.920_CB_1 | 920(元長線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 53 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 940_CB | 北港東北線(940_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.940_CB_1 | 940(北港東北線) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 54 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | MTR | MTR |  | A_M | [25 empty] | RPDC_AD | [8 empty] | 北港PS.MTR_A/M | MTR OLTC A/M | MTR |  |  | LCP_3PTR |  |  | 55 | CalcDIPoint | [38 empty] | AUTO/MANUAL | AUTO
P04 | 北港PS | 0 |  | OSC啟動 | 示波器啟動警報點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.OSC啟動_1 | 示波器啟動警報點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 56 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | RTU_S_L | RTU |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.RTU_S/L_1 | RTU SUPY/LOCAL (D1) | OTHER |  |  | AD_LAMP_DD_4 |  |  | 57 | CalcDIPoint | [38 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P04 | 北港PS | 0 |  | 變電所重故障點燈 | 變電所重故障點燈 |  | SUBA | [25 empty] | ADCS_N | [8 empty] | 北港PS.變電所重故障 | 變電所重故障點燈 (AD) | OTHER | P04/0/CalcPoint/SUBA |  | STATION_FAULT_16 |  |  | 58 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 變電所輕故障點燈 | 變電所輕故障點燈 |  | SUBF | [25 empty] | ADCS_N | [8 empty] | 北港PS.變電所輕故障 | 變電所輕故障點燈 (AD) | OTHER | P04/0/CalcPoint/SUBF |  | STATION_FAULT_3 |  |  | 59 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 變電所重故障 | 變電所重故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.變電所重故障_1 | 變電所重故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 60 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.變電所輕故障_1 | 變電所輕故障點燈 (D1) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 61 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 變電所重故障 | 變電所重故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 北港PS.變電所重故障_2 | 變電所重故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 62 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 變電所輕故障 | 變電所輕故障點燈 | [27 empty] | DDCS2_1 | [8 empty] | 北港PS.變電所輕故障_2 | 變電所輕故障點燈 (D2) | OTHER |  |  | AD_LAMP_DD_2 |  |  | 63 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560_AMP | 台西二路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1560_AMP_A | 台西二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 64 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 161 | 161kV | 1570_AMP | 雲林北港雲高線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1570_AMP_A | 雲林北港雲高線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 65 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 161 | 161kV | 1580_AMP | 北港台西線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1580_AMP_A | 北港台西線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 66 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 161 | 161kV | 1630_AMP | 嘉民南線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1630_AMP_A | 嘉民南線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 67 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 161 | 161kV | 1640_AMP | 嘉民北線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1640_AMP_A | 嘉民北線 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 68 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 610_AMP | 北港口湖線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.610_AMP_A | 北港口湖線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 69 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 610_AMP | 北港口湖線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.610_AMP_1 | 北港口湖線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 70 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 630_AMP | 北港水林一路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.630_AMP_A | 北港水林一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 71 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 630_AMP | 北港水林一路 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.630_AMP_1 | 北港水林一路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 72 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 640_AMP | 北港朴子線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.640_AMP_A | 北港朴子線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 73 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 640_AMP | 北港朴子線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.640_AMP_1 | 北港朴子線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 74 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 670_AMP | 北港新港一路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.670_AMP_A | 北港新港一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 75 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 670_AMP | 北港新港一路 | [27 empty] | DDCS2_2 | [8 empty] | 北港PS.670_AMP_2 | 北港新港一路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 76 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 680_AMP | 北港新港二路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.680_AMP_A | 北港新港二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 77 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 680_AMP | 北港新港二路 | [27 empty] | DDCS2_2 | [8 empty] | 北港PS.680_AMP_2 | 北港新港二路 AMP 點燈 (D2) | LINE69 |  |  | MAP_SET |  |  | 78 | CalcDIPoint |  |  |  |  | D_KEY | [33 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 710_AMP | 雲港一路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.710_AMP_A | 雲港一路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 79 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 710_AMP | 雲港一路 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.710_AMP_1 | 雲港一路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 80 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 720_AMP | 雲港二路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.720_AMP_A | 雲港二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 81 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 720_AMP | 雲港二路 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.720_AMP_1 | 雲港二路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 82 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 910_AMP | 北港土庫線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.910_AMP_A | 北港土庫線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 83 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 910_AMP | 北港土庫線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.910_AMP_1 | 北港土庫線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 84 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 920_AMP | 元長線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.920_AMP_A | 元長線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 85 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 920_AMP | 元長線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.920_AMP_1 | 元長線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 86 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 940_AMP | 北港東北線 | [27 empty] | ADCS_N | [8 empty] | 北港PS.940_AMP_A | 北港東北線 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 87 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 940_AMP | 北港東北線 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.940_AMP_1 | 北港東北線 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 88 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 2MTR_MVA | #2MTR | [27 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_MVA_A | #2MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 89 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_PERM | #2MTR TAP PERMISSION POINT | MTR | P04//2MTR/TR_PERM |  | MTR_PERM |  |  | 90 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 3MTR_MVA | #3MTR | [27 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_MVA_A | #3MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 91 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_PERM | #3MTR TAP PERMISSION POINT | MTR | P04//3MTR/TR_PERM |  | MTR_PERM |  |  | 92 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 4MTR_MVA | #4MTR | [27 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_MVA_A | #4MTR MVA 點燈 (AD) | MTR |  |  | MAP_SET |  |  | 93 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | PERM | [25 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_PERM | #4MTR TAP PERMISSION POINT | MTR | P04//4MTR/TR_PERM |  | MTR_PERM |  |  | 94 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 161 | 161kV | 1510_AMP | 北港四湖一路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1510_AMP_A | 北港四湖一路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 95 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 161 | 161kV | 1520_AMP | 北港四湖二路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.1520_AMP_A | 北港四湖二路 AMP 點燈 (AD) | LINE161 |  |  | MAP_SET |  |  | 96 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 0 |  | 全所全停電 | 全所全停電 |  | PWRFAIL | [25 empty] | ADCS_N | [8 empty] | 北港PS.PWRFAIL | 全所全停電 點燈 (AD) | OTHER |  |  | PWR_FAIL_CAL_PS |  |  | 97 | CalcDIPoint | [38 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620_AMP | 北港水林二路 | [27 empty] | ADCS_N | [8 empty] | 北港PS.620_AMP_A | 北港水林二路 AMP 點燈 (AD) | LINE69 |  |  | MAP_SET |  |  | 98 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 620_AMP | 北港水林二路 |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.620_AMP_1 | 北港水林二路 AMP 點燈 (D1) | LINE69 |  |  | MAP_SET |  |  | 99 | CalcDIPoint | [38 empty] | NORMAL/ALARM | NORMAL
P04 | 北港PS | 69 | 69kV | 620_CB | 北港水林二路(620_CB) |  | 1 | [25 empty] | DDCS1_2 | [8 empty] | 北港PS.620_CB_1 | 620(北港水林二路) CB (D1) | LINE69 |  |  | AD_LAMP_DD_1 |  |  | 100 | CalcDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | AI | AI |  | ADCH1 | [17 empty] | 1-81 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.AI_ADCH1 | AI 90%參考點 ADCH1 | OTHER | P04/0/RTU/ADCH1 |  |  |  | CDC | 101 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | AI | AI |  | ADCH2 | [17 empty] | 1-C1 | [5 empty] | ADCH_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.AI_ADCH2 | AI 90%參考點 ADCH2 | OTHER | P04/0/RTU/ADCH2 |  |  |  | CDC | 102 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCH | 1810.000000 | 1810.000000 | 1810.000000 | 1810.000000 | 10.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1790.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | AI | AI |  | ADCL1 | [17 empty] | 1-80 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.AI_ADCL1 | AI 10%參考點 ADCL1 | OTHER | P04/0/RTU/ADCL1 |  |  |  | CDC | 103 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | AI | AI |  | ADCL2 | [17 empty] | 1-C0 | [5 empty] | ADCL_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.AI_ADCL2 | AI 10%參考點 ADCL2 | OTHER | P04/0/RTU/ADCL2 |  |  |  | CDC | 104 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_ADCL | 210.000000 | 210.000000 | 210.000000 | 210.000000 | 10.000000 | 190.000000 | 190.000000 | 190.000000 | 190.000000 | 1.000000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1BUS | #1BUS |  | V | [17 empty] | 1-88 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161KV#1BUS_KV | 161KV #1BUS KV | BUS | P04/161/1BUS/V |  |  |  | CDC | 105 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P04 | 北港PS | 161 | 161kV | 2BUS | #2BUS |  | V | [17 empty] | 1-89 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161KV#2BUS_KV | 161KV #2BUS KV | BUS | P04/161/2BUS/V |  |  |  | CDC | 106 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 4.000000 | 10.000000
P04 | 北港PS | 69 | 69kV | 1BUS | #1BUS |  | V | [17 empty] | 1-94 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.69KV#1BUS_KV | 69KV #1BUS KV | BUS | P04/69/1BUS/V |  |  |  | CDC | 107 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P04 | 北港PS | 69 | 69kV | 2BUS | #2BUS |  | V | [17 empty] | 1-95 | [5 empty] | kV_-90_90(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.69KV#2BUS_KV | 69KV #2BUS KV | BUS | P04/69/2BUS/V |  |  |  | CDC | 108 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000 | 4.000000 | 5.000000
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | MW | [17 empty] | 1-C3 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1510_MW | 北港四湖一路 MW | LINE161 | P04/161/1510/MW |  |  |  | CDC | 109 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | MVAR | [17 empty] | 1-C4 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1510_MVAR | 北港四湖一路 MVAR | LINE161 | P04/161/1510/MVAR |  |  |  | CDC | 110 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | MW | [17 empty] | 1-C5 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1520_MW | 北港四湖二路 MW | LINE161 | P04/161/1520/MW |  |  |  | CDC | 111 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | MVAR | [17 empty] | 1-C6 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1520_MVAR | 北港四湖二路 MVAR | LINE161 | P04/161/1520/MVAR |  |  |  | CDC | 112 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | MW | [17 empty] | 1-BF | [5 empty] | MW_-448_448(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1560_MW | 台西二路 MW | LINE161 | P04/161/1560/MW |  |  |  | CDC | 113 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | MVAR | [17 empty] | 1-B2 | [5 empty] | MVAR_-448_448(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1560_MVAR | 台西二路 MVAR | LINE161 | P04/161/1560/MVAR |  |  |  | CDC | 114 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.896000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | MW | [17 empty] | 1-82 | [5 empty] | MW_-336_336(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1570_MW | 雲林北港雲高線 MW | LINE161 | P04/161/1570/MW |  |  |  | CDC | 115 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | MVAR | [17 empty] | 1-83 | [5 empty] | MVAR_-336_336(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1570_MVAR | 雲林北港雲高線 MVAR | LINE161 | P04/161/1570/MVAR |  |  |  | CDC | 116 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | MW | [17 empty] | 1-BA | [5 empty] | MW_-336_336(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1580_MW | 北港台西線 MW | LINE161 | P04/161/1580/MW |  |  |  | CDC | 117 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | MVAR | [17 empty] | 1-BB | [5 empty] | MVAR_-336_336(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1580_MVAR | 北港台西線 MVAR | LINE161 | P04/161/1580/MVAR |  |  |  | CDC | 118 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.672000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | MW | [17 empty] | 1-86 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1630_MW | 嘉民南線 MW | LINE161 | P04/161/1630/MW |  |  |  | CDC | 119 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | MVAR | [17 empty] | 1-87 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1630_MVAR | 嘉民南線 MVAR | LINE161 | P04/161/1630/MVAR |  |  |  | CDC | 120 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1630LPD | 嘉民南線(1630) |  | V | [17 empty] | 1-B3 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1630LPD_KV | 嘉民南線(1630) LPD KV | LINE161 | P04/161/1630/V |  |  |  | CDC | 121 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_16LPD | 169.000000 | 169.000000 | 172.000000 | 210.000000 | 0.500000 | 153.000000 | 153.000000 | 151.000000 | 0.000000 | 5.000000 | 10.000000
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | MW | [17 empty] | 1-84 | [5 empty] | MW_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1640_MW | 嘉民北線 MW | LINE161 | P04/161/1640/MW |  |  |  | CDC | 122 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | MVAR | [17 empty] | 1-85 | [5 empty] | MVAR_-560_560(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1640_MVAR | 嘉民北線 MVAR | LINE161 | P04/161/1640/MVAR |  |  |  | CDC | 123 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 1.120000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1640LPD | 嘉民北線(1640) |  | V | [17 empty] | 1-C2 | [5 empty] | kV_-210_210(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1640LPD_KV | 嘉民北線(1640) LPD KV | LINE161 | P04/161/1640/V |  |  |  | CDC | 124 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_161 | 167.000000 | 167.000000 | 169.000000 | 210.000000 | 0.500000 | 155.000000 | 155.000000 | 153.000000 | 0.000000 | 5.000000 | 10.000000
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | MW | [17 empty] | 1-97 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.610_MW | 北港口湖線 MW | LINE69 | P04/69/610/MW |  |  |  | CDC | 125 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | MVAR | [17 empty] | 1-98 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.610_MVAR | 北港口湖線 MVAR | LINE69 | P04/69/610/MVAR |  |  |  | CDC | 126 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | MW | [17 empty] | 1-9B | [5 empty] | MW_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.630_MW | 北港水林一路 MW | LINE69 | P04/69/630/MW |  |  |  | CDC | 127 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | MVAR | [17 empty] | 1-9C | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.630_MVAR | 北港水林一路 MVAR | LINE69 | P04/69/630/MVAR |  |  |  | CDC | 128 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | MW | [17 empty] | 1-9D | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.640_MW | 北港朴子線 MW | LINE69 | P04/69/640/MW |  |  |  | CDC | 129 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | MVAR | [17 empty] | 1-9E | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.640_MVAR | 北港朴子線 MVAR | LINE69 | P04/69/640/MVAR |  |  |  | CDC | 130 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | MW | [17 empty] | 1-9F | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.670_MW | 北港新港一路 MW | LINE69 | P04/69/670/MW |  |  |  | CDC | 131 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | MVAR | [17 empty] | 1-A0 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.670_MVAR | 北港新港一路 MVAR | LINE69 | P04/69/670/MVAR |  |  |  | CDC | 132 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | MW | [17 empty] | 1-A1 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.680_MW | 北港新港二路 MW | LINE69 | P04/69/680/MW |  |  |  | CDC | 133 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | MVAR | [17 empty] | 1-A2 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.680_MVAR | 北港新港二路 MVAR | LINE69 | P04/69/680/MVAR |  |  |  | CDC | 134 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | MW | [17 empty] | 1-A3 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.710_MW | 雲港一路 MW | LINE69 | P04/69/710/MW |  |  |  | CDC | 135 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | MVAR | [17 empty] | 1-A4 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.710_MVAR | 雲港一路 MVAR | LINE69 | P04/69/710/MVAR |  |  |  | CDC | 136 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | MW | [17 empty] | 1-A5 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.720_MW | 雲港二路 MW | LINE69 | P04/69/720/MW |  |  |  | CDC | 137 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | MVAR | [17 empty] | 1-A6 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.720_MVAR | 雲港二路 MVAR | LINE69 | P04/69/720/MVAR |  |  |  | CDC | 138 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | MW | [17 empty] | 1-A7 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.910_MW | 北港土庫線 MW | LINE69 | P04/69/910/MW |  |  |  | CDC | 139 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | MVAR | [17 empty] | 1-A8 | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.910_MVAR | 北港土庫線 MVAR | LINE69 | P04/69/910/MVAR |  |  |  | CDC | 140 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | MW | [17 empty] | 1-A9 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.920_MW | 元長線 MW | LINE69 | P04/69/920/MW |  |  |  | CDC | 141 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | MVAR | [17 empty] | 1-AA | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.920_MVAR | 元長線 MVAR | LINE69 | P04/69/920/MVAR |  |  |  | CDC | 142 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | MW | [17 empty] | 1-AB | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.940_MW | 北港東北線 MW | LINE69 | P04/69/940/MW |  |  |  | CDC | 143 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | MVAR | [17 empty] | 1-AC | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.940_MVAR | 北港東北線 MVAR | LINE69 | P04/69/940/MVAR |  |  |  | CDC | 144 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.288000 | 0.010000
P04 | 北港PS | 0 |  | 1500TIE | 1500TIE |  | I | [17 empty] | 1-8A | [5 empty] | A_-1600_1600(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.1500TIE_AMP | 1500TIE AMP | TIE | P04/161/1500/I |  |  |  | CDC | 145 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | C16R1600 | 1440.000000 | 1440.000000 | 1600.000000 | 1600.000000 | 0.000000 | -200.000000 | -200.000000 | -200.000000 | -200.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | 600TIE | 600TIE |  | I | [17 empty] | 1-96 | [5 empty] | A_-2000_2000(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.600TIE_AMP | 600TIE AMP | TIE | P04/69/600/I |  |  |  | CDC | 146 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | C20R2000 | 1800.000000 | 1800.000000 | 2000.000000 | 2000.000000 | 0.300000 | -1800.000000 | -1800.000000 | -2000.000000 | -2000.000000 | 1.000000 | 0.010000
P04 | 北港PS | 0 |  | 2MTR | #2MTR二次側 |  | MW | [17 empty] | 1-8E | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#2MTR_MW | #2MTR二次側 MW | MTR | P04/69/760/MW |  |  |  | CDC | 147 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P04 | 北港PS | 0 |  | 2MTR | #2MTR二次側 |  | MVAR | [17 empty] | 1-8F | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#2MTR_MVAR | #2MTR二次側 MVAR | MTR | P04/69/760/MVAR |  |  |  | CDC | 148 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | TapPosMv | [17 empty] | 1-AD |  | 1-51 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 北港PS.#2MTR_TAP | #2MTR OLTC TAP | MTR | P04//2MTR/TapPosMv |  |  |  | CDC | 149 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | OilTemp | [17 empty] | 1-AE | [5 empty] | OIL_-160_160(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#2MTR_OIL | #2MTR 油溫 | MTR | P04//2MTR/OilTemp |  |  |  | CDC | 150 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.320000
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | CoilTemp | [17 empty] | 1-AF | [5 empty] | COIL_-160_160(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#2MTR_COIL | #2MTR 線溫 | MTR | P04//2MTR/CoilTemp |  |  |  | CDC | 151 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.320000
P04 | 北港PS | 0 |  | 3MTR | #3MTR二次側 |  | MW | [17 empty] | 1-90 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#3MTR_MW | #3MTR二次側 MW | MTR | P04/69/770/MW |  |  |  | CDC | 152 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P04 | 北港PS | 0 |  | 3MTR | #3MTR二次側 |  | MVAR | [17 empty] | 1-91 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#3MTR_MVAR | #3MTR二次側 MVAR | MTR | P04/69/770/MVAR |  |  |  | CDC | 153 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | TapPosMv | [17 empty] | 1-B0 |  | 1-5B |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 北港PS.#3MTR_TAP | #3MTR OLTC TAP | MTR | P04//3MTR/TapPosMv |  |  |  | CDC | 154 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | OilTemp | [17 empty] | 1-B1 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#3MTR_OIL | #3MTR 油溫 | MTR | P04//3MTR/OilTemp |  |  |  | CDC | 155 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP3M | 67.000000 | 67.000000 | 83.000000 | 90.000000 | 2.600000 | 20.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | CoilTemp | [17 empty] | 1-B4 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#3MTR_COIL | #3MTR 線溫 | MTR | P04//3MTR/CoilTemp |  |  |  | CDC | 156 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 0 |  | 4MTR | #4MTR二次側 |  | MW | [17 empty] | 1-92 | [5 empty] | MW_-360_360(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#4MTR_MW | #4MTR二次側 MW | MTR | P04/69/780/MW |  |  |  | CDC | 157 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.720000 | 0.010000
P04 | 北港PS | 0 |  | 4MTR | #4MTR二次側 |  | MVAR | [17 empty] | 1-93 | [5 empty] | MVAR_-240_240(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#4MTR_MVAR | #4MTR二次側 MVAR | MTR | P04/69/780/MVAR |  |  |  | CDC | 158 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | TapPosMv | [17 empty] | 1-B5 |  | 1-65 |  |  |  | TAP_-6.5_6.5(0_2000) |  | ADCS_N | [8 empty] | 北港PS.#4MTR_TAP | #4MTR OLTC TAP | MTR | P04//4MTR/TapPosMv |  |  |  | CDC | 159 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | TAP6_6 | 5.000000 | 5.000000 | 6.000000 | 7.500000 | 0.000000 | -5.000000 | -5.000000 | -6.000000 | -7.500000 | 0.100000
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | OilTemp | [17 empty] | 1-B6 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#4MTR_OIL | #4MTR 油溫 | MTR | P04//4MTR/OilTemp |  |  |  | CDC | 160 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | CoilTemp | [17 empty] | 1-B7 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.#4MTR_COIL | #4MTR 線溫 | MTR | P04//4MTR/CoilTemp |  |  |  | CDC | 161 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 0 |  |  |  |  | DCV_N | [17 empty] | 1-B9 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.直流N電源電壓 | 直流N電源電壓 | OTHER | P04/0/StaDev/DCV_N |  |  |  | CDC | 162 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_125N | -60.000000 | -60.000000 | -55.000000 | 150.000000 | 0.200000 | -70.000000 | -70.000000 | -75.000000 | -150.000000 | 0.100000 | 0.010000
P04 | 北港PS | 0 |  |  |  |  | DCV_P | [17 empty] | 1-B8 | [5 empty] | kV_-150_150(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.直流P電源電壓 | 直流P電源電壓 | OTHER | P04/0/StaDev/DCV_P |  |  |  | CDC | 163 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_125P | 70.000000 | 70.000000 | 75.000000 | 150.000000 | 0.200000 | 60.000000 | 60.000000 | 55.000000 | -150.000000 | 0.100000 | 0.010000
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | MW | [17 empty] | 1-99 | [5 empty] | MW_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.620_MW | 北港水林二路 MW | LINE69 | P04/69/620/MW |  |  |  | CDC | 164 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MW | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | MVAR | [17 empty] | 1-9A | [5 empty] | MVAR_-144_144(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.620_MVAR | 北港水林二路 MVAR | LINE69 | P04/69/620/MVAR |  |  |  | CDC | 165 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000 | 0.480000 | 0.010000
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | CoilTemp | [17 empty] | 1-C8 | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#1SHR_COIL | 161KV #1SHR 線溫 | OTHER | P04//1SHR/CoilTemp |  |  |  | CDC | 166 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | OilTemp | [17 empty] | 1-C7 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#1SHR_OIL | 161KV #1SHR 油溫 | OTHER | P04//1SHR/OilTemp |  |  |  | CDC | 167 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | CoilTemp | [17 empty] | 1-CA | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#2SHR_COIL | 161KV #2SHR 線溫 | OTHER | P04//2SHR/CoilTemp |  |  |  | CDC | 168 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | OilTemp | [17 empty] | 1-C9 | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#2SHR_OIL | 161KV #2SHR 油溫 | OTHER | P04//2SHR/OilTemp |  |  |  | CDC | 169 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | CoilTemp | [17 empty] | 1-CC | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#3SHR_COIL | 161KV #3SHR 線溫 | OTHER | P04//3SHR/CoilTemp |  |  |  | CDC | 170 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | OilTemp | [17 empty] | 1-CB | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#3SHR_OIL | 161KV #3SHR 油溫 | OTHER | P04//3SHR/OilTemp |  |  |  | CDC | 171 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | CoilTemp | [17 empty] | 1-CE | [5 empty] | COIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#4SHR_COIL | 161KV #4SHR 線溫 | OTHER | P04//4SHR/CoilTemp |  |  |  | CDC | 172 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP2 | 90.000000 | 100.000000 | 100.000000 | 110.000000 | 1.700000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | OilTemp | [17 empty] | 1-CD | [5 empty] | OIL_-120_120(-2000_2000) |  | ADCS_N | [8 empty] | 北港PS.161#4SHR_OIL | 161KV #4SHR 油溫 | OTHER | P04//4SHR/OilTemp |  |  |  | CDC | 173 | GENERICAIPoint | PS016_L1 | CDC2_AI |  | AI | [17 empty] | LG_TMP1 | 75.000000 | 75.000000 | 83.000000 | 90.000000 | 2.000000 | -10.000000 | -10.000000 | -10.000000 | -10.000000 | 0.240000
P04 | 北港PS | 0 |  | 1510 | 1510 |  | PHA | [17 empty] | 2-00-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_PHA | 北港四湖一路(1510)PHA | OTHER | P04/161/1510/PHA |  |  |  | CDC | 174 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1510 | 1510 |  | GDA | [17 empty] | 2-00-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_GDA | 北港四湖一路(1510)GDA | OTHER | P04/161/1510/GDA |  |  |  | CDC | 175 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | CB | [17 empty] | 2-00-00 |  | 2-48 | [5 empty] | 161KV_N | [8 empty] | 北港PS.1510_CB | 1510(北港四湖一路) CB | LINE161 |  |  |  |  | CDC | 176 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | 79UL | [17 empty] | 2-38-06 |  | 2-6A | [5 empty] | ADCS_N | [8 empty] | 北港PS.1510_79UL | 北港四湖一路(1510) 79RY U/L | LINE161 |  |  |  |  | CDC | 177 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | ABS1 | 1511 | [16 empty] | 2-3E-00 | 2-3E-01 | 2-58 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1511_ABS | 1511(北港四湖一路) ABS | LINE161 | P04/161/1510/ABS1 |  |  |  | CDC | 178 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | ABS2 | 1512 | [16 empty] | 2-3E-02 | 2-3E-03 | 2-59 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1512_ABS | 1512(北港四湖一路) ABS | LINE161 | P04/161/1510/ABS2 |  |  |  | CDC | 179 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | ABS3 | 1513 | [16 empty] | 2-3E-04 | 2-3E-05 | 2-5A | [5 empty] | ADCS_N | [8 empty] | 北港PS.1513_ABS | 1513(北港四湖一路) ABS | LINE161 | P04/161/1510/ABS3 |  |  |  | CDC | 180 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | E3 | 1513E | [16 empty] | 2-3E-06 | 2-3E-07 | 2-5B | [5 empty] | ADCS_N | [8 empty] | 北港PS.1513E_ES | 1513E(北港四湖一路) ES | LINE161 | P04/161/1510/ES3 |  |  |  | CDC | 181 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | PHA | [17 empty] | 2-01-01 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1520_PHA | 北港四湖二路(1520) 相間RY | LINE161 | P04/161/1520/PHA |  |  |  | CDC | 182 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | GDA | [17 empty] | 2-01-00 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1520_GDA | 北港四湖二路(1520) 接地RY | LINE161 | P04/161/1520/GDA |  |  |  | CDC | 183 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | CB | [17 empty] | 2-00-05 |  | 2-49 | [5 empty] | 161KV_N | [8 empty] | 北港PS.1520_CB | 1520(北港四湖二路) CB | LINE161 | P04/161/1520/CB |  |  |  | CDC | 184 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | 79UL | [17 empty] | 2-38-13 |  | 2-6D | [5 empty] | ADCS_N | [8 empty] | 北港PS.1520_79UL | 北港四湖二路(1520) 79RY U/L | LINE161 | P04/161/1520/79UL |  |  |  | CDC | 185 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | ABS1 | 1521 | [16 empty] | 2-3E-08 | 2-3E-09 | 2-5C | [5 empty] | ADCS_N | [8 empty] | 北港PS.1521_ABS | 1521(北港四湖二路) ABS | LINE161 | P04/161/1520/ABS1 |  |  |  | CDC | 186 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | ABS2 | 1522 | [16 empty] | 2-3E-10 | 2-3E-11 | 2-5D | [5 empty] | ADCS_N | [8 empty] | 北港PS.1522_ABS | 1522(北港四湖二路) ABS | LINE161 | P04/161/1520/ABS2 |  |  |  | CDC | 187 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | ABS3 | 1523 | [16 empty] | 2-3E-12 | 2-3E-13 | 2-5E | [5 empty] | ADCS_N | [8 empty] | 北港PS.1523_ABS | 1523(北港四湖二路) ABS | LINE161 | P04/161/1520/ABS3 |  |  |  | CDC | 188 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | E3 | 1523E | [16 empty] | 2-3E-14 | 2-3E-15 | 2-5F | [5 empty] | ADCS_N | [8 empty] | 北港PS.1523E_ES | 1523E(北港四湖二路) ES | LINE161 | P04/161/1520/ES3 |  |  |  | CDC | 189 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | PHA | [17 empty] | 1-0C-04 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1560_PHA | 台西二路(1560) 相間RY | LINE161 | P04/161/1560/PHA |  |  |  | CDC | 190 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | GDA | [17 empty] | 1-0C-05 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1560_GDA | 台西二路(1560) 接地RY | LINE161 | P04/161/1560/GDA |  |  |  | CDC | 191 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | 85A | [17 empty] | 1-0C-03 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1560_85A | 台西二路(1560) 85RY | LINE161 | P04/161/1560/85A |  |  |  | CDC | 192 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | 85UL | [17 empty] | 1-30-05 |  | 2-13 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1560_85UL | 台西二路(1560) 85RY U/L | LINE161 | P04/161/1560/85UL |  |  |  | CDC | 193 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | CB | [17 empty] | 1-0C-02 |  | 1-02 | [5 empty] | 161KV_N | [8 empty] | 北港PS.1560_CB | 1560(台西二路) CB | LINE161 | P04/161/1560/CB |  |  |  | CDC | 194 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | 79UL | [17 empty] | 1-30-04 |  | 2-12 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1560_79UL | 台西二路(1560) 79RY U/L | LINE161 | P04/161/1560/79UL |  |  |  | CDC | 195 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | ABS1 | 1561 | [16 empty] | 1-3F-08 | 1-3F-09 | 2-18 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1561_ABS | 1561(台西二路) ABS | LINE161 | P04/161/1560/ABS1 |  |  |  | CDC | 196 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | ABS2 | 1562 | [16 empty] | 1-3F-10 | 1-3F-11 | 2-19 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1562_ABS | 1562(台西二路) ABS | LINE161 | P04/161/1560/ABS2 |  |  |  | CDC | 197 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | ABS3 | 1563 | [16 empty] | 1-3F-12 | 1-3F-13 | 2-1A | [5 empty] | ADCS_N | [8 empty] | 北港PS.1563_ABS | 1563(台西二路) ABS | LINE161 | P04/161/1560/ABS3 |  |  |  | CDC | 198 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | E3 | 1563E | [16 empty] | 1-3F-14 | 1-3F-15 | 2-1B | [5 empty] | ADCS_N | [8 empty] | 北港PS.1563E_ES | 1563E(台西二路) ES | LINE161 | P04/161/1560/ES3 |  |  |  | CDC | 199 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | PHA | [17 empty] | 1-05-02 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1570_PHA | 雲林北港雲高線(1570) 相間RY | LINE161 | P04/161/1570/PHA |  |  |  | CDC | 200 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | GDA | [17 empty] | 1-05-03 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1570_GDA | 雲林北港雲高線(1570) 接地RY | LINE161 | P04/161/1570/GDA |  |  |  | CDC | 201 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | CB | [17 empty] | 1-05-00 |  | 1-7C | [5 empty] | 161KV_N | [8 empty] | 北港PS.1570_CB | 1570(雲林北港雲高線) CB | LINE161 | P04/161/1570/CB |  |  |  | CDC | 202 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | 79UL | [17 empty] | 1-3B-01 |  | 2-00 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1570_79UL | 雲林北港雲高線(1570) 79RY U/L | LINE161 | P04/161/1570/79UL |  |  |  | CDC | 203 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | ABS1 | 1571 | [16 empty] | 1-31-00 | 1-31-01 | 1-03 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1571_ABS | 1571(雲林北港雲高線) ABS | LINE161 | P04/161/1570/ABS1 |  |  |  | CDC | 204 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | ABS2 | 1572 | [16 empty] | 1-31-02 | 1-31-03 | 1-04 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1572_ABS | 1572(雲林北港雲高線) ABS | LINE161 | P04/161/1570/ABS2 |  |  |  | CDC | 205 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | ABS3 | 1573 | [16 empty] | 1-31-04 | 1-31-05 | 1-05 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1573_ABS | 1573(雲林北港雲高線) ABS | LINE161 | P04/161/1570/ABS3 |  |  |  | CDC | 206 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | E3 | 1573E | [16 empty] | 1-31-06 | 1-31-07 | 1-06 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1573E_ES | 1573E(雲林北港雲高線) ES | LINE161 | P04/161/1570/ES3 |  |  |  | CDC | 207 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | PHA | [17 empty] | 1-0B-02 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1580_PHA | 北港台西線(1580) 相間RY | LINE161 | P04/161/1580/PHA |  |  |  | CDC | 208 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | GDA | [17 empty] | 1-0B-03 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1580_GDA | 北港台西線(1580) 接地RY | LINE161 | P04/161/1580/GDA |  |  |  | CDC | 209 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | CB | [17 empty] | 1-0B-00 |  | 1-7F | [5 empty] | 161KV_N | [8 empty] | 北港PS.1580_CB | 1580(北港台西線) CB | LINE161 | P04/161/1580/CB |  |  |  | CDC | 210 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | 79UL | [17 empty] | 1-30-07 |  | 2-0E | [5 empty] | ADCS_N | [8 empty] | 北港PS.1580_79UL | 北港台西線(1580) 79RY U/L | LINE161 | P04/161/1580/79UL |  |  |  | CDC | 211 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | ABS1 | 1581 | [16 empty] | 1-30-08 | 1-30-09 | 1-75 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1581_ABS | 1581(北港台西線) ABS | LINE161 | P04/161/1580/ABS1 |  |  |  | CDC | 212 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | ABS2 | 1582 | [16 empty] | 1-30-10 | 1-30-11 | 1-76 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1582_ABS | 1582(北港台西線) ABS | LINE161 | P04/161/1580/ABS2 |  |  |  | CDC | 213 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | ABS3 | 1583 | [16 empty] | 1-30-12 | 1-30-13 | 1-77 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1583_ABS | 1583(北港台西線) ABS | LINE161 | P04/161/1580/ABS3 |  |  |  | CDC | 214 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | E3 | 1583E | [16 empty] | 1-30-14 | 1-30-15 | 1-78 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1583E_ES | 1583E(北港台西線) ES | LINE161 | P04/161/1580/ES3 |  |  |  | CDC | 215 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | PHA | [17 empty] | 1-05-06 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1630_PHA | 嘉民南線(1630) 相間RY | LINE161 | P04/161/1630/PHA |  |  |  | CDC | 216 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | GDA | [17 empty] | 1-05-07 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1630_GDA | 嘉民南線(1630) 接地RY | LINE161 | P04/161/1630/GDA |  |  |  | CDC | 217 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | CB | [17 empty] | 1-05-04 |  | 1-7E | [5 empty] | 161KV_N | [8 empty] | 北港PS.1630_CB | 1630(嘉民南線) CB | LINE161 | P04/161/1630/CB |  |  |  | CDC | 218 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | 79UL | [17 empty] | 1-3B-05 |  | 2-04 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1630_79UL | 嘉民南線(1630) 79RY U/L | LINE161 | P04/161/1630/79UL |  |  |  | CDC | 219 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | ABS1 | 1631 | [16 empty] | 1-31-08 | 1-31-09 | 1-0F | [5 empty] | ADCS_N | [8 empty] | 北港PS.1631_ABS | 1631(嘉民南線) ABS | LINE161 | P04/161/1630/ABS1 |  |  |  | CDC | 220 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | ABS2 | 1632 | [16 empty] | 1-31-10 | 1-31-11 | 1-10 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1632_ABS | 1632(嘉民南線) ABS | LINE161 | P04/161/1630/ABS2 |  |  |  | CDC | 221 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | ABS3 | 1633 | [16 empty] | 1-31-12 | 1-31-13 | 1-11 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1633_ABS | 1633(嘉民南線) ABS | LINE161 | P04/161/1630/ABS3 |  |  |  | CDC | 222 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | E3 | 1633E | [16 empty] | 1-31-14 | 1-31-15 | 1-12 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1633E_ES | 1633E(嘉民南線) ES | LINE161 | P04/161/1630/ES3 |  |  |  | CDC | 223 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | PHA | [17 empty] | 1-06-02 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1640_PHA | 嘉民北線(1640) 相間RY | LINE161 | P04/161/1640/PHA |  |  |  | CDC | 224 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | GDA | [17 empty] | 1-06-03 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1640_GDA | 嘉民北線(1640) 接地RY | LINE161 | P04/161/1640/GDA |  |  |  | CDC | 225 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | CB | [17 empty] | 1-06-00 |  | 1-7D | [5 empty] | 161KV_N | [8 empty] | 北港PS.1640_CB | 1640(嘉民北線) CB | LINE161 | P04/161/1640/CB |  |  |  | CDC | 226 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | 79UL | [17 empty] | 1-3B-03 |  | 2-02 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1640_79UL | 嘉民北線(1640) 79RY U/L | LINE161 | P04/161/1640/79UL |  |  |  | CDC | 227 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | ABS1 | 1641 | [16 empty] | 1-32-00 | 1-32-01 | 1-09 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1641_ABS | 1641(嘉民北線) ABS | LINE161 | P04/161/1640/ABS1 |  |  |  | CDC | 228 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | ABS2 | 1642 | [16 empty] | 1-32-02 | 1-32-03 | 1-0A | [5 empty] | ADCS_N | [8 empty] | 北港PS.1642_ABS | 1642(嘉民北線) ABS | LINE161 | P04/161/1640/ABS2 |  |  |  | CDC | 229 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | ABS3 | 1643 | [16 empty] | 1-32-04 | 1-32-05 | 1-0B | [5 empty] | ADCS_N | [8 empty] | 北港PS.1643_ABS | 1643(嘉民北線) ABS | LINE161 | P04/161/1640/ABS3 |  |  |  | CDC | 230 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | E3 | 1643E | [16 empty] | 1-32-06 | 1-32-07 | 1-0C | [5 empty] | ADCS_N | [8 empty] | 北港PS.1643E_ES | 1643E(嘉民北線) ES | LINE161 | P04/161/1640/ES3 |  |  |  | CDC | 231 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | PHA | [17 empty] | 1-00-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.610_PHA | 北港口湖線(610) 相間RY | LINE69 | P04/69/610/PHA |  |  |  | CDC | 232 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | GDA | [17 empty] | 1-00-02 | [7 empty] | 69KV_N | [8 empty] | 北港PS.610_GDA | 北港口湖線(610) 接地RY | LINE69 | P04/69/610/GDA |  |  |  | CDC | 233 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | CB | [17 empty] | 1-00-00 |  | 1-13 | [5 empty] | 69KV_N | [8 empty] | 北港PS.610_CB | 610(北港口湖線) CB | LINE69 | P04/69/610/CB |  |  |  | CDC | 234 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | ABS1 | 611 | [16 empty] | 1-33-00 | 1-33-01 | 1-14 | [5 empty] | ADCS_N | [8 empty] | 北港PS.611_ABS | 611(北港口湖線) ABS | LINE69 | P04/69/610/ABS1 |  |  |  | CDC | 235 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | ABS2 | 612 | [16 empty] | 1-33-02 | 1-33-03 | 1-15 | [5 empty] | ADCS_N | [8 empty] | 北港PS.612_ABS | 612(北港口湖線) ABS | LINE69 | P04/69/610/ABS2 |  |  |  | CDC | 236 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | ABS3 | 613 | [16 empty] | 1-33-04 | 1-33-05 | 1-16 | [5 empty] | ADCS_N | [8 empty] | 北港PS.613_ABS | 613(北港口湖線) ABS | LINE69 | P04/69/610/ABS3 |  |  |  | CDC | 237 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | E3 | 613E | [16 empty] | 1-33-06 | 1-33-07 | 1-17 | [5 empty] | ADCS_N | [8 empty] | 北港PS.613E_ES | 613E(北港口湖線) ES | LINE69 | P04/69/610/ES3 |  |  |  | CDC | 238 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | PHA | [17 empty] | 1-00-07 | [7 empty] | 69KV_N | [8 empty] | 北港PS.630_PHA | 北港水林一路(630) 相間RY | LINE69 | P04/69/630/PHA |  |  |  | CDC | 239 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | GDA | [17 empty] | 1-01-00 | [7 empty] | 69KV_N | [8 empty] | 北港PS.630_GDA | 北港水林一路(630) 接地RY | LINE69 | P04/69/630/GDA |  |  |  | CDC | 240 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | CB | [17 empty] | 1-00-06 |  | 1-3B | [5 empty] | 69KV_N | [8 empty] | 北港PS.630_CB | 630(北港水林一路) CB | LINE69 | P04/69/630/CB |  |  |  | CDC | 241 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | ABS1 | 631 | [16 empty] | 1-37-00 | 1-37-01 | 1-3C | [5 empty] | ADCS_N | [8 empty] | 北港PS.631_ABS | 631(北港水林一路) ABS | LINE69 | P04/69/630/ABS1 |  |  |  | CDC | 242 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | ABS2 | 632 | [16 empty] | 1-37-02 | 1-37-03 | 1-3D | [5 empty] | ADCS_N | [8 empty] | 北港PS.632_ABS | 632(北港水林一路) ABS | LINE69 | P04/69/630/ABS2 |  |  |  | CDC | 243 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | ABS3 | 633 | [16 empty] | 1-37-04 | 1-37-05 | 1-3E | [5 empty] | ADCS_N | [8 empty] | 北港PS.633_ABS | 633(北港水林一路) ABS | LINE69 | P04/69/630/ABS3 |  |  |  | CDC | 244 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | E3 | 633E | [16 empty] | 1-37-06 | 1-37-07 | 1-3F | [5 empty] | ADCS_N | [8 empty] | 北港PS.633E_ES | 633E(北港水林一路) ES | LINE69 | P04/69/630/ES3 |  |  |  | CDC | 245 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | PHA | [17 empty] | 1-01-02 | [7 empty] | 69KV_N | [8 empty] | 北港PS.640_PHA | 北港朴子線(640) 相間RY | LINE69 | P04/69/640/PHA |  |  |  | CDC | 246 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | GDA | [17 empty] | 1-01-03 | [7 empty] | 69KV_N | [8 empty] | 北港PS.640_GDA | 北港朴子線(640) 接地RY | LINE69 | P04/69/640/GDA |  |  |  | CDC | 247 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | CB | [17 empty] | 1-01-01 |  | 1-40 | [5 empty] | 69KV_N | [8 empty] | 北港PS.640_CB | 640(北港朴子線) CB | LINE69 | P04/69/640/CB |  |  |  | CDC | 248 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | ABS1 | 641 | [16 empty] | 1-37-08 | 1-37-09 | 1-41 | [5 empty] | ADCS_N | [8 empty] | 北港PS.641_ABS | 641(北港朴子線) ABS | LINE69 | P04/69/640/ABS1 |  |  |  | CDC | 249 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | ABS2 | 642 | [16 empty] | 1-37-10 | 1-37-11 | 1-42 | [5 empty] | ADCS_N | [8 empty] | 北港PS.642_ABS | 642(北港朴子線) ABS | LINE69 | P04/69/640/ABS2 |  |  |  | CDC | 250 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | ABS3 | 643 | [16 empty] | 1-37-12 | 1-37-13 | 1-43 | [5 empty] | ADCS_N | [8 empty] | 北港PS.643_ABS | 643(北港朴子線) ABS | LINE69 | P04/69/640/ABS3 |  |  |  | CDC | 251 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | E3 | 643E | [16 empty] | 1-37-14 | 1-37-15 | 1-44 | [5 empty] | ADCS_N | [8 empty] | 北港PS.643E_ES | 643E(北港朴子線) ES | LINE69 | P04/69/640/ES3 |  |  |  | CDC | 252 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | PHA | [17 empty] | 1-01-05 | [7 empty] | 69KV_N | [8 empty] | 北港PS.670_PHA | 北港新港一路(670) 相間RY | LINE69 | P04/69/670/PHA |  |  |  | CDC | 253 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | GDA | [17 empty] | 1-01-06 | [7 empty] | 69KV_N | [8 empty] | 北港PS.670_GDA | 北港新港一路(670) 接地RY | LINE69 | P04/69/670/GDA |  |  |  | CDC | 254 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | CB | [17 empty] | 1-01-04 |  | 1-1D | [5 empty] | 69KV_N | [8 empty] | 北港PS.670_CB | 670(北港新港一路) CB | LINE69 | P04/69/670/CB |  |  |  | CDC | 255 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | ABS1 | 671 | [16 empty] | 1-34-00 | 1-34-01 | 1-1E | [5 empty] | ADCS_N | [8 empty] | 北港PS.671_ABS | 671(北港新港一路) ABS | LINE69 | P04/69/670/ABS1 |  |  |  | CDC | 256 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | ABS2 | 672 | [16 empty] | 1-34-02 | 1-34-03 | 1-1F | [5 empty] | ADCS_N | [8 empty] | 北港PS.672_ABS | 672(北港新港一路) ABS | LINE69 | P04/69/670/ABS2 |  |  |  | CDC | 257 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | ABS3 | 673 | [16 empty] | 1-34-04 | 1-34-05 | 1-20 | [5 empty] | ADCS_N | [8 empty] | 北港PS.673_ABS | 673(北港新港一路) ABS | LINE69 | P04/69/670/ABS3 |  |  |  | CDC | 258 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | E3 | 673E | [16 empty] | 1-34-06 | 1-34-07 | 1-21 | [5 empty] | ADCS_N | [8 empty] | 北港PS.673E_ES | 673E(北港新港一路) ES | LINE69 | P04/69/670/ES3 |  |  |  | CDC | 259 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | PHA | [17 empty] | 1-02-00 | [7 empty] | 69KV_N | [8 empty] | 北港PS.680_PHA | 北港新港二路(680) 相間RY | LINE69 | P04/69/680/PHA |  |  |  | CDC | 260 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | GDA | [17 empty] | 1-02-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.680_GDA | 北港新港二路(680) 接地RY | LINE69 | P04/69/680/GDA |  |  |  | CDC | 261 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | CB | [17 empty] | 1-01-07 |  | 1-22 | [5 empty] | 69KV_N | [8 empty] | 北港PS.680_CB | 680(北港新港二路) CB | LINE69 | P04/69/680/CB |  |  |  | CDC | 262 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | ABS1 | 681 | [16 empty] | 1-34-08 | 1-34-09 | 1-23 | [5 empty] | ADCS_N | [8 empty] | 北港PS.681_ABS | 681(北港新港二路) ABS | LINE69 | P04/69/680/ABS1 |  |  |  | CDC | 263 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | ABS2 | 682 | [16 empty] | 1-34-10 | 1-34-11 | 1-24 | [5 empty] | ADCS_N | [8 empty] | 北港PS.682_ABS | 682(北港新港二路) ABS | LINE69 | P04/69/680/ABS2 |  |  |  | CDC | 264 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | ABS3 | 683 | [16 empty] | 1-34-12 | 1-34-13 | 1-25 | [5 empty] | ADCS_N | [8 empty] | 北港PS.683_ABS | 683(北港新港二路) ABS | LINE69 | P04/69/680/ABS3 |  |  |  | CDC | 265 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | E3 | 683E | [16 empty] | 1-34-14 | 1-34-15 | 1-26 | [5 empty] | ADCS_N | [8 empty] | 北港PS.683E_ES | 683E(北港新港二路) ES | LINE69 | P04/69/680/ES3 |  |  |  | CDC | 266 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | PHA | [17 empty] | 1-02-03 | [7 empty] | 69KV_N | [8 empty] | 北港PS.710_PHA | 雲港一路(710) 相間RY | LINE69 | P04/69/710/PHA |  |  |  | CDC | 267 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | GDA | [17 empty] | 1-02-04 | [7 empty] | 69KV_N | [8 empty] | 北港PS.710_GDA | 雲港一路(710) 接地RY | LINE69 | P04/69/710/GDA |  |  |  | CDC | 268 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | CB | [17 empty] | 1-02-02 |  | 1-27 | [5 empty] | 69KV_N | [8 empty] | 北港PS.710_CB | 710(雲港一路) CB | LINE69 | P04/69/710/CB |  |  |  | CDC | 269 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | ABS1 | 711 | [16 empty] | 1-35-00 | 1-35-01 | 1-28 | [5 empty] | ADCS_N | [8 empty] | 北港PS.711_ABS | 711(雲港一路) ABS | LINE69 | P04/69/710/ABS1 |  |  |  | CDC | 270 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | ABS2 | 712 | [16 empty] | 1-35-02 | 1-35-03 | 1-29 | [5 empty] | ADCS_N | [8 empty] | 北港PS.712_ABS | 712(雲港一路) ABS | LINE69 | P04/69/710/ABS2 |  |  |  | CDC | 271 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | ABS3 | 713 | [16 empty] | 1-35-04 | 1-35-05 | 1-2A | [5 empty] | ADCS_N | [8 empty] | 北港PS.713_ABS | 713(雲港一路) ABS | LINE69 | P04/69/710/ABS3 |  |  |  | CDC | 272 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | E3 | 713E | [16 empty] | 1-35-06 | 1-35-07 | 1-2B | [5 empty] | ADCS_N | [8 empty] | 北港PS.713E_ES | 713E(雲港一路) ES | LINE69 | P04/69/710/ES3 |  |  |  | CDC | 273 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | PHA | [17 empty] | 1-02-06 | [7 empty] | 69KV_N | [8 empty] | 北港PS.720_PHA | 雲港二路(720) 相間RY | LINE69 | P04/69/720/PHA |  |  |  | CDC | 274 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | GDA | [17 empty] | 1-02-07 | [7 empty] | 69KV_N | [8 empty] | 北港PS.720_GDA | 雲港二路(720) 接地RY | LINE69 | P04/69/720/GDA |  |  |  | CDC | 275 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | CB | [17 empty] | 1-02-05 |  | 1-2C | [5 empty] | 69KV_N | [8 empty] | 北港PS.720_CB | 720(雲港二路) CB | LINE69 | P04/69/720/CB |  |  |  | CDC | 276 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | 81AS | [17 empty] | 1-0A-07 |  | 1-79 | [5 empty] | 69KV_N | [8 empty] | 北港PS.720_81A/S | (720) 81RY A/S | LINE69 | P04/69/ComPoint/81A |  |  |  | CDC | 277 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/RESET | RESET
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | ABS1 | 721 | [16 empty] | 1-35-08 | 1-35-09 | 1-2D | [5 empty] | ADCS_N | [8 empty] | 北港PS.721_ABS | 721(雲港二路) ABS | LINE69 | P04/69/720/ABS1 |  |  |  | CDC | 278 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | ABS2 | 722 | [16 empty] | 1-35-10 | 1-35-11 | 1-2E | [5 empty] | ADCS_N | [8 empty] | 北港PS.722_ABS | 722(雲港二路) ABS | LINE69 | P04/69/720/ABS2 |  |  |  | CDC | 279 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | ABS3 | 723 | [16 empty] | 1-35-12 | 1-35-13 | 1-2F | [5 empty] | ADCS_N | [8 empty] | 北港PS.723_ABS | 723(雲港二路) ABS | LINE69 | P04/69/720/ABS3 |  |  |  | CDC | 280 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | E3 | 723E | [16 empty] | 1-35-14 | 1-35-15 | 1-30 | [5 empty] | ADCS_N | [8 empty] | 北港PS.723E_ES | 723E(雲港二路) ES | LINE69 | P04/69/720/ES3 |  |  |  | CDC | 281 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | PHA | [17 empty] | 1-03-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.910_PHA | 北港土庫線(910) 相間RY | LINE69 | P04/69/910/PHA |  |  |  | CDC | 282 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | GDA | [17 empty] | 1-03-02 | [7 empty] | 69KV_N | [8 empty] | 北港PS.910_GDA | 北港土庫線(910) 接地RY | LINE69 | P04/69/910/GDA |  |  |  | CDC | 283 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | CB | [17 empty] | 1-03-00 |  | 1-31 | [5 empty] | 69KV_N | [8 empty] | 北港PS.910_CB | 910(北港土庫線) CB | LINE69 | P04/69/910/CB |  |  |  | CDC | 284 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | ABS1 | 911 | [16 empty] | 1-36-00 | 1-36-01 | 1-32 | [5 empty] | ADCS_N | [8 empty] | 北港PS.911_ABS | 911(北港土庫線) ABS | LINE69 | P04/69/910/ABS1 |  |  |  | CDC | 285 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | ABS2 | 912 | [16 empty] | 1-36-02 | 1-36-03 | 1-33 | [5 empty] | ADCS_N | [8 empty] | 北港PS.912_ABS | 912(北港土庫線) ABS | LINE69 | P04/69/910/ABS2 |  |  |  | CDC | 286 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | ABS3 | 913 | [16 empty] | 1-36-04 | 1-36-05 | 1-34 | [5 empty] | ADCS_N | [8 empty] | 北港PS.913_ABS | 913(北港土庫線) ABS | LINE69 | P04/69/910/ABS3 |  |  |  | CDC | 287 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | E3 | 913E | [16 empty] | 1-36-06 | 1-36-07 | 1-35 | [5 empty] | ADCS_N | [8 empty] | 北港PS.913E_ES | 913E(北港土庫線) ES | LINE69 | P04/69/910/ES3 |  |  |  | CDC | 288 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | PHA | [17 empty] | 1-03-04 | [7 empty] | 69KV_N | [8 empty] | 北港PS.920_PHA | 元長線(920) 相間RY | LINE69 | P04/69/920/PHA |  |  |  | CDC | 289 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | GDA | [17 empty] | 1-03-05 | [7 empty] | 69KV_N | [8 empty] | 北港PS.920_GDA | 元長線(920) 接地RY | LINE69 | P04/69/920/GDA |  |  |  | CDC | 290 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | CB | [17 empty] | 1-03-03 |  | 1-45 | [5 empty] | 69KV_N | [8 empty] | 北港PS.920_CB | 920(元長線) CB | LINE69 | P04/69/920/CB |  |  |  | CDC | 291 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | ABS1 | 921 | [16 empty] | 1-36-08 | 1-36-09 | 1-46 | [5 empty] | ADCS_N | [8 empty] | 北港PS.921_ABS | 921(元長線) ABS | LINE69 | P04/69/920/ABS1 |  |  |  | CDC | 292 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | ABS2 | 922 | [16 empty] | 1-36-10 | 1-36-11 | 1-47 | [5 empty] | ADCS_N | [8 empty] | 北港PS.922_ABS | 922(元長線) ABS | LINE69 | P04/69/920/ABS2 |  |  |  | CDC | 293 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | ABS3 | 923 | [16 empty] | 1-36-12 | 1-36-13 | 1-48 | [5 empty] | ADCS_N | [8 empty] | 北港PS.923_ABS | 923(元長線) ABS | LINE69 | P04/69/920/ABS3 |  |  |  | CDC | 294 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | E3 | 923E | [16 empty] | 1-36-14 | 1-36-15 | 1-49 | [5 empty] | ADCS_N | [8 empty] | 北港PS.923E_ES | 923E(元長線) ES | LINE69 | P04/69/920/ES3 |  |  |  | CDC | 295 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | PHA | [17 empty] | 1-03-07 | [7 empty] | 69KV_N | [8 empty] | 北港PS.940_PHA | 北港東北線(940) 相間RY | LINE69 | P04/69/940/PHA |  |  |  | CDC | 296 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | GDA | [17 empty] | 1-04-00 | [7 empty] | 69KV_N | [8 empty] | 北港PS.940_GDA | 北港東北線(940) 接地RY | LINE69 | P04/69/940/GDA |  |  |  | CDC | 297 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | CB | [17 empty] | 1-03-06 |  | 1-36 | [5 empty] | 69KV_N | [8 empty] | 北港PS.940_CB | 940(北港東北線) CB | LINE69 | P04/69/940/CB |  |  |  | CDC | 298 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | ABS1 | 941 | [16 empty] | 1-38-00 | 1-38-01 | 1-37 | [5 empty] | ADCS_N | [8 empty] | 北港PS.941_ABS | 941(北港東北線) ABS | LINE69 | P04/69/940/ABS1 |  |  |  | CDC | 299 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | ABS2 | 942 | [16 empty] | 1-38-02 | 1-38-03 | 1-38 | [5 empty] | ADCS_N | [8 empty] | 北港PS.942_ABS | 942(北港東北線) ABS | LINE69 | P04/69/940/ABS2 |  |  |  | CDC | 300 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | ABS3 | 943 | [16 empty] | 1-38-04 | 1-38-05 | 1-39 | [5 empty] | ADCS_N | [8 empty] | 北港PS.943_ABS | 943(北港東北線) ABS | LINE69 | P04/69/940/ABS3 |  |  |  | CDC | 301 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | E3 | 943E | [16 empty] | 1-38-06 | 1-38-07 | 1-3A | [5 empty] | ADCS_N | [8 empty] | 北港PS.943E_ES | 943E(北港東北線) ES | LINE69 | P04/69/940/ES3 |  |  |  | CDC | 302 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | CB | [17 empty] | 1-09-01 |  | 1-6E | [5 empty] | 161KV_N | [8 empty] | 北港PS.1500_CB | 1500(TIE) CB | TIE | P04/161/1500/CB |  |  |  | CDC | 303 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 1500 | TIE(1500) |  | 50A | [17 empty] | 1-09-02 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1500_50A | 161KV TIE(1500) 50RY | TIE | P04/161/1500/50A |  |  |  | CDC | 304 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS1 | 1501 | [16 empty] | 1-32-08 | 1-32-09 | 1-6F | [5 empty] | ADCS_N | [8 empty] | 北港PS.1501_ABS | 1501(TIE) ABS | TIE | P04/161/1500/ABS1 |  |  |  | CDC | 305 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | ABS2 | 1502 | [16 empty] | 1-32-10 | 1-32-11 | 1-70 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1502_ABS | 1502(TIE) ABS | TIE | P04/161/1500/ABS2 |  |  |  | CDC | 306 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | CB | [17 empty] | 1-09-03 |  | 1-72 | [5 empty] | 69KV_N | [8 empty] | 北港PS.600_CB | 600(TIE) CB | TIE | P04/69/600/CB |  |  |  | CDC | 307 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | ABS1 | 601 | [16 empty] | 1-32-12 | 1-32-13 | 1-73 | [5 empty] | ADCS_N | [8 empty] | 北港PS.601_ABS | 601(TIE) ABS | TIE | P04/69/600/ABS1 |  |  |  | CDC | 308 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | ABS2 | 602 | [16 empty] | 1-32-14 | 1-32-15 | 1-74 | [5 empty] | ADCS_N | [8 empty] | 北港PS.602_ABS | 602(TIE) ABS | TIE | P04/69/600/ABS2 |  |  |  | CDC | 309 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | CB | [17 empty] | 1-07-00 |  | 1-4D | [5 empty] | 161KV_N | [8 empty] | 北港PS.1660_CB | 1660(#2MTR) CB | MTR | P04/161/1660/CB |  |  |  | CDC | 310 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | CB | [17 empty] | 1-07-01 |  | 1-4C | [5 empty] | 69KV_N | [8 empty] | 北港PS.760_CB | 760(#2MTR) CB | MTR | P04/69/760/CB |  |  |  | CDC | 311 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 51ZA | [17 empty] | 1-07-02 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#2MTR_51ZA | #2MTR 51Z RY | MTR | P04//2MTR/51ZA |  |  |  | CDC | 312 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 87A | [17 empty] | 1-06-04 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#2MTR_87A | #2MTR 87RY | MTR | P04//2MTR/87A |  |  |  | CDC | 313 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 96PA | [17 empty] | 1-06-07 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#2MTR_96PA | #2MTR 機械保護動作 | MTR | P04//2MTR/96PA |  |  |  | CDC | 314 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 96D | [17 empty] | 2-31-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_96D | #2MTR 96D RY | MTR | P04//2MTR/96D |  |  |  | CDC | 315 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 96P | [17 empty] | 2-31-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_96P | #2MTR 96P RY | MTR | P04//2MTR/96P |  |  |  | CDC | 316 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 63Q | [17 empty] | 2-31-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_63Q | #2MTR 63Q RY | MTR | P04//2MTR/63Q |  |  |  | CDC | 317 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 96B1 | [17 empty] | 2-31-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_96B1 | #2MTR 96B1 RY | MTR | P04//2MTR/96B1 |  |  |  | CDC | 318 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 96B2 | [17 empty] | 2-31-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_96B2 | #2MTR 96B2 RY | MTR | P04//2MTR/96B2 |  |  |  | CDC | 319 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | TRA | [17 empty] | 1-39-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_TRA | #2MTR 重故障 | MTR | P04//2MTR/TRA |  |  |  | CDC | 320 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | TRF | [17 empty] | 1-39-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_TRF | #2MTR 輕故障 | MTR | P04//2MTR/TRF |  |  |  | CDC | 321 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | SupLocal | [17 empty] | 1-39-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_S/L | #2MTR OLTC S/L | MTR | P04//2MTR/SupLocal |  |  |  | CDC | 322 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | A_M | [17 empty] | 1-39-02 |  | 1-50 | [5 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_A/M | #2MTR OLTC A/M | MTR | P04//2MTR/Tap Chan |  |  |  | CDC | 323 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | M/F/I | [17 empty] | 1-3B-06 | 1-3B-07 | 1-4A | [5 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_M/F/I | #2MTR M/F/I | MTR | P04//2MTR/M_F_I |  |  |  | CDC | 324 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS1 | 1661 | [16 empty] | 1-3B-12 | 1-3B-13 | 1-4E | [5 empty] | ADCS_N | [8 empty] | 北港PS.1661_ABS | 1661(#2MTR) ABS | MTR | P04/161/1660/ABS1 |  |  |  | CDC | 325 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | ABS2 | 1662 | [16 empty] | 1-3B-14 | 1-3B-15 | 1-4F | [5 empty] | ADCS_N | [8 empty] | 北港PS.1662_ABS | 1662(#2MTR) ABS | MTR | P04/161/1660/ABS2 |  |  |  | CDC | 326 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS1 | 761 | [16 empty] | 1-3B-08 | 1-3B-09 | 1-52 | [5 empty] | ADCS_N | [8 empty] | 北港PS.761_ABS | 761(#2MTR) ABS | MTR | P04/69/760/ABS1 |  |  |  | CDC | 327 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | ABS2 | 762 | [16 empty] | 1-3B-10 | 1-3B-11 | 1-53 | [5 empty] | ADCS_N | [8 empty] | 北港PS.762_ABS | 762(#2MTR) ABS | MTR | P04/69/760/ABS2 |  |  |  | CDC | 328 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | CB | [17 empty] | 1-07-07 |  | 1-56 | [5 empty] | 161KV_N | [8 empty] | 北港PS.1670_CB | 1670(#3MTR) CB | MTR | P04/161/1670/CB |  |  |  | CDC | 329 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | CB | [17 empty] | 1-08-00 |  | 1-57 | [5 empty] | 69KV_N | [8 empty] | 北港PS.770_CB | 770(#3MTR) CB | MTR | P04/69/770/CB |  |  |  | CDC | 330 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 51ZA | [17 empty] | 1-08-01 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#3MTR_51ZA | #3MTR 51Z RY | MTR | P04//3MTR/51ZA |  |  |  | CDC | 331 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 87A | [17 empty] | 1-07-03 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#3MTR_87A | #3MTR 87RY | MTR | P04//3MTR/87A |  |  |  | CDC | 332 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 96PA | [17 empty] | 1-07-06 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#3MTR_96PA | #3MTR 機械保護動作 | MTR | P04//3MTR/96PA |  |  |  | CDC | 333 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 96D | [17 empty] | 2-31-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_96D | #3MTR 96D RY | MTR | P04//3MTR/96D |  |  |  | CDC | 334 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 96P | [17 empty] | 2-31-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_96P | #3MTR 96P RY | MTR | P04//3MTR/96P |  |  |  | CDC | 335 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 63Q | [17 empty] | 2-31-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_63Q | #3MTR 63Q RY | MTR | P04//3MTR/63Q |  |  |  | CDC | 336 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 96B1 | [17 empty] | 2-31-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_96B1 | #3MTR 96B1 RY | MTR | P04//3MTR/96B1 |  |  |  | CDC | 337 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 96B2 | [17 empty] | 2-31-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_96B2 | #3MTR 96B2 RY | MTR | P04//3MTR/96B2 |  |  |  | CDC | 338 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | TRA | [17 empty] | 1-39-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_TRA | #3MTR 重故障 | MTR | P04//3MTR/TRA |  |  |  | CDC | 339 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | TRF | [17 empty] | 1-3A-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_TRF | #3MTR 輕故障 | MTR | P04//3MTR/TRF |  |  |  | CDC | 340 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | SupLocal | [17 empty] | 1-3A-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_S/L | #3MTR OLTC S/L | MTR | P04//3MTR/SupLocal |  |  |  | CDC | 341 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | A_M | [17 empty] | 1-3A-01 |  | 1-5A | [5 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_A/M | #3MTR OLTC A/M | MTR | P04//3MTR/Tap Chan |  |  |  | CDC | 342 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | M/F/I | [17 empty] | 1-39-06 | 1-39-07 | 1-54 | [5 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_M/F/I | #3MTR M/F/I | MTR | P04//3MTR/M_F_I |  |  |  | CDC | 343 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS1 | 1671 | [16 empty] | 1-39-08 | 1-39-09 | 1-58 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1671_ABS | 1671(#3MTR) ABS | MTR | P04/161/1670/ABS1 |  |  |  | CDC | 344 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | ABS2 | 1672 | [16 empty] | 1-39-10 | 1-39-11 | 1-59 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1672_ABS | 1672(#3MTR) ABS | MTR | P04/161/1670/ABS2 |  |  |  | CDC | 345 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS1 | 771 | [16 empty] | 1-39-12 | 1-39-13 | 1-5C | [5 empty] | ADCS_N | [8 empty] | 北港PS.771_ABS | 771(#3MTR) ABS | MTR | P04/69/770/ABS1 |  |  |  | CDC | 346 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | ABS2 | 772 | [16 empty] | 1-39-14 | 1-39-15 | 1-5D | [5 empty] | ADCS_N | [8 empty] | 北港PS.772_ABS | 772(#3MTR) ABS | MTR | P04/69/770/ABS2 |  |  |  | CDC | 347 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | CB | [17 empty] | 1-08-06 |  | 1-60 | [5 empty] | 161KV_N | [8 empty] | 北港PS.1680_CB | 1680(#4MTR) CB | MTR | P04/161/1680/CB |  |  |  | CDC | 348 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | CB | [17 empty] | 1-08-07 |  | 1-61 | [5 empty] | 69KV_N | [8 empty] | 北港PS.780_CB | 780(#4MTR) CB | MTR | P04/69/780/CB |  |  |  | CDC | 349 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 51ZA | [17 empty] | 1-09-00 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#4MTR_51ZA | #4MTR 51Z RY | MTR | P04//4MTR/51ZA |  |  |  | CDC | 350 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 87A | [17 empty] | 1-08-02 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#4MTR_87A | #4MTR 87RY | MTR | P04//4MTR/87A |  |  |  | CDC | 351 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 96PA | [17 empty] | 1-08-05 | [7 empty] | 161KV_N | [8 empty] | 北港PS.#4MTR_96PA | #4MTR 機械保護動作 | MTR | P04//4MTR/96PA |  |  |  | CDC | 352 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 96D | [17 empty] | 2-31-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_96D | #4MTR 96D RY | MTR | P04//4MTR/96D |  |  |  | CDC | 353 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 96P | [17 empty] | 2-31-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_96P | #4MTR 96P RY | MTR | P04//4MTR/96P |  |  |  | CDC | 354 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 63Q | [17 empty] | 2-31-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_63Q | #4MTR 63Q RY | MTR | P04//4MTR/63Q |  |  |  | CDC | 355 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 96B1 | [17 empty] | 2-31-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_96B1 | #4MTR 96B1 RY | MTR | P04//4MTR/96B1 |  |  |  | CDC | 356 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 96B2 | [17 empty] | 2-31-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_96B2 | #4MTR 96B2 RY | MTR | P04//4MTR/96B2 |  |  |  | CDC | 357 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | TRA | [17 empty] | 1-3A-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_TRA | #4MTR 重故障 | MTR | P04//4MTR/TRA |  |  |  | CDC | 358 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | TRF | [17 empty] | 1-3A-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_TRF | #4MTR 輕故障 | MTR | P04//4MTR/TRF |  |  |  | CDC | 359 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | SupLocal | [17 empty] | 1-3C-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_S/L | #4MTR OLTC S/L | MTR | P04//4MTR/SupLocal |  |  |  | CDC | 360 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | SUPERVISORY/LOCAL | SUPERVISORY
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | A_M | [17 empty] | 1-3C-00 |  | 1-64 | [5 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_A/M | #4MTR OLTC A/M | MTR | P04//4MTR/Tap Chan |  |  |  | CDC | 361 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | AUTO/MANUAL | AUTO
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | M/F/I | [17 empty] | 1-3A-04 | 1-3A-05 | 1-5E | [5 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_M/F/I | #4MTR M/F/I | MTR | P04//4MTR/M_F_I |  |  |  | CDC | 362 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/FOLLOW/MASTER/INDEPENDENT | MASTER
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | ABS1 | 1681 | [16 empty] | 1-3A-06 | 1-3A-07 | 1-62 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1681_ABS | 1681(#4MTR) ABS | MTR | P04/161/1680/ABS1 |  |  |  | CDC | 363 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | ABS2 | 1682 | [16 empty] | 1-3A-08 | 1-3A-09 | 1-63 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1682_ABS | 1682(#4MTR) ABS | MTR | P04/161/1680/ABS2 |  |  |  | CDC | 364 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | ABS1 | 781 | [16 empty] | 1-3A-10 | 1-3A-11 | 1-66 | [5 empty] | ADCS_N | [8 empty] | 北港PS.781_ABS | 781(#4MTR) ABS | MTR | P04/69/780/ABS1 |  |  |  | CDC | 365 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | ABS2 | 782 | [16 empty] | 1-3A-12 | 1-3A-13 | 1-67 | [5 empty] | ADCS_N | [8 empty] | 北港PS.782_ABS | 782(#4MTR) ABS | MTR | P04/69/780/ABS2 |  |  |  | CDC | 366 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | CB | [17 empty] | 1-04-03 |  | 1-68 | [5 empty] | 69KV_N | [8 empty] | 北港PS.820_CB | 820(69KV #2SC) CB | SC | P04/69/820/CB |  |  |  | CDC | 367 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | ABS1 | 821 | [16 empty] | 1-38-08 | 1-38-09 | 1-69 | [5 empty] | ADCS_N | [8 empty] | 北港PS.821_ABS | 821(69KV #2SC) ABS | SC | P04/69/820/ABS1 |  |  |  | CDC | 368 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | ABS2 | 822 | [16 empty] | 1-38-10 | 1-38-11 | 1-6A | [5 empty] | ADCS_N | [8 empty] | 北港PS.822_ABS | 822(69KV #2SC) ABS | SC | P04/69/820/ABS2 |  |  |  | CDC | 369 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | SCA | [17 empty] | 1-04-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.820_SCA | 69KV #2SC 51,51N RY | SC | P04/69/820/SCA |  |  |  | CDC | 370 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 820 | #2SC(820) |  | UVA | [17 empty] | 1-04-02 | [7 empty] | 69KV_N | [8 empty] | 北港PS.820_OUVA | 69KV #2SC 27,59RY | SC | P04/69/820/UVA |  |  |  | CDC | 371 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | CB | [17 empty] | 1-04-06 |  | 1-6B | [5 empty] | 69KV_N | [8 empty] | 北港PS.830_CB | 830(69KV #3SC) CB | SC | P04/69/830/CB |  |  |  | CDC | 372 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | ABS1 | 831 | [16 empty] | 1-38-12 | 1-38-13 | 1-6C | [5 empty] | ADCS_N | [8 empty] | 北港PS.831_ABS | 831(69KV #3SC) ABS | SC | P04/69/830/ABS1 |  |  |  | CDC | 373 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | ABS2 | 832 | [16 empty] | 1-38-14 | 1-38-15 | 1-6D | [5 empty] | ADCS_N | [8 empty] | 北港PS.832_ABS | 832(69KV #3SC) ABS | SC | P04/69/830/ABS2 |  |  |  | CDC | 374 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | SCA | [17 empty] | 1-04-04 | [7 empty] | 69KV_N | [8 empty] | 北港PS.830_SCA | 69KV #3SC 51,51N RY | SC | P04/69/830/SCA |  |  |  | CDC | 375 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 830 | #3SC(830) |  | UVA | [17 empty] | 1-04-05 | [7 empty] | 69KV_N | [8 empty] | 北港PS.830_OUVA | 69KV #3SC 27,59RY | SC | P04/69/830/UVA |  |  |  | CDC | 376 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611BUS | #1BUS |  | VUA | [17 empty] | 1-3C-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1BUS_VUA | 161KV #1BUS 衡相RY | BUS | P04/161/1BUS/BUS_VUA |  |  |  | CDC | 377 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611BUS | #1BUS |  | 87A | [17 empty] | 1-09-06 | [7 empty] | 161KV_N | [8 empty] | 北港PS.161#1BUS_87A | 161KV #1BUS 87A | BUS | P04/161/1BUS/87A |  |  |  | CDC | 378 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611BUS | #1BUS |  | 87UL | [17 empty] | 1-3C-07 |  | 2-45 | [5 empty] | ADCS_N | [8 empty] | 北港PS.161#1BUS_87UL | 161KV #1BUS 87RY U/L | OTHER | P04/161/1BUS/87UL |  |  |  | CDC | 379 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1612BUS | #2BUS |  | VUA | [17 empty] | 1-3C-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2BUS_VUA | 161KV #2BUS 衡相RY | BUS | P04/161/2BUS/BUS_VUA |  |  |  | CDC | 380 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612BUS | #2BUS |  | 87A | [17 empty] | 1-09-07 | [7 empty] | 161KV_N | [8 empty] | 北港PS.161#2BUS_87A | 161KV #2BUS 87A | BUS | P04/161/2BUS/87A |  |  |  | CDC | 381 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612BUS | #2BUS |  | 87UL | [17 empty] | 1-3C-08 |  | 2-46 | [5 empty] | ADCS_N | [8 empty] | 北港PS.161#2BUS_87UL | 161KV #2BUS 87RY U/L | OTHER | P04/161/2BUS/87UL |  |  |  | CDC | 382 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 691BUS | #1BUS |  | VUA | [17 empty] | 1-3C-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69#1BUS_VUA | 69KV #1BUS 衡相RY | BUS | P04/69/1BUS/BUS_VUA |  |  |  | CDC | 383 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 691BUS | #1BUS |  | 87A | [17 empty] | 1-0A-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.69#1BUS_87A | 69KV #1BUS 87A | BUS | P04/69/1BUS/87A |  |  |  | CDC | 384 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 691BUS | #1BUS |  | 87UL | [17 empty] | 1-3C-09 |  | 2-43 | [5 empty] | ADCS_N | [8 empty] | 北港PS.69#1BUS_87UL | 69KV #1BUS 87RY U/L | OTHER | P04/69/1BUS/87UL |  |  |  | CDC | 385 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 692BUS | #2BUS |  | VUA | [17 empty] | 1-3C-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69#2BUS_VUA | 69KV #2BUS 衡相RY | BUS | P04/69/2BUS/BUS_VUA |  |  |  | CDC | 386 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 692BUS | #2BUS |  | 87A | [17 empty] | 1-0A-02 | [7 empty] | 69KV_N | [8 empty] | 北港PS.69#2BUS_87A | 69KV #2BUS 87A | BUS | P04/69/2BUS/87A |  |  |  | CDC | 387 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 692BUS | #2BUS |  | 87UL | [17 empty] | 1-3C-10 |  | 2-44 | [5 empty] | ADCS_N | [8 empty] | 北港PS.69#2BUS_87UL | 69KV #2BUS 87RY U/L | OTHER | P04/69/2BUS/87UL |  |  |  | CDC | 388 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-3E-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_ABS_89A | 161KV ABS NFB 跳脫警報 | OTHER | P04/161/ComPoint/ABS_89A |  |  |  | CDC | 389 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV |  |  |  | CBA | [17 empty] | 1-3D-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_CBA | 161KV斷路器重故障 | OTHER | P04/161/ComPoint/CBA |  |  |  | CDC | 390 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV |  |  |  | CBF | [17 empty] | 1-3D-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_CBF | 161KV斷路器輕故障 | OTHER | P04/161/ComPoint/CBF |  |  |  | CDC | 391 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | LINE | LINE |  | RCA | [17 empty] | 1-0A-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_RCA | 161KV LINE 79RY(復閉)動作 | OTHER | P04/161/ComPoint/RCA |  |  |  | CDC | 392 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | _ABS | ABS |  | ABS_89A | [17 empty] | 1-3E-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_ABS_89A | 69KV ABS NFB 跳脫警報 | OTHER | P04/69/ComPoint/ABS_89A |  |  |  | CDC | 393 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV |  |  |  | CBA | [17 empty] | 1-3D-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_CBA | 69KV斷路器重故障 | OTHER | P04/69/ComPoint/CBA |  |  |  | CDC | 394 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV |  |  |  | CBF | [17 empty] | 1-3D-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_CBF | 69KV斷路器輕故障 | OTHER | P04/69/ComPoint/CBF |  |  |  | CDC | 395 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | OSCA | [17 empty] | 1-0A-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.OSC啟動 | 示波器啟動警報 | OTHER | P04/161/ComPoint/OSCA |  |  |  | CDC | 396 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | RTU | RTU |  | SupLocal | [17 empty] | 1-30-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.RTU_S/L | RTU SUPY/LOCAL | OTHER | P04/0/RTU/RTU_R_L |  |  |  | CDC | 397 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | LOCAL/SUPERVISORY | SUPERVISORY
P04 | 北港PS | 0 |  | TEST | TEST |  | CB | [17 empty] | 1-30-00 |  | 1-00 | [5 empty] | ADCS_N | [8 empty] | 北港PS.TEST_CB | TEST CB | OTHER | P04/0/RTU/Test_CB |  |  |  | CDC | 398 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  |  |  |  | Fire1 | [17 empty] | 1-3D-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.火災警報(1) | 火災警報(1)受信總機 | OTHER | P04/0/StaDev/Fire1 |  |  |  | CDC | 399 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | Fire2 | [17 empty] | 1-3E-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.火災警報(2) | 火災警報(2)建物-控制大樓CO2 | OTHER | P04/0/StaDev/Fire2 |  |  |  | CDC | 400 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | 25PFA | [17 empty] | 1-3C-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.同步電驛25PFA | 同步校核電驛電源故障警報 | OTHER | P04/0/ComPoint/25PFA |  |  |  | CDC | 401 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | 25TA | [17 empty] | 1-3C-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.同步電驛25TA | 同步校核電驛超時動作警報 | OTHER | P04/0/ComPoint/25TA |  |  |  | CDC | 402 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | ACB1 | [17 empty] | 1-3C-11 |  | 2-06 | [5 empty] | ADCS_N | [8 empty] | 北港PS.所內電源ACB1 | 所內電源開關ACB1 | OTHER | P04/0/StaDev/ACB1 |  |  |  | CDC | 403 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P04 | 北港PS | 0 |  |  |  |  | ACB2 | [17 empty] | 1-3C-12 |  | 2-07 | [5 empty] | ADCS_N | [8 empty] | 北港PS.所內電源ACB2 | 所內電源開關ACB2 | OTHER | P04/0/StaDev/ACB2 |  |  |  | CDC | 404 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | ON
P04 | 北港PS | 0 |  | 所內電源開關ACB | 所內電源開關ACB |  | ACBT | [17 empty] | 1-3C-13 |  | 2-08 | [5 empty] | ADCS_N | [8 empty] | 北港PS.所內電源ACBT | 所內電源開關ACB TIE | OTHER | P04/0/StaDev/ACBT |  |  |  | CDC | 405 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 0 |  |  |  |  | STUV | [17 empty] | 1-3E-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.所內電源欠壓 | 所內電源欠壓警報 | OTHER | P04/0/StaDev/STUV |  |  |  | CDC | 406 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | DCA | [17 empty] | 1-3E-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.直流電源DCA | 直流電源故障警報 | OTHER | P04/0/StaDev/DCA |  |  |  | CDC | 407 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | DCE | [17 empty] | 1-3D-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.直流電源DCE | 直流電源接地故障警報 | OTHER | P04/0/StaDev/DCE |  |  |  | CDC | 408 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | CommACF | [17 empty] | 2-33-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.通訊設備AC故障 | 通訊設備AC故障 | OTHER | P04/0/StaDev/CommACF |  |  |  | CDC | 409 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | Burglar1 | [17 empty] | 1-3E-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.無人化防盜(1) | 無人化防盜(1)控制室保全 | OTHER | P04/0/StaDev/Burglar1 |  |  |  | CDC | 410 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | Burglar2 | [17 empty] | 1-3E-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.無人化防盜(2) | 無人化防盜(2)圍牆保全 | OTHER | P04/0/StaDev/Burglar2 |  |  |  | CDC | 411 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | Door1 | [17 empty] | 1-3D-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.無人化門禁(1) | 無人化門禁(1)變電所大門 | OTHER | P04/0/StaDev/Door1 |  |  |  | CDC | 412 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  |  |  |  | Door2 | [17 empty] | 1-3D-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.無人化門禁(2) | 無人化門禁(2)控制室大門 | OTHER | P04/0/StaDev/Door2 |  |  |  | CDC | 413 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  |  |  |  | Lights1 | [17 empty] | 1-3D-05 |  | 2-09 | [5 empty] | ADCS_N | [8 empty] | 北港PS.開關場照明(A) | 161KV開關場照明(1) | OTHER | P04/0/StaDev/Lights1 |  |  |  | CDC | 414 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 0 |  |  |  |  | Lights2 | [17 empty] | 1-3D-06 |  | 2-0A | [5 empty] | ADCS_N | [8 empty] | 北港PS.開關場照明(B) | 161KV開關場照明(2) | OTHER | P04/0/StaDev/Lights2 |  |  |  | CDC | 415 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 0 |  |  |  |  | Lights3 | [17 empty] | 1-3D-07 |  | 2-0B | [5 empty] | ADCS_N | [8 empty] | 北港PS.開關場照明(C) | 69KV開關場照明(1) | OTHER | P04/0/StaDev/Lights3 |  |  |  | CDC | 416 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 0 |  |  |  |  | Lights4 | [17 empty] | 1-3D-08 |  | 2-0C | [5 empty] | ADCS_N | [8 empty] | 北港PS.開關場照明(D) | 69KV開關場照明(2) | OTHER | P04/0/StaDev/Lights4 |  |  |  | CDC | 417 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 0 |  | 1560 | 台西二路(1560) |  | MDARF | [17 empty] | 2-30-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1560_MDARF | 1560 MDAR RY故障 | OTHER | P04/161/1560/1A5Other |  |  |  | CDC | 418 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1560 | 台西二路(1560) |  | TONEF | [17 empty] | 2-30-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1560_TONEF | 1560 TONE訊號不良 | OTHER | P04/161/1560/85CFA |  |  |  | CDC | 419 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | 空調機跳脫警報 | [17 empty] | 1-3E-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.空調機跳脫警報 | 空調機故障或電源跳脫 | OTHER | P04/0/StaDev/AIRCON |  |  |  | CDC | 420 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | NORMAL/FAULT | NORMAL
P04 | 北港PS | 0 |  |  |  |  | 水位警報(1) | [17 empty] | 1-3E-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.水位警報(1) | 地下室水位警報(1) | OTHER | P04/0/StaDev/Water1 |  |  |  | CDC | 421 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | 水位警報(2) | [17 empty] | 1-3E-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.水位警報(2) | 地下室水位警報(2) | OTHER | P04/0/StaDev/Water2 |  |  |  | CDC | 422 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | CHG1 | [17 empty] | 1-3D-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.直流充電機故障 | #1,#2直流充電機故障 | OTHER | P04/0/StaDev/CHG1 |  |  |  | CDC | 423 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | CHG2 | [17 empty] | 1-3D-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.通訊充電機故障 | 變電所通訊充電機故障 | OTHER | P04/0/StaDev/CHG2 |  |  |  | CDC | 424 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1500TIE | 1500 |  | 50SA | [17 empty] | 1-3D-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1500TIE_50SA | 161KV TIE(1500) 50RY 測試/正常 | OTHER | P04/161/1500/50SA |  |  |  | CDC | 425 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | TEST/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | 通信機房溫度 | [17 empty] | 2-33-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.通信機房溫度 | 通信機房溫度警報 | OTHER | P04/0/StaDev/R_Temp |  |  |  | CDC | 426 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV |  |  |  | OSCF | [17 empty] | 2-33-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_OSCF | 161KV示波器故障/缺紙,電源跳脫 | OTHER | P04/161/ComPoint/OSCF |  |  |  | CDC | 427 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV |  |  |  | OSCA | [17 empty] | 1-0A-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_OSCA | 69KV示波器啟動 | OTHER | P04/69/ComPoint/OSCA |  |  |  | CDC | 428 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV |  |  |  | OSCF | [17 empty] | 2-33-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_OSCF | 69KV示波器故障/缺紙,電源跳脫 | OTHER | P04/69/ComPoint/OSCF |  |  |  | CDC | 429 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | PHA | [17 empty] | 1-00-04 | [7 empty] | 69KV_N | [8 empty] | 北港PS.620_PHA | 北港水林二路(620) 相間RY | LINE69 | P04/69/620/PHA |  |  |  | CDC | 430 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | GDA | [17 empty] | 1-00-05 | [7 empty] | 69KV_N | [8 empty] | 北港PS.620_GDA | 北港水林二路(620) 接地RY | LINE69 | P04/69/620/GDA |  |  |  | CDC | 431 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | CB | [17 empty] | 1-00-03 |  | 1-18 | [5 empty] | 69KV_N | [8 empty] | 北港PS.620_CB | 620(北港水林二路) CB | LINE69 | P04/69/620/CB |  |  |  | CDC | 432 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | ABS1 | 621 | [16 empty] | 1-33-08 | 1-33-09 | 1-19 | [5 empty] | ADCS_N | [8 empty] | 北港PS.621_ABS | 621(北港水林二路) ABS | LINE69 | P04/69/620/ABS1 |  |  |  | CDC | 433 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | ABS2 | 622 | [16 empty] | 1-33-10 | 1-33-11 | 1-1A | [5 empty] | ADCS_N | [8 empty] | 北港PS.622_ABS | 622(北港水林二路) ABS | LINE69 | P04/69/620/ABS2 |  |  |  | CDC | 434 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | ABS3 | 623 | [16 empty] | 1-33-12 | 1-33-13 | 1-1B | [5 empty] | ADCS_N | [8 empty] | 北港PS.623_ABS | 623(北港水林二路) ABS | LINE69 | P04/69/620/ABS3 |  |  |  | CDC | 435 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | E3 | 623E | [16 empty] | 1-33-14 | 1-33-15 | 1-1C | [5 empty] | ADCS_N | [8 empty] | 北港PS.623E_ES | 623E(北港水林二路) ES | LINE69 | P04/69/620/ES3 |  |  |  | CDC | 436 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | 87A | [17 empty] | 1-05-05 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1630_87A | 嘉民南線(1630) 87RY | LINE161 | P04/161/1630/87A |  |  |  | CDC | 437 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | 87UL | [17 empty] | 1-3B-04 |  | 2-05 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1630_87UL | 嘉民南線(1630) 87RY U/L | LINE161 | P04/161/1630/87UL |  |  |  | CDC | 438 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1630 | 嘉民南線(1630) |  | 87CFA | [17 empty] | 1-3E-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1630_87CFA | 北港嘉民南線(1630)87RY通訊故障 | OTHER | P04/161/1630/87CFA |  |  |  | CDC | 439 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1630 | 嘉民南線(1630) |  | DTTA | [17 empty] | 1-0B-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1630_DTTA | 北港嘉民南線(1630)遠方遙跳 | OTHER | P04/161/1630/DTTA |  |  |  | CDC | 440 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1630 | 嘉民南線(1630) |  | RYFA | [17 empty] | 2-33-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1630_RYFA | 北港嘉民南線(1630)數位電驛故障 | OTHER | P04/161/1630/RYFA |  |  |  | CDC | 441 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | 87A | [17 empty] | 1-06-01 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1640_87A | 嘉民北線(1640) 87RY | LINE161 | P04/161/1640/87A |  |  |  | CDC | 442 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | 87UL | [17 empty] | 1-3B-02 |  | 2-03 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1640_87UL | 嘉民北線(1640) 87RY U/L | LINE161 | P04/161/1640/87UL |  |  |  | CDC | 443 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1640 | 嘉民北線(1640) |  | 87CFA | [17 empty] | 1-3E-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1640_87CFA | 北港嘉民北線(1640)87RY通訊故障 | OTHER | P04/161/1640/87CFA |  |  |  | CDC | 444 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1640 | 嘉民北線(1640) |  | DTTA | [17 empty] | 1-0B-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1640_DTTA | 北港嘉民北線(1640)遠方遙跳 | OTHER | P04/161/1640/DTTA |  |  |  | CDC | 445 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1640 | 嘉民北線(1640) |  | RYFA | [17 empty] | 2-33-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1640_RYFA | 北港嘉民北線(1640)數位電驛故障 | OTHER | P04/161/1640/RYFA |  |  |  | CDC | 446 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1570 | 雲林北港雲高線(1570) |  | 87CFA | [17 empty] | 2-33-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1570_87CFA | 雲林北港雲高線(1570)RY通訊故障 | OTHER | P04/161/1570/87CFA |  |  |  | CDC | 447 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1570 | 雲林北港雲高線(1570) |  | RYFA | [17 empty] | 2-33-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1570_RYFA | 雲林北港雲高線(1570)數位RY故障 | OTHER | P04/161/1570/RYFA |  |  |  | CDC | 448 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | 87A2 | [17 empty] | 1-0C-06 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1570_87A2 | 雲林北港雲高線(1570) #2 87RY | LINE161 | P04/161/1570/87A2 |  |  |  | CDC | 449 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | 87A1 | [17 empty] | 1-05-01 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1570_87A1 | 雲林北港雲高線(1570) #1 87RY | LINE161 | P04/161/1570/87A1 |  |  |  | CDC | 450 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | 1_87UL2 | [17 empty] | 1-3B-00 |  | 2-01 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1570_87UL2 | 雲林北港雲高線(1570)#287RY U/L | LINE161 | P04/161/1570/87UL |  |  |  | CDC | 451 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | 1_87UL1 | [17 empty] | 2-33-12 |  | 2-2C | [5 empty] | ADCS_N | [8 empty] | 北港PS.1570_87UL1 | 雲林北港雲高線(1570)#187RY U/L | LINE161 | P04/161/1570/1_87UL1 |  |  |  | CDC | 452 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | 87A2 | [17 empty] | 1-0C-07 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1580_87A2 | 北港台西線(1580) #2 87RY | LINE161 | P04/161/1580/87A2 |  |  |  | CDC | 453 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | 87A1 | [17 empty] | 1-0B-01 | [7 empty] | 161KV_N | [8 empty] | 北港PS.1580_87A1 | 北港台西線(1580) #1 87RY | LINE161 | P04/161/1580/87A1 |  |  |  | CDC | 454 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | 1_87UL2 | [17 empty] | 1-30-06 |  | 2-0F | [5 empty] | ADCS_N | [8 empty] | 北港PS.1580_87UL2 | 北港台西線(1580) #2 87RY U/L | LINE161 | P04/161/1580/87UL |  |  |  | CDC | 455 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | 1_87UL1 | [17 empty] | 2-33-13 |  | 2-2D | [5 empty] | ADCS_N | [8 empty] | 北港PS.1580_87UL1 | 北港台西線(1580) #1 87RY U/L | LINE161 | P04/161/1580/1_87UL1 |  |  |  | CDC | 456 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1580 | 北港台西線(1580) |  | 87CFA | [17 empty] | 2-33-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1580_87CFA | 北港台西線(1580)87RY通訊故障 | OTHER | P04/161/1580/87CFA |  |  |  | CDC | 457 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1580 | 北港台西線(1580) |  | RYFA | [17 empty] | 2-33-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1580_RYFA | 北港台西線(1580)數位電驛故障 | OTHER | P04/161/1580/RYFA |  |  |  | CDC | 458 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1SHR | #1SHR |  | 161#1SHR96PA | [17 empty] | 2-01-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR96PA | 161KV #1SHR 機械保護動作 | OTHER | P04/161/1950/96PA |  |  |  | CDC | 459 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 51A | [17 empty] | 2-01-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_51A | 161KV #1SHR 51RY | OTHER | P04/161/1950/51A |  |  |  | CDC | 460 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 86A | [17 empty] | 2-01-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_86A | 161KV #1SHR 86RY | OTHER | P04/161/1950/MTR_86A |  |  |  | CDC | 461 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 87A | [17 empty] | 2-01-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_87A | 161KV #1SHR 87RY | OTHER | P04/161/1950/87A |  |  |  | CDC | 462 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 1_87UL1 | [17 empty] | 2-38-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_87UL1 | 161KV #1SHR #187RY U/L | OTHER | P04/161/1950/1_87UL1 |  |  |  | CDC | 463 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 1_87UL2 | [17 empty] | 2-38-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_87UL2 | 161KV #1SHR #287RY U/L | OTHER | P04/161/1950/1_87UL2 |  |  |  | CDC | 464 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 96B1 | [17 empty] | 2-39-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_96B1 | 161KV #1SHR 96B1 RY | OTHER | P04/161/1950/96B1 |  |  |  | CDC | 465 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 96B2 | [17 empty] | 2-39-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_96B2 | 161KV #1SHR 96B2 RY | OTHER | P04/161/1950/96B2 |  |  |  | CDC | 466 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 96D | [17 empty] | 2-39-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_96D | 161KV #1SHR 96D RY | OTHER | P04/161/1950/96D |  |  |  | CDC | 467 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | 96P | [17 empty] | 2-39-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_96P | 161KV #1SHR 96P RY | OTHER | P04/161/1950/96P |  |  |  | CDC | 468 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | SHRA | [17 empty] | 2-39-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_SRA | 161KV #1SHR 重故障 | OTHER | P04/161/1950/SHRA |  |  |  | CDC | 469 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1611SHR | #1SHR |  | SRF | [17 empty] | 2-39-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#1SHR_SRF | 161KV #1SHR 輕故障 | OTHER | P04/161/1950/SHRF |  |  |  | CDC | 470 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 161_1SHR | 161_1SHR |  | RYFA | [17 empty] | 2-39-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161_1SHR_RYFA | 161KV 1SHR(1950)數位電驛故障 | OTHER | P04/161/1950/RYFA |  |  |  | CDC | 471 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | CB | [17 empty] | 2-01-02 |  | 2-4A | [5 empty] | ADCS_N | [8 empty] | 北港PS.1950_CB | 1950(161KV #1SHR) CB | OTHER | P04/161/1950/CB |  |  |  | CDC | 472 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS1 | 1951 | [16 empty] | 2-3F-00 | 2-3F-01 | 2-60 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1951_ABS | 1951(161KV #1SHR) ABS | OTHER | P04/161/1950/ABS1 |  |  |  | CDC | 473 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 161 | 161kV | 1950 | #1SHR(1950) |  | ABS2 | 1952 | [16 empty] | 2-3F-02 | 2-3F-03 | 2-61 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1952_ABS | 1952(161KV #1SHR) ABS | OTHER | P04/161/1950/ABS2 |  |  |  | CDC | 474 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV |  |  |  | LPDA | [17 empty] | 2-34-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_LPDA | 161KV LPD電壓偵測 | OTHER | P04/161/ComPoint/LPDA |  |  |  | CDC | 475 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | Fire4 | [17 empty] | 1-3D-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.火災警報(4) | 火災警報(4)#4MTR | OTHER | P04/0/StaDev/Fire4 |  |  |  | CDC | 476 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | 87A | [17 empty] | 1-15-00 | [7 empty] | 69KV_N | [8 empty] | 北港PS.670_87A | 北港新港一路(670) 87RY | LINE69 | P04/69/670/87A |  |  |  | CDC | 477 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | 87UL | [17 empty] | 2-34-12 |  | 2-30 | [5 empty] | ADCS_N | [8 empty] | 北港PS.670_87UL | 北港新港一路(670) 87RY U/L | LINE69 | P04/69/670/87UL |  |  |  | CDC | 478 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | 87A | [17 empty] | 1-15-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.680_87A | 北港新港二路(680) 87RY | LINE69 | P04/69/680/87A |  |  |  | CDC | 479 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | 87UL | [17 empty] | 2-34-15 |  | 2-31 | [5 empty] | ADCS_N | [8 empty] | 北港PS.680_87UL | 北港新港二路(680) 87RY U/L | LINE69 | P04/69/680/87UL |  |  |  | CDC | 480 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 670 | 北港新港一路(670) |  | 87CFA | [17 empty] | 2-34-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.670_87CFA | 北港新港ㄧ路(670)87RY通訊故障 | OTHER | P04/69/670/87CFA |  |  |  | CDC | 481 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 670 | 北港新港一路(670) |  | RYFA | [17 empty] | 2-34-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.670_RYFA | 北港新港ㄧ路(670)數位電驛故障 | OTHER | P04/69/670/RYFA |  |  |  | CDC | 482 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 680 | 北港新港二路(680) |  | 87CFA | [17 empty] | 2-34-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.680_87CFA | 北港新港二路(680)87RY通訊故障 | OTHER | P04/69/680/87CFA |  |  |  | CDC | 483 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 680 | 北港新港二路(680) |  | RYFA | [17 empty] | 2-34-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.680_RYFA | 北港新港二路(680)數位電驛故障 | OTHER | P04/69/680/RYFA |  |  |  | CDC | 484 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | GEN | [17 empty] | 2-31-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.GEN | 緊急發電機運轉 | OTHER | P04/0/StaDev/2A5Other |  |  |  | CDC | 485 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | 87A | [17 empty] | 1-0E-06 | [7 empty] | 69KV_N | [8 empty] | 北港PS.940_87A | 北港東北線(940) 87RY | LINE69 | P04/69/940/87A |  |  |  | CDC | 486 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | 87UL | [17 empty] | 2-35-13 |  | 2-33 | [5 empty] | ADCS_N | [8 empty] | 北港PS.940_87UL | 北港東北線(940) 87RY U/L | LINE69 | P04/69/940/87UL |  |  |  | CDC | 487 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 940 | 北港東北線(940) |  | 87CFA | [17 empty] | 2-35-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.940_87CFA | 北港東北線(940)87RY通訊故障 | OTHER | P04/69/940/87CFA |  |  |  | CDC | 488 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 940 | 北港東北線(940) |  | RYFA | [17 empty] | 2-35-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.940_RYFA | 北港東北線(940)數位電驛故障 | OTHER | P04/69/940/RYFA |  |  |  | CDC | 489 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | 87A | [17 empty] | 1-0E-05 | [7 empty] | 69KV_N | [8 empty] | 北港PS.920_87A | 元長線(920) 87RY | LINE69 | P04/69/920/87A |  |  |  | CDC | 490 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | 87UL | [17 empty] | 1-3E-08 |  | 2-0D | [5 empty] | ADCS_N | [8 empty] | 北港PS.920_87UL | 元長線(920) 87RY U/L | LINE69 | P04/69/920/87UL |  |  |  | CDC | 491 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 920 | 元長線(920) |  | 87CFA | [17 empty] | 1-3E-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.920_87CFA | 北港元長線(920)87RY通訊故障 | OTHER | P04/69/920/87CFA |  |  |  | CDC | 492 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 920 | 元長線(920) |  | RYFA | [17 empty] | 2-35-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.920_RYFA | 北港元長線(920)數位電驛故障 | OTHER | P04/69/920/RYFA |  |  |  | CDC | 493 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | 87A | [17 empty] | 1-0E-07 | [7 empty] | 69KV_N | [8 empty] | 北港PS.910_87A | 北港土庫線(910) 87RY | LINE69 | P04/69/910/87A |  |  |  | CDC | 494 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | 87UL | [17 empty] | 2-35-06 |  | 2-34 | [5 empty] | ADCS_N | [8 empty] | 北港PS.910_87UL | 北港土庫線(910) 87RY U/L | LINE69 | P04/69/910/87UL |  |  |  | CDC | 495 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 910 | 北港土庫線(910) |  | 87CFA | [17 empty] | 2-35-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.910_87CFA | 北港土庫線(910)87RY通訊故障 | OTHER | P04/69/910/87CFA |  |  |  | CDC | 496 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 910 | 北港土庫線(910) |  | RYFA | [17 empty] | 2-35-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.910_RYFA | 北港土庫線(910)數位電驛故障 | OTHER | P04/69/910/RYFA |  |  |  | CDC | 497 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | 87A | [17 empty] | 1-0F-00 | [7 empty] | 69KV_N | [8 empty] | 北港PS.710_87A | 雲港一路(710) 87RY | LINE69 | P04/69/710/87A |  |  |  | CDC | 498 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | 87UL | [17 empty] | 2-36-00 |  | 2-35 | [5 empty] | ADCS_N | [8 empty] | 北港PS.710_87UL | 雲港一路(710) 87RY U/L | LINE69 | P04/69/710/87UL |  |  |  | CDC | 499 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | 87A | [17 empty] | 1-0F-01 | [7 empty] | 69KV_N | [8 empty] | 北港PS.720_87A | 雲港二路(720) 87RY | LINE69 | P04/69/720/87A |  |  |  | CDC | 500 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | 87UL | [17 empty] | 2-36-03 |  | 2-36 | [5 empty] | ADCS_N | [8 empty] | 北港PS.720_87UL | 雲港二路(720) 87RY U/L | LINE69 | P04/69/720/87UL |  |  |  | CDC | 501 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 710 | 雲港一路(710) |  | 87CFA | [17 empty] | 2-35-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.710_87CFA | 北港雲港ㄧ路(710)87RY通訊故障 | OTHER | P04/69/710/87CFA |  |  |  | CDC | 502 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 710 | 雲港一路(710) |  | RYFA | [17 empty] | 2-35-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.710_RYFA | 北港雲港ㄧ路(710)數位電驛故障 | OTHER | P04/69/710/RYFA |  |  |  | CDC | 503 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 720 | 雲港二路(720) |  | 87CFA | [17 empty] | 2-36-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.720_87CFA | 北港雲港二路(720)87RY通訊故障 | OTHER | P04/69/720/87CFA |  |  |  | CDC | 504 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 720 | 雲港二路(720) |  | RYFA | [17 empty] | 2-36-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.720_RYFA | 北港雲港二路(720)數位電驛故障 | OTHER | P04/69/720/RYFA |  |  |  | CDC | 505 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | 87A1 | [17 empty] | 2-00-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_87A1 | 北港四湖一路(1510)第一套87RY | OTHER | P04/161/1510/87A1 |  |  |  | CDC | 506 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | 87A2 | [17 empty] | 2-00-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_87A2 | 北港四湖一路(1510)第二套87RY | OTHER | P04/161/1510/87A2 |  |  |  | CDC | 507 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | 87CFA | [17 empty] | 2-38-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_87CFA | 北港四湖一路(1510)87RY通訊故障 | OTHER | P04/161/1510/87CFA |  |  |  | CDC | 508 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | 1_87UL1 | [17 empty] | 2-38-04 |  | 2-68 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1510_87UL1 | 北港四湖一路(1510)#1 87RY U/L | OTHER |  |  |  |  | CDC | 509 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | 1_87UL2 | [17 empty] | 2-38-05 |  | 2-69 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1510_87UL2 | 北港四湖一路(1510)#2 87RY U/L | OTHER |  |  |  |  | CDC | 510 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | RYFA | [17 empty] | 2-38-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_RYFA | 北港四湖一路(1510)數位電驛故障 | OTHER | P04/161/1510/RYFA |  |  |  | CDC | 511 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | 87A1 | [17 empty] | 2-00-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1520_87A1 | 北港四湖二路(1520) #1 87RY | OTHER | P04/161/1520/87A1 |  |  |  | CDC | 512 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | 87A2 | [17 empty] | 2-00-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1520_87A2 | 北港四湖二路(1520) #2 87RY | OTHER | P04/161/1520/87A2 |  |  |  | CDC | 513 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | 87CFA | [17 empty] | 2-38-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1520_87CFA | 北港四湖二路(1520)87RY通訊故障 | OTHER | P04/161/1520/87CFA |  |  |  | CDC | 514 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | 1_87UL1 | [17 empty] | 2-38-11 |  | 2-6B | [5 empty] | ADCS_N | [8 empty] | 北港PS.1520_87UL1 | 北港四湖二路(1520)#1 87RY U/L | OTHER | P04/161/1520/1_87UL1 |  |  |  | CDC | 515 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | 1_87UL2 | [17 empty] | 2-38-12 |  | 2-6C | [5 empty] | ADCS_N | [8 empty] | 北港PS.1520_87UL2 | 北港四湖二路(1520)#2 87RY U/L | OTHER | P04/161/1520/1_87UL2 |  |  |  | CDC | 516 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | RYFA | [17 empty] | 2-38-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1520_RYFA | 北港四湖二路(1520)數位電驛故障 | OTHER | P04/161/1520/RYFA |  |  |  | CDC | 517 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | 87A | [17 empty] | 1-0F-04 | [7 empty] | 69KV_N | [8 empty] | 北港PS.640_87A | 北港朴子線(640) 87RY | LINE69 | P04/69/640/87A |  |  |  | CDC | 518 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | 87UL | [17 empty] | 2-36-06 |  | 2-39 | [5 empty] | ADCS_N | [8 empty] | 北港PS.640_87UL | 北港朴子線(640) 87RY U/L | LINE69 | P04/69/640/87UL |  |  |  | CDC | 519 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 640 | 北港朴子線(640) |  | 87CFA | [17 empty] | 2-36-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.640_87CFA | 北港朴子線(640)87RY通訊故障 | OTHER | P04/69/640/87CFA |  |  |  | CDC | 520 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 640 | 北港朴子線(640) |  | RYFA | [17 empty] | 2-36-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.640_RYFA | 北港朴子線(640)數位電驛故障 | OTHER | P04/69/640/RYFA |  |  |  | CDC | 521 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | 87A | [17 empty] | 1-15-02 | [7 empty] | 69KV_N | [8 empty] | 北港PS.610_87A | 北港口湖線(610) 87RY | LINE69 | P04/69/610/87A |  |  |  | CDC | 522 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | 87UL | [17 empty] | 2-35-10 |  | 2-32 | [5 empty] | ADCS_N | [8 empty] | 北港PS.610_87UL | 北港口湖線(610) 87RY U/L | LINE69 | P04/69/610/87UL |  |  |  | CDC | 523 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 610 | 北港口湖線(610) |  | 87CFA | [17 empty] | 2-35-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.610_87CFA | 北港口湖線(610)87RY通訊故障 | OTHER | P04/69/610/87CFA |  |  |  | CDC | 524 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 610 | 北港口湖線(610) |  | RYFA | [17 empty] | 2-35-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.610_RYFA | 北港口湖線(610)數位電驛故障 | OTHER | P04/69/610/RYFA |  |  |  | CDC | 525 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 51Z_UL | [17 empty] | 2-36-14 |  | 2-3C | [5 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_51ZUL | #3MTR 51ZRY U/L | OTHER | P04//3MTR/51Z_UL |  |  |  | CDC | 526 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | MTR_86A | [17 empty] | 1-0F-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_86A | #3MTR 86RY | OTHER | P04//3MTR/MTR_86A |  |  |  | CDC | 527 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 1_87UL1 | [17 empty] | 1-3A-03 |  | 2-3A | [5 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_87UL1 | #3MTR #1 87RY U/L | OTHER | P04//3MTR/1_87UL1 |  |  |  | CDC | 528 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | 1_87UL2 | [17 empty] | 2-36-12 |  | 2-3B | [5 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_87UL2 | #3MTR #2 87RY U/L | OTHER | P04//3MTR/87UL |  |  |  | CDC | 529 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | GDA | [17 empty] | 1-07-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_GDA | #3MTR GDA | OTHER | P04//3MTR/GDA |  |  |  | CDC | 530 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | PHA | [17 empty] | 1-07-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_PHA | #3MTR PHA | OTHER | P04//3MTR/PHA |  |  |  | CDC | 531 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MTR | #3MTR |  | RYFA | [17 empty] | 2-36-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#3MTR_RYFA | #3MTR數位電驛故障 | OTHER | P04//3MTR/RYFA |  |  |  | CDC | 532 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | ACBA | [17 empty] | 2-37-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.所內電源ACBA | 所內電源故障警報 | OTHER | P04/0/StaDev/ACBA |  |  |  | CDC | 533 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 51Z_UL | [17 empty] | 2-37-01 |  | 2-3F | [5 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_51ZUL | #4MTR 51ZRY U/L | OTHER | P04//4MTR/51Z_UL |  |  |  | CDC | 534 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | MTR_86A | [17 empty] | 1-0F-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_86A | #4MTR 86RY | OTHER | P04//4MTR/MTR_86A |  |  |  | CDC | 535 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 1_87UL1 | [17 empty] | 1-3C-02 |  | 2-3D | [5 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_87UL1 | #4MTR #1 87RY U/L | OTHER | P04//4MTR/1_87UL1 |  |  |  | CDC | 536 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | 1_87UL2 | [17 empty] | 2-36-15 |  | 2-3E | [5 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_87UL2 | #4MTR #2 87RY U/L | OTHER | P04//4MTR/87UL |  |  |  | CDC | 537 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | GDA | [17 empty] | 1-08-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_GDA | #4MTR GDA | OTHER | P04//4MTR/GDA |  |  |  | CDC | 538 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | PHA | [17 empty] | 1-08-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_PHA | #4MTR PHA | OTHER | P04//4MTR/PHA |  |  |  | CDC | 539 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MTR | #4MTR |  | RYFA | [17 empty] | 2-37-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#4MTR_RYFA | #4MTR數位電驛故障 | OTHER | P04//4MTR/RYFA |  |  |  | CDC | 540 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 51Z_UL | [17 empty] | 2-36-11 |  | 2-1E | [5 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_51ZUL | #2MTR 51ZRY U/L | OTHER | P04//2MTR/51Z_UL |  |  |  | CDC | 541 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | MTR_86A | [17 empty] | 1-0F-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_86A | #2MTR 86RY | OTHER | P04//2MTR/MTR_86A |  |  |  | CDC | 542 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 1_87UL1 | [17 empty] | 1-39-04 |  | 1-7A | [5 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_87UL1 | #2MTR #1 87RY U/L | OTHER | P04//2MTR/1_87UL1 |  |  |  | CDC | 543 | GENERICDIPoint | PS016_L1 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | 1_87UL2 | [17 empty] | 2-36-09 |  | 1-7B | [5 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_87UL2 | #2MTR #2 87RY U/L | OTHER | P04//2MTR/87UL |  |  |  | CDC | 544 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | GDA | [17 empty] | 1-06-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_GDA | #2MTR GDA | OTHER | P04//2MTR/GDA |  |  |  | CDC | 545 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | PHA | [17 empty] | 1-06-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_PHA | #2MTR PHA | OTHER | P04//2MTR/PHA |  |  |  | CDC | 546 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MTR | #2MTR |  | RYFA | [17 empty] | 2-36-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.#2MTR_RYFA | #2MTR數位電驛故障 | OTHER | P04//2MTR/RYFA |  |  |  | CDC | 547 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | 87A | [17 empty] | 1-15-03 | [7 empty] | 69KV_N | [8 empty] | 北港PS.620_87A | 北港水林二路(620) 87RY | LINE69 | P04/69/620/87A |  |  |  | CDC | 548 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | 87UL | [17 empty] | 2-37-05 |  | 1-0D | [5 empty] | ADCS_N | [8 empty] | 北港PS.620_87UL | 北港水林二路(620) 87RY U/L | LINE69 | P04/69/620/87UL |  |  |  | CDC | 549 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | 87A | [17 empty] | 1-15-04 | [7 empty] | 69KV_N | [8 empty] | 北港PS.630_87A | 北港水林一路(630) 87RY | LINE69 | P04/69/630/87A |  |  |  | CDC | 550 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | 87UL | [17 empty] | 2-37-08 |  | 1-0E | [5 empty] | ADCS_N | [8 empty] | 北港PS.630_87UL | 北港水林一路(630) 87RY U/L | LINE69 | P04/69/630/87UL |  |  |  | CDC | 551 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 620 | 北港水林二路(620) |  | 87CFA | [17 empty] | 2-37-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.620_87CFA | 北港水林二路(620)87RY通訊故障 | OTHER | P04/69/620/87CFA |  |  |  | CDC | 552 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 620 | 北港水林二路(620) |  | RYFA | [17 empty] | 2-37-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.620_RYFA | 北港水林二路(620)數位電驛故障 | OTHER | P04/69/620/RYFA |  |  |  | CDC | 553 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 630 | 北港水林一路(630) |  | 87CFA | [17 empty] | 2-37-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.630_87CFA | 北港水林一路(630)87RY通訊故障 | OTHER | P04/69/630/87CFA |  |  |  | CDC | 554 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 630 | 北港水林一路(630) |  | RYFA | [17 empty] | 2-37-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.630_RYFA | 北港水林一路(630)數位電驛故障 | OTHER | P04/69/630/RYFA |  |  |  | CDC | 555 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | GDA1 | [17 empty] | 1-09-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.600_GDA1 | 69KV 600 TIE #1 GDA | OTHER | P04/69/600/GDA1 |  |  |  | CDC | 556 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | GDA2 | [17 empty] | 1-10-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.600_GDA2 | 69KV 600 TIE #2 GDA | OTHER | P04/69/600/GDA2 |  |  |  | CDC | 557 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | PHA1 | [17 empty] | 1-09-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.600_PHA1 | 69KV 600 TIE #1 PHA | OTHER | P04/69/600/PHA1 |  |  |  | CDC | 558 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | PHA2 | [17 empty] | 1-10-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.600_PHA2 | 69KV 600 TIE #2 PHA | OTHER | P04/69/600/PHA2 |  |  |  | CDC | 559 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 600 | TIE(600) |  | RYFA | [17 empty] | 2-37-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.600_RYFA | 600 TIE 數位電驛故障 | OTHER | P04/69/600/RYFA |  |  |  | CDC | 560 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 2MOLTC | #2MTR |  | TAP連動 | [17 empty] | 1-18-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.2MOLTC_TAP連動 | #2MTR OLTC TAP連動,請確認處理 | OTHER | P04//2MTR/OLTC_A |  |  |  | CDC | 561 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 3MOLTC | #3MTR |  | TAP連動 | [17 empty] | 1-18-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.3MOLTC_TAP連動 | #3MTR OLTC TAP連動,請確認處理 | OTHER | P04//3MTR/OLTC_A |  |  |  | CDC | 562 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 4MOLTC | #4MTR |  | TAP連動 | [17 empty] | 1-18-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.4MOLTC_TAP連動 | #4MTR OLTC TAP連動,請確認處理 | OTHER | P04//4MTR/OLTC_A |  |  |  | CDC | 563 | GENERICDIPoint | PS016_L1 | CDC2_CD2B |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-37-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_BUS_CTFA | 69KV BUS CT回路故障 | OTHER | P04/69/ComPoint/12B_CTFA |  |  |  | CDC | 564 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 69 | 69kV | _BUS | BUS |  | RYFA | [17 empty] | 2-37-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.69KV_BUS_RYFA | 69KV BUS 數位電驛故障 | OTHER | P04/69/ComPoint/BUS_RYFA |  |  |  | CDC | 565 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | _BUS | BUS |  | 87CTFA | [17 empty] | 2-37-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_BUS_CTFA | 161KV BUS CT回路故障 | OTHER | P04/161/ComPoint/12B_CTFA |  |  |  | CDC | 566 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | _BUS | BUS |  | RYFA | [17 empty] | 2-37-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161KV_BUS_RYFA | 161KV BUS 數位電驛故障 | OTHER | P04/161/ComPoint/BUS_RYFA |  |  |  | CDC | 567 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 2SHR | #2SHR |  | 161#2SHR96PA | [17 empty] | 2-02-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR96PA | 161KV #2SHR 機械保護動作 | OTHER | P04/161/1960/96PA |  |  |  | CDC | 568 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 51A | [17 empty] | 2-02-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_51A | 161KV #2SHR 51RY | OTHER | P04/161/1960/51A |  |  |  | CDC | 569 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 86A | [17 empty] | 2-02-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_86A | 161KV #2SHR 86RY | OTHER | P04/161/1960/MTR_86A |  |  |  | CDC | 570 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 87A | [17 empty] | 2-02-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_87A | 161KV #2SHR 87RY | OTHER | P04/161/1960/87A |  |  |  | CDC | 571 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 1_87UL1 | [17 empty] | 2-39-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_87UL1 | 161KV #2SHR #187RY U/L | OTHER | P04/161/1960/1_87UL1 |  |  |  | CDC | 572 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 1_87UL2 | [17 empty] | 2-39-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_87UL2 | 161KV #2SHR #287RY U/L | OTHER | P04/161/1960/1_87UL2 |  |  |  | CDC | 573 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 96B1 | [17 empty] | 2-39-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_96B1 | 161KV #2SHR 96B1 RY | OTHER | P04/161/1960/96B1 |  |  |  | CDC | 574 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 96B2 | [17 empty] | 2-39-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_96B2 | 161KV #2SHR 96B2 RY | OTHER | P04/161/1960/96B2 |  |  |  | CDC | 575 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 96D | [17 empty] | 2-39-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_96D | 161KV #2SHR 96D RY | OTHER | P04/161/1960/96D |  |  |  | CDC | 576 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | 96P | [17 empty] | 2-39-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_96P | 161KV #2SHR 96P RY | OTHER | P04/161/1960/96P |  |  |  | CDC | 577 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | SHRA | [17 empty] | 2-39-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_SRA | 161KV #2SHR 重故障 | OTHER | P04/161/1960/SHRA |  |  |  | CDC | 578 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1612SHR | #2SHR |  | SRF | [17 empty] | 2-39-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#2SHR_SRF | 161KV #2SHR 輕故障 | OTHER | P04/161/1960/SHRF |  |  |  | CDC | 579 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 161_2SHR | 161_2SHR |  | RYFA | [17 empty] | 2-39-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161_2SHR_RYFA | 161KV 2SHR(1960)數位電驛故障 | OTHER | P04/161/1960/RYFA |  |  |  | CDC | 580 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | CB | [17 empty] | 2-01-07 |  | 2-4B | [5 empty] | ADCS_N | [8 empty] | 北港PS.1960_CB | 1960(161KV #2SHR) CB | OTHER | P04/161/1960/CB |  |  |  | CDC | 581 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | ABS1 | 1961 | [16 empty] | 2-3F-04 | 2-3F-05 | 2-62 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1961_ABS | 1961(161KV #2SHR) ABS | OTHER | P04/161/1960/ABS1 |  |  |  | CDC | 582 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | OPEN
P04 | 北港PS | 161 | 161kV | 1960 | #2SHR(1960) |  | ABS2 | 1962 | [16 empty] | 2-3F-06 | 2-3F-07 | 2-63 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1962_ABS | 1962(161KV #2SHR) ABS | OTHER | P04/161/1960/ABS2 |  |  |  | CDC | 583 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | DTTA | [17 empty] | 2-38-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_DTTA | 北港四湖一路(1510) 遠方遙跳 | OTHER | P04/161/1510/DTTA |  |  |  | CDC | 584 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | DTTA | [17 empty] | 2-38-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1520_DTTA | 北港四湖二路(1520) 遠方遙跳 | OTHER | P04/161/1520/DTTA |  |  |  | CDC | 585 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 3SHR | #3SHR |  | 161#3SHR96PA | [17 empty] | 2-03-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR96PA | 161KV #3SHR 機械保護動作 | OTHER | P04/161/1970/96PA |  |  |  | CDC | 586 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 51A | [17 empty] | 2-02-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_51A | 161KV #3SHR 51RY | OTHER | P04/161/1970/51A |  |  |  | CDC | 587 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 86A | [17 empty] | 2-02-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_86A | 161KV #3SHR 86RY | OTHER | P04/161/1970/MTR_86A |  |  |  | CDC | 588 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 87A | [17 empty] | 2-02-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_87A | 161KV #3SHR 87RY | OTHER | P04/161/1970/87A |  |  |  | CDC | 589 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 1_87UL1 | [17 empty] | 2-3A-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_87UL1 | 161KV #3SHR #187RY U/L | OTHER | P04/161/1970/1_87UL1 |  |  |  | CDC | 590 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 1_87UL2 | [17 empty] | 2-3A-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_87UL2 | 161KV #3SHR #287RY U/L | OTHER | P04/161/1970/1_87UL2 |  |  |  | CDC | 591 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 96B1 | [17 empty] | 2-3A-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_96B1 | 161KV #3SHR 96B1 RY | OTHER | P04/161/1970/96B1 |  |  |  | CDC | 592 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 96B2 | [17 empty] | 2-3A-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_96B2 | 161KV #3SHR 96B2 RY | OTHER | P04/161/1970/96B2 |  |  |  | CDC | 593 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 96D | [17 empty] | 2-3A-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_96D | 161KV #3SHR 96D RY | OTHER | P04/161/1970/96D |  |  |  | CDC | 594 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | 96P | [17 empty] | 2-3A-06 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_96P | 161KV #3SHR 96P RY | OTHER | P04/161/1970/96P |  |  |  | CDC | 595 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | SHRA | [17 empty] | 2-3A-08 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_SRA | 161KV #3SHR 重故障 | OTHER | P04/161/1970/SHRA |  |  |  | CDC | 596 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1613SHR | #3SHR |  | SRF | [17 empty] | 2-3A-07 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#3SHR_SRF | 161KV #3SHR 輕故障 | OTHER | P04/161/1970/SHRF |  |  |  | CDC | 597 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 161_3SHR | 161_3SHR |  | RYFA | [17 empty] | 2-3A-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161_3SHR_RYFA | 161KV 3SHR(1970)數位電驛故障 | OTHER | P04/161/1970/RYFA |  |  |  | CDC | 598 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | CB | [17 empty] | 2-02-04 |  | 2-4C | [5 empty] | ADCS_N | [8 empty] | 北港PS.1970_CB | 1970(161KV #3SHR) CB | OTHER | P04/161/1970/CB |  |  |  | CDC | 599 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1970 | #3SHR(1970) |  | ABS1 | 1971 | [16 empty] | 2-3F-08 | 2-3F-09 | 2-64 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1971_ABS | 1971(161KV #3SHR) DS | OTHER | P04/161/1970/ABS1 |  |  |  | CDC | 600 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 0 |  |  |  |  | PMA | [17 empty] | 2-3B-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.PMA | 電力量測表計故障 | OTHER | P04/0/StaDev/PMA |  |  |  | CDC | 601 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 4SHR | #4SHR |  | 161#4SHR96PA | [17 empty] | 2-03-05 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR96PA | 161KV #4SHR 機械保護動作 | OTHER | P04/161/1980/96PA |  |  |  | CDC | 602 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 51A | [17 empty] | 2-03-04 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_51A | 161KV #4SHR 51RY | OTHER | P04/161/1980/51A |  |  |  | CDC | 603 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 86A | [17 empty] | 2-03-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_86A | 161KV #4SHR 86RY | OTHER | P04/161/1980/MTR_86A |  |  |  | CDC | 604 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 87A | [17 empty] | 2-03-02 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_87A | 161KV #4SHR 87RY | OTHER | P04/161/1980/87A |  |  |  | CDC | 605 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | TRIP/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 1_87UL1 | [17 empty] | 2-3A-09 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_87UL1 | 161KV #4SHR #187RY U/L | OTHER | P04/161/1980/1_87UL1 |  |  |  | CDC | 606 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 1_87UL2 | [17 empty] | 2-3A-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_87UL2 | 161KV #4SHR #287RY U/L | OTHER | P04/161/1980/1_87UL2 |  |  |  | CDC | 607 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | USE/LOCK | USE
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 96B1 | [17 empty] | 2-3A-12 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_96B1 | 161KV #4SHR 96B1 RY | OTHER | P04/161/1980/96B1 |  |  |  | CDC | 608 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 96B2 | [17 empty] | 2-3A-13 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_96B2 | 161KV #4SHR 96B2 RY | OTHER | P04/161/1980/96B2 |  |  |  | CDC | 609 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 96D | [17 empty] | 2-3A-14 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_96D | 161KV #4SHR 96D RY | OTHER | P04/161/1980/96D |  |  |  | CDC | 610 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | 96P | [17 empty] | 2-3A-15 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_96P | 161KV #4SHR 96P RY | OTHER | P04/161/1980/96P |  |  |  | CDC | 611 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | SHRA | [17 empty] | 2-3B-01 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_SRA | 161KV #4SHR 重故障 | OTHER | P04/161/1980/SHRA |  |  |  | CDC | 612 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1614SHR | #4SHR |  | SRF | [17 empty] | 2-3B-00 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161#4SHR_SRF | 161KV #4SHR 輕故障 | OTHER | P04/161/1980/SHRF |  |  |  | CDC | 613 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 161_4SHR | 161_4SHR |  | RYFA | [17 empty] | 2-3A-11 | [7 empty] | ADCS_N | [8 empty] | 北港PS.161_4SHR_RYFA | 161KV 4SHR(1980)數位電驛故障 | OTHER | P04/161/1980/RYFA |  |  |  | CDC | 614 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | FAULT/NORMAL | NORMAL
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | CB | [17 empty] | 2-03-01 |  | 2-4D | [5 empty] | ADCS_N | [8 empty] | 北港PS.1980_CB | 1980(161KV #4SHR) CB | OTHER | P04/161/1980/CB |  |  |  | CDC | 615 | GENERICDIPoint | PS016_L2 | CDC2_CD2B |  | DI | [34 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1980 | #4SHR(1980) |  | ABS1 | 1981 | [16 empty] | 2-3F-10 | 2-3F-11 | 2-65 | [5 empty] | ADCS_N | [8 empty] | 北港PS.1981_ABS | 1981(161KV #4SHR) ABS | OTHER | P04/161/1980/ABS1 |  |  |  | CDC | 616 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | INVALID/OPEN/CLOSE/IN_TRANSIT | CLOSE
P04 | 北港PS | 0 |  | 1520 | 北港四湖二路(1520) |  | LPDA | [17 empty] | 2-38-10 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1520_LPDA | 北港四湖二路(1520) LPD電壓偵測 | OTHER | P04/161/1520/LPDA |  |  |  | CDC | 617 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  | 1510 | 北港四湖一路(1510) |  | LPDA | [17 empty] | 2-38-03 | [7 empty] | ADCS_N | [8 empty] | 北港PS.1510_LPDA | 北港四湖一路(1510) LPD電壓偵測 | OTHER | P04/161/1510/LPDA |  |  |  | CDC | 618 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ALARM/NORMAL | NORMAL
P04 | 北港PS | 0 |  |  |  |  | Lights | [17 empty] | 2-3B-03 |  | 2-6E | [5 empty] | ADCS_N | [8 empty] | 北港PS.開關場照明(E) | 雲林北港雲高線ABS夜間照明 | OTHER | P04/0/StaDev/Lights |  |  |  | CDC | 619 | GENERICDIPoint | PS016_L2 | CDC2_DI |  | DI | [34 empty] | ON/OFF | OFF
P04 | 北港PS | 69 | 69kV | 820_SC | #2SC | 43.200001 | CAP | [25 empty] | ADCS_N | [8 empty] | 北港PS.820_SC_CAP | 69KV#2SC 容量 | SC | [5 empty] | 620 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 69 | 69kV | 830_SC | #3SC | 28.799999 | CAP | [25 empty] | ADCS_N | [8 empty] | 北港PS.830_SC_CAP | 69KV#3SC 容量 | SC | [5 empty] | 621 | NotelAIPoint | [21 empty] | LG_MVAR | 20000.000000 | 20000.000000 | 20000.000000 | 20000.000000 | 1.000000 | -20000.000000 | -20000.000000 | -20000.000000 | -20000.000000
P04 | 北港PS | 0 |  | TRD | 北港PS |  | 129 | [25 empty] | TRAIN_AD | [8 empty] | 北港PS.TRD_129 | 北港PS NT 69KV_Hi_Limit | [6 empty] | 622 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P04 | 北港PS | 0 |  | TRD | 北港PS |  | 130 | [25 empty] | TRAIN_AD | [8 empty] | 北港PS.TRD_130 | 北港PS NT 69KV_Lo_Limit | [6 empty] | 623 | NotelAIPoint | [21 empty] | LG_69 | 70.300003 | 70.300003 | 72.500000 | 90.000000 | 0.200000 | 65.000000 | 65.000000 | 63.000000 | 0.000000
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | LE0 | 1510LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1510LE | 1510LE (非取樣點) | LINE161 | [5 empty] | 624 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1510 | 北港四湖一路(1510) |  | BE0 | 1510BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1510BE | 1510BE (非取樣點) | LINE161 | [5 empty] | 625 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | LE0 | 1520LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1520LE | 1520LE (非取樣點) | LINE161 | P04/161/1520/LE0 |  |  |  |  | 626 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1520 | 北港四湖二路(1520) |  | BE0 | 1520BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1520BE | 1520BE (非取樣點) | LINE161 | P04/161/1520/BE0 |  |  |  |  | 627 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1550 | 1550 |  | LE0 | 1550LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1550LE | 1550LE (非取樣點) | LINE161 | P04/161/1510/LE0 |  |  |  |  | 628 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1550 | 1550 |  | BE0 | 1550BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1550BE | 1550BE (非取樣點) | LINE161 | P04/161/1510/BE0 |  |  |  |  | 629 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | LE0 | 1560LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1560LE | 1560LE (非取樣點) | LINE161 | P04/161/1560/LE0 |  |  |  |  | 630 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1560 | 台西二路(1560) |  | BE0 | 1560BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1560BE | 1560BE (非取樣點) | LINE161 | P04/161/1560/BE0 |  |  |  |  | 631 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | LE0 | 1570LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1570LE | 1570LE (非取樣點) | LINE161 | P04/161/1570/LE0 |  |  |  |  | 632 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1570 | 雲林北港雲高線(1570) |  | BE0 | 1570BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1570BE | 1570BE (非取樣點) | LINE161 | P04/161/1570/BE0 |  |  |  |  | 633 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | LE0 | 1580LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1580LE | 1580LE (非取樣點) | LINE161 | P04/161/1580/LE0 |  |  |  |  | 634 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1580 | 北港台西線(1580) |  | BE0 | 1580BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1580BE | 1580BE (非取樣點) | LINE161 | P04/161/1580/BE0 |  |  |  |  | 635 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | LE0 | 1630LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1630LE | 1630LE (非取樣點) | LINE161 | P04/161/1630/LE0 |  |  |  |  | 636 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1630 | 嘉民南線(1630) |  | BE0 | 1630BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1630BE | 1630BE (非取樣點) | LINE161 | P04/161/1630/BE0 |  |  |  |  | 637 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | LE0 | 1640LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1640LE | 1640LE (非取樣點) | LINE161 | P04/161/1640/LE0 |  |  |  |  | 638 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1640 | 嘉民北線(1640) |  | BE0 | 1640BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1640BE | 1640BE (非取樣點) | LINE161 | P04/161/1640/BE0 |  |  |  |  | 639 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | LE0 | 610LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.610LE | 610LE (非取樣點) | LINE69 | P04/69/610/LE0 |  |  |  |  | 640 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 610 | 北港口湖線(610) |  | BE0 | 610BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.610BE | 610BE (非取樣點) | LINE69 | P04/69/610/BE0 |  |  |  |  | 641 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | LE0 | 630LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.630LE | 630LE (非取樣點) | LINE69 | P04/69/630/LE0 |  |  |  |  | 642 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 630 | 北港水林一路(630) |  | BE0 | 630BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.630BE | 630BE (非取樣點) | LINE69 | P04/69/630/BE0 |  |  |  |  | 643 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | LE0 | 640LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.640LE | 640LE (非取樣點) | LINE69 | P04/69/640/LE0 |  |  |  |  | 644 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 640 | 北港朴子線(640) |  | BE0 | 640BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.640BE | 640BE (非取樣點) | LINE69 | P04/69/640/BE0 |  |  |  |  | 645 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | LE0 | 670LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.670LE | 670LE (非取樣點) | LINE69 | P04/69/670/LE0 |  |  |  |  | 646 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 670 | 北港新港一路(670) |  | BE0 | 670BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.670BE | 670BE (非取樣點) | LINE69 | P04/69/670/BE0 |  |  |  |  | 647 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | LE0 | 680LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.680LE | 680LE (非取樣點) | LINE69 | P04/69/680/LE0 |  |  |  |  | 648 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 680 | 北港新港二路(680) |  | BE0 | 680BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.680BE | 680BE (非取樣點) | LINE69 | P04/69/680/BE0 |  |  |  |  | 649 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | LE0 | 710LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.710LE | 710LE (非取樣點) | LINE69 | P04/69/710/LE0 |  |  |  |  | 650 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 710 | 雲港一路(710) |  | BE0 | 710BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.710BE | 710BE (非取樣點) | LINE69 | P04/69/710/BE0 |  |  |  |  | 651 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | LE0 | 720LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.720LE | 720LE (非取樣點) | LINE69 | P04/69/720/LE0 |  |  |  |  | 652 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 720 | 雲港二路(720) |  | BE0 | 720BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.720BE | 720BE (非取樣點) | LINE69 | P04/69/720/BE0 |  |  |  |  | 653 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | LE0 | 910LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.910LE | 910LE (非取樣點) | LINE69 | P04/69/910/LE0 |  |  |  |  | 654 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 910 | 北港土庫線(910) |  | BE0 | 910BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.910BE | 910BE (非取樣點) | LINE69 | P04/69/910/BE0 |  |  |  |  | 655 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | LE0 | 920LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.920LE | 920LE (非取樣點) | LINE69 | P04/69/920/LE0 |  |  |  |  | 656 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | BE0 | 920BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.920BE | 920BE (非取樣點) | LINE69 | P04/69/920/BE0 |  |  |  |  | 657 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | LE0 | 940LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.940LE | 940LE (非取樣點) | LINE69 | P04/69/940/LE0 |  |  |  |  | 658 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 940 | 北港東北線(940) |  | BE0 | 940BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.940BE | 940BE (非取樣點) | LINE69 | P04/69/940/BE0 |  |  |  |  | 659 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | E1 | 1501E | [24 empty] | ADCS_N | [8 empty] | 北港PS.1501E | 1501E (非取樣點) | TIE | P04/161/1500/E1 |  |  |  |  | 660 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1500 | TIE(1500) |  | E2 | 1502E | [24 empty] | ADCS_N | [8 empty] | 北港PS.1502E | 1502E (非取樣點) | TIE | P04/161/1500/E2 |  |  |  |  | 661 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | E1 | 601E | [24 empty] | ADCS_N | [8 empty] | 北港PS.601E | 601E (非取樣點) | TIE | P04/69/600/E1 |  |  |  |  | 662 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 600 | TIE(600) |  | E2 | 602E | [24 empty] | ADCS_N | [8 empty] | 北港PS.602E | 602E (非取樣點) | TIE | P04/69/600/E2 |  |  |  |  | 663 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | TE0 | 1660TE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1660TE | 1660TE (非取樣點) | MTR | P04/161/1660/TE0 |  |  |  |  | 664 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | TE0 | 760TE | [24 empty] | ADCS_N | [8 empty] | 北港PS.760TE | 760TE (非取樣點) | MTR | P04/69/760/TE0 |  |  |  |  | 665 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | NE0 | 1661N | [24 empty] | ADCS_N | [8 empty] | 北港PS.1661N | 1661N (非取樣點) | MTR | P04/161/1660/NE0 |  |  |  |  | 666 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1660 | #2MTR(1660) |  | BE0 | 1660BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1660BE | 1660BE (非取樣點) | MTR | P04/161/1660/BE0 |  |  |  |  | 667 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 760 | #2MTR(760) |  | BE0 | 760BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.760BE | 760BE (非取樣點) | MTR | P04/69/760/BE0 |  |  |  |  | 668 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | TE0 | 1670TE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1670TE | 1670TE (非取樣點) | MTR | P04/161/1670/TE0 |  |  |  |  | 669 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | TE0 | 770TE | [24 empty] | ADCS_N | [8 empty] | 北港PS.770TE | 770TE (非取樣點) | MTR | P04/69/770/TE0 |  |  |  |  | 670 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | NE0 | 1671N | [24 empty] | ADCS_N | [8 empty] | 北港PS.1671N | 1671N (非取樣點) | MTR | P04/161/1670/NE0 |  |  |  |  | 671 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 161 | 161kV | 1670 | #3MTR(1670) |  | BE0 | 1670BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1670BE | 1670BE (非取樣點) | MTR | P04/161/1670/BE0 |  |  |  |  | 672 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 770 | #3MTR(770) |  | BE0 | 770BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.770BE | 770BE (非取樣點) | MTR | P04/69/770/BE0 |  |  |  |  | 673 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | TE0 | 1680TE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1680TE | 1680TE (非取樣點) | MTR | P04/161/1680/TE0 |  |  |  |  | 674 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | TE0 | 780TE | [24 empty] | ADCS_N | [8 empty] | 北港PS.780TE | 780TE (非取樣點) | MTR | P04/69/780/TE0 |  |  |  |  | 675 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | NE0 | 1681N | [24 empty] | ADCS_N | [8 empty] | 北港PS.1681N | 1681N (非取樣點) | MTR | P04/161/1680/NE0 |  |  |  |  | 676 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 161 | 161kV | 1680 | #4MTR(1680) |  | BE0 | 1680BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1680BE | 1680BE (非取樣點) | MTR | P04/161/1680/BE0 |  |  |  |  | 677 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 780 | #4MTR(780) |  | BE0 | 780BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.780BE | 780BE (非取樣點) | MTR | P04/69/780/BE0 |  |  |  |  | 678 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 820BE | 820BE |  | 820BE | 820BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.820BE | 820BE (非取樣點) | SC | P04/69/820/BE0 |  |  |  |  | 679 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 820CE | 820CE |  | 820CE | 820CE | [24 empty] | ADCS_N | [8 empty] | 北港PS.820CE | 820CE (非取樣點) | SC | P04/69/820/CE0 |  |  |  |  | 680 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 830BE | 830BE |  | 830BE | 830BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.830BE | 830BE (非取樣點) | SC | P04/69/830/BE0 |  |  |  |  | 681 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 830CE | 830CE |  | 830CE | 830CE | [24 empty] | ADCS_N | [8 empty] | 北港PS.830CE | 830CE (非取樣點) | SC | P04/69/830/CE0 |  |  |  |  | 682 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 160 | 160 |  | BE1 | 161B1E | [24 empty] | ADCS_N | [8 empty] | 北港PS.161B1E | 161B1E (非取樣點) | BUS | P04/161/161B1E/BE1 |  |  |  |  | 683 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 160 | 160 |  | BE2 | 161B2E | [24 empty] | ADCS_N | [8 empty] | 北港PS.161B2E | 161B2E (非取樣點) | BUS | P04/161/161B2E/BE2 |  |  |  |  | 684 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 69B1E | 69B1E |  | BE1 | 69B1E | [24 empty] | ADCS_N | [8 empty] | 北港PS.69B1E | 69B1E (非取樣點) | BUS | P04/69/69B1E/BE1 |  |  |  |  | 685 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | 69B2E | 69B2E |  | BE2 | 69B2E | [24 empty] | ADCS_N | [8 empty] | 北港PS.69B2E | 69B2E (非取樣點) | BUS | P04/69/69B2E/BE2 |  |  |  |  | 686 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  | UF | UF |  | RESTORE | UF_RESTORE | [24 empty] | ADCS_N | [8 empty] | 北港PS.UF_RESTORE | 低頻電驛復電(非取樣點) | OTHER | [5 empty] | 687 | NotelDIPoint | [38 empty] | START/STOP | STOP
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | PW1UL | 920_PW1UL | [24 empty] | ADCS_N | [8 empty] | 北港PS.920_PW1UL | 元長線(920)PW1_UL(非取樣點) | LINE69 | [5 empty] | 688 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | PW2UL | 920_PW2UL | [24 empty] | ADCS_N | [8 empty] | 北港PS.920_PW2UL | 元長線(920)PW2_UL(非取樣點) | LINE69 | [5 empty] | 689 | NotelDIPoint | [38 empty] | USE/LOCK | LOCK
P04 | 北港PS | 69 | 69kV | 920 | 元長線(920) |  | HCBUL | 920_HCBUL | [24 empty] | ADCS_N | [8 empty] | 北港PS.920_HCBUL | 元長線(920)HCB_UL(非取樣點) | LINE69 | [5 empty] | 690 | NotelDIPoint | [38 empty] | USE/LOCK | USE
P04 | 北港PS | 0 |  | 1SSTR | #1SSTR |  | LBS | #1SSTR_LBS | [24 empty] | ADCS_N | [8 empty] | 北港PS.#1SSTR_LBS | #1SSTR LBS(非取樣點) | OTHER | [5 empty] | 691 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 1SSTR | #1SSTR |  | PF | #1SSTR_PF | [24 empty] | ADCS_N | [8 empty] | 北港PS.#1SSTR_PF | #1SSTR PF(非取樣點) | OTHER | [5 empty] | 692 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 2SSTR | #2SSTR |  | LBS | #2SSTR_LBS | [24 empty] | ADCS_N | [8 empty] | 北港PS.#2SSTR_LBS | #2SSTR LBS(非取樣點) | OTHER | [5 empty] | 693 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 0 |  | 2SSTR | #2SSTR |  | PF | #2SSTR_PF | [24 empty] | ADCS_N | [8 empty] | 北港PS.#2SSTR_PF | #2SSTR PF(非取樣點) | OTHER | [5 empty] | 694 | NotelDIPoint | [38 empty] | CLOSE/OPEN | CLOSE
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | LE0 | 620LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.620LE | 620LE (非取樣點) | LINE69 | P04/69/620/LE0 |  |  |  |  | 695 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 69 | 69kV | 620 | 北港水林二路(620) |  | BE0 | 620BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.620BE | 620BE (非取樣點) | LINE69 | P04/69/620/BE0 |  |  |  |  | 696 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1950BE | 1950BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1950BE | 1950BE(非取樣點) | OTHER | P04/161/1950/BE0 |  |  |  |  | 697 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1950RE | 1950RE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1950RE | 1950RE(非取樣點) | OTHER | P04/161/1950/RE0 |  |  |  |  | 698 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1960BE | 1960BE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1960BE | 1960BE(非取樣點) | OTHER | P04/161/1960/BE0 |  |  |  |  | 699 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1960RE | 1960RE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1960RE | 1960RE(非取樣點) | OTHER | P04/161/1960/RE0 |  |  |  |  | 700 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1970LE | 1970LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1970LE | 1970LE(非取樣點) | OTHER | P04/161/1970/LE0 |  |  |  |  | 701 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1970RE | 1970RE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1970RE | 1970RE(非取樣點) | OTHER | P04/161/1970/RE0 |  |  |  |  | 702 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1980LE | 1980LE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1980LE | 1980LE(非取樣點) | OTHER | P04/161/1980/LE0 |  |  |  |  | 703 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN
P04 | 北港PS | 0 |  |  |  |  | 1980RE | 1980RE | [24 empty] | ADCS_N | [8 empty] | 北港PS.1980RE | 1980RE(非取樣點) | OTHER | P04/161/1980/RE0 |  |  |  |  | 704 | NotelDIPoint | [38 empty] | CLOSE/OPEN | OPEN

## 剔除比對
B1 Name | B1 Text | B2 Name | B2 Text | B3 Name | B3 Text | Element Desc | Element Name | Element Text | Manual Adjustment | Info Name | Info Text | ValueName | GenSUM | AL1/3/5/7 | AI/DI Type | Info Order | Topo_Type | Topo_ExtN1 | Topo_ExtN2 | Topo_ExtN3 | Topo_ExtN4 | DNP Mon1 | DNP Mon2 | DNP Cmd | CDC Mon1 | CDC Mon2 | CDC Cmd | DEV locate | Unit_Status | Descript | CharacteristicCurve | Postion | AoR | Spu | Qpu | CT | MVA | V-FS | A-FS | P-FS | Q-FS | PointName | PointDesc | GraphicDesc | Point Ref | Point Memo | Point Area | Point Class | OldRow | Tag | Tag Mon1 | Tag Mon2 | Tag Cmd | Tag Info | Compare Memo